## SummaryResults
Climate Zone | Boiler Gas Usage [therms/unit/yr] |  |  |  |  | Pumping Electric Usage [kWh/unit/yr] |  |  |  |  | Total Cost Savings [$/unit/ yr]
| Baseline | Proposed | Savings | Savings [%] | Savings therms/kBtuh input cap. | Baseline | Proposed | Savings | Savings [%] | Savings kWh/kBtuh input cap.
1 | 169.7985 | 115.7765 | 54.022 | 31.82% | 47.5167 | 65.2415 | 21.7217 | 43.5199 | 66.71% | 38.2793 | 67.078
2 | 151.55 | 99.2463 | 52.3036 | 34.51% | 46.0053 | 64.8682 | 19.5925 | 45.2757 | 69.8% | 39.8237 | 65.8863
3 | 153.6522 | 100.4494 | 53.2028 | 34.63% | 46.7962 | 64.931 | 19.8524 | 45.0786 | 69.43% | 39.6503 | 66.7264
4 | 144.5866 | 92.5548 | 52.0318 | 35.99% | 45.7662 | 64.5189 | 18.9261 | 45.5929 | 70.67% | 40.1026 | 65.7096
5 | 155.6916 | 102.5725 | 53.1191 | 34.12% | 46.7225 | 64.9255 | 20.0876 | 44.8379 | 69.06% | 39.4385 | 66.5704
6 | 138.7361 | 86.623 | 52.1131 | 37.56% | 45.8377 | 64.4093 | 18.1915 | 46.2177 | 71.76% | 40.6523 | 65.9784
7 | 135.9082 | 84.4225 | 51.4856 | 37.88% | 45.2858 | 64.1687 | 17.8721 | 46.2965 | 72.15% | 40.7216 | 65.3746
8 | 131.2508 | 80.2317 | 51.0191 | 38.87% | 44.8755 | 63.974 | 17.4357 | 46.5383 | 72.75% | 40.9342 | 64.9806
9 | 131.9786 | 81.0481 | 50.9305 | 38.59% | 44.7975 | 64.0633 | 17.5649 | 46.4985 | 72.58% | 40.8992 | 64.88
10 | 130.9018 | 80.4852 | 50.4165 | 38.51% | 44.3454 | 63.9687 | 17.4605 | 46.5082 | 72.7% | 40.9077 | 64.369
11 | 135.2181 | 84.929 | 50.2891 | 37.19% | 44.2333 | 64.0242 | 18.0915 | 45.9326 | 71.74% | 40.4015 | 64.0688
12 | 141.2632 | 90.0451 | 51.2181 | 36.26% | 45.0505 | 64.4431 | 18.6279 | 45.8152 | 71.09% | 40.2982 | 64.9627
13 | 131.1486 | 81.3853 | 49.7633 | 37.94% | 43.7709 | 63.7444 | 17.6386 | 46.1058 | 72.33% | 40.5538 | 63.5951
14 | 137.2431 | 86.7813 | 50.4617 | 36.77% | 44.3852 | 64.1843 | 18.2679 | 45.9164 | 71.54% | 40.3872 | 64.2366
15 | 98.5408 | 54.3238 | 44.217 | 44.87% | 38.8925 | 61.535 | 14.9118 | 46.6232 | 75.77% | 41.0089 | 58.204
16 | 168.5775 | 116.0473 | 52.5302 | 31.16% | 46.2046 | 65.0181 | 21.7017 | 43.3164 | 66.62% | 38.1003 | 65.5251
141.0028

## Results
CZ# & Pre/Post |  | Annual Value [kBtu] | therms | therms/unit | % total demand |  | Electricity Annual Value [kWh] | kWh/unit |  | Gas Annual Value [therms] | Gas Annual Value [kBtu] | therms/unit |  | Annual Value [ft3] | gal/yr/bldg | gal/yr/unit | gal/day/unit | Heating Equipment COP | Gas Annual Value [therms] Before Post-Processing | Gas Annual Value [kBtu] Before Post-Processing | therms/unit Before Post-Processing | Legend
1 | MYWATERUSEEQUIPLOAD | 891756.48 | 11146.9561 | 132.7019 | 76.95% | Pumps:Electricity | 5480.29 | 65.2415 | NaturalGas:Facility | 14263.0716 | 1426307.16 | 169.7985 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8 |  |  |  |  | OpenStudio output, baseline
Pre | MYBOILERLOAD | 1141045.73 | 14263.0717 | 169.7985 | [8 empty] | MYHOTWATER | 203939.13 | 1525570.7407 | 18161.5564 | 49.7577 | [5 empty] | OpenStudio output, retrofit
| MYTANKHEATLOSSENERGY | -5158.3 | 64.4788 | 0.7676 | 0.4451% | [7 empty] | MYCOLDWATER | 62696.05 | 468999.0559 | 5583.3221 | 15.2968 | [5 empty] | Post-processed retrofit output
| MYPIPEFLUIDHEATTRANSFERENERGY | 260753.27 | 3259.4159 | 38.8026 | 22.5% | [17 empty] | Important calculations
| MYPUMPFLDHTGAINENERGY | 17776.4 | 222.205 | 2.6453
| total heat in | 1158822.13 | 14485.2767 | 172.4438
| total heat out | 1157668.05 | 14341.8932 | 170.7368 | 99.9%
| uncategorized | 1154.08 | 143.3835 | 1.7069 | 0.09959%
1 | MYWATERUSEEQUIPLOAD | 891695.43 | 7656.5048 | 91.1489 | 83.55% | Pumps:Electricity | 1824.62 | 21.7217 | NaturalGas:Facility | 9725.2237 | 972522.3707 | 115.7765 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.0913 | 11282.8781 | 1128287.81 | 134.32
Post | MYBOILERLOAD | 1061315.04 | 9112.9363 | 108.4873 | [8 empty] | MYHOTWATER | 211802.33 | 1584391.5656 | 18861.8044 | 51.6762
| MYTANKHEATLOSSENERGY | -5338.1 | 45.8354 | 0.54566 | 0.5002% | [7 empty] | MYCOLDWATER | 54832.85 | 410178.2311 | 4883.0742 | 13.3783 |  | % savings | 20.89%
| MYPIPEFLUIDHEATTRANSFERENERGY | 166336.76 | 1428.2435 | 17.0029 | 15.59%
| MYPUMPFLDHTGAINENERGY | 5918.5 | 50.8189 | 0.60499
| total heat in | 1067233.54 | 9163.7553 | 109.0923
| total heat out | 1063370.29 | 9038.9129 | 107.6061 | 99.64%
| uncategorized | 3863.25 | 124.8424 | 1.4862 | 0.362%
1 | MYWATERUSEEQUIPLOAD | 61.05 |  |  | -0.006846% | Pumps:Electricity | 3655.67 | 43.5199 | NaturalGas:Facility | 4537.8479 |  | 54.022 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 79730.69 |  |  | -6.988% | [7 empty] | MYHOTWATER | -7863.2 | -58820.8249 | -700.2479 | -1.9185
| MYTANKHEATLOSSENERGY | 179.8 |  |  | 3.486% | % savings | 66.71% |  | % savings | 31.82% |  |  | MYCOLDWATER | 7863.2 | 58820.8249 | 700.2479 | 1.9185
| MYPIPEFLUIDHEATTRANSFERENERGY | 94416.51 |  |  | -36.21%
| MYPUMPFLDHTGAINENERGY | 11857.9 |  |  | -66.71% | [7 empty] | % savings | -3.856%
2 | MYWATERUSEEQUIPLOAD | 793569.86 | 9919.6233 | 118.0908 | 76.59% | Pumps:Electricity | 5448.93 | 64.8682 | NaturalGas:Facility | 12730.1958 | 1273019.58 | 151.55 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 1018415.67 | 12730.196 | 151.55 | [8 empty] | MYHOTWATER | 195226.26 | 1460393.9425 | 17385.6422 | 47.6319
| MYTANKHEATLOSSENERGY | -4752.2 | 59.4025 | 0.70717 | 0.4587% | [7 empty] | MYCOLDWATER | 71408.92 | 534175.8542 | 6359.2364 | 17.4226
| MYPIPEFLUIDHEATTRANSFERENERGY | 236495.7 | 2956.1963 | 35.1928 | 22.83%
| MYPUMPFLDHTGAINENERGY | 17674.67 | 220.9334 | 2.6302
| total heat in | 1036090.34 | 12951.1293 | 154.1801
| total heat out | 1034817.76 | 12816.4171 | 152.5764 | 99.88%
| uncategorized | 1272.58 | 134.7123 | 1.6037 | 0.1228%
2 | MYWATERUSEEQUIPLOAD | 793513.84 | 6813.4727 | 81.1128 | 84.22% | Pumps:Electricity | 1645.77 | 19.5925 | NaturalGas:Facility | 8336.6909 | 833669.0935 | 99.2463 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1237 | 9871.1408 | 987114.08 | 117.5136
Post | MYBOILERLOAD | 936798.37 | 8043.7793 | 95.7593 | [8 empty] | MYHOTWATER | 203325.25 | 1520978.5991 | 18106.8881 | 49.6079
| MYTANKHEATLOSSENERGY | -4900.3 | 42.0762 | 0.50091 | 0.5201% | [7 empty] | MYCOLDWATER | 63309.93 | 473591.1976 | 5637.9904 | 15.4465 |  | % savings | 22.46%
| MYPIPEFLUIDHEATTRANSFERENERGY | 148422.95 | 1274.4273 | 15.1718 | 15.75%
| MYPUMPFLDHTGAINENERGY | 5338.37 | 45.8377 | 0.54569
| total heat in | 942136.74 | 8089.6169 | 96.305
| total heat out | 946837.09 | 8045.8239 | 95.7836 | 100.5%
| uncategorized | -4700.35 | 43.7931 | 0.52135 | 0.4989%
2 | MYWATERUSEEQUIPLOAD | 56.02 |  |  | -0.007059% | Pumps:Electricity | 3803.16 | 45.2757 | NaturalGas:Facility | 4393.5049 |  | 52.3036 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 81617.3 |  |  | -8.014% | [7 empty] | MYHOTWATER | -8098.99 | -60584.6567 | -721.2459 | -1.976
| MYTANKHEATLOSSENERGY | 148.1 |  |  | 3.116% | % savings | 69.8% |  | % savings | 34.51% |  |  | MYCOLDWATER | 8098.99 | 60584.6567 | 721.2459 | 1.976
| MYPIPEFLUIDHEATTRANSFERENERGY | 88072.75 |  |  | -37.24%
| MYPUMPFLDHTGAINENERGY | 12336.3 |  |  | -69.8% | [7 empty] | % savings | -4.149%
3 | MYWATERUSEEQUIPLOAD | 797464.91 | 9968.3114 | 118.6704 | 75.93% | Pumps:Electricity | 5454.2 | 64.931 | NaturalGas:Facility | 12906.785 | 1290678.5 | 153.6522 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 1032542.8 | 12906.7851 | 153.6522 | [8 empty] | MYHOTWATER | 195882.18 | 1465300.5651 | 17444.0543 | 47.7919
| MYTANKHEATLOSSENERGY | -4738.5 | 59.2313 | 0.70513 | 0.4512% | [7 empty] | MYCOLDWATER | 70753 | 529269.2316 | 6300.8242 | 17.2625
| MYPIPEFLUIDHEATTRANSFERENERGY | 246909.59 | 3086.3699 | 36.7425 | 23.51%
| MYPUMPFLDHTGAINENERGY | 17691.77 | 221.1471 | 2.6327
| total heat in | 1050234.57 | 13127.9322 | 156.2849
| total heat out | 1049113 | 12995.4501 | 154.7077 | 99.89%
| uncategorized | 1121.57 | 132.4821 | 1.5772 | 0.1068%
3 | MYWATERUSEEQUIPLOAD | 797408.23 | 6846.9118 | 81.5109 | 83.26% | Pumps:Electricity | 1667.6 | 19.8524 | NaturalGas:Facility | 8437.7459 | 843774.5911 | 100.4494 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1286 | 10041.5971 | 1004159.71 | 119.5428
Post | MYBOILERLOAD | 952313.84 | 8177.0022 | 97.3453 | [8 empty] | MYHOTWATER | 204227.14 | 1527725.2053 | 18187.2048 | 49.828
| MYTANKHEATLOSSENERGY | -4891.3 | 41.9989 | 0.49999 | 0.5107% | [7 empty] | MYCOLDWATER | 62408.04 | 466844.5914 | 5557.6737 | 15.2265 |  | % savings | 22.2%
| MYPIPEFLUIDHEATTRANSFERENERGY | 158295.61 | 1359.1985 | 16.1809 | 16.53%
| MYPUMPFLDHTGAINENERGY | 5409.18 | 46.4457 | 0.55292
| total heat in | 957723.02 | 8223.4479 | 97.8982
| total heat out | 960595.14 | 8164.1113 | 97.1918 | 100.3%
| uncategorized | -2872.12 | 59.3365 | 0.70639 | 0.2999%
3 | MYWATERUSEEQUIPLOAD | 56.68 |  |  | -0.007108% | Pumps:Electricity | 3786.6 | 45.0786 | NaturalGas:Facility | 4469.0391 |  | 53.2028 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 80228.96 |  |  | -7.77% | [7 empty] | MYHOTWATER | -8344.96 | -62424.6402 | -743.1505 | -2.036
| MYTANKHEATLOSSENERGY | 152.8 |  |  | 3.225% | % savings | 69.43% |  | % savings | 34.63% |  |  | MYCOLDWATER | 8344.96 | 62424.6402 | 743.1505 | 2.036
| MYPIPEFLUIDHEATTRANSFERENERGY | 88613.98 |  |  | -35.89%
| MYPUMPFLDHTGAINENERGY | 12282.59 |  |  | -69.43% | [7 empty] | % savings | -4.26%
4 | MYWATERUSEEQUIPLOAD | 756688.6 | 9458.6076 | 112.6025 | 76.49% | Pumps:Electricity | 5419.59 | 64.5189 | NaturalGas:Facility | 12145.2717 | 1214527.17 | 144.5866 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 971621.74 | 12145.2718 | 144.5866 | [8 empty] | MYHOTWATER | 191600.72 | 1433273.018 | 17062.774 | 46.7473
| MYTANKHEATLOSSENERGY | -4488.8 | 56.11 | 0.66798 | 0.4538% | [7 empty] | MYCOLDWATER | 75034.46 | 561296.7787 | 6682.1045 | 18.3071
| MYPIPEFLUIDHEATTRANSFERENERGY | 227622.16 | 2845.277 | 33.8723 | 23.01%
| MYPUMPFLDHTGAINENERGY | 17579.51 | 219.7439 | 2.616
| total heat in | 989201.25 | 12365.0157 | 147.2026
| total heat out | 988799.56 | 12247.7746 | 145.8068 | 99.96%
| uncategorized | 401.69 | 117.2411 | 1.3957 | 0.04061%
4 | MYWATERUSEEQUIPLOAD | 756635.47 | 6496.8182 | 77.3431 | 84.74% | Pumps:Electricity | 1589.79 | 18.9261 | NaturalGas:Facility | 7774.6022 | 777460.222 | 92.5548 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1418 | 9328.1991 | 932819.91 | 111.05
Post | MYBOILERLOAD | 887734.34 | 7622.493 | 90.744 | [8 empty] | MYHOTWATER | 199667.73 | 1493618.4476 | 17781.172 | 48.7155
| MYTANKHEATLOSSENERGY | -4627.2 | 39.7313 | 0.47299 | 0.5182% | [7 empty] | MYCOLDWATER | 66967.45 | 500951.3491 | 5963.7065 | 16.3389 |  | % savings | 23.19%
| MYPIPEFLUIDHEATTRANSFERENERGY | 142078.7 | 1219.9527 | 14.5232 | 15.91%
| MYPUMPFLDHTGAINENERGY | 5156.8 | 44.2786 | 0.52713
| total heat in | 892891.14 | 7666.7717 | 91.2711
| total heat out | 903341.37 | 7677.0396 | 91.3933 | 101.2%
| uncategorized | -10450.23 | -10.2679 | -0.12224 | 1.17%
4 | MYWATERUSEEQUIPLOAD | 53.13 |  |  | -0.007021% | Pumps:Electricity | 3829.8 | 45.5929 | NaturalGas:Facility | 4370.6695 |  | 52.0318 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 83887.4 |  |  | -8.634% | [7 empty] | MYHOTWATER | -8067.01 | -60345.4296 | -718.398 | -1.9682
| MYTANKHEATLOSSENERGY | 138.4 |  |  | 3.083% | % savings | 70.67% |  | % savings | 35.99% |  |  | MYCOLDWATER | 8067.01 | 60345.4296 | 718.398 | 1.9682
| MYPIPEFLUIDHEATTRANSFERENERGY | 85543.46 |  |  | -37.58%
| MYPUMPFLDHTGAINENERGY | 12422.71 |  |  | -70.67% | [7 empty] | % savings | -4.21%
5 | MYWATERUSEEQUIPLOAD | 817711.71 | 10221.3964 | 121.6833 | 76.86% | Pumps:Electricity | 5453.74 | 64.9255 | NaturalGas:Facility | 13078.0937 | 1307809.37 | 155.6916 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 1046247.5 | 13078.0938 | 155.6916 | [8 empty] | MYHOTWATER | 197505.79 | 1477446.0122 | 17588.643 | 48.1881
| MYTANKHEATLOSSENERGY | -4734.6 | 59.1825 | 0.70455 | 0.445% | [7 empty] | MYCOLDWATER | 69129.39 | 517123.7845 | 6156.2355 | 16.8664
| MYPIPEFLUIDHEATTRANSFERENERGY | 240503.84 | 3006.298 | 35.7893 | 22.61%
| MYPUMPFLDHTGAINENERGY | 17690.27 | 221.1284 | 2.6325
| total heat in | 1063937.77 | 13299.2222 | 158.3241
| total heat out | 1062950.15 | 13168.512 | 156.768 | 99.91%
| uncategorized | 987.62 | 130.7103 | 1.5561 | 0.09283%
5 | MYWATERUSEEQUIPLOAD | 817654 | 7020.7512 | 83.5804 | 83.88% | Pumps:Electricity | 1687.36 | 20.0876 | NaturalGas:Facility | 8616.0908 | 861609.0801 | 102.5725 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1251 | 10232.733 | 1023273.3 | 121.8183
Post | MYBOILERLOAD | 969366.42 | 8323.4234 | 99.0884 | [8 empty] | MYHOTWATER | 205152.66 | 1534648.5762 | 18269.6259 | 50.0538
| MYTANKHEATLOSSENERGY | -4893.2 | 42.0153 | 0.50018 | 0.5019% | [7 empty] | MYCOLDWATER | 61482.52 | 459921.2205 | 5475.2526 | 15.0007 |  | % savings | 21.76%
| MYPIPEFLUIDHEATTRANSFERENERGY | 150903.82 | 1295.7292 | 15.4253 | 15.48%
| MYPUMPFLDHTGAINENERGY | 5473.27 | 46.996 | 0.55948
| total heat in | 974839.69 | 8370.4194 | 99.6479
| total heat out | 973451.02 | 8274.4652 | 98.5055 | 99.86%
| uncategorized | 1388.67 | 95.9543 | 1.1423 | 0.1425%
5 | MYWATERUSEEQUIPLOAD | 57.71 |  |  | -0.007057% | Pumps:Electricity | 3766.38 | 44.8379 | NaturalGas:Facility | 4462.0029 |  | 53.1191 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 76881.08 |  |  | -7.348% | [7 empty] | MYHOTWATER | -7646.87 | -57202.564 | -680.9829 | -1.8657
| MYTANKHEATLOSSENERGY | 158.6 |  |  | 3.35% | % savings | 69.06% |  | % savings | 34.12% |  |  | MYCOLDWATER | 7646.87 | 57202.564 | 680.9829 | 1.8657
| MYPIPEFLUIDHEATTRANSFERENERGY | 89600.02 |  |  | -37.26%
| MYPUMPFLDHTGAINENERGY | 12217 |  |  | -69.06% | [7 empty] | % savings | -3.872%
6 | MYWATERUSEEQUIPLOAD | 719312.95 | 8991.4118 | 107.0406 | 75.73% | Pumps:Electricity | 5410.38 | 64.4093 | NaturalGas:Facility | 11653.8337 | 1165383.37 | 138.7361 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 932306.7 | 11653.8337 | 138.7361 | [8 empty] | MYHOTWATER | 188060.47 | 1406790.107 | 16747.5013 | 45.8836
| MYTANKHEATLOSSENERGY | -4341.2 | 54.265 | 0.64601 | 0.457% | [7 empty] | MYCOLDWATER | 78574.71 | 587779.6896 | 6997.3773 | 19.1709
| MYPIPEFLUIDHEATTRANSFERENERGY | 225205.08 | 2815.0635 | 33.5127 | 23.71%
| MYPUMPFLDHTGAINENERGY | 17549.63 | 219.3704 | 2.6116
| total heat in | 949856.33 | 11873.2041 | 141.3477
| total heat out | 948859.23 | 11752.2103 | 139.9073 | 99.9%
| uncategorized | 997.1 | 120.9937 | 1.4404 | 0.105%
6 | MYWATERUSEEQUIPLOAD | 719263.58 | 6201.0765 | 73.8223 | 84.72% | Pumps:Electricity | 1528.09 | 18.1915 | NaturalGas:Facility | 7276.335 | 727633.502 | 86.623 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1599 | 8839.2552 | 883925.52 | 105.2292
Post | MYBOILERLOAD | 843982.94 | 7276.335 | 86.623 | [8 empty] | MYHOTWATER | 196623.33 | 1470844.7525 | 17510.0566 | 47.9728
| MYTANKHEATLOSSENERGY | -4465.9 | 38.5024 | 0.45836 | 0.5261% | [7 empty] | MYCOLDWATER | 70011.85 | 523725.0442 | 6234.822 | 17.0817 |  | % savings | 24.15%
| MYPIPEFLUIDHEATTRANSFERENERGY | 141986.54 | 1224.1262 | 14.5729 | 16.73%
| MYPUMPFLDHTGAINENERGY | 4956.66 | 42.7335 | 0.50873
| total heat in | 848939.6 | 7319.0685 | 87.1318
| total heat out | 865716.02 | 7386.7003 | 87.9369 | 102%
| uncategorized | -16776.42 | -67.6318 | -0.80514 | 1.976%
6 | MYWATERUSEEQUIPLOAD | 49.37 |  |  | -0.006863% | Pumps:Electricity | 3882.29 | 46.2177 | NaturalGas:Facility | 4377.4987 |  | 52.1131 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 88323.76 |  |  | -9.474% | [7 empty] | MYHOTWATER | -8562.86 | -64054.6455 | -762.5553 | -2.0892
| MYTANKHEATLOSSENERGY | 124.7 |  |  | 2.872% | % savings | 71.76% |  | % savings | 37.56% |  |  | MYCOLDWATER | 8562.86 | 64054.6455 | 762.5553 | 2.0892
| MYPIPEFLUIDHEATTRANSFERENERGY | 83218.54 |  |  | -36.95%
| MYPUMPFLDHTGAINENERGY | 12592.97 |  |  | -71.76% | [7 empty] | % savings | -4.553%
7 | MYWATERUSEEQUIPLOAD | 706056.35 | 8825.7044 | 105.0679 | 75.86% | Pumps:Electricity | 5390.17 | 64.1687 | NaturalGas:Facility | 11416.2871 | 1141628.71 | 135.9082 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 913302.96 | 11416.2871 | 135.9082 | [8 empty] | MYHOTWATER | 186746.86 | 1396963.6212 | 16630.5193 | 45.5631
| MYTANKHEATLOSSENERGY | -4332.1 | 54.1513 | 0.64466 | 0.4654% | [7 empty] | MYCOLDWATER | 79888.32 | 597606.1755 | 7114.3592 | 19.4914
| MYPIPEFLUIDHEATTRANSFERENERGY | 219740 | 2746.75 | 32.6994 | 23.61%
| MYPUMPFLDHTGAINENERGY | 17484.07 | 218.5509 | 2.6018
| total heat in | 930787.03 | 11634.838 | 138.51
| total heat out | 930128.45 | 11518.3032 | 137.1227 | 99.93%
| uncategorized | 658.58 | 116.5348 | 1.3873 | 0.07076%
7 | MYWATERUSEEQUIPLOAD | 706007.84 | 6062.1062 | 72.1679 | 84.9% | Pumps:Electricity | 1501.26 | 17.8721 | NaturalGas:Facility | 7091.4936 | 709149.3615 | 84.4225 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1657 | 8645.2247 | 864522.47 | 102.9193
Post | MYBOILERLOAD | 826676.96 | 7098.2265 | 84.5027 | [8 empty] | MYHOTWATER | 195497.98 | 1462426.5493 | 17409.8399 | 47.6982
| MYTANKHEATLOSSENERGY | -4452.1 | 38.2278 | 0.45509 | 0.5354% | [7 empty] | MYCOLDWATER | 71137.2 | 532143.2473 | 6335.0387 | 17.3563 |  | % savings | 24.27%
| MYPIPEFLUIDHEATTRANSFERENERGY | 137785.76 | 1183.0916 | 14.0844 | 16.57%
| MYPUMPFLDHTGAINENERGY | 4869.62 | 41.8128 | 0.49777
| total heat in | 831546.58 | 7140.0392 | 85.0005
| total heat out | 848245.7 | 7206.97 | 85.7973 | 102%
| uncategorized | -16699.12 | -66.9307 | -0.79679 | 2.008%
7 | MYWATERUSEEQUIPLOAD | 48.51 |  |  | -0.006871% | Pumps:Electricity | 3888.91 | 46.2965 | NaturalGas:Facility | 4324.7935 |  | 51.4856 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 86626 |  |  | -9.485% | [7 empty] | MYHOTWATER | -8751.12 | -65462.9282 | -779.3206 | -2.1351
| MYTANKHEATLOSSENERGY | 120 |  |  | 2.77% | % savings | 72.15% |  | % savings | 37.88% |  |  | MYCOLDWATER | 8751.12 | 65462.9282 | 779.3206 | 2.1351
| MYPIPEFLUIDHEATTRANSFERENERGY | 81954.24 |  |  | -37.3%
| MYPUMPFLDHTGAINENERGY | 12614.45 |  |  | -72.15% | [7 empty] | % savings | -4.686%
8 | MYWATERUSEEQUIPLOAD | 686349.87 | 8579.3734 | 102.1354 | 76.31% | Pumps:Electricity | 5373.82 | 63.974 | NaturalGas:Facility | 11025.0699 | 1102506.99 | 131.2508 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 882005.59 | 11025.0699 | 131.2508 | [8 empty] | MYHOTWATER | 184312.87 | 1378756.1103 | 16413.7632 | 44.9692
| MYTANKHEATLOSSENERGY | -4215.4 | 52.6925 | 0.62729 | 0.4687% | [7 empty] | MYCOLDWATER | 82322.31 | 615813.6864 | 7331.1153 | 20.0852
| MYPIPEFLUIDHEATTRANSFERENERGY | 207764.85 | 2597.0606 | 30.9174 | 23.1%
| MYPUMPFLDHTGAINENERGY | 17431.05 | 217.8881 | 2.5939
| total heat in | 899436.64 | 11242.9581 | 133.8447
| total heat out | 898330.12 | 11123.7416 | 132.4255 | 99.88%
| uncategorized | 1106.52 | 119.2165 | 1.4192 | 0.123%
8 | MYWATERUSEEQUIPLOAD | 686303.5 | 5892.9157 | 70.1538 | 86.54% | Pumps:Electricity | 1464.6 | 17.4357 | NaturalGas:Facility | 6739.4618 | 673946.1808 | 80.2317 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1696 | 8231.1999 | 823119.99 | 97.9905
Post | MYBOILERLOAD | 788254.08 | 6768.31 | 80.5751 | [8 empty] | MYHOTWATER | 192867.5 | 1442749.1911 | 17175.5856 | 47.0564
| MYTANKHEATLOSSENERGY | -4324.8 | 37.1347 | 0.44208 | 0.5454% | [7 empty] | MYCOLDWATER | 73767.68 | 551820.6056 | 6569.2929 | 17.9981 |  | % savings | 25.34%
| MYPIPEFLUIDHEATTRANSFERENERGY | 127412.2 | 1094.0194 | 13.024 | 16.07%
| MYPUMPFLDHTGAINENERGY | 4750.72 | 40.7919 | 0.48562
| total heat in | 793004.8 | 6809.1019 | 81.0607
| total heat out | 818040.5 | 6949.8004 | 82.7357 | 103.2%
| uncategorized | -25035.7 | -140.6985 | -1.675 | 3.157%
8 | MYWATERUSEEQUIPLOAD | 46.37 |  |  | -0.006756% | Pumps:Electricity | 3909.22 | 46.5383 | NaturalGas:Facility | 4285.6081 |  | 51.0191 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 93751.51 |  |  | -10.63% | [7 empty] | MYHOTWATER | -8554.63 | -63993.0808 | -761.8224 | -2.0872
| MYTANKHEATLOSSENERGY | 109.4 |  |  | 2.595% | % savings | 72.75% |  | % savings | 38.87% |  |  | MYCOLDWATER | 8554.63 | 63993.0808 | 761.8224 | 2.0872
| MYPIPEFLUIDHEATTRANSFERENERGY | 80352.65 |  |  | -38.67%
| MYPUMPFLDHTGAINENERGY | 12680.33 |  |  | -72.75% | [7 empty] | % savings | -4.641%
9 | MYWATERUSEEQUIPLOAD | 685052.05 | 8563.1507 | 101.9423 | 75.75% | Pumps:Electricity | 5381.32 | 64.0633 | NaturalGas:Facility | 11086.2012 | 1108620.12 | 131.9786 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 886896.09 | 11086.2012 | 131.9786 | [8 empty] | MYHOTWATER | 184194.15 | 1377868.023 | 16403.1907 | 44.9402
| MYTANKHEATLOSSENERGY | -4254.6 | 53.1825 | 0.63313 | 0.4705% | [7 empty] | MYCOLDWATER | 82441.03 | 616701.7737 | 7341.6878 | 20.1142
| MYPIPEFLUIDHEATTRANSFERENERGY | 214207.41 | 2677.5926 | 31.8761 | 23.69%
| MYPUMPFLDHTGAINENERGY | 17455.36 | 218.192 | 2.5975
| total heat in | 904351.45 | 11304.3932 | 134.5761
| total heat out | 903514.06 | 11187.5608 | 133.1852 | 99.91%
| uncategorized | 837.39 | 116.8324 | 1.3909 | 0.0926%
9 | MYWATERUSEEQUIPLOAD | 685006.26 | 5881.777 | 70.0212 | 85.88% | Pumps:Electricity | 1475.45 | 17.5649 | NaturalGas:Facility | 6808.041 | 680804.1037 | 81.0481 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1646 | 8284.9502 | 828495.02 | 98.6304
Post | MYBOILERLOAD | 792881.25 | 6808.041 | 81.0481 | [8 empty] | MYHOTWATER | 193045.92 | 1444083.8655 | 17191.4746 | 47.0999
| MYTANKHEATLOSSENERGY | -4366.1 | 37.4893 | 0.4463 | 0.5474% | [7 empty] | MYCOLDWATER | 73589.26 | 550485.9312 | 6553.4039 | 17.9545 |  | % savings | 25.27%
| MYPIPEFLUIDHEATTRANSFERENERGY | 133789.14 | 1148.7747 | 13.6759 | 16.77%
| MYPUMPFLDHTGAINENERGY | 4785.92 | 41.0941 | 0.48922
| total heat in | 797667.17 | 6849.1351 | 81.5373
| total heat out | 823161.5 | 6993.0624 | 83.2507 | 103.2%
| uncategorized | -25494.33 | -143.9273 | -1.7134 | 3.196%
9 | MYWATERUSEEQUIPLOAD | 45.79 |  |  | -0.006684% | Pumps:Electricity | 3905.87 | 46.4985 | NaturalGas:Facility | 4278.1602 |  | 50.9305 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 94014.84 |  |  | -10.6% | [7 empty] | MYHOTWATER | -8851.77 | -66215.8425 | -788.2838 | -2.1597
| MYTANKHEATLOSSENERGY | 111.5 |  |  | 2.621% | % savings | 72.58% |  | % savings | 38.59% |  |  | MYCOLDWATER | 8851.77 | 66215.8425 | 788.2838 | 2.1597
| MYPIPEFLUIDHEATTRANSFERENERGY | 80418.27 |  |  | -37.54%
| MYPUMPFLDHTGAINENERGY | 12669.44 |  |  | -72.58% | [7 empty] | % savings | -4.806%
10 | MYWATERUSEEQUIPLOAD | 679649.71 | 8495.6214 | 101.1384 | 75.76% | Pumps:Electricity | 5373.37 | 63.9687 | NaturalGas:Facility | 10995.7471 | 1099574.71 | 130.9018 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 879659.77 | 10995.7472 | 130.9018 | [8 empty] | MYHOTWATER | 183432.91 | 1372173.5519 | 16335.3994 | 44.7545
| MYTANKHEATLOSSENERGY | -4238.8 | 52.985 | 0.63077 | 0.4725% | [7 empty] | MYCOLDWATER | 83202.27 | 622396.2448 | 7409.4791 | 20.2999
| MYPIPEFLUIDHEATTRANSFERENERGY | 212523.93 | 2656.5491 | 31.6256 | 23.69%
| MYPUMPFLDHTGAINENERGY | 17429.57 | 217.8696 | 2.5937
| total heat in | 897089.34 | 11213.6168 | 133.4954
| total heat out | 896412.44 | 11099.1856 | 132.1332 | 99.92%
| uncategorized | 676.9 | 114.4313 | 1.3623 | 0.07546%
10 | MYWATERUSEEQUIPLOAD | 679604.49 | 5835.395 | 69.469 | 85.97% | Pumps:Electricity | 1466.68 | 17.4605 | NaturalGas:Facility | 6760.758 | 676075.8006 | 80.4852 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1623 | 8207.9275 | 820792.75 | 97.7134
Post | MYBOILERLOAD | 785776.78 | 6747.0388 | 80.3219 | [8 empty] | MYHOTWATER | 192288.52 | 1438418.1196 | 17124.0252 | 46.9151
| MYTANKHEATLOSSENERGY | -4349.2 | 37.3442 | 0.44457 | 0.5502% | [7 empty] | MYCOLDWATER | 74346.66 | 556151.6771 | 6620.8533 | 18.1393 |  | % savings | 25.35%
| MYPIPEFLUIDHEATTRANSFERENERGY | 132281.54 | 1135.8298 | 13.5218 | 16.73%
| MYPUMPFLDHTGAINENERGY | 4757.45 | 40.8496 | 0.48631
| total heat in | 790534.23 | 6787.8885 | 80.8082
| total heat out | 816235.23 | 6933.8805 | 82.5462 | 103.3%
| uncategorized | -25701 | -145.9921 | -1.738 | 3.251%
10 | MYWATERUSEEQUIPLOAD | 45.22 |  |  | -0.006653% | Pumps:Electricity | 3906.69 | 46.5082 | NaturalGas:Facility | 4234.9891 |  | 50.4165 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 93882.99 |  |  | -10.67% | [7 empty] | MYHOTWATER | -8855.61 | -66244.5677 | -788.6258 | -2.1606
| MYTANKHEATLOSSENERGY | 110.4 |  |  | 2.605% | % savings | 72.7% |  | % savings | 38.51% |  |  | MYCOLDWATER | 8855.61 | 66244.5677 | 788.6258 | 2.1606
| MYPIPEFLUIDHEATTRANSFERENERGY | 80242.39 |  |  | -37.76%
| MYPUMPFLDHTGAINENERGY | 12672.12 |  |  | -72.7% | [7 empty] | % savings | -4.828%
11 | MYWATERUSEEQUIPLOAD | 695827.35 | 8697.8419 | 103.5457 | 75.13% | Pumps:Electricity | 5378.03 | 64.0242 | NaturalGas:Facility | 11358.3201 | 1135832.01 | 135.2181 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 908665.61 | 11358.3202 | 135.2181 | [8 empty] | MYHOTWATER | 184355.99 | 1379078.6703 | 16417.6032 | 44.9797
| MYTANKHEATLOSSENERGY | -4330.4 | 54.13 | 0.6444 | 0.4676% | [7 empty] | MYCOLDWATER | 82279.19 | 615491.1264 | 7327.2753 | 20.0747
| MYPIPEFLUIDHEATTRANSFERENERGY | 224913.01 | 2811.4126 | 33.4692 | 24.29%
| MYPUMPFLDHTGAINENERGY | 17444.68 | 218.0585 | 2.5959
| total heat in | 926110.29 | 11576.3787 | 137.814
| total heat out | 925070.76 | 11455.1246 | 136.3705 | 99.89%
| uncategorized | 1039.53 | 121.2541 | 1.4435 | 0.1122%
11 | MYWATERUSEEQUIPLOAD | 695780.27 | 5974.2876 | 71.1225 | 85.01% | Pumps:Electricity | 1519.69 | 18.0915 | NaturalGas:Facility | 7134.0388 | 713403.8807 | 84.929 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1403 | 8533.9628 | 853396.28 | 101.5948
Post | MYBOILERLOAD | 813494.77 | 6985.0381 | 83.1552 | [8 empty] | MYHOTWATER | 193738.79 | 1449266.8934 | 17253.1773 | 47.269
| MYTANKHEATLOSSENERGY | -4445.5 | 38.1711 | 0.45442 | 0.5432% | [7 empty] | MYCOLDWATER | 72896.39 | 545302.9033 | 6491.7012 | 17.7855 |  | % savings | 24.87%
| MYPIPEFLUIDHEATTRANSFERENERGY | 143731.83 | 1234.1472 | 14.6922 | 17.56%
| MYPUMPFLDHTGAINENERGY | 4929.4 | 42.3261 | 0.50388
| total heat in | 818424.17 | 7027.3642 | 83.6591
| total heat out | 843957.6 | 7170.2637 | 85.3603 | 103.1%
| uncategorized | -25533.43 | -142.8995 | -1.7012 | 3.12%
11 | MYWATERUSEEQUIPLOAD | 47.08 |  |  | -0.006766% | Pumps:Electricity | 3858.34 | 45.9326 | NaturalGas:Facility | 4224.2813 |  | 50.2891 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 95170.84 |  |  | -10.47% | [7 empty] | MYHOTWATER | -9382.8 | -70188.2231 | -835.5741 | -2.2892
| MYTANKHEATLOSSENERGY | 115.1 |  |  | 2.658% | % savings | 71.74% |  | % savings | 37.19% |  |  | MYCOLDWATER | 9382.8 | 70188.2231 | 835.5741 | 2.2892
| MYPIPEFLUIDHEATTRANSFERENERGY | 81181.18 |  |  | -36.09%
| MYPUMPFLDHTGAINENERGY | 12515.28 |  |  | -71.74% | [7 empty] | % savings | -5.09%
12 | MYWATERUSEEQUIPLOAD | 734052.81 | 9175.6602 | 109.234 | 75.92% | Pumps:Electricity | 5413.22 | 64.4431 | NaturalGas:Facility | 11866.1124 | 1186611.24 | 141.2632 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 949288.99 | 11866.1125 | 141.2632 | [8 empty] | MYHOTWATER | 189093.91 | 1414520.7756 | 16839.533 | 46.1357
| MYTANKHEATLOSSENERGY | -4496.7 | 56.2088 | 0.66915 | 0.4651% | [7 empty] | MYCOLDWATER | 77541.27 | 580049.0211 | 6905.3455 | 18.9188
| MYPIPEFLUIDHEATTRANSFERENERGY | 227862.2 | 2848.2775 | 33.9081 | 23.57%
| MYPUMPFLDHTGAINENERGY | 17558.85 | 219.4856 | 2.6129
| total heat in | 966847.84 | 12085.5981 | 143.8762
| total heat out | 966411.71 | 11967.729 | 142.473 | 99.95%
| uncategorized | 436.13 | 117.8691 | 1.4032 | 0.04511%
12 | MYWATERUSEEQUIPLOAD | 734002.05 | 6302.4773 | 75.0295 | 84.67% | Pumps:Electricity | 1564.74 | 18.6279 | NaturalGas:Facility | 7563.7904 | 756379.035 | 90.0451 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1394 | 9047.2414 | 904724.14 | 107.7053
Post | MYBOILERLOAD | 861782.48 | 7399.6585 | 88.0912 | [8 empty] | MYHOTWATER | 197722.09 | 1479064.0487 | 17607.9053 | 48.2408
| MYTANKHEATLOSSENERGY | -4627.1 | 39.7304 | 0.47298 | 0.5338% | [7 empty] | MYCOLDWATER | 68913.09 | 515505.748 | 6136.9732 | 16.8136 |  | % savings | 23.76%
| MYPIPEFLUIDHEATTRANSFERENERGY | 143926.51 | 1235.8188 | 14.7121 | 16.6%
| MYPUMPFLDHTGAINENERGY | 5075.53 | 43.5808 | 0.51882
| total heat in | 866858.01 | 7443.2393 | 88.61
| total heat out | 882555.66 | 7498.5657 | 89.2686 | 101.8%
| uncategorized | -15697.65 | -55.3264 | -0.65865 | 1.811%
12 | MYWATERUSEEQUIPLOAD | 50.76 |  |  | -0.006915% | Pumps:Electricity | 3848.48 | 45.8152 | NaturalGas:Facility | 4302.322 |  | 51.2181 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 87506.51 |  |  | -9.218% | [7 empty] | MYHOTWATER | -8628.18 | -64543.2731 | -768.3723 | -2.1051
| MYTANKHEATLOSSENERGY | 130.4 |  |  | 2.9% | % savings | 71.09% |  | % savings | 36.26% |  |  | MYCOLDWATER | 8628.18 | 64543.2731 | 768.3723 | 2.1051
| MYPIPEFLUIDHEATTRANSFERENERGY | 83935.69 |  |  | -36.84%
| MYPUMPFLDHTGAINENERGY | 12483.32 |  |  | -71.09% | [7 empty] | % savings | -4.563%
13 | MYWATERUSEEQUIPLOAD | 680716.86 | 8508.9608 | 101.2972 | 75.75% | Pumps:Electricity | 5354.53 | 63.7444 | NaturalGas:Facility | 11016.4817 | 1101648.17 | 131.1486 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 881318.53 | 11016.4817 | 131.1486 | [8 empty] | MYHOTWATER | 182548.78 | 1365559.7998 | 16256.6643 | 44.5388
| MYTANKHEATLOSSENERGY | -4209.1 | 52.6138 | 0.62635 | 0.4684% | [7 empty] | MYCOLDWATER | 84086.4 | 629009.9969 | 7488.2142 | 20.5157
| MYPIPEFLUIDHEATTRANSFERENERGY | 212879.54 | 2660.9943 | 31.6785 | 23.69%
| MYPUMPFLDHTGAINENERGY | 17368.46 | 217.1058 | 2.5846
| total heat in | 898686.99 | 11233.5875 | 133.7332
| total heat out | 897805.5 | 11117.3413 | 132.3493 | 99.9%
| uncategorized | 881.49 | 116.2461 | 1.3839 | 0.09809%
13 | MYWATERUSEEQUIPLOAD | 680671.98 | 5844.5609 | 69.5781 | 86.01% | Pumps:Electricity | 1481.64 | 17.6386 | NaturalGas:Facility | 6836.3621 | 683636.2051 | 81.3853 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1506 | 8234.5189 | 823451.89 | 98.03
Post | MYBOILERLOAD | 786565.31 | 6753.8095 | 80.4025 | [8 empty] | MYHOTWATER | 191614.7 | 1433377.5956 | 17064.019 | 46.7507
| MYTANKHEATLOSSENERGY | -4318.3 | 37.0789 | 0.44142 | 0.5457% | [7 empty] | MYCOLDWATER | 75020.48 | 561192.201 | 6680.8595 | 18.3037 |  | % savings | 25.25%
| MYPIPEFLUIDHEATTRANSFERENERGY | 132994.19 | 1141.9489 | 13.5946 | 16.81%
| MYPUMPFLDHTGAINENERGY | 4806.01 | 41.2666 | 0.49127
| total heat in | 791371.32 | 6795.0761 | 80.8938
| total heat out | 817984.47 | 6949.431 | 82.7313 | 103.4%
| uncategorized | -26613.15 | -154.3549 | -1.8376 | 3.363%
13 | MYWATERUSEEQUIPLOAD | 44.88 |  |  | -0.006593% | Pumps:Electricity | 3872.89 | 46.1058 | NaturalGas:Facility | 4180.1196 |  | 49.7633 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 94753.22 |  |  | -10.75% | [7 empty] | MYHOTWATER | -9065.92 | -67817.7959 | -807.3547 | -2.2119
| MYTANKHEATLOSSENERGY | 109.2 |  |  | 2.594% | % savings | 72.33% |  | % savings | 37.94% |  |  | MYCOLDWATER | 9065.92 | 67817.7959 | 807.3547 | 2.2119
| MYPIPEFLUIDHEATTRANSFERENERGY | 79885.35 |  |  | -37.53%
| MYPUMPFLDHTGAINENERGY | 12562.45 |  |  | -72.33% | [7 empty] | % savings | -4.966%
14 | MYWATERUSEEQUIPLOAD | 704574.82 | 8807.1853 | 104.8474 | 74.97% | Pumps:Electricity | 5391.48 | 64.1843 | NaturalGas:Facility | 11528.4162 | 1152841.62 | 137.2431 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 922273.3 | 11528.4163 | 137.2431 | [8 empty] | MYHOTWATER | 185273.08 | 1385938.9804 | 16499.2736 | 45.2035
| MYTANKHEATLOSSENERGY | -4356.4 | 54.455 | 0.64827 | 0.4636% | [7 empty] | MYCOLDWATER | 81362.1 | 608630.8163 | 7245.605 | 19.851
| MYPIPEFLUIDHEATTRANSFERENERGY | 230037.18 | 2875.4648 | 34.2317 | 24.48%
| MYPUMPFLDHTGAINENERGY | 17488.32 | 218.604 | 2.6024
| total heat in | 939761.62 | 11747.0203 | 139.8455
| total heat out | 938968.4 | 11628.1951 | 138.4309 | 99.92%
| uncategorized | 793.22 | 118.8253 | 1.4146 | 0.08441%
14 | MYWATERUSEEQUIPLOAD | 704526.7 | 6049.3885 | 72.0165 | 84.61% | Pumps:Electricity | 1534.5 | 18.2679 | NaturalGas:Facility | 7289.6316 | 728963.1622 | 86.7813 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1354 | 8688.4758 | 868847.58 | 103.4342
Post | MYBOILERLOAD | 827661.9 | 7106.6836 | 84.6034 | [8 empty] | MYHOTWATER | 194650.84 | 1456089.5016 | 17334.3988 | 47.4915
| MYTANKHEATLOSSENERGY | -4475.3 | 38.427 | 0.45746 | 0.5375% | [7 empty] | MYCOLDWATER | 71984.34 | 538480.2951 | 6410.4797 | 17.563 |  | % savings | 24.63%
| MYPIPEFLUIDHEATTRANSFERENERGY | 147615.27 | 1267.4922 | 15.0892 | 17.73%
| MYPUMPFLDHTGAINENERGY | 4977.47 | 42.7388 | 0.5088
| total heat in | 832639.37 | 7149.4224 | 85.1122
| total heat out | 856617.27 | 7278.4537 | 86.6483 | 102.9%
| uncategorized | -23977.9 | -129.0313 | -1.5361 | 2.88%
14 | MYWATERUSEEQUIPLOAD | 48.12 |  |  | -0.00683% | Pumps:Electricity | 3856.98 | 45.9164 | NaturalGas:Facility | 4238.7846 |  | 50.4617 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 94611.4 |  |  | -10.26% | [7 empty] | MYHOTWATER | -9377.76 | -70150.5212 | -835.1253 | -2.288
| MYTANKHEATLOSSENERGY | 118.9 |  |  | 2.729% | % savings | 71.54% |  | % savings | 36.77% |  |  | MYCOLDWATER | 9377.76 | 70150.5212 | 835.1253 | 2.288
| MYPIPEFLUIDHEATTRANSFERENERGY | 82421.91 |  |  | -35.83%
| MYPUMPFLDHTGAINENERGY | 12510.85 |  |  | -71.54% | [7 empty] | % savings | -5.062%
15 | MYWATERUSEEQUIPLOAD | 491758.21 | 6146.9777 | 73.1783 | 72.43% | Pumps:Electricity | 5168.94 | 61.535 | NaturalGas:Facility | 8277.4265 | 827742.65 | 98.5408 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 662194.12 | 8277.4266 | 98.5408 | [8 empty] | MYHOTWATER | 156587.41 | 1171355.2523 | 13944.7054 | 38.2047
| MYTANKHEATLOSSENERGY | -3552.4 | 44.405 | 0.52863 | 0.5232% | [7 empty] | MYCOLDWATER | 110047.77 | 823214.5444 | 9800.1731 | 26.8498
| MYPIPEFLUIDHEATTRANSFERENERGY | 181988.05 | 2274.8506 | 27.0816 | 26.8%
| MYPUMPFLDHTGAINENERGY | 16766.46 | 209.5808 | 2.495
| total heat in | 678960.58 | 8487.0073 | 101.0358
| total heat out | 677298.66 | 8377.4233 | 99.7312 | 99.76%
| uncategorized | 1661.92 | 109.584 | 1.3046 | 0.2448%
15 | MYWATERUSEEQUIPLOAD | 491734.41 | 4222.2565 | 50.265 | 89.65% | Pumps:Electricity | 1252.59 | 14.9118 | NaturalGas:Facility | 4563.1966 | 456319.6555 | 54.3238 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.1931 | 5653.0099 | 565300.99 | 67.2977
Post | MYBOILERLOAD | 544419.96 | 4674.6388 | 55.6505 | [8 empty] | MYHOTWATER | 168804.61 | 1262746.2612 | 15032.6936 | 41.1855
| MYTANKHEATLOSSENERGY | -3595.2 | 30.87 | 0.3675 | 0.6555% | [7 empty] | MYCOLDWATER | 97830.57 | 731823.5355 | 8712.1849 | 23.869 |  | % savings | 31.71%
| MYPIPEFLUIDHEATTRANSFERENERGY | 115015.34 | 987.5743 | 11.7568 | 20.97%
| MYPUMPFLDHTGAINENERGY | 4063.01 | 34.8869 | 0.41532
| total heat in | 548482.97 | 4709.5256 | 56.0658
| total heat out | 610344.95 | 5178.9608 | 61.6543 | 111.3%
| uncategorized | -61861.98 | -469.4352 | -5.5885 | 11.28%
15 | MYWATERUSEEQUIPLOAD | 23.8 |  |  | -0.00484% | Pumps:Electricity | 3916.35 | 46.6232 | NaturalGas:Facility | 3714.2299 |  | 44.217 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 117774.16 |  |  | -17.79% | [7 empty] | MYHOTWATER | -12217.2 | -91391.0089 | -1087.9882 | -2.9808
| MYTANKHEATLOSSENERGY | 42.8 |  |  | 1.205% | % savings | 75.77% |  | % savings | 44.87% |  |  | MYCOLDWATER | 12217.2 | 91391.0089 | 1087.9882 | 2.9808
| MYPIPEFLUIDHEATTRANSFERENERGY | 66972.71 |  |  | -36.8%
| MYPUMPFLDHTGAINENERGY | 12703.45 |  |  | -75.77% | [7 empty] | % savings | -7.802%
16 | MYWATERUSEEQUIPLOAD | 885754.8 | 11071.935 | 131.8087 | 76.98% | Pumps:Electricity | 5461.52 | 65.0181 | NaturalGas:Facility | 14160.5137 | 1416051.37 | 168.5775 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 0.8
Pre | MYBOILERLOAD | 1132841.1 | 14160.5137 | 168.5775 | [8 empty] | MYHOTWATER | 202755.76 | 1516718.5178 | 18056.1728 | 49.469
| MYTANKHEATLOSSENERGY | -5066.7 | 63.3337 | 0.75397 | 0.4404% | [7 empty] | MYCOLDWATER | 63879.42 | 477851.2789 | 5688.7057 | 15.5855
| MYPIPEFLUIDHEATTRANSFERENERGY | 258563.38 | 3232.0422 | 38.4767 | 22.47%
| MYPUMPFLDHTGAINENERGY | 17715.52 | 221.444 | 2.6362
| total heat in | 1150556.62 | 14381.9577 | 171.2138
| total heat out | 1149384.88 | 14240.6434 | 169.5315 | 99.9%
| uncategorized | 1171.74 | 141.3142 | 1.6823 | 0.1018%
16 | MYWATERUSEEQUIPLOAD | 885957.16 | 8231.1038 | 97.9893 | 83.97% | Pumps:Electricity | 1822.94 | 21.7017 | NaturalGas:Facility | 9747.9771 | 974797.7137 | 116.0473 | MYWATERMETER | 266635.18 | 1994569.7967 | 23744.8785 | 65.0545 | 1.0764 | 11169.1042 | 1116910.42 | 132.9655
Post | MYBOILERLOAD | 1049226.24 | 9747.9771 | 116.0473 | [8 empty] | MYHOTWATER | 210576 | 1575217.9795 | 18752.595 | 51.377
| MYTANKHEATLOSSENERGY | -5243.2 | 48.7127 | 0.57991 | 0.4969% | [7 empty] | MYCOLDWATER | 56059.18 | 419351.8172 | 4992.2835 | 13.6775 |  | % savings | 21.13%
| MYPIPEFLUIDHEATTRANSFERENERGY | 165329.45 | 1536.0154 | 18.2859 | 15.67%
| MYPUMPFLDHTGAINENERGY | 5913.07 | 54.9362 | 0.654
| total heat in | 1055139.31 | 9802.9133 | 116.7013
| total heat out | 1056529.81 | 9718.4066 | 115.6953 | 100.1%
| uncategorized | -1390.5 | 84.5067 | 1.006 | 0.1318%
16 | MYWATERUSEEQUIPLOAD | -202.36 |  |  | 0.02285% | Pumps:Electricity | 3638.58 | 43.3164 | NaturalGas:Facility | 4412.5366 |  | 52.5302 | MYWATERMETER | 0 | 0 | 0 | 0
Diff | MYBOILERLOAD | 83614.86 |  |  | -7.381% | [7 empty] | MYHOTWATER | -7820.24 | -58499.4617 | -696.4222 | -1.908
| MYTANKHEATLOSSENERGY | 176.5 |  |  | 3.484% | % savings | 66.62% |  | % savings | 31.16% |  |  | MYCOLDWATER | 7820.24 | 58499.4617 | 696.4222 | 1.908
| MYPIPEFLUIDHEATTRANSFERENERGY | 93233.93 |  |  | -36.06%
| MYPUMPFLDHTGAINENERGY | 11802.45 |  |  | -66.62% | [7 empty] | % savings | -3.857%

## Supporting
Conversion factors |  |  | Robur unit; possible conditions |  |  | T_in limited |  | T_out limited |  | "Scratch paper" calculations |  | CZ9 DEER MF 2003 data for calibration | Value | Notes
7.4805 | gal/ft3 |  | Heat Output [Btu/hr] | gpm | delta T [R] | T_in [F] | T_out [F] | T_in [F] | T_out [F] | Converting lbs/s to gpm |  | DHW [therms/yr] | 118.5379 | DEER WH Calculator spreadsheet for CZ 9 MF; Stor_EF_Gas_060gal_0.80EF
100000 | Btu/therm |  | 123500 | 6.2 | 39.8387 | 122 | 161.8387 | 100.1613 | 140 | 2.4 | lbs/s
100 | kBtu/therm |  | 123500 | 10 | 24.7 | 122 | 146.7 | 115.3 | 140 | 144 | lbs/min
|  |  | 123500 | 13.6 | 18.1618 | 122 | 140.1618 | 121.8382 | 140 | 17.561 | gal/min | 135F Water [gal/yr] | 13710.6564
Water Properties |  |  | 123500 | 19 | 13 | 122 | 135 | 127 | 140 | Converting gpm to lbs/s |  | 135F Water [gal/dy] | 37.5634 | DEER WH Calulator spreadsheet for CZ 9 MF; assuming 135F water
8.2 | lbs/gal, density of water |  | 123500 | 20 | 12.35 | 122 | 134.35 | 127.65 | 140 | 8.11 | gpm
1 | Btu/(lb*F), cp at 100F H2O |  | 123500 | 22 | 11.2273 | 122 | 133.2273 | 128.7727 | 140 | 66.502 | lbs/min | Water Heater Size, MFM WB Program (see below)
[10 empty] | 1.1084 | lbs/s |  | 13.4 | kBtu/h input rate per residential unit
Assumed blended energy rates |  |  | Notes | [9 empty] | 1125.6 | kBtu/h Boiler Input Rate
1 | $/therm |  | 1. The temperatures in red are not allowed per the manufacturer | [6 empty] | 16.22 |  |  | 1125600 | Btu/h Boiler Input Rate
0.3 | $/kWh | [8 empty] | 48.66 |  |  | 900480 | Btu/h Boiler Output Rate
97.32
Other variables
84 | residential units
Assumptions for Both Scenarios |  |  | Boilers
15 | ft head primary pumps |  | Heat Output [Btu/hr] | gpm | delta T [R] | T_in [F] | T_out [F] | T_in [F] | T_out [F]
160 | F max temperature of boilers | 1 | 250000 | 50 | 10 | 125 | 135 | 128 | 138
130 | F primary loop setpoint | 0.4 | 100000 | 50 | 4 | 125 | 129 | 128 | 132
130 | F secondary loop setpoint | 0.2 | 50000 | 50 | 2 | 125 | 127 | 128 | 130
200 | gal tank
0.25 | hour indirect water heating recovery time
5 | F tank Deadband Temperature Difference
40 | ft head secondary pump
SequentialLoad equipment sequencing
0.2 | minimum and optimum part load ratio for boilers
2 | Boiler quantity
500000 | Btu/h Total Output Rate
0.8 | boiler efficiency
5 | Boiler Turndown
312500 | Btu/h Boiler Input Rate
250000 | Btu/h Boiler Output Rate |  | Steps to create other climate zones (same for baseline and retrofit)
50000 | Btu/h min. Output Rate |  | 1 | start with the baseline or retrofit model
50 | gpm constant speed intermittent primary pumps for boilers |  | 2 | on main page, change weather file, delete DDY data, and upload correct DDY data
136.5 | F design loop exit temperature for equipment sizing (likely used for boiler pump autosizing but that's it) |  | 3 | on tank, change cold temperature schedule to the correct climate zone
16.5 | F loop design temperature difference for equipment sizing (likely used for boiler pump autosizing but that's it) |  | 4 | use the Set Mains Temp measure
| boiler flow mode: NotModulated |  | 5 | for retrofit only, do post processing
12 | simulation steps per hour
Steps to create Retrofit model
Baseline Scenario Assumptions |  |  | 1 | start with the latest baseline model
25 | gpm secondary pump; constant speed, continuous |  | 2 | add a heat exhanger
| No GAHP |  | 3 | add loop with 1 GAHP, pump, 130F setpoint, and SequentialLoad
|  |  | 4 | change secondary pump to variable flow
Retrofit Scenario Assumptions |  |  | 5 | change secondary loop min flow rate to 2 gpm
2 to 25 | gpm secondary pump; variable speed, continuous |  | 6 | run
1 | GAHP quantity
95500 | Btu/h GAHP input Rate |  | Steps to create baseline model
123500 | Btu/h GAHP output Rate |  | 1 | start with the latest retrofit model
623500 | Btu/h Total Output Rate |  | 2 | delete the GAHP primary loop
13.6 | gpm GAHP pump flow rate; constant speed |  | 3 | delete the HX and the variable speed pump in the secondary loop
18.1618 | F delta T GAHP |  | 4 | add a constant speed pump in the secondary loop and correct the details (name, flow rate, head, efficiency, continuous)
Curve | GAHP efficiency (1 in OpenStudio because that is the maximum) |  | 5 | in the secondary PlantLoop object, change the max temp to 212 and the min flow rate to 0 gpm
122 | F max inlet temperature of GAHP (not in the model; but confirmed in post-processing) |  | 6 | run
135 | F max outlet temperature of GAHP, related PlantLoop, and HX (placed in model, works better than 140F)
SequentialLoad equipment sequencing for boilers and GAHPs
1 | F delta R, Min Temp Diff to Activate HX
CounterFlow Heat Exchange Model Type for the HX
UncontrolledOn Control Type for the HX
Autosized | Btu/h*R HX U-Factor times Area Value