CPUC Comments on SWHC004-02 Space Heating Boiler

Lead PA: PGE SCG

Workpaper Submittal Date: 1/4/2021

CPUC Review Date: 03/08/2021

SCG Response Date: 04/30/2021

Please note responses to comments in the table below, revise workpaper, and upload the entire package to the WPA. If needed, please reach out to Workpaper Review Team to set up a call to discuss.

| CPUC Comment | PA Response |
| --- | --- |
| A description of the OA Reset Controls is not found anywhere in the WP. I think what is being referred to here is modulation of supply water temperature based on outside air temperature. This needs to be clearly described in the workpaper, technology summary, and/or measure case description. Additionally, is there any consideration for higher supply water temperatures causing return water to be too high for optimal condensing? | Measure description are taken directly from DEER. Please see attached spreadsheet “DEER2016 Commercial Boiler Update” for details. We will add some explanation based on our understanding and what is written in this file. |
| How would OA reset controls (140-165°F) work for steam boilers, the supply temperature is dictated by steam pressure. Unless the boiler is operating at vacuum pressures, the steam supply temperature will not be less than 212°F. | Per the “DEER2016 Commercial Boiler Update” - Hot water loop temperature reset control for baseline simulations: “Hot water loop temperature reset control was added to all simulations for vintages starting with 2006 based on Title 24 requirements that have been in place since October 2005. The baseline reset control for DEER is assumed to be an outdoor temperature based control that resets hot water temperature between 165 and 140 F. This is applied to both steam and hot water boilers. For steam boilers, it is assumed that the secondary piping loop is hot water.” It is assumed that the steam boiler goes to a heat exchanger that heats a secondary hot water loop that then goes to the building for heating purposes, which is where the OA reset control is applied. We added some explanation based on this understand to the workpaper. |
| In the Energy Impact EAD table, no match in PEAR for "cAVVG" building HVAC type. Should the HVAC type be "cSVVG" for built-up variable air volume system with gas boiler? | The cAVVG HVAC type is pulled directly the DEER energy impacts export. This may be a typo since it does not exist in the READI database. We have fixed the HVAC type to the correct value of “cSVVG” See attached spreadsheet for details. |
| For measure offering SWHC004I [Steam boiler (> 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F)] The thermal efficiency is only 1% better than the code 79% for steam boilers. The measure savings appears to be exclusively based on the OA reset controls. Measure offering SWHC004J is functionally the same offering (size, OA controls) but with a proposed 82% thermal efficiency. Besides the proposed efficiency difference, these two offering do not apply to the same set of commercial building types in the EAD and Measure Data Spec workbooks. SWHC004I has energy impacts for universities, hospitals, hotels, manufacturing/biotech, and nursing homes. While SWHC004J has energy impacts for large & small offices, large retail, and nursing homes. Could SWHC004J be offered to all the building types I and J are currently? As it stands now, it appears that if a hotel installs a >2500 kbtu/hr steam boiler with 82% thermal efficiency or better, and OA reset controls, the savings will be based on SWHC004I, based on lower proposed savings. | This was an error in the Measure DataSpec file. All DEER measures should be using all the same building types (ECC, Ese, EUn, Hsp, Htl, MBT, Nrs, OfL, OfS, and Rt3). This will be updated in the next submission to match the impacts from found in the EAD. |
| The workpaper should include a table of the building types which are applicable for each measure offering. | This information is added to the workpaper. |
| The table shows an Outside Air reset for a steam boiler with settings of 140-165 F. Please explain this temperature setting i.e. if the steam boiler has another form of OA controls that explains this temperature setpoint. | Per the DEER2016 Commercial Boiler Update - Hot water loop temperature reset control for baseline simulations: “For steam boilers, it is assumed that the secondary piping loop is hot water.” It is assumed that the steam boiler goes to a heat exchanger that heats a secondary hot water loop that then goes to the building for heating purposes, which is where the OA reset control is applied. We will add some explanation based on this understand to the workpaper. See attached spreadsheet for details. |
| On Page 4 it says on January 15, 2021 the code efficiency is 84% but the table above it says an 82% efficiency. Shouldn’t the base case be 84%? | Yes, the consumption values for the 84% AFUE baseline had already been modeled as the measure case for the previous version. We have updated the measure case to 94% AFUE and the base case to 84% AFUE Condensing boiler consumption for a MFm building with 94% TE (HIR = 1.0638) have been modelled for the other measures. The modelled consumption values for 94% TE were used to calculate savings for the SWHC004A offering, but the measure case efficiency requirement has been converted to AFUE for eligibility purposes. Based on the conversion formula from the MASControl file “TechData_Plant.xlsx”, TechData a 94% TE corresponds to a 95.4% AFUE. |

Files:

DEER2016 OA Reset Modelling Notes

DEER2020 Data

MASControl TechData file

CEC Database export