## Background
General Background on cost documentation supporting workpaper update
1 | How was the baseline cost determined? Was it also determined using a single chiller manufacturer?
Reply: The cost data is from one manufacturer for sample units that they provided.
2 | Is cost documentation for both base and measure cases based on 2017 market availability? Please confirm that program data was not used for determining 2017 measure cost.
Reply: Yes the data is based on market availability the program does not collect program data and is not used for measure costs.
3 | If there is very limited equipment availability for the 10% tier and nothing for the 15% tier, how was the cost determined (and/or extrapolated) for both 10% and 15%?
Reply: The manufacturer did have some equipment that met the 15% tier for centrifugal equipment, although they only had one size category of positive displacement chillers. In order to come up with data for these size categories the data was estimated using a trend line based on the difference in pricing between size categories for centrifugal chillers. There is little participation expected for these measures.
4 | Did EnergySolution indicated sample data points supporting each tier and measure (size) category?
Reply: Energy Solutions provided the attached worksheets as the raw data used to supply IMC data. They also compared that data to some data that was previously collected to ensure that IMCs were still in line with what we have seen before.

## SCE Measure Summary
SCE*
| Compressor | Size | Tier | Title 24 IPLV (at AHRI) | Percent over Title 24 | Tier % over Title 24 IPLV Requirement | Tier kW/ton (at AHRI) | Title 24 Full Load (at AHRI) | Tier % over Title 24 kW/ton | Tier kW/ton (at AHRI) | DEER Measure kW/ton | DEER Measure kWh/ton | Tier kW/ton Demand Reduction | Tier kWh/ton Energy Savings | IMC | Baseline Cost | GMC | Proposed Incentive | Estimated Annual Participation | kW | kWh
Screw/Scroll <75 Tons Tier 1 | Postive Displacement (Screw, Scroll, Helical Rotary) | <75 Tons | 1 | 0.6 | 10% | 10% | 0.54 | 0.78 | 10% | 0.702 | 0.048 | 88.4 | 0.048 | 88.4 | 161.6037 | 636.3 | 797.9037 | 120 | 0 | 0 | 0
Screw/Scroll <75 Tons Tier 2 |  | <75 Tons | 2 | 0.6 | 15% | 15% | 0.51 | 0.78 | 15% | 0.663 | 0.048 | 88.4 | 0.072 | 132.6 | 295.5328 | 636.3 | 931.8328 | 200 | 0 | 0 | 0
Screw/Scroll 75-150 Tons Tier 1 |  | 75-150 Tons | 1 | 0.56 | 10% | 10% | 0.504 | 0.75 | 10% | 0.675 | 0.046 | 84.8 | 0.046 | 84.8 | 143.5437 | 448.316 | 591.8597 | 120 | 100 | 4.6 | 8480
Screw/Scroll 75-150 Tons Tier 2 |  | 75-150 Tons | 2 | 0.56 | 15% | 15% | 0.476 | 0.75 | 15% | 0.6375 | 0.046 | 84.8 | 0.069 | 127.2 | 244.7926 | 448.316 | 693.1086 | 200 | 75 | 5.175 | 9540
Screw/Scroll 150-300 Tons Tier 1 |  | 150-300 Tons | 1 | 0.54 | 10% | 10% | 0.486 | 0.68 | 10% | 0.612 | 0.042 | 77.8 | 0.042 | 77.8 | 123.4317 | 320.636 | 444.0677 | 70 | 200 | 8.4 | 15560
Screw/Scroll 150-300 Tons Tier 2 |  | 150-300 Tons | 2 | 0.54 | 15% | 15% | 0.459 | 0.68 | 15% | 0.578 | 0.042 | 77.8 | 0.063 | 116.7 | 206.7596 | 320.636 | 527.3956 | 140 | 0 | 0 | 0
Screw/Scroll 300 -600 Tons Tier 1 |  | 300 -600 Tons | 1 | 0.52 | 10% | 10% | 0.468 | 0.625 | 10% | 0.5625 | 0.039 | 71.9 | 0.039 | 71.9 | 101.2677 | 253.26 | 354.5277 | 70 | 0 | 0 | 0
Screw/Scroll 300 -600 Tons Tier 2 |  | 300 -600 Tons | 2 | 0.52 | 15% | 15% | 0.442 | 0.625 | 15% | 0.53125 | 0.039 | 71.9 | 0.0585 | 107.85 | 181.4338 | 253.26 | 434.6938 | 140 | 0 | 0 | 0
Screw/Scroll >600 Tons Tier 1 |  | >600 Tons | 1 | 0.5 | 10% | 10% | 0.45 | 0.585 | 10% | 0.5265 | 0.036 | 66 | 0.036 | 66 | 77.0517 | 246.188 | 323.2397 | 70 | 0 | 0 | 0
Screw/Scroll >600 Tons Tier 2 |  | >600 Tons | 2 | 0.5 | 15% | 15% | 0.425 | 0.585 | 15% | 0.49725 | 0.036 | 66 | 0.054 | 99 | 168.8152 | 246.188 | 415.0032 | 140 | 0 | 0 | 0
Screw/Scroll <150 Tons Tier 1 | Centrifugal | <150 Tons | 1 | 0.44 | 10% | 10% | 0.396 | 0.695 | 10% | 0.6255 | 0.061 | 125.5 | 0.040667 | 83.6667 | 132.4276 | 642.21 | 774.6376 | 70 | 100 | 4.0667 | 8366.6667
Screw/Scroll <150 Tons Tier 2 |  | <150 Tons | 2 | 0.44 | 15% | 15% | 0.374 | 0.695 | 15% | 0.59075 | 0.061 | 125.5 | 0.061 | 125.5 | 248.6069 | 642.21 | 890.8169 | 140 | 0 | 0 | 0
Screw/Scroll 150-300 Tons Tier 1 |  | 150-300 Tons | 1 | 0.4 | 10% | 10% | 0.36 | 0.635 | 10% | 0.5715 | 0.056 | 114.6 | 0.037333 | 76.4 | 98.128 | 399.236 | 497.364 | 70 | 600 | 22.4 | 45840
Screw/Scroll 150-300 Tons Tier 2 |  | 150-300 Tons | 2 | 0.4 | 15% | 15% | 0.34 | 0.635 | 15% | 0.53975 | 0.056 | 114.6 | 0.056 | 114.6 | 168.5 | 399.236 | 567.736 | 140 | 150 | 8.4 | 17190
Screw/Scroll 300 -400 Tons Tier 1 |  | 300 -400 Tons | 1 | 0.39 | 10% | 10% | 0.351 | 0.595 | 10% | 0.5355 | 0.052 | 107.4 | 0.034667 | 71.6 | 97.8886 | 301.577 | 399.4656 | 70 | 600 | 20.8 | 42960
Screw/Scroll 300-400 Tons Tier 2 |  | 300-400 Tons | 2 | 0.39 | 15% | 15% | 0.3315 | 0.595 | 15% | 0.50575 | 0.052 | 107.4 | 0.052 | 107.4 | 144.1286 | 301.577 | 445.7056 | 140 | 300 | 15.6 | 32220
Screw/Scroll 400-600 Tons Tier 1 |  | 400-600 Tons | 1 | 0.38 | 10% | 10% | 0.342 | 0.585 | 10% | 0.5265 | 0.051 | 105.6 | 0.034 | 70.4 | 68.4565 | 284.13 | 352.5865 | 40 | 900 | 30.6 | 63360
Screw/Scroll 400-600 Tons Tier 2 |  | 400-600 Tons | 2 | 0.38 | 15% | 15% | 0.323 | 0.585 | 15% | 0.49725 | 0.051 | 105.6 | 0.051 | 105.6 | 150.2141 | 284.13 | 434.3441 | 90 | 0 | 0 | 0
Screw/Scroll >600 Tons Tier 1 |  | >600 Tons | 1 | 0.38 | 10% | 10% | 0.342 | 0.585 | 10% | 0.5265 | 0.051 | 105.6 | 0.034 | 70.4 | 41.5712 | 212.112 | 253.6832 | 40 | 2900 | 98.6 | 204160
Screw/Scroll >600 Tons Tier 2 |  | >600 Tons | 2 | 0.38 | 15% | 15% | 0.323 | 0.585 | 15% | 0.49725 | 0.051 | 105.6 | 0.051 | 105.6 | 99.3542 | 212.112 | 311.4662 | 90 | 600 | 30.6 | 63360
[18 empty] | Total | 6525 | 249.2417 | 511036.6667
[11 empty] | *Uses Com Building Type and IOU CZ for SCE IOU | [8 empty] | Estimated TRC: | 1.2
Savings estimates are directly from DEER and interpolation techinique descripted in the Short Term Workpaper Approach. Participation estimates are based on previous participation.

## PG&E Measure Summary
PG&E*
| Compressor | Size | Tier | Title 24 IPLV (at AHRI) | Tier % over Title 24 IPLV Requirement | Tier kW/ton (at AHRI) | Title 24 Full Load (at AHRI) | Tier % over Title 24 kW/ton | Tier kW/ton (at AHRI) | DEER Measure kW/ton | DEER Measure kWh/ton | Tier kW/ton Demand Reduction | Tier kWh/ton Energy Savings | Estimated Annual Participation | kW | kWh | IMC | Baseline Cost | GMC | Proposed Incentive
Screw/Scroll <75 Tons Tier 1 | Postive Displacement (Screw, Scroll, Helical Rotary) | <75 Tons | 1 | 0.6 | 10% | 0.54 | 0.78 | 10% | 0.702 | 0.029 | 63.7 | 0.019333 | 42.4667 | 0 | 0 | 0 | 161.6037 | 636.3 | 797.9037 | 120
Screw/Scroll <75 Tons Tier 2 |  | <75 Tons | 2 | 0.6 | 15% | 0.51 | 0.78 | 15% | 0.663 | 0.029 | 63.7 | 0.029 | 63.7 | 0 | 0 | 0 | 295.5328 | 636.3 | 931.8328 | 200
Screw/Scroll 75-150 Tons Tier 1 |  | 75-150 Tons | 1 | 0.56 | 10% | 0.504 | 0.75 | 10% | 0.675 | 0.027 | 61.1 | 0.018 | 40.7333 | 180 | 3.24 | 7332 | 143.5437 | 448.316 | 591.8597 | 120
Screw/Scroll 75-150 Tons Tier 2 |  | 75-150 Tons | 2 | 0.56 | 15% | 0.476 | 0.75 | 15% | 0.6375 | 0.027 | 61.1 | 0.027 | 61.1 | 90 | 2.43 | 5499 | 244.7926 | 448.316 | 693.1086 | 200
Screw/Scroll 150-300 Tons Tier 1 |  | 150-300 Tons | 1 | 0.54 | 10% | 0.486 | 0.68 | 10% | 0.612 | 0.025 | 56 | 0.016667 | 37.3333 | 170 | 2.8333 | 6346.6667 | 123.4317 | 320.636 | 444.0677 | 70
Screw/Scroll 150-300 Tons Tier 2 |  | 150-300 Tons | 2 | 0.54 | 15% | 0.459 | 0.68 | 15% | 0.578 | 0.025 | 56 | 0.025 | 56 | 150 | 3.75 | 8400 | 206.7596 | 320.636 | 527.3956 | 140
Screw/Scroll 300 -600 Tons Tier 1 |  | 300 -600 Tons | 1 | 0.52 | 10% | 0.468 | 0.625 | 10% | 0.5625 | 0.023 | 51.8 | 0.015333 | 34.5333 | 450 | 6.9 | 15540 | 101.2677 | 253.26 | 354.5277 | 70
Screw/Scroll 300 -600 Tons Tier 2 |  | 300 -600 Tons | 2 | 0.52 | 15% | 0.442 | 0.625 | 15% | 0.53125 | 0.023 | 51.8 | 0.023 | 51.8 | 0 | 0 | 0 | 181.4338 | 253.26 | 434.6938 | 140
Screw/Scroll >600 Tons Tier 1 |  | >600 Tons | 1 | 0.5 | 10% | 0.45 | 0.585 | 10% | 0.5265 | 0.021 | 47.5 | 0.014 | 31.6667 | 0 | 0 | 0 | 77.0517 | 246.188 | 323.2397 | 70
Screw/Scroll >600 Tons Tier 2 |  | >600 Tons | 2 | 0.5 | 15% | 0.425 | 0.585 | 15% | 0.49725 | 0.021 | 47.5 | 0.021 | 47.5 | 0 | 0 | 0 | 168.8152 | 246.188 | 415.0032 | 140
Screw/Scroll <150 Tons Tier 1 | Centrifugal | <150 Tons | 1 | 0.44 | 10% | 0.396 | 0.695 | 10% | 0.6255 | 0.037 | 94.7 | 0.024667 | 63.1333 | 0 | 0 | 0 | 132.4276 | 642.21 | 774.6376 | 70
Screw/Scroll <150 Tons Tier 2 |  | <150 Tons | 2 | 0.44 | 15% | 0.374 | 0.695 | 15% | 0.59075 | 0.037 | 94.7 | 0.037 | 94.7 | 0 | 0 | 0 | 248.6069 | 642.21 | 890.8169 | 140
Screw/Scroll 150-300 Tons Tier 1 |  | 150-300 Tons | 1 | 0.4 | 10% | 0.36 | 0.635 | 10% | 0.5715 | 0.034 | 86.5 | 0.022667 | 57.6667 | 720 | 16.32 | 41520 | 98.128 | 399.236 | 497.364 | 70
Screw/Scroll 150-300 Tons Tier 2 |  | 150-300 Tons | 2 | 0.4 | 15% | 0.34 | 0.635 | 15% | 0.53975 | 0.034 | 86.5 | 0.034 | 86.5 | 180 | 6.12 | 15570 | 168.5 | 399.236 | 567.736 | 140
Screw/Scroll 300 -400 Tons Tier 1 |  | 300 -400 Tons | 1 | 0.39 | 10% | 0.351 | 0.595 | 10% | 0.5355 | 0.032 | 81.1 | 0.021333 | 54.0667 | 720 | 15.36 | 38928 | 97.8886 | 301.577 | 399.4656 | 70
Screw/Scroll 300-400 Tons Tier 2 |  | 300-400 Tons | 2 | 0.39 | 15% | 0.3315 | 0.595 | 15% | 0.50575 | 0.032 | 81.1 | 0.032 | 81.1 | 360 | 11.52 | 29196 | 144.1286 | 301.577 | 445.7056 | 140
Screw/Scroll 400-600 Tons Tier 1 |  | 400-600 Tons | 1 | 0.38 | 10% | 0.342 | 0.585 | 10% | 0.5265 | 0.031 | 79.7 | 0.020667 | 53.1333 | 1080 | 22.32 | 57384 | 68.4565 | 284.13 | 352.5865 | 40
Screw/Scroll 400-600 Tons Tier 2 |  | 400-600 Tons | 2 | 0.38 | 15% | 0.323 | 0.585 | 15% | 0.49725 | 0.031 | 79.7 | 0.031 | 79.7 | 0 | 0 | 0 | 150.2141 | 284.13 | 434.3441 | 90
Screw/Scroll >600 Tons Tier 1 |  | >600 Tons | 1 | 0.38 | 10% | 0.342 | 0.585 | 10% | 0.5265 | 0.031 | 79.7 | 0.020667 | 53.1333 | 3480 | 71.92 | 184904 | 41.5712 | 212.112 | 253.6832 | 40
Screw/Scroll >600 Tons Tier 2 |  | >600 Tons | 2 | 0.38 | 15% | 0.323 | 0.585 | 15% | 0.49725 | 0.031 | 79.7 | 0.031 | 79.7 | 720 | 22.32 | 57384 | 99.3542 | 212.112 | 311.4662 | 90
[13 empty] | Total | 8300 | 185.0333 | 468003.6667
*Uses Com Building Type and IOU CZ for PG&E IOU
Savings estimates are directly from DEER and interpolation techinique descripted in the Short Term Workpaper Approach. Participation estimates are based on previous participation.

## Cost per Solution Code
Solution Code | Chiller Type | Measure ID | Tier | GMC | IMC | Baseline Cost | Size Category
AC-20031 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-150to299tons-0.519kwpton-0.468IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-150to299tons-0.519kwpton-0.468IPLV | 2 | 567.736 | 168.5 | 399.236
AC-20032 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-150to299tons-0.549kwpton-0.495IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-150to299tons-0.549kwpton-0.495IPLV | 1 | 497.364 | 98.128 | 399.236
AC-20033 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | 2 | 567.74 | 168.5 | 399.24
AC-20034 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | 1 | 497.36 | 98.13 | 399.23
AC-20035 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | 2 | 445.71 | 144.13 | 301.58
AC-20036 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | 1 | 399.47 | 97.89 | 301.58
AC-20037 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 434.34 | 150.21 | 284.13
AC-20038 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 352.59 | 68.46 | 284.13
AC-20039 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 311.47 | 99.35 | 212.12
AC-20040 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 253.68 | 41.57 | 212.11
AC-20041 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | 2 | 890.82 | 248.61 | 642.21
AC-20043 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | 1 | 774.64 | 132.43 | 642.21
AC-20044 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-300to399tons-0.476kwpton-0.442IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-300to399tons-0.476kwpton-0.442IPLV | 2 | 445.7056 | 144.1286 | 301.577 |  | 527.4 | 206.7596 | 320.6404
AC-20045 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-300to399tons-0.504kwpton-0.468IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-300to399tons-0.504kwpton-0.468IPLV | 1 | 399.4656 | 97.8886 | 301.577 |  | 444.07 | 123.4317 | 320.6383
AC-20046 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-400to599tons-0.476kwpton-0.425IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-400to599tons-0.476kwpton-0.425IPLV | 2 | 434.3441 | 150.2141 | 284.13 |  | 434.69 | 181.4338 | 253.2562
AC-20047 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-400to599tons-0.504kwpton-0.5IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-400to599tons-0.504kwpton-0.5IPLV | 1 | 352.5865 | 68.4565 | 284.13 |  | 354.53 | 101.2677 | 253.2623
AC-20048 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-gte600tons-0.476kwpton-0.425IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-gte600tons-0.476kwpton-0.425IPLV | 2 | 311.4662 | 99.3542 | 212.112 |  | 693.11 | 244.7926 | 448.3174
AC-20049 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-gte600tons-0.504kwpton-0.45IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-gte600tons-0.504kwpton-0.45IPLV | 1 | 253.6832 | 41.5712 | 212.112 |  | 591.86 | 143.5437 | 448.3163
AC-20050 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-lt150tons-0.519kwpton-0.468IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-lt150tons-0.519kwpton-0.468IPLV | 2 | 890.8169 | 248.6069 | 642.21 |  | 415 | 168.8152 | 246.1848
AC-20051 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-lt150tons-0.549kwpton-0.495IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-lt150tons-0.549kwpton-0.495IPLV | 1 | 774.6376 | 132.4276 | 642.21 |  | 323.24 | 77.0517 | 246.1883
AC-20052 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | 2 | 567.736 | 168.5 | 399.236 |  | 931.83 | 295.5328 | 636.2972
AC-20053 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | 1 | 497.364 | 98.128 | 399.236 |  | 797.9 | 161.6037 | 636.2963
AC-20054 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | 2 | 445.7056 | 144.1286 | 301.577
AC-20055 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | 1 | 399.4656 | 97.8886 | 301.577
AC-20057 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 434.3441 | 150.2141 | 284.13
AC-20058 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 352.5865 | 68.4565 | 284.13
AC-20059 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 311.4662 | 99.3542 | 212.112
AC-20060 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 253.6832 | 41.5712 | 212.112
AC-20061 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | 2 | 890.8169 | 248.6069 | 642.21
AC-20062 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | 1 | 774.6376 | 132.4276 | 642.21
AC-20063 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | 2 | 567.736 | 168.5 | 399.236
AC-20064 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | 1 | 497.364 | 98.128 | 399.236
AC-20065 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | 2 | 445.7056 | 144.1286 | 301.577
AC-20066 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | 1 | 399.4656 | 97.8886 | 301.577
AC-20067 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 434.3441 | 150.2141 | 284.13
AC-20068 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 352.5865 | 68.4565 | 284.13
AC-20069 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 311.4662 | 99.3542 | 212.112
AC-20070 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 253.6832 | 41.5712 | 212.112
AC-20071 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | 2 | 890.8169 | 248.6069 | 642.21
AC-20072 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | 1 | 774.6376 | 132.4276 | 642.21
AC-20073 | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.561kwpton-0.459IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.561kwpton-0.459IPLV | 2 | 527.3956 | 206.7596 | 320.636
AC-20074 | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.578kwpton-0.374IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.578kwpton-0.374IPLV-VarSpd | 2 | 527.4 | 206.76 | 320.64
AC-20075 | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.594kwpton-0.486IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.594kwpton-0.486IPLV | 1 | 444.0677 | 123.4317 | 320.636
AC-20076 | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.612kwpton-0.396IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.612kwpton-0.396IPLV-VarSpd | 1 | 444.07 | 123.43 | 320.64
AC-20077 | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.519kwpton-0.442IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.519kwpton-0.442IPLV | 2 | 434.6938 | 181.4338 | 253.26
AC-20078 | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.531kwpton-0.349IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.531kwpton-0.349IPLV-VarSpd | 2 | 434.69 | 181.43 | 253.26
AC-20079 | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.549kwpton-0.468IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.549kwpton-0.468IPLV | 1 | 354.5277 | 101.2677 | 253.26
AC-20080 | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.563kwpton-0.369IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.563kwpton-0.369IPLV-VarSpd | 1 | 354.53 | 101.27 | 253.26
AC-20081 | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.612kwpton-0.476IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.612kwpton-0.476IPLV | 2 | 693.1086 | 244.7926 | 448.316
AC-20082 | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.638kwpton-0.417IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.638kwpton-0.417IPLV-VarSpd | 2 | 693.11 | 244.79 | 448.32
AC-20083 | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.648kwpton-0.504IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.648kwpton-0.504IPLV | 1 | 591.8597 | 143.5437 | 448.316
AC-20084 | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.675kwpton-0.441IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.675kwpton-0.441IPLV-VarSpd | 1 | 591.86 | 143.54 | 448.32
AC-20085 | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.476kwpton-0.425IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.476kwpton-0.425IPLV | 2 | 415.0032 | 168.8152 | 246.188
AC-20086 | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.497kwpton-0.323IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.497kwpton-0.323IPLV-VarSpd | 2 | 415 | 168.82 | 246.18
AC-20088 | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.504kwpton-0.45IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.504kwpton-0.45IPLV | 1 | 323.2397 | 77.0517 | 246.188
AC-20089 | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.527kwpton-0.342IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.527kwpton-0.342IPLV-VarSpd | 1 | 323.24 | 77.05 | 246.19
AC-20090 | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.638kwpton-0.51IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.638kwpton-0.51IPLV | 2 | 931.8328 | 295.5328 | 636.3
AC-20091 | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.663kwpton-0.425IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.663kwpton-0.425IPLV-VarSpd | 2 | 931.83 | 295.53 | 636.3 | 1
AC-20092 | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.675kwpton-0.54IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.675kwpton-0.54IPLV | 1 | 797.9037 | 161.6037 | 636.3
AC-20093 | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.702kwpton-0.45IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.702kwpton-0.45IPLV-VarSpd | 1 | 797.9 | 161.6 | 636.3 | 1

## IMC Summary
|  | New Data | [5 empty] | Old Data |  |  | Percent Difference
| Capacity Range | Baseline Cost | Tier 1 IMC | Tier 2 IMC | Size Category | Tier 1 GMC | Tier 2 GMC | Baseline Cost | Tier 1 IMC | Tier 2 IMC | Baseline Cost | Tier 1 IMC | Tier 2 IMC
Water Cooled Variable Speed Screw Chiller | < 75 tons | 636.3 | 161.6037 | 295.5328 | 1 | 797.9037 | 931.8328 | 0 | 0 | 0 | 0 | 0 | 0
| 75 to 149 tons | 448.316 | 143.5437 | 244.7926 | 2 | 591.8597 | 693.1086 | 0 | 0 | 0 | 0 | 0 | 0
| 150 to 299 tons | 320.636 | 123.4317 | 206.7596 | 3 | 444.0677 | 527.3956 | 0 | 0 | 0 | 0 | 0 | 0
| 300 to 599 tons | 253.26 | 101.2677 | 181.4338 | 4 | 354.5277 | 434.6938 | 278 | 59.68 | 0 | -24.74 | 41.5877 | 0
| >= 600 tons | 246.188 | 77.0517 | 168.8152 | 5 | 323.2397 | 415.0032 | 0 | 0 | 0 |  |  | 0
Water Cooled Variable Speed Centrifugal Chiller (Conventional Compressor) | < 150 tons | 642.21 | 132.4276 | 248.6069 | 1 | 774.6376 | 890.8169 | 0 | 0 | 0 |  |  | 0
| 150 to 299 tons | 399.236 | 98.128 | 168.5 | 2 | 497.364 | 567.736 | 0 | 0 | 0 |  |  | 0
| 300 to 399 tons | 301.577 | 97.8886 | 144.1286 | 3 | 399.4656 | 445.7056 | 482.28 | 93.6667 | 0 | -180.703 | 4.2219 | 0
| 400 to 599 tons | 284.13 | 68.4565 | 150.2141 | 4 | 352.5865 | 434.3441 | 330.5 | 77.5 | 0 | -46.37 | -9.0435 | 0
| >= 600 tons | 212.112 | 41.5712 | 99.3542 | 5 | 253.6832 | 311.4662 | 317.63 | 64.67 | 0 | -105.518 | -23.0988 | 0
| Data was not provided for cells in red. Trend lines were created to estimate IMC and Baseline Costs | [6 empty] | Because a limited data set was provided for IMCs, old cost data was compared to ensure data was accurate. IMCs were generally found to be similar, but generally had lower baselines costs.
For each size category the trend line for the centrifgual units was used to fill in missing data for scroll units. For this analysis it was assumed that the cost by size category for positive displacement chillers was similar to those of centrifugal chillers. Although this trend may not be 100% accurate is the best available data. In addition, very little participation is expected for positive displacement chillers.
Baseline Centrifugal Trend Line | 30.152 | -278.44 | 301.67
Value for 400-599 Tons | -631.328 | 884.588
Baseline Screw/Scroll Trend Line | 30.152 | -278.44 | 884.588
Tier 1 Centrifugal Trend Line | -1.026 | -14.982 | 301.67
Value for 400-599 Tons | -76.344 | 177.6117
Tier 1 Screw/Scroll Trend Line | -1.026 | -14.982 | 177.6117
Tier 2 Centrifugal Trend Line | 6.3536 | -69.801 | 143.93
Value for 400-599 Tons | -177.5464 | 358.9802
Tier 2 Screw/Scroll Trend Line | 6.3536 | -69.801 | 358.9802

## Raw Data
[8 empty] | Example Product 1 |  |  |  | Example Product 2
Chiller Type | Capacity Range | Efficiency Category | Path | Full Load Rating | Full Load | IPLV | Tier | Tons | FLE | IPLV | Cost/ton | Tons | FLE | IPLV | Cost/ton
Water Cooled Variable Speed Screw Chiller | < 75 tons | Code Baseline | B | kW/ton | 0.78 | 0.5 | 0
|  | Measure (+10%) | B | kW/ton | 0.702 | 0.45 | 1
|  | Measure (+15%) | B | kW/ton | 0.663 | 0.425 | 2
| 75 to 149 tons | Code Baseline | B | kW/ton | 0.75 | 0.49 | 0
|  | Measure (+10%) | B | kW/ton | 0.675 | 0.441 | 1
|  | Measure (+15%) | B | kW/ton | 0.638 | 0.417 | 2
| 150 to 299 tons | Code Baseline | B | kW/ton | 0.68 | 0.44 | 0
|  | Measure (+10%) | B | kW/ton | 0.612 | 0.396 | 1
|  | Measure (+15%) | B | kW/ton | 0.578 | 0.374 | 2
| 300 to 599 tons | Code Baseline | B | kW/ton | 0.625 | 0.41 | 0 | 325 | 0.611 | 0.41 | 253.2646
|  | Measure (+10%) | B | kW/ton | 0.563 | 0.369 | 1 | 325 | 0.561 | 0.363 | 354.5323
|  | Measure (+15%) | B | kW/ton | 0.531 | 0.349 | 2 | 325 | 0.53 | 0.347 | 434.6985
| >= 600 tons | Code Baseline | B | kW/ton | 0.585 | 0.38 | 0
|  | Measure (+10%) | B | kW/ton | 0.527 | 0.342 | 1
|  | Measure (+15%) | B | kW/ton | 0.497 | 0.323 | 2
Water Cooled Variable Speed Centrifugal Chiller (Conventional Compressor) | < 150 tons | Code Baseline | B | kW/ton | 0.695 | 0.44 | 0 | 145 | 0.612 | 0.418 | 642.2069
|  | Measure (+10%) | B | kW/ton | 0.626 | 0.396 | 1 | 145 | 0.587 | 0.393 | 774.6345
|  | Measure (+15%) | B | kW/ton | 0.591 | 0.374 | 2 | 145 | 0.553 | 0.371 | 890.8138
| 150 to 299 tons | Code Baseline | B | kW/ton | 0.635 | 0.4 | 0 | 250 | 0.626 | 0.386 | 399.236
|  | Measure (+10%) | B | kW/ton | 0.572 | 0.36 | 1 | 250 | 0.561 | 0.351 | 497.364
|  | Measure (+15%) | B | kW/ton | 0.54 | 0.34 | 2 | 250 | 0.531 | 0.339 | 567.736
| 300 to 399 tons | Code Baseline | B | kW/ton | 0.595 | 0.39 | 0 | 350 | 0.594 | 0.386 | 301.5771
|  | Measure (+10%) | B | kW/ton | 0.536 | 0.351 | 1 | 350 | 0.535 | 0.346 | 399.4657
|  | Measure (+15%) | B | kW/ton | 0.506 | 0.332 | 2 | 350 | 0.506 | 0.328 | 445.7057
| 400 to 599 tons | Code Baseline | B | kW/ton | 0.585 | 0.38 | 0 | 425 | 0.581 | 0.359 | 284.1341
|  | Measure (+10%) | B | kW/ton | 0.527 | 0.342 | 1 | 425 | 0.527 | 0.341 | 352.5906
|  | Measure (+15%) | B | kW/ton | 0.497 | 0.323 | 2 | 425 | 0.496 | 0.321 | 434.3482
| >= 600 tons | Code Baseline | B | kW/ton | 0.585 | 0.38 | 0 | 750 | 0.578 | 0.366 | 212.112 | 1000 | 0.575 | 0.358 | 183.819
|  | Measure (+10%) | B | kW/ton | 0.527 | 0.342 | 1 | 750 | 0.526 | 0.328 | 254.0693 | 1000 | 0.526 | 0.341 | 225.004
|  | Measure (+15%) | B | kW/ton | 0.497 | 0.323 | 2 | 750 | 0.495 | 0.315 | 331.4093 | 1000 | 0.495 | 0.318 | 263.23