## Background
Air-Cooled Chiller (ACC) (SWHC020-02) and Water-Cooled Chiller (WCC) (SWHC005-02) Cost Data
Prepared by Southern California Edison
November 2020
Introduction
In order to support updates to the WCC DEER workpaper, equipment cost data was collected in October-November 2020. The data was requested for each measure offering at the baseline and measure case efficiency levels. Data was gathered from two manufacturers. The manufacturers were not able to provide a full set of data for the WCC offerings due to equipment gaps at some high efficiency levels. In oder to support a full map of cost information, a mixture of extrapolation and a reliance on the previous versions of the workpapers' costing (from 2016-17) was used. The offering-by-offering methodology is detailed in the individual WCC worksheets that follow.

## SCE Measure Summary (hidden)
SCE*
| Compressor | Size | Tier | Title 24 IPLV (at AHRI) | Percent over Title 24 | Tier % over Title 24 IPLV Requirement | Tier kW/ton (at AHRI) | Title 24 Full Load (at AHRI) | Tier % over Title 24 kW/ton | Tier kW/ton (at AHRI) | DEER Measure kW/ton | DEER Measure kWh/ton | Tier kW/ton Demand Reduction | Tier kWh/ton Energy Savings | IMC | Baseline Cost | GMC | Proposed Incentive | Estimated Annual Participation | kW | kWh
Screw/Scroll <75 Tons Tier 1 | Postive Displacement (Screw, Scroll, Helical Rotary) | <75 Tons | 1 | 0.6 | 10% | 10% | 0.54 | 0.78 | 10% | 0.702 | 0.048 | 88.4 | 0.048 | 88.4 | 105.6566 | 416.5384 | 522.195 | 120 | 0 | 0 | 0
Screw/Scroll <75 Tons Tier 2 |  | <75 Tons | 2 | 0.6 | 15% | 15% | 0.51 | 0.78 | 15% | 0.663 | 0.048 | 88.4 | 0.072 | 132.6 | 193.4616 | 416.5384 | 610 | 200 | 0 | 0 | 0
Screw/Scroll 75-150 Tons Tier 1 |  | 75-150 Tons | 1 | 0.56 | 10% | 10% | 0.504 | 0.75 | 10% | 0.675 | 0.046 | 84.8 | 0.046 | 84.8 | 21.17 | 1086 | 1107.17 | 120 | 100 | 4.6 | 8480
Screw/Scroll 75-150 Tons Tier 2 |  | 75-150 Tons | 2 | 0.56 | 15% | 15% | 0.476 | 0.75 | 15% | 0.6375 | 0.046 | 84.8 | 0.069 | 127.2 | 38.9 | 1086 | 1124.9 | 200 | 75 | 5.175 | 9540
Screw/Scroll 150-300 Tons Tier 1 |  | 150-300 Tons | 1 | 0.54 | 10% | 10% | 0.486 | 0.68 | 10% | 0.612 | 0.042 | 77.8 | 0.042 | 77.8 | 36.705 | 519.14 | 555.845 | 70 | 200 | 8.4 | 15560
Screw/Scroll 150-300 Tons Tier 2 |  | 150-300 Tons | 2 | 0.54 | 15% | 15% | 0.459 | 0.68 | 15% | 0.578 | 0.042 | 77.8 | 0.063 | 116.7 | 166.71 | 519.14 | 685.85 | 140 | 0 | 0 | 0
Screw/Scroll 300 -600 Tons Tier 1 |  | 300 -600 Tons | 1 | 0.52 | 10% | 10% | 0.468 | 0.625 | 10% | 0.5625 | 0.039 | 71.9 | 0.039 | 71.9 | 179.7037 | 449.41 | 629.1137 | 70 | 0 | 0 | 0
Screw/Scroll 300 -600 Tons Tier 2 |  | 300 -600 Tons | 2 | 0.52 | 15% | 15% | 0.442 | 0.625 | 15% | 0.53125 | 0.039 | 71.9 | 0.0585 | 107.85 | 321.9476 | 449.41 | 771.3576 | 140 | 0 | 0 | 0
Screw/Scroll >600 Tons Tier 1 |  | >600 Tons | 1 | 0.5 | 10% | 10% | 0.45 | 0.585 | 10% | 0.5265 | 0.036 | 66 | 0.036 | 66 | 161.6 | 636.3 | 797.9 | 70 | 0 | 0 | 0
Screw/Scroll >600 Tons Tier 2 |  | >600 Tons | 2 | 0.5 | 15% | 15% | 0.425 | 0.585 | 15% | 0.49725 | 0.036 | 66 | 0.054 | 99 | 295.53 | 636.3 | 931.83 | 140 | 0 | 0 | 0
Screw/Scroll <150 Tons Tier 1 | Centrifugal | <150 Tons | 1 | 0.44 | 10% | 10% | 0.396 | 0.695 | 10% | 0.6255 | 0.061 | 125.5 | 0.040667 | 83.6667 | 185 | 660 | 845 | 70 | 100 | 4.0667 | 8366.6667
Screw/Scroll <150 Tons Tier 2 |  | <150 Tons | 2 | 0.44 | 15% | 15% | 0.374 | 0.695 | 15% | 0.59075 | 0.061 | 125.5 | 0.061 | 125.5 | 263 | 660 | 923 | 140 | 0 | 0 | 0
Screw/Scroll 150-300 Tons Tier 1 |  | 150-300 Tons | 1 | 0.4 | 10% | 10% | 0.36 | 0.635 | 10% | 0.5715 | 0.056 | 114.6 | 0.037333 | 76.4 | 72.125 | 656.885 | 729.01 | 70 | 600 | 22.4 | 45840
Screw/Scroll 150-300 Tons Tier 2 |  | 150-300 Tons | 2 | 0.4 | 15% | 15% | 0.34 | 0.635 | 15% | 0.53975 | 0.056 | 114.6 | 0.056 | 114.6 | 274.955 | 656.885 | 931.84 | 140 | 150 | 8.4 | 17190
Screw/Scroll 300 -400 Tons Tier 1 |  | 300 -400 Tons | 1 | 0.39 | 10% | 10% | 0.351 | 0.595 | 10% | 0.5355 | 0.052 | 107.4 | 0.034667 | 71.6 | 158.415 | 515.125 | 673.54 | 70 | 600 | 20.8 | 42960
Screw/Scroll 300-400 Tons Tier 2 |  | 300-400 Tons | 2 | 0.39 | 15% | 15% | 0.3315 | 0.595 | 15% | 0.50575 | 0.052 | 107.4 | 0.052 | 107.4 | 226.435 | 515.125 | 741.56 | 140 | 300 | 15.6 | 32220
Screw/Scroll 400-600 Tons Tier 1 |  | 400-600 Tons | 1 | 0.38 | 10% | 10% | 0.342 | 0.585 | 10% | 0.5265 | 0.051 | 105.6 | 0.034 | 70.4 | 193.84 | 448.525 | 642.365 | 40 | 900 | 30.6 | 63360
Screw/Scroll 400-600 Tons Tier 2 |  | 400-600 Tons | 2 | 0.38 | 15% | 15% | 0.323 | 0.585 | 15% | 0.49725 | 0.051 | 105.6 | 0.051 | 105.6 | 249.825 | 448.525 | 698.35 | 90 | 0 | 0 | 0
Screw/Scroll >600 Tons Tier 1 |  | >600 Tons | 1 | 0.38 | 10% | 10% | 0.342 | 0.585 | 10% | 0.5265 | 0.051 | 105.6 | 0.034 | 70.4 | 65.7 | 392.565 | 458.265 | 40 | 2900 | 98.6 | 204160
Screw/Scroll >600 Tons Tier 2 |  | >600 Tons | 2 | 0.38 | 15% | 15% | 0.323 | 0.585 | 15% | 0.49725 | 0.051 | 105.6 | 0.051 | 105.6 | 98.55 | 392.565 | 491.115 | 90 | 600 | 30.6 | 63360
[18 empty] | Total | 6525 | 249.2417 | 511036.6667
[11 empty] | *Uses Com Building Type and IOU CZ for SCE IOU | [8 empty] | Estimated TRC: | 1.2
Savings estimates are directly from DEER and interpolation techinique descripted in the Short Term Workpaper Approach. Participation estimates are based on previous participation.

## PG&E Measure Summary (hidden)
PG&E*
| Compressor | Size | Tier | Title 24 IPLV (at AHRI) | Tier % over Title 24 IPLV Requirement | Tier kW/ton (at AHRI) | Title 24 Full Load (at AHRI) | Tier % over Title 24 kW/ton | Tier kW/ton (at AHRI) | DEER Measure kW/ton | DEER Measure kWh/ton | Tier kW/ton Demand Reduction | Tier kWh/ton Energy Savings | Estimated Annual Participation | kW | kWh | IMC | Baseline Cost | GMC | Proposed Incentive
Screw/Scroll <75 Tons Tier 1 | Postive Displacement (Screw, Scroll, Helical Rotary) | <75 Tons | 1 | 0.6 | 10% | 0.54 | 0.78 | 10% | 0.702 | 0.029 | 63.7 | 0.019333 | 42.4667 | 0 | 0 | 0 | 105.6566 | 416.5384 | 522.195 | 120
Screw/Scroll <75 Tons Tier 2 |  | <75 Tons | 2 | 0.6 | 15% | 0.51 | 0.78 | 15% | 0.663 | 0.029 | 63.7 | 0.029 | 63.7 | 0 | 0 | 0 | 193.4616 | 416.5384 | 610 | 200
Screw/Scroll 75-150 Tons Tier 1 |  | 75-150 Tons | 1 | 0.56 | 10% | 0.504 | 0.75 | 10% | 0.675 | 0.027 | 61.1 | 0.018 | 40.7333 | 180 | 3.24 | 7332 | 21.17 | 1086 | 1107.17 | 120
Screw/Scroll 75-150 Tons Tier 2 |  | 75-150 Tons | 2 | 0.56 | 15% | 0.476 | 0.75 | 15% | 0.6375 | 0.027 | 61.1 | 0.027 | 61.1 | 90 | 2.43 | 5499 | 38.9 | 1086 | 1124.9 | 200
Screw/Scroll 150-300 Tons Tier 1 |  | 150-300 Tons | 1 | 0.54 | 10% | 0.486 | 0.68 | 10% | 0.612 | 0.025 | 56 | 0.016667 | 37.3333 | 170 | 2.8333 | 6346.6667 | 36.705 | 519.14 | 555.845 | 70
Screw/Scroll 150-300 Tons Tier 2 |  | 150-300 Tons | 2 | 0.54 | 15% | 0.459 | 0.68 | 15% | 0.578 | 0.025 | 56 | 0.025 | 56 | 150 | 3.75 | 8400 | 166.71 | 519.14 | 685.85 | 140
Screw/Scroll 300 -600 Tons Tier 1 |  | 300 -600 Tons | 1 | 0.52 | 10% | 0.468 | 0.625 | 10% | 0.5625 | 0.023 | 51.8 | 0.015333 | 34.5333 | 450 | 6.9 | 15540 | 179.7037 | 449.41 | 629.1137 | 70
Screw/Scroll 300 -600 Tons Tier 2 |  | 300 -600 Tons | 2 | 0.52 | 15% | 0.442 | 0.625 | 15% | 0.53125 | 0.023 | 51.8 | 0.023 | 51.8 | 0 | 0 | 0 | 321.9476 | 449.41 | 771.3576 | 140
Screw/Scroll >600 Tons Tier 1 |  | >600 Tons | 1 | 0.5 | 10% | 0.45 | 0.585 | 10% | 0.5265 | 0.021 | 47.5 | 0.014 | 31.6667 | 0 | 0 | 0 | 161.6 | 636.3 | 797.9 | 70
Screw/Scroll >600 Tons Tier 2 |  | >600 Tons | 2 | 0.5 | 15% | 0.425 | 0.585 | 15% | 0.49725 | 0.021 | 47.5 | 0.021 | 47.5 | 0 | 0 | 0 | 295.53 | 636.3 | 931.83 | 140
Screw/Scroll <150 Tons Tier 1 | Centrifugal | <150 Tons | 1 | 0.44 | 10% | 0.396 | 0.695 | 10% | 0.6255 | 0.037 | 94.7 | 0.024667 | 63.1333 | 0 | 0 | 0 | 185 | 660 | 845 | 70
Screw/Scroll <150 Tons Tier 2 |  | <150 Tons | 2 | 0.44 | 15% | 0.374 | 0.695 | 15% | 0.59075 | 0.037 | 94.7 | 0.037 | 94.7 | 0 | 0 | 0 | 263 | 660 | 923 | 140
Screw/Scroll 150-300 Tons Tier 1 |  | 150-300 Tons | 1 | 0.4 | 10% | 0.36 | 0.635 | 10% | 0.5715 | 0.034 | 86.5 | 0.022667 | 57.6667 | 720 | 16.32 | 41520 | 72.125 | 656.885 | 729.01 | 70
Screw/Scroll 150-300 Tons Tier 2 |  | 150-300 Tons | 2 | 0.4 | 15% | 0.34 | 0.635 | 15% | 0.53975 | 0.034 | 86.5 | 0.034 | 86.5 | 180 | 6.12 | 15570 | 274.955 | 656.885 | 931.84 | 140
Screw/Scroll 300 -400 Tons Tier 1 |  | 300 -400 Tons | 1 | 0.39 | 10% | 0.351 | 0.595 | 10% | 0.5355 | 0.032 | 81.1 | 0.021333 | 54.0667 | 720 | 15.36 | 38928 | 158.415 | 515.125 | 673.54 | 70
Screw/Scroll 300-400 Tons Tier 2 |  | 300-400 Tons | 2 | 0.39 | 15% | 0.3315 | 0.595 | 15% | 0.50575 | 0.032 | 81.1 | 0.032 | 81.1 | 360 | 11.52 | 29196 | 226.435 | 515.125 | 741.56 | 140
Screw/Scroll 400-600 Tons Tier 1 |  | 400-600 Tons | 1 | 0.38 | 10% | 0.342 | 0.585 | 10% | 0.5265 | 0.031 | 79.7 | 0.020667 | 53.1333 | 1080 | 22.32 | 57384 | 193.84 | 448.525 | 642.365 | 40
Screw/Scroll 400-600 Tons Tier 2 |  | 400-600 Tons | 2 | 0.38 | 15% | 0.323 | 0.585 | 15% | 0.49725 | 0.031 | 79.7 | 0.031 | 79.7 | 0 | 0 | 0 | 249.825 | 448.525 | 698.35 | 90
Screw/Scroll >600 Tons Tier 1 |  | >600 Tons | 1 | 0.38 | 10% | 0.342 | 0.585 | 10% | 0.5265 | 0.031 | 79.7 | 0.020667 | 53.1333 | 3480 | 71.92 | 184904 | 65.7 | 392.565 | 458.265 | 40
Screw/Scroll >600 Tons Tier 2 |  | >600 Tons | 2 | 0.38 | 15% | 0.323 | 0.585 | 15% | 0.49725 | 0.031 | 79.7 | 0.031 | 79.7 | 720 | 22.32 | 57384 | 98.55 | 392.565 | 491.115 | 90
[13 empty] | Total | 8300 | 185.0333 | 468003.6667
*Uses Com Building Type and IOU CZ for PG&E IOU
Savings estimates are directly from DEER and interpolation techinique descripted in the Short Term Workpaper Approach. Participation estimates are based on previous participation.

## Cost per Solution Code
Solution Code | Chiller Type | Measure ID | Tier | GMC | IMC | Baseline Cost | Size Category
AC-20031 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-150to299tons-0.519kwpton-0.468IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-150to299tons-0.519kwpton-0.468IPLV | 2 | 931.84 | 274.955 | 656.885
AC-20032 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-150to299tons-0.549kwpton-0.495IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-150to299tons-0.549kwpton-0.495IPLV | 1 | 729.01 | 72.125 | 656.885
AC-20033 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | 2 | 931.84 | 274.955 | 656.885
AC-20034 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | 1 | 729.01 | 72.125 | 656.885
AC-20035 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | 2 | 741.56 | 226.435 | 515.125
AC-20036 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | 1 | 673.54 | 158.415 | 515.125
AC-20037 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 698.35 | 249.825 | 448.525
AC-20038 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 642.365 | 193.84 | 448.525
AC-20039 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 491.115 | 98.55 | 392.565
AC-20040 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 458.265 | 65.7 | 392.565
AC-20041 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | 2 | 923 | 263 | 660
AC-20043 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-Conv-1Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | 1 | 845 | 185 | 660
AC-20044 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-300to399tons-0.476kwpton-0.442IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-300to399tons-0.476kwpton-0.442IPLV | 2 | 741.56 | 226.435 | 515.125 |  | 527.4 | 206.7596 | 320.6404 | 416.5384 | <75
AC-20045 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-300to399tons-0.504kwpton-0.468IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-300to399tons-0.504kwpton-0.468IPLV | 1 | 673.54 | 158.415 | 515.125 |  | 444.07 | 123.4317 | 320.6383 | 1086 | 75-149
AC-20046 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-400to599tons-0.476kwpton-0.425IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-400to599tons-0.476kwpton-0.425IPLV | 2 | 698.35 | 249.825 | 448.525 |  | 434.69 | 181.4338 | 253.2562 | 519.14 | 150-299
AC-20047 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-400to599tons-0.504kwpton-0.5IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-400to599tons-0.504kwpton-0.5IPLV | 1 | 642.365 | 193.84 | 448.525 |  | 354.53 | 101.2677 | 253.2623 | 449.41 | 300-599
AC-20048 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-gte600tons-0.476kwpton-0.425IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-gte600tons-0.476kwpton-0.425IPLV | 2 | 491.115 | 98.55 | 392.565 |  | 693.11 | 244.7926 | 448.3174 | 636.3 | >600
AC-20049 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-gte600tons-0.504kwpton-0.45IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-gte600tons-0.504kwpton-0.45IPLV | 1 | 458.265 | 65.7 | 392.565 |  | 591.86 | 143.5437 | 448.3163 | 660 | <150
AC-20050 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-lt150tons-0.519kwpton-0.468IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-lt150tons-0.519kwpton-0.468IPLV | 2 | 923 | 263 | 660 |  | 415 | 168.8152 | 246.1848 | 656.885 | 150-299
AC-20051 | NE-HVAC-Chlr-WtrCldCentChlr-Conv-lt150tons-0.549kwpton-0.495IPLV | NE-HVAC-Chlr-WtrCldCentChlr-Conv-lt150tons-0.549kwpton-0.495IPLV | 1 | 845 | 185 | 660 |  | 323.24 | 77.0517 | 246.1883 | 515.125 | 300-399
AC-20052 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | 2 | 931.84 | 274.955 | 656.885 |  | 931.83 | 295.5328 | 636.2972 | 448.525 | 400-599
AC-20053 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | 1 | 729.01 | 72.125 | 656.885 |  | 797.9 | 161.6037 | 636.2963 | 392.565 | >600
AC-20054 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | 2 | 741.56 | 226.435 | 515.125
AC-20055 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | 1 | 673.54 | 158.415 | 515.125
AC-20057 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 698.35 | 249.825 | 448.525
AC-20058 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 642.365 | 193.84 | 448.525
AC-20059 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 491.115 | 98.55 | 392.565
AC-20060 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 458.265 | 65.7 | 392.565
AC-20061 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | 2 | 923 | 263 | 660
AC-20062 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-1Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | 1 | 845 | 185 | 660
AC-20063 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-150to299tons-0.54kwpton-0.34IPLV-VarSpd-CndRlf | 2 | 931.84 | 274.955 | 656.885
AC-20064 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-150to299tons-0.572kwpton-0.36IPLV-VarSpd-CndRlf | 1 | 729.01 | 72.125 | 656.885
AC-20065 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-300to399tons-0.506kwpton-0.332IPLV-VarSpd-CndRlf | 2 | 741.56 | 226.435 | 515.125
AC-20066 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-300to399tons-0.536kwpton-0.351IPLV-VarSpd-CndRlf | 1 | 673.54 | 158.415 | 515.125
AC-20067 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-400to599tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 698.35 | 249.825 | 448.525
AC-20068 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-400to599tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 642.365 | 193.84 | 448.525
AC-20069 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-gte600tons-0.497kwpton-0.323IPLV-VarSpd-CndRlf | 2 | 491.115 | 98.55 | 392.565
AC-20070 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-gte600tons-0.527kwpton-0.342IPLV-VarSpd-CndRlf | 1 | 458.265 | 65.7 | 392.565
AC-20071 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-lt150tons-0.591kwpton-0.374IPLV-VarSpd-CndRlf | 2 | 923 | 263 | 660
AC-20072 | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | NE-HVAC-Chlr-WtrCldCentChlr-NoFric-2Cmp-lt150tons-0.626kwpton-0.396IPLV-VarSpd-CndRlf | 1 | 845 | 185 | 660
AC-20073 | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.561kwpton-0.459IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.561kwpton-0.459IPLV | 2 | 685.85 | 166.71 | 519.14
AC-20074 | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.578kwpton-0.374IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.578kwpton-0.374IPLV-VarSpd | 2 | 685.85 | 166.71 | 519.14
AC-20075 | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.594kwpton-0.486IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.594kwpton-0.486IPLV | 1 | 555.845 | 36.705 | 519.14
AC-20076 | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.612kwpton-0.396IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-150to299tons-0.612kwpton-0.396IPLV-VarSpd | 1 | 555.845 | 36.705 | 519.14
AC-20077 | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.519kwpton-0.442IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.519kwpton-0.442IPLV | 2 | 771.3576 | 321.9476 | 449.41
AC-20078 | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.531kwpton-0.349IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.531kwpton-0.349IPLV-VarSpd | 2 | 771.3576 | 321.9476 | 449.41
AC-20079 | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.549kwpton-0.468IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.549kwpton-0.468IPLV | 1 | 629.1137 | 179.7037 | 449.41
AC-20080 | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.563kwpton-0.369IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-300to599tons-0.563kwpton-0.369IPLV-VarSpd | 1 | 629.1137 | 179.7037 | 449.41
AC-20081 | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.612kwpton-0.476IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.612kwpton-0.476IPLV | 2 | 1124.9 | 38.9 | 1086
AC-20082 | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.638kwpton-0.417IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.638kwpton-0.417IPLV-VarSpd | 2 | 1124.9 | 38.9 | 1086
AC-20083 | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.648kwpton-0.504IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.648kwpton-0.504IPLV | 1 | 1107.17 | 21.17 | 1086
AC-20084 | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.675kwpton-0.441IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-75to149tons-0.675kwpton-0.441IPLV-VarSpd | 1 | 1107.17 | 21.17 | 1086
AC-20085 | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.476kwpton-0.425IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.476kwpton-0.425IPLV | 2 | 931.83 | 295.53 | 636.3
AC-20086 | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.497kwpton-0.323IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.497kwpton-0.323IPLV-VarSpd | 2 | 931.83 | 295.53 | 636.3
AC-20088 | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.504kwpton-0.45IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.504kwpton-0.45IPLV | 1 | 797.9 | 161.6 | 636.3
AC-20089 | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.527kwpton-0.342IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-gte600tons-0.527kwpton-0.342IPLV-VarSpd | 1 | 797.9 | 161.6 | 636.3
AC-20090 | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.638kwpton-0.51IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.638kwpton-0.51IPLV | 2 | 610 | 193.4616 | 416.5384
AC-20091 | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.663kwpton-0.425IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.663kwpton-0.425IPLV-VarSpd | 2 | 610 | 193.4616 | 416.5384 | 1
AC-20092 | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.675kwpton-0.54IPLV | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.675kwpton-0.54IPLV | 1 | 522.195 | 105.6566 | 416.5384
AC-20093 | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.702kwpton-0.45IPLV-VarSpd | NE-HVAC-Chlr-WtrCldScrewChlr-lt75tons-0.702kwpton-0.45IPLV-VarSpd | 1 | 522.195 | 105.6566 | 416.5384 | 1

## WCC Path B (SWHC005-02)
[8 empty] | Raw Cost Data (2020) |  | SWHC005-02 Cost Data |  | SWHC005-01 Data
Chiller Type | Capacity Range | Efficiency Category | Path | Full Load Rating | Full Load | IPLV | Tier | Manufacturer A | Manufacturer B | GMC | IMC | GMC | IMC | Methodology
Water Cooled Variable Speed Screw Chiller | < 75 tons | Code Baseline | B | kW/ton | 0.78 | 0.5 | 0 | N/A | N/A | 416.5384 | N/A | 636.3 | N/A | Calculated GMC based SWHC005-01 scaled to 2020 data based on Tier 2 data point provided
|  | Measure (+10%) | B | kW/ton | 0.702 | 0.45 | 1 | N/A | N/A | 522.195 | 105.6566 | 797.7 | 161.4 | Calculated GMC based SWHC005-01 scaled to 2020 data based on Tier 2 data point provided
|  | Measure (+15%) | B | kW/ton | 0.663 | 0.425 | 2 | 610 | N/A | 610 | 193.4616 | 931.83 | 295.53 | Provided by distributor
| 75 to 149 tons | Code Baseline | B | kW/ton | 0.75 | 0.49 | 0 | N/A | 1086 | 1086 | N/A | 448.32 | N/A | Provided by distributor
|  | Measure (+10%) | B | kW/ton | 0.675 | 0.441 | 1 | N/A | 1107.17 | 1107.17 | 21.17 | 591.86 | 143.54 | Provided by distributor
|  | Measure (+15%) | B | kW/ton | 0.638 | 0.417 | 2 | N/A | 1124.9 | 1124.9 | 38.9 | 693.11 | 244.79 | Provided by distributor
| 150 to 299 tons | Code Baseline | B | kW/ton | 0.68 | 0.44 | 0 | 420 | 618.28 | 519.14 | N/A | 320.64 | N/A | Provided by distributor
|  | Measure (+10%) | B | kW/ton | 0.612 | 0.396 | 1 | 450 | 661.69 | 555.845 | 36.705 | 444.07 | 123.43 | Provided by distributor
|  | Measure (+15%) | B | kW/ton | 0.578 | 0.374 | 2 | N/A | 685.85 | 685.85 | 166.71 | 527.4 | 206.76 | Provided by distributor
| 300 to 599 tons | Code Baseline | B | kW/ton | 0.625 | 0.41 | 0 | N/A | 449.41 | 449.41 | N/A | 253.26 | N/A | Provided by distributor
|  | Measure (+10%) | B | kW/ton | 0.563 | 0.369 | 1 | N/A | 429.76 | 629.1137 | 179.7037 | 354.53 | 101.27 | Calculated GMC based SWHC005-01 scaled to 2020 data based on Base Case data points provided
|  | Measure (+15%) | B | kW/ton | 0.531 | 0.349 | 2 | N/A | N/A | 771.3576 | 321.9476 | 434.69 | 181.43 | Calculated GMC based SWHC005-01 scaled to 2020 data based on Base Case data points provided
| >= 600 tons | Code Baseline | B | kW/ton | 0.585 | 0.38 | 0 | N/A | N/A | 636.3 | N/A | 636.3 | N/A | Used Data from SWHC005-01 since no data available in 2020
|  | Measure (+10%) | B | kW/ton | 0.527 | 0.342 | 1 | N/A | N/A | 797.9 | 161.6 | 797.9 | 161.6 | Used Data from SWHC005-01 since no data available in 2020
|  | Measure (+15%) | B | kW/ton | 0.497 | 0.323 | 2 | N/A | N/A | 931.83 | 295.53 | 931.83 | 295.53 | Used Data from SWHC005-01 since no data available in 2020
Water Cooled Variable Speed Centrifugal Chiller (Conventional Compressor) | < 150 tons | Code Baseline | B | kW/ton | 0.695 | 0.44 | 0 | 660 | N/A | 660 | N/A | 642.21 | N/A | Provided by distributor
|  | Measure (+10%) | B | kW/ton | 0.626 | 0.396 | 1 | 845 | N/A | 845 | 185 | 774.64 | 132.43 | Provided by distributor
|  | Measure (+15%) | B | kW/ton | 0.591 | 0.374 | 2 | 923 | N/A | 923 | 263 | 890.82 | 248.61 | Provided by distributor
| 150 to 299 tons | Code Baseline | B | kW/ton | 0.635 | 0.4 | 0 | 800 | 513.77 | 656.885 | N/A | 399.24 | N/A | Provided by distributor
|  | Measure (+10%) | B | kW/ton | 0.572 | 0.36 | 1 | 825 | 633.02 | 729.01 | 72.125 | 467.36 | 68.12 | Provided by distributor
|  | Measure (+15%) | B | kW/ton | 0.54 | 0.34 | 2 | 864 | 999.68 | 931.84 | 274.955 | 567.74 | 168.5 | Provided by distributor
| 300 to 399 tons | Code Baseline | B | kW/ton | 0.595 | 0.39 | 0 | 520 | 510.25 | 515.125 | N/A | 301.58 | N/A | Provided by distributor
|  | Measure (+10%) | B | kW/ton | 0.536 | 0.351 | 1 | 550 | 797.08 | 673.54 | 158.415 | 399.47 | 97.89 | Provided by distributor
|  | Measure (+15%) | B | kW/ton | 0.506 | 0.332 | 2 | 670 | 813.12 | 741.56 | 226.435 | 445.71 | 144.13 | Provided by distributor
| 400 to 599 tons | Code Baseline | B | kW/ton | 0.585 | 0.38 | 0 | 450 | 447.05 | 448.525 | N/A | 284.13 | N/A | Provided by distributor
|  | Measure (+10%) | B | kW/ton | 0.527 | 0.342 | 1 | 610 | 674.73 | 642.365 | 193.84 | 352.59 | 68.46 | Provided by distributor
|  | Measure (+15%) | B | kW/ton | 0.497 | 0.323 | 2 | N/A | 698.35 | 698.35 | 249.825 | 434.34 | 150.21 | Provided by distributor
| >= 600 tons | Code Baseline | B | kW/ton | 0.585 | 0.38 | 0 | 410 | 375.13 | 392.565 | N/A | 212.11 | N/A | Provided by distributor
|  | Measure (+10%) | B | kW/ton | 0.527 | 0.342 | 1 | 440 | 476.53 | 458.265 | 65.7 | 253.68 | 41.57 | Provided by distributor
|  | Measure (+15%) | B | kW/ton | 0.497 | 0.323 | 2 | N/A | N/A | 491.115 | 98.55 | 311.47 | 99.36 | Extrapolated from 2020 Tier 1 data point