## Summary
BldgType | BldgLoc | Base_kWh/ton | Base_kW/ton | Base_therms/ton | Measure_kWh/ton | Measure_kW/ton | Measure_therms/ton | Savings_kWh/ton | Savings_kW/ton | Savings_therms/ton
EPr | CZ01 | 1884.57 | 0.37 | 96.13 | 1882.05 | 0.34 | 85.27 | 2.52 | 0.03 | 10.86
EPr | CZ02 | 2061.14 | 0.07 | 54.62 | 2023.22 | 0.07 | 49 | 37.92 | 0 | 5.62
EPr | CZ03 | 1704.66 | 0.03 | 46.55 | 1690.94 | 0.03 | 41.01 | 13.72 | 0 | 5.54
EPr | CZ04 | 1936.73 | 0.6 | 38.29 | 1900.17 | 0.45 | 33.96 | 36.56 | 0.15 | 4.33
EPr | CZ05 | 1766.9 | 0.39 | 45.58 | 1754.66 | 0.33 | 39.74 | 12.24 | 0.06 | 5.84
EPr | CZ06 | 1699.79 | 0.48 | 18.9 | 1677.44 | 0.36 | 16.13 | 22.35 | 0.12 | 2.77
EPr | CZ07 | 1687.93 | 0.43 | 14.7 | 1669.23 | 0.33 | 12.35 | 18.7 | 0.1 | 2.35
EPr | CZ08 | 1826.86 | 0.51 | 16.42 | 1789.87 | 0.38 | 14.25 | 36.99 | 0.13 | 2.17
EPr | CZ09 | 1537.34 | 0.55 | 19.01 | 1501.15 | 0.41 | 16.65 | 36.19 | 0.14 | 2.36
EPr | CZ10 | 1779.72 | 0.61 | 18.72 | 1736.3 | 0.47 | 16.33 | 43.42 | 0.14 | 2.39
EPr | CZ11 | 1752.59 | 0.17 | 40.76 | 1713.96 | 0.17 | 36.65 | 38.63 | 0 | 4.11
EPr | CZ12 | 1894.89 | 0.11 | 44.82 | 1853.95 | 0.12 | 40.37 | 40.94 | -0.01 | 4.45
EPr | CZ13 | 1804.56 | 0.13 | 36.38 | 1762.68 | 0.13 | 32.63 | 41.88 | 0 | 3.75
EPr | CZ14 | 1711.1 | 0.57 | 36.97 | 1672.97 | 0.45 | 33.03 | 38.13 | 0.12 | 3.94
EPr | CZ15 | 1685.36 | 0.55 | 5.53 | 1638.02 | 0.43 | 4.74 | 47.34 | 0.12 | 0.79
EPr | CZ16 | 1720.94 | 0.05 | 114.88 | 1708.84 | 0.05 | 105.52 | 12.1 | 0 | 9.36
ESe | CZ01 | 1980.69 | 0.32 | 91.31 | 1976.35 | 0.28 | 82.39 | 4.34 | 0.04 | 8.92
ESe | CZ02 | 2171.65 | 0.17 | 55.6 | 2135.09 | 0.17 | 50.82 | 36.56 | 0 | 4.78
ESe | CZ03 | 1773.94 | 0.09 | 37.82 | 1756.11 | 0.09 | 34.05 | 17.83 | 0 | 3.77
ESe | CZ04 | 2070.28 | 0.55 | 34.97 | 2032.88 | 0.4 | 31.72 | 37.4 | 0.15 | 3.25
ESe | CZ05 | 1832.44 | 0.35 | 36.46 | 1815.27 | 0.28 | 32.82 | 17.17 | 0.07 | 3.64
ESe | CZ06 | 1805.57 | 0.43 | 14.64 | 1778.88 | 0.31 | 13.05 | 26.69 | 0.12 | 1.59
ESe | CZ07 | 1809.4 | 0.39 | 10.16 | 1784.69 | 0.28 | 8.93 | 24.71 | 0.11 | 1.23
ESe | CZ08 | 2027.98 | 0.48 | 13.78 | 1988.29 | 0.34 | 12.38 | 39.69 | 0.14 | 1.4
ESe | CZ09 | 1746.46 | 0.52 | 15.74 | 1708.93 | 0.39 | 14.18 | 37.53 | 0.13 | 1.56
ESe | CZ10 | 1963.67 | 0.58 | 19.56 | 1920.62 | 0.43 | 17.68 | 43.05 | 0.15 | 1.88
ESe | CZ11 | 1972.89 | 0.23 | 43.57 | 1935.02 | 0.23 | 39.88 | 37.87 | 0 | 3.69
ESe | CZ12 | 2061.66 | 0.21 | 47.01 | 2021.67 | 0.21 | 43 | 39.99 | 0 | 4.01
ESe | CZ13 | 2016.14 | 0.2 | 38.29 | 1975.2 | 0.2 | 34.98 | 40.94 | 0 | 3.31
ESe | CZ14 | 1894.01 | 0.54 | 40.02 | 1856.31 | 0.4 | 36.63 | 37.7 | 0.14 | 3.39
ESe | CZ15 | 1915.81 | 0.52 | 5.95 | 1869.66 | 0.41 | 5.29 | 46.15 | 0.11 | 0.66
ESe | CZ16 | 1827.54 | 0.13 | 108.82 | 1814.53 | 0.13 | 100.91 | 13.01 | 0 | 7.91
ERC | CZ01 | 2412.72 | 0.24 | 0 | 2369.18 | 0.25 | 0 | 43.54 | -0.01 | 0
ERC | CZ02 | 2105.81 | 0.14 | 0 | 2032.84 | 0.14 | 0 | 72.97 | 0 | 0
ERC | CZ03 | 1771.31 | 0.03 | 0 | 1721.69 | 0.03 | 0 | 49.62 | 0 | 0
ERC | CZ04 | 1838.6 | 0.32 | 0 | 1772.03 | 0.36 | 0 | 66.57 | -0.04 | 0
ERC | CZ05 | 1956.02 | 0.24 | 0 | 1898.58 | 0.27 | 0 | 57.44 | -0.03 | 0
ERC | CZ06 | 1620.21 | 0.27 | 0 | 1549.24 | 0.31 | 0 | 70.97 | -0.04 | 0
ERC | CZ07 | 1557.93 | 0.24 | 0 | 1495.88 | 0.28 | 0 | 62.05 | -0.04 | 0
ERC | CZ08 | 1639.75 | 0.28 | 0 | 1559.8 | 0.31 | 0 | 79.95 | -0.03 | 0
ERC | CZ09 | 1375.37 | 0.28 | 0 | 1309.38 | 0.32 | 0 | 65.99 | -0.04 | 0
ERC | CZ10 | 1569.69 | 0.31 | 0 | 1496.64 | 0.36 | 0 | 73.05 | -0.05 | 0
ERC | CZ11 | 1742.46 | 0.23 | 0 | 1682.52 | 0.23 | 0 | 59.94 | 0 | 0
ERC | CZ12 | 1847.95 | 0.19 | 0 | 1782.02 | 0.19 | 0 | 65.93 | 0 | 0
ERC | CZ13 | 1743.56 | 0.19 | 0 | 1681.11 | 0.19 | 0 | 62.45 | 0 | 0
ERC | CZ14 | 1704 | 0.31 | 0 | 1644.45 | 0.35 | 0 | 59.55 | -0.04 | 0
ERC | CZ15 | 1489.58 | 0.3 | 0 | 1430.08 | 0.34 | 0 | 59.5 | -0.04 | 0
ERC | CZ16 | 2562.52 | 0.07 | 0 | 2497.99 | 0.07 | 0 | 64.53 | 0 | 0

## Std_sim_annual
TechID | SizingID | BldgType | BldgVint | BldgLoc | BldgHVAC | BldgHVAC_2 | normunit | numunits | measarea | kwh_tot | kwh_ltg | kwh_task | kwh_equip | kwh_htg | kwh_clg | kwh_twr | kwh_aux | kwh_vent | kwh_venthtg | kwh_ventclg | kwh_refg | kwh_hpsup | kwh_shw | kwh_ext | thm_tot | thm_equip | thm_htg | thm_shw | deskw_ltg | deskw_equ | lastmod | kW_49 | ClCap_BTUH | ClCap_ton | kWh/ton | therms/ton | Count of AC units
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | DXSZCap | 109.851 | 50000.14 | 207022.3 | 80054.27 | 0 | 98033.33 | 0 | 3052.391 | 0 | 3227.084 | 22655.24 | 17633.66 | 2437.375 | 0 | 0 | 0 | 0 | 1055994000 | 1761412 | 1054233000 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:55 | 40.7637 | 1318212.225 | 109.851 | 1884.5733 | 96.1297 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | DXSZCap | 112.5433 | 50000.14 | 231967.5 | 80054.27 | 0 | 98033.33 | 0 | 28340.03 | 0 | 2609.24 | 22930.8 | 10677.63 | 9548.636 | 0 | 0 | 0 | 0 | 614713300 | 1761412 | 612951700 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:56 | 7.4986 | 1350519.818 | 112.5433 | 2061.1397 | 54.6202 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | DXSZCap | 130.341 | 50000.14 | 222186.5 | 80054.27 | 0 | 98033.33 | 0 | 15808.99 | 0 | 1749.437 | 26540.52 | 13548.62 | 8900.923 | 0 | 0 | 0 | 0 | 606763500 | 1761412 | 605001900 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:56 | 3.8569 | 1564091.804 | 130.341 | 1704.6557 | 46.552 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | DXSZCap | 123.2136 | 50000.14 | 238631.2 | 80054.27 | 0 | 98033.33 | 0 | 33620.87 | 0 | 1894.075 | 25028.71 | 9632.068 | 11968.63 | 0 | 0 | 0 | 0 | 471778800 | 1761412 | 470016800 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:57 | 73.4699 | 1478563.091 | 123.2136 | 1936.7279 | 38.2895 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | DXSZCap | 125.726 | 50000.14 | 222145.2 | 80054.27 | 0 | 98033.33 | 0 | 16166.9 | 0 | 2271.659 | 25619.09 | 11994.84 | 9435.454 | 0 | 0 | 0 | 0 | 573079900 | 1761412 | 571317700 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:58 | 48.9463 | 1508711.776 | 125.726 | 1766.8997 | 45.5817 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | DXSZCap | 143.2119 | 50000.14 | 243430.1 | 80054.27 | 0 | 98033.33 | 0 | 35108.21 | 0 | 1138.678 | 29095.62 | 8002.885 | 16462.59 | 0 | 0 | 0 | 0 | 270698700 | 1761412 | 268936800 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:58 | 69.2515 | 1718542.718 | 143.2119 | 1699.7897 | 18.902 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | DXSZCap | 140.913 | 50000.14 | 237851.5 | 80054.27 | 0 | 98033.33 | 0 | 30840.17 | 0 | 280.6558 | 28643.11 | 7486.416 | 16041.38 | 0 | 0 | 0 | 0 | 207159600 | 1761412 | 205398200 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:59 | 60.3922 | 1690955.85 | 140.913 | 1687.9317 | 14.7012 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | DXSZCap | 139.4614 | 50000.14 | 254776.2 | 80054.27 | 0 | 98033.33 | 0 | 47454.86 | 0 | 815.1143 | 28418.62 | 6622.288 | 17877.83 | 0 | 0 | 0 | 0 | 229000800 | 1761412 | 227239200 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:00 | 71.2489 | 1673537.108 | 139.4614 | 1826.8578 | 16.4204 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | DXSZCap | 175.3999 | 50000.14 | 269648.9 | 80054.27 | 0 | 98033.33 | 0 | 54342.77 | 0 | 1507.373 | 35711.25 | 10082.59 | 20821.66 | 0 | 0 | 0 | 0 | 333500200 | 1761412 | 331737600 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:01 | 96.0003 | 2104798.213 | 175.3999 | 1537.3382 | 19.0137 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | DXSZCap | 150.7078 | 50000.14 | 268217.8 | 80054.27 | 0 | 98033.33 | 0 | 57604.59 | 0 | 1719.429 | 30806.25 | 7932.181 | 19031.14 | 0 | 0 | 0 | 0 | 282068700 | 1761412 | 280306600 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:01 | 92.2527 | 1808493.546 | 150.7078 | 1779.7208 | 18.7163 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | DXSZCap | 154.465 | 50000.14 | 270714 | 80054.27 | 0 | 98033.33 | 0 | 57372.59 | 0 | 3107.563 | 32146.35 | 13143.38 | 15879.01 | 0 | 0 | 0 | 0 | 629664800 | 1761412 | 627903400 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:02 | 25.9427 | 1853579.485 | 154.465 | 1752.5917 | 40.7642 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | DXSZCap | 132.3875 | 50000.14 | 250859.3 | 80054.27 | 0 | 98033.33 | 0 | 43077.21 | 0 | 2512.063 | 27182.45 | 11466.72 | 12891.41 | 0 | 0 | 0 | 0 | 593371500 | 1761412 | 591610000 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:03 | 15.223 | 1588649.674 | 132.3875 | 1894.887 | 44.8208 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | DXSZCap | 152.8819 | 50000.14 | 275884.8 | 80054.27 | 0 | 98033.33 | 0 | 63226.18 | 0 | 2791.311 | 31779.87 | 11912.85 | 16913.34 | 0 | 0 | 0 | 0 | 556167900 | 1761412 | 554406100 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:04 | 20.309 | 1834582.747 | 152.8819 | 1804.5616 | 36.3789 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | DXSZCap | 162.7306 | 50000.14 | 278448.4 | 80054.27 | 0 | 98033.33 | 0 | 63169.9 | 0 | 3531.492 | 33659.47 | 12542.58 | 17872.62 | 0 | 0 | 0 | 0 | 601689800 | 1761412 | 599928800 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:05 | 93.4799 | 1952767.52 | 162.7306 | 1711.1002 | 36.9746 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | DXSZCap | 221.8155 | 50000.14 | 373839 | 80054.27 | 0 | 98033.33 | 0 | 148413 | 0 | 988.3467 | 46350.07 | 5196.212 | 37445.55 | 0 | 0 | 0 | 0 | 122658500 | 1761412 | 120897200 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:06 | 120.9325 | 2661786.487 | 221.8155 | 1685.3598 | 5.5298 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | DXSZCap | 131.0541 | 50000.14 | 225536.1 | 80054.27 | 0 | 98033.33 | 0 | 15413.15 | 0 | 4812.645 | 27222.74 | 17906.61 | 7377.829 | 0 | 0 | 0 | 0 | 1505612000 | 1761412 | 1503852000 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:07 | 6.3127 | 1572649.714 | 131.0541 | 1720.9383 | 114.8847 | 27
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | DXSZCap | 350.8434 | 149998.6 | 694911.8 | 303095 | 0 | 287781.7 | 0 | 15765.75 | 0 | 10289.36 | 77980.73 | 55242.5 | 11738.92 | 0 | 0 | 0 | 0 | 3203684000 | 2641667 | 3201044000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:08 | 112.2669 | 4210120.694 | 350.8434 | 1980.6894 | 91.3138 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | DXSZCap | 359.435 | 149998.6 | 780567 | 303095 | 0 | 287781.7 | 0 | 101092.1 | 0 | 8307.459 | 80291.55 | 35901.81 | 34516.98 | 0 | 0 | 0 | 0 | 1998571000 | 2641667 | 1995930000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:09 | 62.5839 | 4313219.506 | 359.435 | 2171.6502 | 55.6031 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | DXSZCap | 432.4231 | 149998.6 | 767093.8 | 303095 | 0 | 287781.7 | 0 | 75458.3 | 0 | 5793.706 | 94965.71 | 38238.92 | 40589.46 | 0 | 0 | 0 | 0 | 1635560000 | 2641667 | 1632918000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:10 | 39.1105 | 5189077.732 | 432.4231 | 1773.9425 | 37.8231 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | DXSZCap | 398.5807 | 149998.6 | 825174.4 | 303095 | 0 | 287781.7 | 0 | 138933.6 | 0 | 6113.09 | 89252.02 | 29766.26 | 47755.43 | 0 | 0 | 0 | 0 | 1393773000 | 2641667 | 1391131000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:11 | 218.3507 | 4782968.329 | 398.5807 | 2070.2819 | 34.9684 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | DXSZCap | 419.1716 | 149998.6 | 768108.8 | 303095 | 0 | 287781.7 | 0 | 77768.69 | 0 | 7558.723 | 91905.6 | 33503.76 | 42951.3 | 0 | 0 | 0 | 0 | 1528449000 | 2641667 | 1525808000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:12 | 145.9601 | 5030059.333 | 419.1716 | 1832.4447 | 36.4636 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | DXSZCap | 471.6901 | 149998.6 | 851671.2 | 303095 | 0 | 287781.7 | 0 | 153189.2 | 0 | 3743.054 | 103862.7 | 20768.72 | 68528.42 | 0 | 0 | 0 | 0 | 690588500 | 2641667 | 687947800 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:12 | 205.0211 | 5660281.361 | 471.6901 | 1805.5736 | 14.6407 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | DXSZCap | 465.195 | 149998.6 | 841723.9 | 303095 | 0 | 287781.7 | 0 | 147492 | 0 | 923.83 | 102431.9 | 16706.4 | 70106.55 | 0 | 0 | 0 | 0 | 472558700 | 2641667 | 469916500 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:13 | 179.7515 | 5582339.691 | 465.195 | 1809.4002 | 10.1583 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | DXSZCap | 438.518 | 149998.6 | 889307.4 | 303095 | 0 | 287781.7 | 0 | 197416.8 | 0 | 2554.821 | 98460.22 | 18095.4 | 68165.23 | 0 | 0 | 0 | 0 | 604491000 | 2641667 | 601850600 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:14 | 209.6513 | 5262216.25 | 438.518 | 2027.9837 | 13.7849 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | DXSZCap | 535.2732 | 149998.6 | 934833.2 | 303095 | 0 | 287781.7 | 0 | 219657.7 | 0 | 4588.07 | 119711.4 | 26851.57 | 78180.88 | 0 | 0 | 0 | 0 | 842603100 | 2641667 | 839962200 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:15 | 279.8537 | 6423278.83 | 535.2732 | 1746.4598 | 15.7416 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | DXSZCap | 459.2544 | 149998.6 | 901826.1 | 303095 | 0 | 287781.7 | 0 | 202889.4 | 0 | 5227.949 | 102832.6 | 25044.9 | 65302.65 | 0 | 0 | 0 | 0 | 898459800 | 2641667 | 895818600 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:16 | 264.2169 | 5511052.48 | 459.2544 | 1963.6745 | 19.5634 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | DXSZCap | 462.8215 | 149998.6 | 913096.8 | 303095 | 0 | 287781.7 | 0 | 206531.5 | 0 | 9294.378 | 106394.8 | 41017.34 | 54916.56 | 0 | 0 | 0 | 0 | 2016681000 | 2641667 | 2014038000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:17 | 108.3695 | 5553857.47 | 462.8215 | 1972.8921 | 43.5736 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | DXSZCap | 410.1864 | 149998.6 | 845664.8 | 303095 | 0 | 287781.7 | 0 | 154350.9 | 0 | 7766.575 | 92671.88 | 37188.48 | 45676.71 | 0 | 0 | 0 | 0 | 1928197000 | 2641667 | 1925554000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:18 | 85.6274 | 4922236.82 | 410.1864 | 2061.6598 | 47.0078 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | DXSZCap | 461.8668 | 149998.6 | 931189.1 | 303095 | 0 | 287781.7 | 0 | 225685.9 | 0 | 8419.206 | 106207.8 | 37169.59 | 58669.19 | 0 | 0 | 0 | 0 | 1768382000 | 2641667 | 1765739000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:19 | 93.0775 | 5542402.11 | 461.8668 | 2016.1419 | 38.2877 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | DXSZCap | 491.1069 | 149998.6 | 930160.6 | 303095 | 0 | 287781.7 | 0 | 217138.8 | 0 | 10641.54 | 111504 | 40182.03 | 60228.46 | 0 | 0 | 0 | 0 | 1965326000 | 2641667 | 1962685000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:20 | 264.0119 | 5893282.52 | 491.1069 | 1894.0085 | 40.0183 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | DXSZCap | 649.8906 | 149998.6 | 1245066 | 303095 | 0 | 287781.7 | 0 | 500625.4 | 0 | 2891.062 | 150673.5 | 16501.5 | 122997.6 | 0 | 0 | 0 | 0 | 386998800 | 2641667 | 384357000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:21 | 339.3057 | 7798687.42 | 649.8906 | 1915.8085 | 5.9548 | 45
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | DXSZCap | 421.0049 | 149998.6 | 769404.6 | 303095 | 0 | 287781.7 | 0 | 67982.69 | 0 | 15433.99 | 95111.9 | 58221.36 | 29584 | 0 | 0 | 0 | 0 | 4581333000 | 2641667 | 4578695000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:22 | 53.1107 | 5052058.751 | 421.0049 | 1827.5431 | 108.819 | 45
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | PkgHP | DXSZCap | 4.7649 | 1920.017 | 11496.51 | 2636.864 | 0 | 3720.005 | 3563.268 | 82.566 | 0 | 98.7006 | 826.7906 | 658.9958 | 71.4265 | 0 | 568.3339 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:22 | 1.1507 | 57179.39 | 4.7649 | 2412.7246 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | PkgHP | DXSZCap | 5.4135 | 1920.017 | 11399.9 | 2636.864 | 0 | 3720.005 | 2546.98 | 1132.626 | 0 | 89.8984 | 874.0139 | 481.587 | 322.9236 | 0 | 399.5325 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:23 | 0.74507 | 64962.49 | 5.4135 | 2105.8121 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | PkgHP | DXSZCap | 5.7144 | 1920.017 | 10121.93 | 2636.864 | 0 | 3720.005 | 2028.185 | 704.4915 | 0 | 57.1814 | 886.1401 | 469.044 | 305.4717 | 0 | 89.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:23 | 0.2 | 68572.49 | 5.7144 | 1771.3103 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | PkgHP | DXSZCap | 6.0073 | 1920.017 | 11044.96 | 2636.864 | 0 | 3720.005 | 1941.502 | 1440.368 | 0 | 69.7732 | 942.809 | 412.1996 | 429.8502 | 0 | 293.6506 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:23 | 1.9029 | 72087.23 | 6.0073 | 1838.5992 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | PkgHP | DXSZCap | 5.3796 | 1920.017 | 10522.59 | 2636.864 | 0 | 3720.005 | 2198.888 | 828.623 | 0 | 74.2685 | 858.3624 | 405.8078 | 357.1251 | 0 | 205.6015 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:24 | 1.2803 | 64555.07 | 5.3796 | 1956.0211 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | PkgHP | DXSZCap | 6.1999 | 1920.017 | 10045.18 | 2636.864 | 0 | 3720.005 | 1043.876 | 1653.26 | 0 | 41.5968 | 914.5531 | 251.9569 | 568.4484 | 0 | 35.0384 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:24 | 1.6719 | 74399.09 | 6.1999 | 1620.2101 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | PkgHP | DXSZCap | 5.9749 | 1920.017 | 9308.48 | 2636.864 | 0 | 3720.005 | 650.7612 | 1430.178 | 0 | 9.443 | 861.2448 | 203.3117 | 558.5414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:25 | 1.4578 | 71698.84 | 5.9749 | 1557.9298 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | PkgHP | DXSZCap | 6.3334 | 1920.017 | 10385.15 | 2636.864 | 0 | 3720.005 | 945.3198 | 2105.968 | 0 | 29.7335 | 939.1949 | 247.0519 | 613.8896 | 0 | 8.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:25 | 1.7482 | 76000.4 | 6.3334 | 1639.7519 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | PkgHP | DXSZCap | 8.2361 | 1920.017 | 11327.67 | 2636.864 | 0 | 3720.005 | 1252.986 | 2418.724 | 0 | 54.8106 | 1228.515 | 353.1826 | 760.4959 | 0 | 15.7808 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:25 | 2.3034 | 98833.13 | 8.2361 | 1375.3692 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | PkgHP | DXSZCap | 7.2139 | 1920.017 | 11323.51 | 2636.864 | 0 | 3720.005 | 1252.769 | 2490.37 | 0 | 65.9595 | 1089.745 | 315.3344 | 673.3276 | 0 | 67.8167 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:26 | 2.2643 | 86566.4 | 7.2139 | 1569.6866 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | PkgHP | DXSZCap | 7.4207 | 1920.017 | 12930.19 | 2636.864 | 0 | 3720.005 | 2429.49 | 2587.444 | 0 | 108.442 | 1190.629 | 520.267 | 569.9703 | 0 | 257.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:26 | 1.7303 | 89047.83 | 7.4207 | 1742.46 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | PkgHP | DXSZCap | 6.4017 | 1920.017 | 11829.97 | 2636.864 | 0 | 3720.005 | 2291.628 | 1790.81 | 0 | 87.0003 | 1014.677 | 479.5901 | 442.2947 | 0 | 288.9963 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:27 | 1.2291 | 76820.01 | 6.4017 | 1847.9513 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | PkgHP | DXSZCap | 7.3752 | 1920.017 | 12859.19 | 2636.864 | 0 | 3720.005 | 2127.654 | 2854.115 | 0 | 100.0728 | 1180.217 | 486.3208 | 614.4788 | 0 | 240.2815 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:27 | 1.3782 | 88502.91 | 7.3752 | 1743.5617 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | PkgHP | DXSZCap | 7.8501 | 1920.017 | 13376.52 | 2636.864 | 0 | 3720.005 | 2468.863 | 2853.298 | 0 | 127.8876 | 1266.062 | 508.1178 | 653.9103 | 0 | 303.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:28 | 2.426 | 94200.61 | 7.8501 | 1704.0043 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | PkgHP | DXSZCap | 10.5388 | 1920.017 | 15698.44 | 2636.864 | 0 | 3720.005 | 495.8239 | 7143.951 | 0 | 38.5569 | 1661.447 | 204.8416 | 1364.948 | 0 | 1.8117 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:28 | 3.1481 | 126466.1 | 10.5388 | 1489.5793 | 0 | 1
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | PkgHP | DXSZCap | 5.7895 | 1920.017 | 14835.67 | 2636.864 | 0 | 3720.005 | 5152.772 | 619.5067 | 0 | 133.0352 | 1062.116 | 769.316 | 239.251 | 0 | 1511.383 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:28 | 0.4054 | 69473.77 | 5.7895 | 2562.5217 | 0 | 1

## Msr_sim_annual
TechID | SizingID | BldgType | BldgVint | BldgLoc | BldgHVAC | tstat | normunit | numunits | measarea | kwh_tot | kwh_ltg | kwh_task | kwh_equip | kwh_htg | kwh_clg | kwh_twr | kwh_aux | kwh_vent | kwh_venthtg | kwh_ventclg | kwh_refg | kwh_hpsup | kwh_shw | kwh_ext | thm_tot | thm_equip | thm_htg | thm_shw | deskw_ltg | deskw_equ | lastmod | kW_49 | Cap_tons | Kwh/ton | therms/ton
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | 0 | DXSZCap | 109.851 | 50000.14 | 206745.1 | 80054.27 | 0 | 98033.33 | 0 | 2651.501 | 0 | 3227.303 | 22778.73 | 14411.17 | 2058.3 | 0 | 0 | 0 | 0 | 936658800 | 1761412 | 934897100 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:55 | 37.3733 | 109.851 | 1882.0499 | 85.2663
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | 0 | DXSZCap | 112.5433 | 50000.14 | 227699.4 | 80054.27 | 0 | 98033.33 | 0 | 24041.98 | 0 | 2608.769 | 22961.14 | 8793.971 | 7852.234 | 0 | 0 | 0 | 0 | 551483000 | 1761412 | 549720900 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:56 | 7.5026 | 112.5433 | 2023.2156 | 49.0018
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | 0 | DXSZCap | 130.341 | 50000.14 | 220398.8 | 80054.27 | 0 | 98033.33 | 0 | 13996.92 | 0 | 1749.483 | 26564.87 | 10949.27 | 7329.726 | 0 | 0 | 0 | 0 | 534556700 | 1761412 | 532794800 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:56 | 3.8575 | 130.341 | 1690.9401 | 41.0122
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | 0 | DXSZCap | 123.2136 | 50000.14 | 234126.2 | 80054.27 | 0 | 98033.33 | 0 | 29086.41 | 0 | 1894.083 | 25058.11 | 7745.735 | 10014.98 | 0 | 0 | 0 | 0 | 418397000 | 1761412 | 416634500 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:57 | 54.9408 | 123.2136 | 1900.1654 | 33.957
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | 0 | DXSZCap | 125.726 | 50000.14 | 220606.6 | 80054.27 | 0 | 98033.33 | 0 | 14615.26 | 0 | 2271.687 | 25632.18 | 9455.652 | 8034.652 | 0 | 0 | 0 | 0 | 499689500 | 1761412 | 497927100 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:58 | 41.8131 | 125.726 | 1754.662 | 39.7443
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | 0 | DXSZCap | 143.2119 | 50000.14 | 240229 | 80054.27 | 0 | 98033.33 | 0 | 31888.77 | 0 | 1138.67 | 29113.95 | 6178.471 | 13920.82 | 0 | 0 | 0 | 0 | 231001800 | 1761412 | 229240300 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:58 | 51.9541 | 143.2119 | 1677.4375 | 16.1301
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | 0 | DXSZCap | 140.913 | 50000.14 | 235215.5 | 80054.27 | 0 | 98033.33 | 0 | 28179.26 | 0 | 280.6552 | 28668.13 | 5717.607 | 13621.66 | 0 | 0 | 0 | 0 | 174093100 | 1761412 | 172331900 | 0 | 57.1128 | 53.8851 | 2019-06-11 18:59 | 46.7841 | 140.913 | 1669.2251 | 12.3547
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | 0 | DXSZCap | 139.4614 | 50000.14 | 249618.2 | 80054.27 | 0 | 98033.33 | 0 | 42269.25 | 0 | 815.1058 | 28446.21 | 5234.636 | 15088.58 | 0 | 0 | 0 | 0 | 198703300 | 1761412 | 196942000 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:00 | 52.9381 | 139.4614 | 1789.8727 | 14.2479
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | 0 | DXSZCap | 175.3999 | 50000.14 | 263301.4 | 80054.27 | 0 | 98033.33 | 0 | 47950.56 | 0 | 1507.366 | 35756.02 | 8071.608 | 17778.5 | 0 | 0 | 0 | 0 | 292065900 | 1761412 | 290303300 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:01 | 71.1343 | 175.3999 | 1501.1495 | 16.6514
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | 0 | DXSZCap | 150.7078 | 50000.14 | 261674 | 80054.27 | 0 | 98033.33 | 0 | 51021.34 | 0 | 1719.376 | 30845.75 | 6370.917 | 16434.33 | 0 | 0 | 0 | 0 | 246039200 | 1761412 | 244277300 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:01 | 70.5065 | 150.7078 | 1736.3004 | 16.3256
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | 0 | DXSZCap | 154.465 | 50000.14 | 264747.2 | 80054.27 | 0 | 98033.33 | 0 | 51279.08 | 0 | 3107.47 | 32273 | 10813.75 | 14060.65 | 0 | 0 | 0 | 0 | 566140000 | 1761412 | 564378300 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:02 | 25.948 | 154.465 | 1713.9629 | 36.6517
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | 0 | DXSZCap | 132.3875 | 50000.14 | 245439.9 | 80054.27 | 0 | 98033.33 | 0 | 37560.02 | 0 | 2512.049 | 27280.32 | 9425.339 | 11160.25 | 0 | 0 | 0 | 0 | 534499900 | 1761412 | 532738000 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:03 | 15.2588 | 132.3875 | 1853.9511 | 40.3739
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | 0 | DXSZCap | 152.8819 | 50000.14 | 269481.1 | 80054.27 | 0 | 98033.33 | 0 | 56682.21 | 0 | 2791.341 | 31920.11 | 9708.616 | 15003.86 | 0 | 0 | 0 | 0 | 498821700 | 1761412 | 497059500 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:04 | 20.313 | 152.8819 | 1762.675 | 32.6279
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | 0 | DXSZCap | 162.7306 | 50000.14 | 272243.2 | 80054.27 | 0 | 98033.33 | 0 | 56880.23 | 0 | 3531.242 | 33744.21 | 10244.01 | 15869.4 | 0 | 0 | 0 | 0 | 537446300 | 1761412 | 535685100 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:05 | 72.5065 | 162.7306 | 1672.9684 | 33.0267
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | 0 | DXSZCap | 221.8155 | 50000.14 | 363339.4 | 80054.27 | 0 | 98033.33 | 0 | 137694.2 | 0 | 988.2095 | 46569.34 | 4125.975 | 34020.48 | 0 | 0 | 0 | 0 | 105186900 | 1761412 | 103425700 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:06 | 96.1889 | 221.8155 | 1638.025 | 4.7421
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | 0 | DXSZCap | 131.0541 | 50000.14 | 223950.4 | 80054.27 | 0 | 98033.33 | 0 | 13687.05 | 0 | 4813.318 | 27362.48 | 15949.82 | 6066.948 | 0 | 0 | 0 | 0 | 1382925000 | 1761412 | 1381165000 | 0 | 57.1128 | 53.8851 | 2019-06-11 19:07 | 6.3153 | 131.0541 | 1708.8388 | 105.5232
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | 0 | DXSZCap | 350.8434 | 149998.6 | 693389.9 | 303095 | 0 | 287781.7 | 0 | 14102.6 | 0 | 10290.16 | 78121.19 | 45750.96 | 9900.916 | 0 | 0 | 0 | 0 | 2890751000 | 2641667 | 2888111000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:08 | 99.9022 | 350.8434 | 1976.3516 | 82.3943
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | 0 | DXSZCap | 359.435 | 149998.6 | 767427.1 | 303095 | 0 | 287781.7 | 0 | 87753.91 | 0 | 8299.216 | 80498.06 | 30275.16 | 28806.66 | 0 | 0 | 0 | 0 | 1826719000 | 2641667 | 1824076000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:09 | 62.5665 | 359.435 | 2135.0931 | 50.822
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | 0 | DXSZCap | 432.4231 | 149998.6 | 759380.8 | 303095 | 0 | 287781.7 | 0 | 67629.71 | 0 | 5793.188 | 95081.87 | 31693.04 | 33890.44 | 0 | 0 | 0 | 0 | 1472311000 | 2641667 | 1469669000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:10 | 39.1247 | 432.4231 | 1756.1058 | 34.0479
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | 0 | DXSZCap | 398.5807 | 149998.6 | 810268.1 | 303095 | 0 | 287781.7 | 0 | 123757 | 0 | 6110.732 | 89524.54 | 24864.8 | 40943.77 | 0 | 0 | 0 | 0 | 1264345000 | 2641667 | 1261703000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:11 | 159.2757 | 398.5807 | 2032.8835 | 31.7212
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | 0 | DXSZCap | 419.1716 | 149998.6 | 760910.1 | 303095 | 0 | 287781.7 | 0 | 70490.25 | 0 | 7556.715 | 91987.14 | 27683.62 | 36074.36 | 0 | 0 | 0 | 0 | 1375683000 | 2641667 | 1373042000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:12 | 116.4301 | 419.1716 | 1815.2711 | 32.8191
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | 0 | DXSZCap | 471.6901 | 149998.6 | 839081.3 | 303095 | 0 | 287781.7 | 0 | 140411 | 0 | 3741.535 | 104052.8 | 17130.66 | 57802.63 | 0 | 0 | 0 | 0 | 615404300 | 2641667 | 612763600 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:12 | 147.436 | 471.6901 | 1778.8825 | 13.0468
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | 0 | DXSZCap | 465.195 | 149998.6 | 830227.9 | 303095 | 0 | 287781.7 | 0 | 135800.8 | 0 | 923.5104 | 102627.4 | 13700.6 | 59312.16 | 0 | 0 | 0 | 0 | 415520100 | 2641667 | 412877500 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:13 | 131.7566 | 465.195 | 1784.688 | 8.9322
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | 0 | DXSZCap | 438.518 | 149998.6 | 871901.9 | 303095 | 0 | 287781.7 | 0 | 179667.4 | 0 | 2553.104 | 98805.45 | 15125.17 | 58314.12 | 0 | 0 | 0 | 0 | 542939800 | 2641667 | 540299100 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:14 | 151.1749 | 438.518 | 1988.2921 | 12.3812
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | 0 | DXSZCap | 535.2732 | 149998.6 | 914747.1 | 303095 | 0 | 287781.7 | 0 | 199149.2 | 0 | 4585.841 | 120136 | 22572.27 | 67927.67 | 0 | 0 | 0 | 0 | 758758800 | 2641667 | 756119100 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:15 | 208.2817 | 535.2732 | 1708.9349 | 14.1752
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | 0 | DXSZCap | 459.2544 | 149998.6 | 882053.4 | 303095 | 0 | 287781.7 | 0 | 182757.1 | 0 | 5224.691 | 103195.7 | 21146.54 | 56795.12 | 0 | 0 | 0 | 0 | 811996100 | 2641667 | 809355800 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:16 | 196.7731 | 459.2544 | 1920.6206 | 17.6807
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | 0 | DXSZCap | 462.8215 | 149998.6 | 895569.9 | 303095 | 0 | 287781.7 | 0 | 188512 | 0 | 9292.941 | 106889 | 34513.58 | 48989.32 | 0 | 0 | 0 | 0 | 1845784000 | 2641667 | 1843140000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:17 | 108.3889 | 462.8215 | 1935.0224 | 39.8811
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | 0 | DXSZCap | 410.1864 | 149998.6 | 829260.6 | 303095 | 0 | 287781.7 | 0 | 137583.8 | 0 | 7764.516 | 93036.75 | 31232.76 | 39855.92 | 0 | 0 | 0 | 0 | 1763763000 | 2641667 | 1761121000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:18 | 85.6289 | 410.1864 | 2021.6677 | 42.9991
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | 0 | DXSZCap | 461.8668 | 149998.6 | 912277.3 | 303095 | 0 | 287781.7 | 0 | 206225.1 | 0 | 8418.643 | 106757.5 | 31139.78 | 52754.64 | 0 | 0 | 0 | 0 | 1615428000 | 2641667 | 1612785000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:19 | 93.0768 | 461.8668 | 1975.1955 | 34.9761
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | 0 | DXSZCap | 491.1069 | 149998.6 | 911644.6 | 303095 | 0 | 287781.7 | 0 | 198159.5 | 0 | 10638.56 | 111970.4 | 33813.5 | 53819.32 | 0 | 0 | 0 | 0 | 1798834000 | 2641667 | 1796193000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:20 | 198.3111 | 491.1069 | 1856.3059 | 36.6282
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | 0 | DXSZCap | 649.8906 | 149998.6 | 1215077 | 303095 | 0 | 287781.7 | 0 | 469519.7 | 0 | 2890.032 | 151790.9 | 13735.58 | 112801.2 | 0 | 0 | 0 | 0 | 343731500 | 2641667 | 341089400 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:21 | 263.8159 | 649.8906 | 1869.6639 | 5.2891
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | 0 | DXSZCap | 421.0049 | 149998.6 | 763925.9 | 303095 | 0 | 287781.7 | 0 | 62080.11 | 0 | 15437.3 | 95532.63 | 51282.32 | 24684.86 | 0 | 0 | 0 | 0 | 4248440000 | 2641667 | 4245804000 | 0 | 164.4465 | 150.6356 | 2019-06-11 19:22 | 53.1131 | 421.0049 | 1814.5297 | 100.9119
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | 0 | DXSZCap | 4.7649 | 1920.017 | 11289 | 2636.864 | 0 | 3720.005 | 3360.81 | 56.5972 | 0 | 99.8839 | 831.7167 | 546.7828 | 46.8094 | 0 | 583.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:22 | 1.1908 | 4.7649 | 2369.1753 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | 0 | DXSZCap | 5.4135 | 1920.017 | 11004.85 | 2636.864 | 0 | 3720.005 | 2430.717 | 843.1398 | 0 | 90.5348 | 880.7369 | 423.5325 | 240.4753 | 0 | 402.869 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:23 | 0.7508 | 5.4135 | 2032.8377 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | 0 | DXSZCap | 5.7144 | 1920.017 | 9838.358 | 2636.864 | 0 | 3720.005 | 1929.212 | 513.8241 | 0 | 57.4957 | 890.2933 | 400.8652 | 207.408 | 0 | 90.6805 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:23 | 0.2 | 5.7144 | 1721.686 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | 0 | DXSZCap | 6.0073 | 1920.017 | 10645.08 | 2636.864 | 0 | 3720.005 | 1857.723 | 1114.437 | 0 | 69.9086 | 950.0203 | 358.626 | 333.4824 | 0 | 296.1404 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:23 | 2.1833 | 6.0073 | 1772.0331 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | 0 | DXSZCap | 5.3796 | 1920.017 | 10213.59 | 2636.864 | 0 | 3720.005 | 2114.895 | 600.8101 | 0 | 74.4219 | 861.1528 | 365.4283 | 236.1687 | 0 | 205.4707 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:24 | 1.4264 | 5.3796 | 1898.5818 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | 0 | DXSZCap | 6.1999 | 1920.017 | 9605.166 | 2636.864 | 0 | 3720.005 | 993.8417 | 1257.922 | 0 | 41.7379 | 919.5892 | 222.9863 | 418.0094 | 0 | 35.2242 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:24 | 1.914 | 6.1999 | 1549.2393 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | 0 | DXSZCap | 5.9749 | 1920.017 | 8937.721 | 2636.864 | 0 | 3720.005 | 612.5673 | 1092.417 | 0 | 9.4501 | 866.431 | 180.2246 | 399.577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:25 | 1.6543 | 5.9749 | 1495.8771 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | 0 | DXSZCap | 6.3334 | 1920.017 | 9878.795 | 2636.864 | 0 | 3720.005 | 888.1101 | 1649.368 | 0 | 29.8719 | 946.5986 | 214.4363 | 481.6676 | 0 | 7.9933 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:25 | 1.9897 | 6.3334 | 1559.8015 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | 0 | DXSZCap | 8.2361 | 1920.017 | 10784.15 | 2636.864 | 0 | 3720.005 | 1167.664 | 1952.548 | 0 | 55.1543 | 1235.841 | 307.4789 | 606.0241 | 0 | 16.0887 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:25 | 2.616 | 8.2361 | 1309.3767 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | 0 | DXSZCap | 7.2139 | 1920.017 | 10796.57 | 2636.864 | 0 | 3720.005 | 1173.16 | 2032.767 | 0 | 66.2292 | 1099.542 | 278.9431 | 552.2098 | 0 | 68.0169 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:26 | 2.5714 | 7.2139 | 1496.6412 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | 0 | DXSZCap | 7.4207 | 1920.017 | 12485.41 | 2636.864 | 0 | 3720.005 | 2291.31 | 2260.203 | 0 | 110.69 | 1202.743 | 450.3892 | 499.8365 | 0 | 263.6082 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:26 | 1.7403 | 7.4207 | 1682.5219 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | 0 | DXSZCap | 6.4017 | 1920.017 | 11407.9 | 2636.864 | 0 | 3720.005 | 2172.018 | 1470.55 | 0 | 88.0307 | 1025.859 | 415.6389 | 369.4002 | 0 | 294.5901 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:27 | 1.2351 | 6.4017 | 1782.0201 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | 0 | DXSZCap | 7.3752 | 1920.017 | 12398.58 | 2636.864 | 0 | 3720.005 | 2003.733 | 2497.737 | 0 | 101.7487 | 1193.772 | 415.1232 | 539.3811 | 0 | 244.7383 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:27 | 1.3847 | 7.3752 | 1681.1081 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | 0 | DXSZCap | 7.8501 | 1920.017 | 12908.98 | 2636.864 | 0 | 3720.005 | 2347.213 | 2489.021 | 0 | 129.9706 | 1277.147 | 446.0084 | 565.6339 | 0 | 308.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:27 | 2.7353 | 7.8501 | 1644.4454 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | 0 | DXSZCap | 10.5388 | 1920.017 | 15071.35 | 2636.864 | 0 | 3720.005 | 452.586 | 6541.396 | 0 | 39.0908 | 1679.624 | 176.1677 | 1251.034 | 0 | 1.8041 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:28 | 3.5361 | 10.5388 | 1430.0765 | 0
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | 0 | DXSZCap | 5.7895 | 1920.017 | 14462.08 | 2636.864 | 0 | 3720.005 | 4861.837 | 484.6637 | 0 | 138.7617 | 1079.024 | 696.0516 | 181.5639 | 0 | 1540.943 | 0 | 0 | 0 | 0 | 0 | 0 | 2.304 | 1.92 | 2019-06-11 19:28 | 0.4066 | 5.7895 | 2497.9926 | 0

## Std_sim_peakper
TechID | SizingID | BldgType | BldgVint | BldgLoc | BldgHVAC | tstat | bldg_kw25 | bldg_kw49
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | 0 | 82.3797 | 40.7637
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | 0 | 11.4689 | 7.4986
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | 0 | 7.1784 | 3.8569
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | 0 | 141.4122 | 73.4699
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | 0 | 103.5633 | 48.9463
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | 0 | 133.0373 | 69.2515
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | 0 | 122.1208 | 60.3922
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | 0 | 147.0249 | 71.2489
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | 0 | 186.3108 | 96.0003
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | 0 | 181.1461 | 92.2527
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | 0 | 29.7237 | 25.9427
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | 0 | 19.2759 | 15.223
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | 0 | 26.6143 | 20.309
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | 0 | 176.3572 | 93.4799
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | 0 | 217.631 | 120.9325
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | 0 | 8.9434 | 6.3127
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | 0 | 242.1776 | 112.2669
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | 0 | 75.8079 | 62.5839
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | 0 | 53.8739 | 39.1105
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | 0 | 428.1566 | 218.3507
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | 0 | 315.8644 | 145.9601
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | 0 | 401.3974 | 205.0211
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | 0 | 371.1776 | 179.7515
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | 0 | 439.6091 | 209.6513
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | 0 | 549.641 | 279.8537
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | 0 | 527.1792 | 264.2169
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | 0 | 115.2364 | 108.3695
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | 0 | 93.7171 | 85.6274
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | 0 | 105.886 | 93.0775
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | 0 | 508.4758 | 264.0119
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | 0 | 623.743 | 339.3057
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | 0 | 66.0299 | 53.1107
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | 0 | 3.1571 | 1.1507
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | 0 | 1.0003 | 0.74507
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | 0 | 0.421 | 0.2
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | 0 | 5.5704 | 1.9029
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | 0 | 4.025 | 1.2803
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | 0 | 5.0561 | 1.6719
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | 0 | 4.6238 | 1.4578
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | 0 | 5.7423 | 1.7482
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | 0 | 7.1774 | 2.3034
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | 0 | 7.0596 | 2.2643
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | 0 | 1.871 | 1.7303
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | 0 | 1.3937 | 1.2291
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | 0 | 1.6761 | 1.3782
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | 0 | 6.8026 | 2.426
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | 0 | 8.3546 | 3.1481
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | 0 | 0.64556 | 0.4054

## Msr_sim_peakper
TechID | SizingID | BldgType | BldgVint | BldgLoc | BldgHVAC | tstat | bldg_kw25 | bldg_kw49
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | 0 | 82.028 | 37.3733
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | 0 | 11.4711 | 7.5026
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | 0 | 7.1791 | 3.8575
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | 0 | 143.7262 | 54.9408
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | 0 | 104.4497 | 41.8131
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | 0 | 134.8997 | 51.9541
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | 0 | 123.6198 | 46.7841
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | 0 | 149.069 | 52.9381
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | 0 | 189.0688 | 71.1343
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | 0 | 184.1619 | 70.5065
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | 0 | 29.7292 | 25.948
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | 0 | 19.3258 | 15.2588
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | 0 | 26.6192 | 20.313
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | 0 | 179.4559 | 72.5065
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | 0 | 220.6897 | 96.1889
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | 0 | 8.9459 | 6.3153
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | 0 | 241.8831 | 99.9022
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | 0 | 75.8144 | 62.5665
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | 0 | 53.888 | 39.1247
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | 0 | 433.7989 | 159.2757
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | 0 | 319.0153 | 116.4301
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | 0 | 406.3492 | 147.436
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | 0 | 375.5416 | 131.7566
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | 0 | 444.768 | 151.1749
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | 0 | 555.59 | 208.2817
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | 0 | 533.943 | 196.7731
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | 0 | 115.2666 | 108.3889
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | 0 | 93.7198 | 85.6289
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | 0 | 106.1344 | 93.0768
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | 0 | 515.3374 | 198.3111
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | 0 | 629.5983 | 263.8159
MsrNResPkgAC-lt55-S15 | PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | 0 | 66.0294 | 53.1131
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | 0 | 2.6442 | 1.1908
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | 0 | 1.0081 | 0.7508
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | 0 | 0.421 | 0.2
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | 0 | 4.4054 | 2.1833
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | 0 | 3.0718 | 1.4264
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | 0 | 3.8801 | 1.914
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | 0 | 3.3909 | 1.6543
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | 0 | 4.5514 | 1.9897
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | 0 | 5.6936 | 2.616
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | 0 | 5.707 | 2.5714
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | 0 | 1.8808 | 1.7403
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | 0 | 1.3998 | 1.2351
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | 0 | 1.6831 | 1.3847
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | 0 | 5.4504 | 2.7353
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | 0 | 6.6232 | 3.5361
MsrNResPkgHP-lt55-S15-H8.2 | PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | 0 | 0.64733 | 0.4066

## Std_sizdat
TechID | BldgType | BldgVint | BldgLoc | BldgHVAC | BldgHVAC_2 | ParamID | ParamVal | lastmod | IntermediateParam | Inter_Val
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | AltAdjFactor | 1.0075 | 2019-06-12 00:13 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 5096 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 2980.345 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 5672.293 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 4012.11 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 879.4269 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 743.4388 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 189.8993 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 161.3583 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 241.8853 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 161.3583 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 394.2641 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 240.2176 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 425.8293 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 308.5275 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 104.301 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 64.354 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 125.619 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 105.0106 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 358.9877 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 890.1682 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 361.4607 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1034.494 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 908.6153 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 989.0789 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 745.3788 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 2241.116 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2551.377 | 2019-06-12 00:13 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 5096 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 2980.345 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 5672.293 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 4012.11 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 879.4269 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 743.4388 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 189.8993 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 161.3583 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 241.8853 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 161.3583 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 394.2641 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 240.2176 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 425.8293 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 308.5275 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 104.301 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 64.354 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 125.619 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 105.0106 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 358.9877 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 890.1682 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 361.4607 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1034.494 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 908.6153 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 989.0789 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 745.3788 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 2241.116 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2551.377 | 2019-06-12 00:13 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 5096 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 2980.345 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 5672.293 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 4012.11 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 879.4269 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 743.4388 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 189.8993 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 161.3583 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 241.8853 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 161.3583 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 394.2641 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 240.2176 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 425.8293 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 308.5275 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 104.301 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 64.354 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 125.619 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 105.0106 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 358.9877 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 890.1682 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 361.4607 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1034.494 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 908.6153 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 989.0789 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 745.3788 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 2241.116 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2551.377 | 2019-06-12 00:13 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 5096 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 2980.345 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 5672.293 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 4012.11 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 879.4269 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 743.4388 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 189.8993 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 161.3583 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 241.8853 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 161.3583 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 394.2641 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 240.2176 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 425.8293 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 308.5275 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 104.301 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 64.354 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 125.619 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 105.0106 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 358.9877 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 890.1682 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 361.4607 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1034.494 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 908.6153 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 989.0789 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 745.3788 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 2241.116 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2551.377 | 2019-06-12 00:13 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 220708.5 | 2019-06-12 00:13 | ClCap | 220708.5
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 129079.2 | 2019-06-12 00:13 | ClCap | 129079.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 245667.9 | 2019-06-12 00:13 | ClCap | 245667.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 173765.1 | 2019-06-12 00:13 | ClCap | 173765.1
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 29926.37 | 2019-06-12 00:13 | ClCap | 29926.37
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 25298.78 | 2019-06-12 00:13 | ClCap | 25298.78
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 8224.566 | 2019-06-12 00:13 | ClCap | 8224.566
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 6988.452 | 2019-06-12 00:13 | ClCap | 6988.452
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 10476.09 | 2019-06-12 00:13 | ClCap | 10476.09
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 6988.452 | 2019-06-12 00:13 | ClCap | 6988.452
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 13416.57 | 2019-06-12 00:13 | ClCap | 13416.57
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 8174.46 | 2019-06-12 00:13 | ClCap | 8174.46
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 14490.71 | 2019-06-12 00:13 | ClCap | 14490.71
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 10499.01 | 2019-06-12 00:13 | ClCap | 10499.01
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 3549.3 | 2019-06-12 00:13 | ClCap | 3549.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 2189.929 | 2019-06-12 00:13 | ClCap | 2189.929
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 4274.738 | 2019-06-12 00:13 | ClCap | 4274.738
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 3573.448 | 2019-06-12 00:13 | ClCap | 3573.448
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 12216.14 | 2019-06-12 00:13 | ClCap | 12216.14
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 30291.89 | 2019-06-12 00:13 | ClCap | 30291.89
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 12300.29 | 2019-06-12 00:13 | ClCap | 12300.29
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 35203.21 | 2019-06-12 00:13 | ClCap | 35203.21
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 30919.63 | 2019-06-12 00:13 | ClCap | 30919.63
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 33657.76 | 2019-06-12 00:13 | ClCap | 33657.76
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 25364.79 | 2019-06-12 00:13 | ClCap | 25364.79
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 76263.84 | 2019-06-12 00:13 | ClCap | 76263.84
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 144703.1 | 2019-06-12 00:13 | ClCap | 144703.1
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -287787.8 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -204090.3 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -309401.5 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -247103.5 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -36775.16 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -38232.38 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -12859.48 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -11049.61 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -14647.34 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -11049.61 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -17814.61 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -12087.1 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -18980.63 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -14657.05 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -5784.496 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -4273.415 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -6577.574 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -5810.87 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -17884.3 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -37290.63 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -18316.62 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -41584.85 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -37896.88 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -42579.07 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -38088.19 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -153468.8 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -174715.1 | 2019-06-12 00:13 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | AltAdjFactor | 1.0046 | 2019-06-12 00:14 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 4562.629 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 3817.738 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 5083.024 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 4966.482 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 856.8878 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 800.9102 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 223.5593 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 154.0373 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 243.9286 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 224.3347 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 378.1376 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 308.3815 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 410.4385 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 377.6913 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 125.2504 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 88.2199 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 155.6033 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 156.9307 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 436.4927 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 848.9396 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 568.4436 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 997.9329 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1037.562 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 561.7641 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 362.2282 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 3893.25 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 1605.167 | 2019-06-12 00:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 6171.917 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 3907.617 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 6415.167 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 5124.587 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 909.2984 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 800.9101 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 254.6079 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 164.3748 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 294.7144 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 224.3347 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 443.428 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 308.3815 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 460.4708 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 377.6913 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 145.0373 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 88.2199 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 157.3281 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 156.9307 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 436.4927 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1024.746 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 568.4436 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1138.944 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1087.098 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 986.2438 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 743.2422 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 3893.25 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2544.064 | 2019-06-12 00:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 4562.629 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 3817.738 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 5083.024 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 4966.482 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 856.8878 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 800.9101 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 223.5593 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 154.0373 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 243.9286 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 224.3347 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 378.1376 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 308.3815 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 410.4385 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 377.6913 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 125.2504 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 88.2199 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 155.6033 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 156.9307 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 436.4927 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 848.9396 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 568.4436 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 997.9329 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1037.562 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 561.7641 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 362.2282 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 3893.25 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 1605.167 | 2019-06-12 00:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 4562.629 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 3817.738 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 5083.024 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 4966.482 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 856.8878 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 800.9101 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 223.5593 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 154.0373 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 243.9286 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 224.3347 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 378.1376 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 308.3815 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 410.4385 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 377.6913 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 125.2504 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 88.2199 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 155.6033 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 156.9307 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 436.4927 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 848.9396 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 568.4436 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 997.9329 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1037.562 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 561.7641 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 362.2282 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 3893.25 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 1605.167 | 2019-06-12 00:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 198176.2 | 2019-06-12 00:14 | ClCap | 198176.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 165822.1 | 2019-06-12 00:14 | ClCap | 165822.1
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 220779.4 | 2019-06-12 00:14 | ClCap | 220779.4
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 215717.4 | 2019-06-12 00:14 | ClCap | 215717.4
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 29243.2 | 2019-06-12 00:14 | ClCap | 29243.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 27332.84 | 2019-06-12 00:14 | ClCap | 27332.84
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 9710.22 | 2019-06-12 00:14 | ClCap | 9710.22
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 6690.555 | 2019-06-12 00:14 | ClCap | 6690.555
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 10594.95 | 2019-06-12 00:14 | ClCap | 10594.95
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 9743.896 | 2019-06-12 00:14 | ClCap | 9743.896
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 12904.79 | 2019-06-12 00:14 | ClCap | 12904.79
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 10524.2 | 2019-06-12 00:14 | ClCap | 10524.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 14007.13 | 2019-06-12 00:14 | ClCap | 14007.13
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 12889.56 | 2019-06-12 00:14 | ClCap | 12889.56
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 4274.449 | 2019-06-12 00:14 | ClCap | 4274.449
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 3010.701 | 2019-06-12 00:14 | ClCap | 3010.701
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 5310.309 | 2019-06-12 00:14 | ClCap | 5310.309
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 5355.608 | 2019-06-12 00:14 | ClCap | 5355.608
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 14896.28 | 2019-06-12 00:14 | ClCap | 14896.28
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 28971.95 | 2019-06-12 00:14 | ClCap | 28971.95
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 19399.4 | 2019-06-12 00:14 | ClCap | 19399.4
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 34056.68 | 2019-06-12 00:14 | ClCap | 34056.68
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 35409.11 | 2019-06-12 00:14 | ClCap | 35409.11
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 19171.45 | 2019-06-12 00:14 | ClCap | 19171.45
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 12361.84 | 2019-06-12 00:14 | ClCap | 12361.84
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 132865.8 | 2019-06-12 00:14 | ClCap | 132865.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 91299.8 | 2019-06-12 00:14 | ClCap | 91299.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -340249.9 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -256176.3 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -349623.5 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -301942.6 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -38205.81 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -41670.11 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -15900.47 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -11966.44 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -17242.77 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -14903.22 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -19999.76 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -15223.01 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -20637.73 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -17752.18 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -7557.18 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -6010.932 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -8009.514 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -8189.142 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -21749.63 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -42601.64 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -26979.07 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -45782.07 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -44658.16 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -43012.03 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -39441.2 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -248317.2 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -185207.2 | 2019-06-12 00:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | AltAdjFactor | 1.0003 | 2019-06-12 00:16 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 6245.756 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 3650.958 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 6604.435 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 5234.046 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 893.4185 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 760.2932 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 257.7383 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 160.1927 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 309.8002 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 226.3571 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 451.8203 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 277.861 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 473.4864 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 372.2928 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 152.3387 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 69.0247 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 166.5452 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 147.9349 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 389.5717 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1110.717 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 483.2687 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1207.214 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1132.437 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 981.9342 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 739.9945 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 2721.943 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2532.947 | 2019-06-12 00:16 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 6245.756 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 3650.958 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 6604.435 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 5234.046 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 893.4185 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 760.2932 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 257.7383 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 160.1927 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 309.8002 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 226.3571 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 451.8203 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 277.861 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 473.4864 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 372.2928 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 152.3387 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 69.0247 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 166.5452 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 147.9349 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 389.5717 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1110.717 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 483.2687 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1207.214 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1132.437 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 981.9342 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 739.9945 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 2721.943 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2532.947 | 2019-06-12 00:16 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 6245.756 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 3650.958 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 6604.435 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 5234.046 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 893.4185 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 760.2932 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 257.7383 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 160.1927 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 309.8002 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 226.3571 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 451.8203 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 277.861 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 473.4864 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 372.2928 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 152.3387 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 69.0247 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 166.5452 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 147.9349 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 389.5717 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1110.717 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 483.2687 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1207.214 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1132.437 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 981.9343 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 739.9945 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 2721.943 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2532.947 | 2019-06-12 00:16 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 6245.756 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 3650.958 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 6604.435 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 5234.046 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 893.4185 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 760.2932 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 257.7383 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 160.1927 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 309.8002 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 226.3571 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 451.8203 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 277.861 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 473.4864 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 372.2928 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 152.3387 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 69.0247 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 166.5452 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 147.9349 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 389.5717 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1110.717 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 483.2687 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1207.214 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1132.437 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 981.9342 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 739.9945 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 2721.943 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2532.947 | 2019-06-12 00:16 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 272472.8 | 2019-06-12 00:16 | ClCap | 272472.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 159274 | 2019-06-12 00:16 | ClCap | 159274
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 288120.3 | 2019-06-12 00:16 | ClCap | 288120.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 228336.7 | 2019-06-12 00:16 | ClCap | 228336.7
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 30623.71 | 2019-06-12 00:16 | ClCap | 30623.71
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 26060.57 | 2019-06-12 00:16 | ClCap | 26060.57
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 11243.9 | 2019-06-12 00:16 | ClCap | 11243.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 6988.452 | 2019-06-12 00:16 | ClCap | 6988.452
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 13515.12 | 2019-06-12 00:16 | ClCap | 13515.12
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 9874.891 | 2019-06-12 00:16 | ClCap | 9874.891
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 15487.05 | 2019-06-12 00:16 | ClCap | 15487.05
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 9524.241 | 2019-06-12 00:16 | ClCap | 9524.241
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 16229.69 | 2019-06-12 00:16 | ClCap | 16229.69
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 12761.08 | 2019-06-12 00:16 | ClCap | 12761.08
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 5221.715 | 2019-06-12 00:16 | ClCap | 5221.715
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 2365.96 | 2019-06-12 00:16 | ClCap | 2365.96
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 5708.67 | 2019-06-12 00:16 | ClCap | 5708.67
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 5070.765 | 2019-06-12 00:16 | ClCap | 5070.765
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 13353.35 | 2019-06-12 00:16 | ClCap | 13353.35
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 38072.05 | 2019-06-12 00:16 | ClCap | 38072.05
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 16565 | 2019-06-12 00:16 | ClCap | 16565
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 41379.67 | 2019-06-12 00:16 | ClCap | 41379.67
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 38816.53 | 2019-06-12 00:16 | ClCap | 38816.53
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 33657.76 | 2019-06-12 00:16 | ClCap | 33657.76
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 25364.79 | 2019-06-12 00:16 | ClCap | 25364.79
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 93300.04 | 2019-06-12 00:16 | ClCap | 93300.04
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 144703 | 2019-06-12 00:16 | ClCap | 144703
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -328688.5 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -232175.5 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -342161.5 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -291762.7 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -37045.05 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -38579.68 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -15153.7 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -10947.88 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -16896.71 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -14070.31 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -19829.71 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -13461.05 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -20647.15 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -16961.73 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -7542.767 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -4431.923 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -8061.92 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -7381.836 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -18958.79 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -44917.82 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -22935.68 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -47582.28 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -45625.56 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -42057.42 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -37776.17 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -173319.6 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -173106.5 | 2019-06-12 00:16 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | AltAdjFactor | 1.005 | 2019-06-12 00:55 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 4712.105 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 4113.98 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 6061.524 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 5436.944 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 869.8976 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 925.342 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 228.0329 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 173.7535 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 292.5548 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 244.4038 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 405.5515 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 328.7522 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 474.7834 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 416.4435 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 140.9788 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 100.0111 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 180.5259 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 176.8554 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 442.7514 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 962.4164 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 625.8412 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1129.552 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1184.015 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 598.6387 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 397.2014 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 4222.142 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 1618.142 | 2019-06-12 00:55 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 6778.763 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 4338.713 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 7057.917 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 5836.586 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 918.4704 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 997.8939 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 287.6129 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 186.3384 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 337.9355 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 257.6222 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 478.3902 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 328.7522 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 496.4036 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 416.4435 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 169.0451 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 100.0111 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 181.6376 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 176.8554 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 442.7514 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1189.13 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 625.8412 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1273.025 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1243.763 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 986.6068 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 743.5158 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 4222.142 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2545 | 2019-06-12 00:55 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 4712.105 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 4113.98 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 6061.524 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 5436.944 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 869.8976 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 925.342 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 228.0329 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 173.7535 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 292.5548 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 244.4038 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 405.5515 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 328.7522 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 474.7834 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 416.4435 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 140.9788 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 100.0111 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 180.5259 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 176.8554 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 442.7514 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 962.4164 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 625.8412 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1129.552 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1184.015 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 598.6387 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 397.2014 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 4222.142 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 1618.142 | 2019-06-12 00:55 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 4712.105 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 4113.98 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 6061.524 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 5436.944 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 869.8976 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 925.342 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 228.0329 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 173.7535 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 292.5548 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 244.4038 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 405.5515 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 328.7522 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 474.7834 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 416.4435 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 140.9788 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 100.0111 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 180.5259 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 176.8554 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 442.7514 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 962.4164 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 625.8412 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1129.552 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1184.015 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 598.6387 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 397.2014 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 4222.142 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 1618.142 | 2019-06-12 00:55 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 204593.3 | 2019-06-12 00:55 | ClCap | 204593.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 178623.5 | 2019-06-12 00:55 | ClCap | 178623.5
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 263183.3 | 2019-06-12 00:55 | ClCap | 263183.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 236064.8 | 2019-06-12 00:55 | ClCap | 236064.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 29676.27 | 2019-06-12 00:55 | ClCap | 29676.27
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 31567.73 | 2019-06-12 00:55 | ClCap | 31567.73
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 9900.882 | 2019-06-12 00:55 | ClCap | 9900.882
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 7544.145 | 2019-06-12 00:55 | ClCap | 7544.145
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 12702.34 | 2019-06-12 00:55 | ClCap | 12702.34
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 10611.69 | 2019-06-12 00:55 | ClCap | 10611.69
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 13835.25 | 2019-06-12 00:55 | ClCap | 13835.25
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 11215.27 | 2019-06-12 00:55 | ClCap | 11215.27
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 16197.08 | 2019-06-12 00:55 | ClCap | 16197.08
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 14206.83 | 2019-06-12 00:55 | ClCap | 14206.83
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 4809.445 | 2019-06-12 00:55 | ClCap | 4809.445
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 3411.844 | 2019-06-12 00:55 | ClCap | 3411.844
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 6158.582 | 2019-06-12 00:55 | ClCap | 6158.582
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 6033.363 | 2019-06-12 00:55 | ClCap | 6033.363
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 15104.32 | 2019-06-12 00:55 | ClCap | 15104.32
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 32832.51 | 2019-06-12 00:55 | ClCap | 32832.51
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 21350.37 | 2019-06-12 00:55 | ClCap | 21350.37
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 38534.27 | 2019-06-12 00:55 | ClCap | 38534.27
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 40392.29 | 2019-06-12 00:55 | ClCap | 40392.29
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 20422.36 | 2019-06-12 00:55 | ClCap | 20422.36
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 13550.39 | 2019-06-12 00:55 | ClCap | 13550.39
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 144037 | 2019-06-12 00:55 | ClCap | 144037
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 92003.96 | 2019-06-12 00:55 | ClCap | 92003.96
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -360514.3 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -272058.3 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -370453.7 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -326917.5 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -38013.96 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -48555 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -17021.14 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -13531.28 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -18660.25 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -16002.15 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -21024.03 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -15796 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -21664.19 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -18929.51 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -8395.211 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -6293.363 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -8849.014 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -8817.48 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -21757.48 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -48013.56 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -28845.59 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -50032.88 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -49773.96 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -42341.2 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -39239.77 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -251835.3 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -185442.6 | 2019-06-12 00:55 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | AltAdjFactor | 1.0094 | 2019-06-12 00:56 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 5919.149 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 3419.23 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 6722.22 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 5066.168 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 889.746 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 744.808 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 236.9618 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 161.6555 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 319.9128 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 216.323 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 434.9097 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 266.4446 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 479.3852 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 367.5741 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 138.2313 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 67.1505 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 170.2032 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 143.4422 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 375.1988 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1061.405 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 444.9176 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1213.284 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1121.74 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 990.9004 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 746.7515 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 2422.552 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2556.076 | 2019-06-12 00:56 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 5919.149 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 3419.23 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 6722.22 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 5066.168 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 889.746 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 744.808 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 236.9618 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 161.6555 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 319.9128 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 216.323 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 434.9097 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 266.4446 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 479.3852 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 367.5741 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 138.2313 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 67.1505 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 170.2032 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 143.4422 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 375.1988 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1061.405 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 444.9176 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1213.284 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1121.74 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 990.9004 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 746.7515 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 2422.552 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2556.076 | 2019-06-12 00:56 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 5919.149 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 3419.23 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 6722.22 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 5066.168 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 889.746 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 744.808 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 236.9618 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 161.6555 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 319.9128 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 216.323 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 434.9097 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 266.4446 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 479.3852 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 367.5741 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 138.2313 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 67.1505 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 170.2032 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 143.4422 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 375.1988 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1061.405 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 444.9176 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1213.284 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1121.74 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 990.9003 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 746.7515 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 2422.552 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2556.076 | 2019-06-12 00:56 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 5919.149 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 3419.23 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 6722.22 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 5066.168 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 889.746 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 744.808 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 236.9618 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 161.6555 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 319.9128 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 216.323 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 434.9097 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 266.4446 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 479.3852 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 367.5741 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 138.2313 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 67.1505 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 170.2032 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 143.4422 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 375.1988 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1061.405 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 444.9176 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1213.284 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1121.74 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 990.9004 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 746.7515 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 2422.552 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2556.076 | 2019-06-12 00:56 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 255887.9 | 2019-06-12 00:56 | ClCap | 255887.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 147815.1 | 2019-06-12 00:56 | ClCap | 147815.1
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 290605.1 | 2019-06-12 00:56 | ClCap | 290605.1
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 219013.1 | 2019-06-12 00:56 | ClCap | 219013.1
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 30221.86 | 2019-06-12 00:56 | ClCap | 30221.86
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 25298.78 | 2019-06-12 00:56 | ClCap | 25298.78
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 10243.98 | 2019-06-12 00:56 | ClCap | 10243.98
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 6988.451 | 2019-06-12 00:56 | ClCap | 6988.451
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 13830 | 2019-06-12 00:56 | ClCap | 13830
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 9351.757 | 2019-06-12 00:56 | ClCap | 9351.757
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 14772.51 | 2019-06-12 00:56 | ClCap | 14772.51
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 9050.282 | 2019-06-12 00:56 | ClCap | 9050.282
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 16283.2 | 2019-06-12 00:56 | ClCap | 16283.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 12485.33 | 2019-06-12 00:56 | ClCap | 12485.33
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 4695.281 | 2019-06-12 00:56 | ClCap | 4695.281
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 2280.89 | 2019-06-12 00:56 | ClCap | 2280.89
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 5781.266 | 2019-06-12 00:56 | ClCap | 5781.266
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 4872.279 | 2019-06-12 00:56 | ClCap | 4872.279
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 12744.32 | 2019-06-12 00:56 | ClCap | 12744.32
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 36052.58 | 2019-06-12 00:56 | ClCap | 36052.58
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 15112.45 | 2019-06-12 00:56 | ClCap | 15112.45
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 41211.42 | 2019-06-12 00:56 | ClCap | 41211.42
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 38101.96 | 2019-06-12 00:56 | ClCap | 38101.96
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 33657.76 | 2019-06-12 00:56 | ClCap | 33657.76
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 25364.79 | 2019-06-12 00:56 | ClCap | 25364.79
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 82286.43 | 2019-06-12 00:56 | ClCap | 82286.43
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 144703 | 2019-06-12 00:56 | ClCap | 144703
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -315153.5 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -224557.8 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -343602.5 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -284764.6 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -36101.61 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -37644.01 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -14496.28 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -11096.6 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -17202.91 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -13798.5 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -18831.26 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -12835.07 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -20393.89 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -16460.13 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -6966.142 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -4385.108 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -8098.635 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -7151.4 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -18290.79 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -42703.4 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -21293.57 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -46872.81 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -44660.48 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -41261.99 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -37671.23 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -166292.4 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -175458 | 2019-06-12 00:56 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | AltAdjFactor | 1.0033 | 2019-06-12 00:57 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 6680.472 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 4214.374 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 7185.158 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 5813.997 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 919.1714 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 1056.162 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 285.4041 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 185.7887 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 348.5514 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 251.6366 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 470.4729 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 311.2821 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 500.6957 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 404.3114 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 168.0089 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 79.0402 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 185.556 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 164.0109 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 420.3329 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1200.548 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 566.1732 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1277.04 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1236.043 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 984.9019 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 742.231 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 3593.985 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2540.602 | 2019-06-12 00:57 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 6680.472 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 4214.374 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 7185.158 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 5813.997 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 919.1714 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 1056.162 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 285.4041 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 185.7887 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 348.5514 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 251.6366 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 470.4729 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 311.2821 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 500.6957 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 404.3114 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 168.0089 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 79.0402 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 185.556 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 164.0109 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 420.3329 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1200.548 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 566.1732 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1277.04 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1236.043 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 984.9019 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 742.231 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 3593.985 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2540.602 | 2019-06-12 00:57 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 6680.471 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 4214.374 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 7185.158 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 5813.997 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 919.1714 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 1056.162 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 285.4041 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 185.7887 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 348.5514 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 251.6366 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 470.4729 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 311.2821 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 500.6957 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 404.3114 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 168.0089 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 79.0402 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 185.556 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 164.0109 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 420.3329 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1200.548 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 566.1732 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1277.04 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1236.043 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 984.9019 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 742.231 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 3593.985 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2540.602 | 2019-06-12 00:57 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 6680.472 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 4214.374 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 7185.158 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 5813.997 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 919.1714 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 1056.162 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 285.4041 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 185.7887 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 348.5514 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 251.6366 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 470.4729 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 311.2821 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 500.6957 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 404.3114 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 168.0089 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 79.0402 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 185.556 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 164.0109 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 420.3329 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1200.548 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 566.1732 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1277.04 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1236.043 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 984.9019 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 742.231 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 3593.985 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2540.602 | 2019-06-12 00:57 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 290559.3 | 2019-06-12 00:57 | ClCap | 290559.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 183299.3 | 2019-06-12 00:57 | ClCap | 183299.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 312510 | 2019-06-12 00:57 | ClCap | 312510
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 252873 | 2019-06-12 00:57 | ClCap | 252873
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 31411.51 | 2019-06-12 00:57 | ClCap | 31411.51
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 36092.98 | 2019-06-12 00:57 | ClCap | 36092.98
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 12413.32 | 2019-06-12 00:57 | ClCap | 12413.32
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 8080.661 | 2019-06-12 00:57 | ClCap | 8080.661
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 15159.84 | 2019-06-12 00:57 | ClCap | 15159.84
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 10944.64 | 2019-06-12 00:57 | ClCap | 10944.64
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 16077.81 | 2019-06-12 00:57 | ClCap | 16077.81
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 10637.67 | 2019-06-12 00:57 | ClCap | 10637.67
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 17110.64 | 2019-06-12 00:57 | ClCap | 17110.64
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 13816.83 | 2019-06-12 00:57 | ClCap | 13816.83
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 5741.491 | 2019-06-12 00:57 | ClCap | 5741.491
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 2701.096 | 2019-06-12 00:57 | ClCap | 2701.096
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 6341.138 | 2019-06-12 00:57 | ClCap | 6341.138
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 5604.862 | 2019-06-12 00:57 | ClCap | 5604.862
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 14364.34 | 2019-06-12 00:57 | ClCap | 14364.34
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 41027.18 | 2019-06-12 00:57 | ClCap | 41027.18
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 19348.24 | 2019-06-12 00:57 | ClCap | 19348.24
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 43641.22 | 2019-06-12 00:57 | ClCap | 43641.22
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 42240.2 | 2019-06-12 00:57 | ClCap | 42240.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 33657.76 | 2019-06-12 00:57 | ClCap | 33657.76
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 25364.79 | 2019-06-12 00:57 | ClCap | 25364.79
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 122819.9 | 2019-06-12 00:57 | ClCap | 122819.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 144703 | 2019-06-12 00:57 | ClCap | 144703
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -331663.2 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -241700.9 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -350891.9 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -300650.8 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -37191.82 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -48214.73 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -15427.76 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -11960.14 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -17514.58 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -14267.82 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -20057.89 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -14300.86 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -21232.21 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -17686.26 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -7884.734 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -4590.956 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -8523.221 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -7740.151 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -19363.85 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -46145.89 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -25187.43 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -48258.04 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -48002.46 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -41411.1 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -36697.17 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -189106.7 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -163947.3 | 2019-06-12 00:57 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | AltAdjFactor | 1.0005 | 2019-06-12 00:59 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 6642.29 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 4104.396 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 7006.067 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 5714.627 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 914.3396 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 998.9053 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 285.2718 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 182.1912 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 340.8684 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 250.0691 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 467.7229 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 304.034 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 490.3607 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 398.2288 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 168.5745 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 74.2922 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 179.1983 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 160.5607 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 413.0598 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1201.146 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 531.9589 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1233.771 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1217.394 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 982.1872 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 740.1852 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 3431.574 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2533.6 | 2019-06-12 00:59 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 6642.29 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 4104.396 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 7006.067 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 5714.627 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 914.3396 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 998.9053 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 285.2718 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 182.1912 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 340.8684 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 250.0691 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 467.7229 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 304.034 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 490.3607 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 398.2288 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 168.5745 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 74.2922 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 179.1983 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 160.5607 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 413.0598 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1201.146 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 531.9589 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1233.771 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1217.394 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 982.1872 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 740.1852 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 3431.574 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2533.6 | 2019-06-12 00:59 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 6642.29 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 4104.396 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 7006.067 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 5714.627 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 914.3396 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 998.9053 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 285.2718 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 182.1912 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 340.8684 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 250.0691 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 467.7229 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 304.034 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 490.3607 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 398.2288 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 168.5745 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 74.2922 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 179.1983 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 160.5607 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 413.0598 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1201.146 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 531.9589 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1233.771 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1217.394 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 982.1871 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 740.1852 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 3431.574 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2533.6 | 2019-06-12 00:59 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 6642.29 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 4104.396 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 7006.067 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 5714.627 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 914.3396 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 998.9053 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 285.2718 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 182.1912 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 340.8684 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 250.0691 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 467.7229 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 304.034 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 490.3607 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 398.2288 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 168.5745 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 74.2922 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 179.1983 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 160.5607 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 413.0598 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1201.146 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 531.9589 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1233.771 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1217.394 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 982.1872 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 740.1852 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 3431.574 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2533.6 | 2019-06-12 00:59 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 289697.1 | 2019-06-12 00:59 | ClCap | 289697.1
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 179009.3 | 2019-06-12 00:59 | ClCap | 179009.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 305562.9 | 2019-06-12 00:59 | ClCap | 305562.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 249238 | 2019-06-12 00:59 | ClCap | 249238
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 31332.75 | 2019-06-12 00:59 | ClCap | 31332.75
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 34230.66 | 2019-06-12 00:59 | ClCap | 34230.66
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 12441.85 | 2019-06-12 00:59 | ClCap | 12441.85
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 7946.093 | 2019-06-12 00:59 | ClCap | 7946.093
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 14866.65 | 2019-06-12 00:59 | ClCap | 14866.65
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 10906.52 | 2019-06-12 00:59 | ClCap | 10906.52
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 16028.01 | 2019-06-12 00:59 | ClCap | 16028.01
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 10418.69 | 2019-06-12 00:59 | ClCap | 10418.69
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 16803.76 | 2019-06-12 00:59 | ClCap | 16803.76
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 13646.57 | 2019-06-12 00:59 | ClCap | 13646.57
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 5776.741 | 2019-06-12 00:59 | ClCap | 5776.741
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 2545.856 | 2019-06-12 00:59 | ClCap | 2545.856
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 6140.797 | 2019-06-12 00:59 | ClCap | 6140.797
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 5502.123 | 2019-06-12 00:59 | ClCap | 5502.123
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 14154.81 | 2019-06-12 00:59 | ClCap | 14154.81
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 41161.09 | 2019-06-12 00:59 | ClCap | 41161.09
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 18229.26 | 2019-06-12 00:59 | ClCap | 18229.26
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 42279.09 | 2019-06-12 00:59 | ClCap | 42279.09
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 41717.88 | 2019-06-12 00:59 | ClCap | 41717.88
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 33657.76 | 2019-06-12 00:59 | ClCap | 33657.76
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 25364.79 | 2019-06-12 00:59 | ClCap | 25364.79
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 117593.8 | 2019-06-12 00:59 | ClCap | 117593.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 144703 | 2019-06-12 00:59 | ClCap | 144703
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -307606.2 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -216327.5 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -321464.9 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -275091.5 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -35764.51 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -43552.07 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -14122.05 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -10544.42 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -15962.23 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -12932.04 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -19151.64 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -13277.39 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -19998.88 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -16684.52 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -7439.43 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -4000.232 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -7822.014 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -7153.922 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -17931.04 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -44935.71 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -22684.29 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -44753.96 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -45741.97 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -39815.36 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -34177.75 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -168201.1 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -146633.6 | 2019-06-12 00:59 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | AltAdjFactor | 1.0147 | 2019-06-12 01:00 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 5961.522 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 4825.87 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 6334.603 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 6038.367 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 942.7163 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 1053.955 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 278.7255 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 221.577 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 306.2961 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 282.2731 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 481.7601 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 372.6822 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 495.1383 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 455.2543 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 180.1947 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 118.6199 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 189.022 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 198.6828 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 482.2986 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1112.467 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 685.8225 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1154.757 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1250.86 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 686.6749 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 399.366 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 4952.837 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2071.254 | 2019-06-12 01:00 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 7059.95 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 4825.87 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 7531.143 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 6160.549 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 942.7163 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 1142.48 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 307.1869 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 221.577 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 368.8402 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 282.2731 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 492.4019 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 372.6822 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 520.5759 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 455.2543 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 180.1946 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 118.6199 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 196.7743 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 198.6828 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 482.2986 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1246.773 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 685.8225 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1339.059 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1302.231 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 996.092 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 750.6639 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 4952.837 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2569.468 | 2019-06-12 01:00 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 5961.522 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 4825.87 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 6334.603 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 6038.367 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 942.7163 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 1053.955 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 278.7255 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 221.577 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 306.2961 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 282.2731 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 481.7601 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 372.6822 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 495.1383 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 455.2543 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 180.1946 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 118.6199 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 189.022 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 198.6828 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 482.2986 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1112.467 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 685.8225 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1154.757 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1250.86 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 686.675 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 399.366 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 4952.837 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2071.254 | 2019-06-12 01:00 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 5961.522 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 4825.87 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 6334.603 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 6038.367 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 942.7163 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 1053.955 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 278.7255 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 221.577 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 306.2961 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 282.2731 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 481.7601 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 372.6822 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 495.1383 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 455.2543 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 180.1946 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 118.6199 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 189.022 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 198.6828 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 482.2986 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1112.467 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 685.8225 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1154.757 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1250.86 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 686.675 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 399.366 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 4952.837 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2071.254 | 2019-06-12 01:00 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 256376.6 | 2019-06-12 01:00 | ClCap | 256376.6
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 207537.6 | 2019-06-12 01:00 | ClCap | 207537.6
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 272420.9 | 2019-06-12 01:00 | ClCap | 272420.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 259681.3 | 2019-06-12 01:00 | ClCap | 259681.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 31854.21 | 2019-06-12 01:00 | ClCap | 31854.21
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 35612.93 | 2019-06-12 01:00 | ClCap | 35612.93
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 11986.65 | 2019-06-12 01:00 | ClCap | 11986.65
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 9528.966 | 2019-06-12 01:00 | ClCap | 9528.966
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 13172.33 | 2019-06-12 01:00 | ClCap | 13172.33
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 12139.21 | 2019-06-12 01:00 | ClCap | 12139.21
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 16278.58 | 2019-06-12 01:00 | ClCap | 16278.58
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 12592.86 | 2019-06-12 01:00 | ClCap | 12592.86
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 16730.63 | 2019-06-12 01:00 | ClCap | 16730.63
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 15382.96 | 2019-06-12 01:00 | ClCap | 15382.96
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 6088.743 | 2019-06-12 01:00 | ClCap | 6088.743
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 4008.143 | 2019-06-12 01:00 | ClCap | 4008.143
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 6387.02 | 2019-06-12 01:00 | ClCap | 6387.02
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 6713.456 | 2019-06-12 01:00 | ClCap | 6713.456
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 16296.78 | 2019-06-12 01:00 | ClCap | 16296.78
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 37590.05 | 2019-06-12 01:00 | ClCap | 37590.05
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 23173.81 | 2019-06-12 01:00 | ClCap | 23173.81
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 39019.04 | 2019-06-12 01:00 | ClCap | 39019.04
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 42266.32 | 2019-06-12 01:00 | ClCap | 42266.32
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 23202.62 | 2019-06-12 01:00 | ClCap | 23202.62
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 13494.5 | 2019-06-12 01:00 | ClCap | 13494.5
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 167355.4 | 2019-06-12 01:00 | ClCap | 167355.4
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 116645.5 | 2019-06-12 01:00 | ClCap | 116645.5
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -344773.6 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -267554.2 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -362866.6 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -312901.3 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -37893.97 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -51265.18 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -16157.6 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -13494.03 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -18174.55 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -15480.75 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -20824.07 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -16883.74 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -21926.42 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -19736.62 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -8311.257 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -6540.182 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -8899.962 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -9206.297 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -21961.19 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -47547.9 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -29759.31 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -50071.5 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -49954.04 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -41759.09 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -36885.91 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -250302.6 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -164911.3 | 2019-06-12 01:00 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | AltAdjFactor | 1.0277 | 2019-06-12 01:01 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 7160.89 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 6418.271 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 8217.484 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 7646.861 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 1078.395 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 1400.806 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 357.1487 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 304.8181 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 411.6398 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 366.1729 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 557.4712 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 467.2549 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 609.9946 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 555.6664 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 217.3519 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 165.2916 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 248.1264 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 251.2117 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 585.9374 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1252.568 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 886.5037 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1365.987 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1492.748 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 865.5565 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 578.2207 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 6643.306 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2736.434 | 2019-06-12 01:01 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 7516.839 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 6418.271 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 8217.484 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 7646.862 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 1078.395 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 1400.806 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 357.1487 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 304.8181 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 411.6398 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 366.1729 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 557.4712 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 467.2549 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 609.9946 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 555.6664 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 217.3519 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 165.2916 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 248.1264 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 251.2117 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 585.9374 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1314.035 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 886.5037 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1365.987 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1492.748 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 1008.856 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 760.2831 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 6643.306 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2736.434 | 2019-06-12 01:01 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 7160.89 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 6418.271 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 8217.484 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 7646.862 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 1078.395 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 1400.806 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 357.1487 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 304.8181 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 411.6398 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 366.1729 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 557.4712 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 467.2549 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 609.9946 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 555.6664 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 217.3519 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 165.2916 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 248.1264 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 251.2117 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 585.9374 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1252.568 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 886.5037 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1365.987 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1492.748 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 865.5565 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 578.2207 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 6643.306 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2736.434 | 2019-06-12 01:01 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 7160.89 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 6418.271 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 8217.484 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 7646.862 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 1078.395 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 1400.806 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 357.1487 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 304.8181 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 411.6398 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 366.1729 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 557.4712 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 467.2549 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 609.9946 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 555.6664 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 217.3519 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 165.2916 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 248.1264 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 251.2117 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 585.9374 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1252.568 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 886.5037 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1365.987 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1492.748 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 865.5565 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 578.2207 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 6643.306 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2736.434 | 2019-06-12 01:01 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 304059.3 | 2019-06-12 01:01 | ClCap | 304059.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 272526.9 | 2019-06-12 01:01 | ClCap | 272526.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 348923.5 | 2019-06-12 01:01 | ClCap | 348923.5
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 324694.3 | 2019-06-12 01:01 | ClCap | 324694.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 35977.72 | 2019-06-12 01:01 | ClCap | 35977.72
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 46734.11 | 2019-06-12 01:01 | ClCap | 46734.11
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 15164.93 | 2019-06-12 01:01 | ClCap | 15164.93
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 12942.91 | 2019-06-12 01:01 | ClCap | 12942.91
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 17478.69 | 2019-06-12 01:01 | ClCap | 17478.69
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 15548.11 | 2019-06-12 01:01 | ClCap | 15548.11
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 18598.52 | 2019-06-12 01:01 | ClCap | 18598.52
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 15588.7 | 2019-06-12 01:01 | ClCap | 15588.7
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 20350.82 | 2019-06-12 01:01 | ClCap | 20350.82
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 18538.31 | 2019-06-12 01:01 | ClCap | 18538.31
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 7251.358 | 2019-06-12 01:01 | ClCap | 7251.358
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 5514.509 | 2019-06-12 01:01 | ClCap | 5514.509
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 8278.067 | 2019-06-12 01:01 | ClCap | 8278.067
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 8380.999 | 2019-06-12 01:01 | ClCap | 8380.999
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 19548.22 | 2019-06-12 01:01 | ClCap | 19548.22
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 41788.54 | 2019-06-12 01:01 | ClCap | 41788.54
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 29575.8 | 2019-06-12 01:01 | ClCap | 29575.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 45572.48 | 2019-06-12 01:01 | ClCap | 45572.48
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 49801.49 | 2019-06-12 01:01 | ClCap | 49801.49
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 28876.96 | 2019-06-12 01:01 | ClCap | 28876.96
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 19290.77 | 2019-06-12 01:01 | ClCap | 19290.77
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 221636 | 2019-06-12 01:01 | ClCap | 221636
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 152156.2 | 2019-06-12 01:01 | ClCap | 152156.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -357573.3 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -336713.6 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -391038.8 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -375662.3 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -42609.77 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -60202.96 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -18096.3 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -17248.4 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -20042.45 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -19327.98 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -23146.69 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -20536.18 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -25403.41 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -23567.44 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -9777.736 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -8486.527 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -11096.12 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -11303.11 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -26067.2 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -49418.11 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -37040.37 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -50642.77 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -56095.98 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -41767.6 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -36918.4 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -313053.4 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -173426.6 | 2019-06-12 01:01 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | AltAdjFactor | 1.0314 | 2019-06-12 01:03 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 6212.512 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 5601.419 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 7043.494 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 6658.497 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 1010.884 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 1182.216 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 311.998 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 253.9681 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 340.56 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 310.1223 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 483.7376 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 410.9997 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 530.2648 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 483.9816 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 178.139 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 139.7361 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 204.0677 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 211.2705 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 543.0514 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1072.159 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 780.2935 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1186.83 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1320.435 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 763.6677 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 547.4508 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 5542.769 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2274.199 | 2019-06-12 01:03 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 7077.846 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 5601.419 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 7419.757 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 6658.498 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 1010.884 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 1270.004 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 311.9979 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 253.9681 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 363.817 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 310.1223 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 490.7154 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 410.9997 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 530.2648 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 483.9816 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 178.139 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 139.7361 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 204.0677 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 211.2705 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 543.0514 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1188.731 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 780.2935 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1280.103 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1320.435 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 1012.538 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 763.058 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 5542.769 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2611.892 | 2019-06-12 01:03 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 6212.512 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 5601.419 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 7043.494 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 6658.498 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 1010.884 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 1182.216 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 311.9979 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 253.9681 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 340.56 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 310.1223 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 483.7376 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 410.9997 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 530.2648 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 483.9816 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 178.139 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 139.7361 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 204.0677 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 211.2705 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 543.0514 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1072.159 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 780.2935 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1186.83 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1320.435 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 763.6677 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 547.4508 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 5542.769 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2274.199 | 2019-06-12 01:03 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 6212.512 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 5601.419 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 7043.494 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 6658.498 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 1010.884 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 1182.216 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 311.9979 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 253.9681 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 340.56 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 310.1223 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 483.7376 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 410.9997 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 530.2648 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 483.9816 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 178.139 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 139.7361 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 204.0677 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 211.2705 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 543.0514 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1072.159 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 780.2935 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1186.83 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1320.435 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 763.6677 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 547.4508 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 5542.769 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2274.199 | 2019-06-12 01:03 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 262830.8 | 2019-06-12 01:03 | ClCap | 262830.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 236977.5 | 2019-06-12 01:03 | ClCap | 236977.5
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 297986.9 | 2019-06-12 01:03 | ClCap | 297986.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 281699 | 2019-06-12 01:03 | ClCap | 281699
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 33602.78 | 2019-06-12 01:03 | ClCap | 33602.78
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 39298 | 2019-06-12 01:03 | ClCap | 39298
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 13199.6 | 2019-06-12 01:03 | ClCap | 13199.6
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 10744.55 | 2019-06-12 01:03 | ClCap | 10744.55
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 14407.97 | 2019-06-12 01:03 | ClCap | 14407.97
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 13120.25 | 2019-06-12 01:03 | ClCap | 13120.25
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 16079.91 | 2019-06-12 01:03 | ClCap | 16079.91
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 13662.03 | 2019-06-12 01:03 | ClCap | 13662.03
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 17626.52 | 2019-06-12 01:03 | ClCap | 17626.52
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 16088.02 | 2019-06-12 01:03 | ClCap | 16088.02
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 5921.514 | 2019-06-12 01:03 | ClCap | 5921.514
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 4644.964 | 2019-06-12 01:03 | ClCap | 4644.964
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 6783.411 | 2019-06-12 01:03 | ClCap | 6783.411
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 7022.837 | 2019-06-12 01:03 | ClCap | 7022.837
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 18051.56 | 2019-06-12 01:03 | ClCap | 18051.56
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 35639.62 | 2019-06-12 01:03 | ClCap | 35639.62
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 25937.71 | 2019-06-12 01:03 | ClCap | 25937.71
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 39451.39 | 2019-06-12 01:03 | ClCap | 39451.39
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 43892.55 | 2019-06-12 01:03 | ClCap | 43892.55
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 25385.06 | 2019-06-12 01:03 | ClCap | 25385.06
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 18197.8 | 2019-06-12 01:03 | ClCap | 18197.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 184247 | 2019-06-12 01:03 | ClCap | 184247
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 125994.3 | 2019-06-12 01:03 | ClCap | 125994.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -339946.6 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -301018.2 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -352644.5 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -334412.7 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -38960.7 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -54319.01 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -16379.09 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -15101.52 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -17799.96 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -17067.2 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -20027.63 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -17879.27 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -21559.99 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -20326.37 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -8084.417 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -7423.291 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -9093.934 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -9634.776 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -24121.85 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -44155.26 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -32726.45 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -47057.19 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -49609.27 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -40590.85 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -36681.5 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -281427.6 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -167948 | 2019-06-12 01:03 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | AltAdjFactor | 1.0129 | 2019-06-12 01:05 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 6342.036 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 5691.079 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 6835.645 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 6550.158 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 1026.911 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 1306.39 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 317.7416 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 265.4156 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 333.1832 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 313.5586 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 490.0362 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 426.3522 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 524.9274 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 488.7295 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 185.2293 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 151.2332 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 205.9488 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 214.9654 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 545.4633 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1100.617 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 833.9316 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1176.669 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1311.63 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 805.6633 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 629.0081 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 5529.927 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2334.711 | 2019-06-12 01:05 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 7292.439 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 5691.079 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 7158.196 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 6550.158 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 1026.911 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 1377.041 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 322.5323 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 265.4156 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 341.3523 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 313.5586 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 506.512 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 426.3522 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 524.9274 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 488.7295 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 185.2293 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 151.2332 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 205.9488 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 214.9654 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 545.4633 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1211.192 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 833.9316 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1256.96 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1311.63 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 994.3705 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 749.3666 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 5529.927 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2565.027 | 2019-06-12 01:05 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 6342.036 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 5691.079 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 6835.645 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 6550.158 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 1026.911 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 1306.39 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 317.7416 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 265.4156 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 333.1832 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 313.5586 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 490.0362 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 426.3522 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 524.9274 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 488.7295 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 185.0988 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 151.2332 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 205.9488 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 214.9654 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 545.4633 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1100.617 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 833.9316 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1176.669 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1311.63 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 805.6633 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 629.0081 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 5529.927 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2334.711 | 2019-06-12 01:05 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 6342.036 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 5691.079 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 6835.645 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 6550.158 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 1026.911 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 1306.39 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 317.7416 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 265.4156 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 333.1832 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 313.5586 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 490.0362 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 426.3522 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 524.9274 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 488.7295 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 185.0988 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 151.2332 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 205.9488 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 214.9654 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 545.4633 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1100.617 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 833.9316 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1176.669 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1311.63 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 805.6633 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 629.0081 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 5529.927 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2334.711 | 2019-06-12 01:05 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 273212.8 | 2019-06-12 01:05 | ClCap | 273212.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 245169.8 | 2019-06-12 01:05 | ClCap | 245169.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 294477.3 | 2019-06-12 01:05 | ClCap | 294477.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 282178.6 | 2019-06-12 01:05 | ClCap | 282178.6
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 34759.2 | 2019-06-12 01:05 | ClCap | 34759.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 44219.07 | 2019-06-12 01:05 | ClCap | 44219.07
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 13688.2 | 2019-06-12 01:05 | ClCap | 13688.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 11434.02 | 2019-06-12 01:05 | ClCap | 11434.02
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 14353.42 | 2019-06-12 01:05 | ClCap | 14353.42
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 13508 | 2019-06-12 01:05 | ClCap | 13508
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 16586.89 | 2019-06-12 01:05 | ClCap | 16586.89
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 14431.3 | 2019-06-12 01:05 | ClCap | 14431.3
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 17767.9 | 2019-06-12 01:05 | ClCap | 17767.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 16542.67 | 2019-06-12 01:05 | ClCap | 16542.67
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 6265.283 | 2019-06-12 01:05 | ClCap | 6265.283
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 5118.989 | 2019-06-12 01:05 | ClCap | 5118.989
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 6971.018 | 2019-06-12 01:05 | ClCap | 6971.018
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 7276.215 | 2019-06-12 01:05 | ClCap | 7276.215
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 18463.01 | 2019-06-12 01:05 | ClCap | 18463.01
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 37254.01 | 2019-06-12 01:05 | ClCap | 37254.01
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 28227.17 | 2019-06-12 01:05 | ClCap | 28227.17
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 39828.25 | 2019-06-12 01:05 | ClCap | 39828.25
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 44396.47 | 2019-06-12 01:05 | ClCap | 44396.47
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 27270.34 | 2019-06-12 01:05 | ClCap | 27270.34
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 21290.86 | 2019-06-12 01:05 | ClCap | 21290.86
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 187178.7 | 2019-06-12 01:05 | ClCap | 187178.7
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 131710 | 2019-06-12 01:05 | ClCap | 131710
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -371740.8 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -320965.8 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -368006.5 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -352445.5 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -42017.75 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -61906.46 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -17749.87 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -16392.15 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -18365.06 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -18252.15 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -21999.66 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -19703.24 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -22910.12 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -22009.67 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -8865.682 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -8325.619 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -9912.474 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -10386.22 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -25723.27 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -48225.16 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -36492.48 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -49517.23 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -51971.43 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -42744.93 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -38817.47 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -293228.8 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -179578.8 | 2019-06-12 01:05 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | AltAdjFactor | 1.0006 | 2019-06-12 01:06 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 5336.343 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 4691.739 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 5830.596 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 5690.971 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 932.8013 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 1019.39 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 266.1728 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 204.6864 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 279.6818 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 260.8209 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 430.2299 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 361.3318 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 462.199 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 428.4203 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 152.753 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 115.5183 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 176.2295 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 182.16 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 484.3125 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 967.1533 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 695.2498 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1088.727 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1176.015 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 683.3752 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 486.8713 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 4670.162 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 1882.526 | 2019-06-12 01:06 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 6776.858 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 4691.739 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 6820.604 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 5699.403 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 932.8013 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 1161.187 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 288.5576 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 207.1607 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 323.4237 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 260.8209 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 474.3279 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 361.3317 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 478.4692 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 428.4203 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 166.9359 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 115.5183 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 176.2295 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 182.16 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 484.3125 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1122.943 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 695.2498 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1194.876 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1176.015 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 982.2957 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 740.2669 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 4670.162 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2533.88 | 2019-06-12 01:06 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 5336.343 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 4691.739 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 5830.596 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 5690.971 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 932.8013 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 1019.39 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 266.1728 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 204.6864 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 279.6818 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 260.8209 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 430.2299 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 361.3317 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 462.199 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 428.4203 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 152.753 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 115.5183 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 176.2295 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 182.16 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 484.3125 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 967.1534 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 695.2498 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1088.727 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1176.015 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 683.3752 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 486.8713 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 4670.162 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 1882.526 | 2019-06-12 01:06 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 5336.343 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 4691.739 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 5830.596 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 5690.971 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 932.8013 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 1019.39 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 266.1728 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 204.6864 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 279.6818 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 260.8209 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 430.2299 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 361.3317 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 462.199 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 428.4203 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 152.753 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 115.5183 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 176.2295 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 182.16 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 484.3125 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 967.1534 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 695.2498 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1088.727 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1176.015 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 683.3752 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 486.8713 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 4670.162 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 1882.526 | 2019-06-12 01:06 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 232713.8 | 2019-06-12 01:06 | ClCap | 232713.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 204603.1 | 2019-06-12 01:06 | ClCap | 204603.1
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 254267.7 | 2019-06-12 01:06 | ClCap | 254267.7
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 248178.8 | 2019-06-12 01:06 | ClCap | 248178.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 31961.87 | 2019-06-12 01:06 | ClCap | 31961.87
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 34928.78 | 2019-06-12 01:06 | ClCap | 34928.78
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 11607.59 | 2019-06-12 01:06 | ClCap | 11607.59
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 8926.217 | 2019-06-12 01:06 | ClCap | 8926.217
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 12196.71 | 2019-06-12 01:06 | ClCap | 12196.71
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 11374.2 | 2019-06-12 01:06 | ClCap | 11374.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 14741.57 | 2019-06-12 01:06 | ClCap | 14741.57
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 12380.81 | 2019-06-12 01:06 | ClCap | 12380.81
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 15836.96 | 2019-06-12 01:06 | ClCap | 15836.96
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 14679.56 | 2019-06-12 01:06 | ClCap | 14679.56
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 5233.988 | 2019-06-12 01:06 | ClCap | 5233.988
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 3958.163 | 2019-06-12 01:06 | ClCap | 3958.163
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 6038.396 | 2019-06-12 01:06 | ClCap | 6038.396
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 6241.6 | 2019-06-12 01:06 | ClCap | 6241.6
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 16594.67 | 2019-06-12 01:06 | ClCap | 16594.67
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 33138.92 | 2019-06-12 01:06 | ClCap | 33138.92
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 23822.31 | 2019-06-12 01:06 | ClCap | 23822.31
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 37304.55 | 2019-06-12 01:06 | ClCap | 37304.55
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 40295.43 | 2019-06-12 01:06 | ClCap | 40295.43
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 23415.43 | 2019-06-12 01:06 | ClCap | 23415.43
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 16682.35 | 2019-06-12 01:06 | ClCap | 16682.35
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 160020.2 | 2019-06-12 01:06 | ClCap | 160020.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 107506 | 2019-06-12 01:06 | ClCap | 107506
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -363270.3 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -287234.8 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -365645.7 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -324293.5 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -39051 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -55238.54 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -17137.94 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -14310.7 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -18299.18 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -16403.81 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -21211.79 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -17427.46 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -21390.16 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -19922.58 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -8399.901 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -7022.164 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -8818.098 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -9238.707 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -23722.46 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -46064.36 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -31887.41 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -47854.2 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -47871.01 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -42990.72 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -39506.37 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -271821.8 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -185516.9 | 2019-06-12 01:06 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | AltAdjFactor | 1.0124 | 2019-06-12 01:08 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 6113.799 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 5542.597 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 7222.15 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 6530.584 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 1005.149 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 1213.911 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 308.8592 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 249.9352 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 353.7531 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 298.7585 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 490.9826 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 413.8185 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 538.9285 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 478.3541 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 181.8715 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 140.5156 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 212.7255 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 206.9832 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 534.8017 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1090.068 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 797.2671 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1217.017 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1298.207 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 778.8583 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 573.9156 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 5500.23 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2172.031 | 2019-06-12 01:08 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 7235.165 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 5542.597 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 7222.15 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 6530.584 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 1005.149 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 1372.577 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 317.6588 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 249.9352 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 353.7531 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 298.7585 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 501.2465 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 413.8185 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 538.9285 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 478.354 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 183.1426 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 140.5156 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 212.7256 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 206.9832 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 534.8017 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1215.599 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 797.2671 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1222.329 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1298.207 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 993.8951 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 749.0083 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 5500.23 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2563.801 | 2019-06-12 01:08 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 6113.799 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 5542.597 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 7222.15 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 6530.584 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 1005.149 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 1213.911 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 308.8592 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 249.9352 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 353.7531 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 298.7585 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 490.9826 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 413.8185 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 538.9285 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 478.354 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 181.8714 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 140.5156 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 212.7256 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 206.9832 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 534.8017 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1090.068 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 797.2671 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1217.017 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1298.207 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 778.8583 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 573.9156 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 5500.23 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2172.031 | 2019-06-12 01:08 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 6113.799 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 5542.597 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 7222.15 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 6530.584 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 1005.149 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 1213.911 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 308.8592 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 249.9352 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 353.7531 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 298.7585 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 490.9826 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 413.8185 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 538.9285 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 478.354 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 181.8714 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 140.5156 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 212.7256 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 206.9832 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 534.8017 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1090.068 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 797.2671 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1217.017 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1298.207 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 778.8583 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 573.9156 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 5500.23 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2172.031 | 2019-06-12 01:08 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 263506.4 | 2019-06-12 01:08 | ClCap | 263506.4
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 238887.5 | 2019-06-12 01:08 | ClCap | 238887.5
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 311276.7 | 2019-06-12 01:08 | ClCap | 311276.7
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 281470 | 2019-06-12 01:08 | ClCap | 281470
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 34038.86 | 2019-06-12 01:08 | ClCap | 34038.86
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 41108.49 | 2019-06-12 01:08 | ClCap | 41108.49
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 13311.92 | 2019-06-12 01:08 | ClCap | 13311.92
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 10772.28 | 2019-06-12 01:08 | ClCap | 10772.28
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 15246.86 | 2019-06-12 01:08 | ClCap | 15246.86
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 12876.57 | 2019-06-12 01:08 | ClCap | 12876.57
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 16626.88 | 2019-06-12 01:08 | ClCap | 16626.88
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 14013.76 | 2019-06-12 01:08 | ClCap | 14013.76
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 18250.54 | 2019-06-12 01:08 | ClCap | 18250.54
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 16199.22 | 2019-06-12 01:08 | ClCap | 16199.22
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 6158.986 | 2019-06-12 01:08 | ClCap | 6158.986
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 4758.492 | 2019-06-12 01:08 | ClCap | 4758.492
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 7203.845 | 2019-06-12 01:08 | ClCap | 7203.845
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 7009.384 | 2019-06-12 01:08 | ClCap | 7009.384
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 18110.79 | 2019-06-12 01:08 | ClCap | 18110.79
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 36914.61 | 2019-06-12 01:08 | ClCap | 36914.61
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 26999.05 | 2019-06-12 01:08 | ClCap | 26999.05
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 41213.67 | 2019-06-12 01:08 | ClCap | 41213.67
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 43963.12 | 2019-06-12 01:08 | ClCap | 43963.12
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 26375.65 | 2019-06-12 01:08 | ClCap | 26375.65
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 19435.37 | 2019-06-12 01:08 | ClCap | 19435.37
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 186262.6 | 2019-06-12 01:08 | ClCap | 186262.6
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 122591.2 | 2019-06-12 01:08 | ClCap | 122591.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -371972.2 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -316185.3 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -374497.4 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -353477.8 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -41393.19 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -62117.28 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -17694.9 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -15660.52 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -19094.21 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -17554.19 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -21927.79 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -19280.66 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -23715.76 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -21646.29 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -8837.611 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -7843.942 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -10335.79 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -10080.16 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -25333.84 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -48495.46 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -35193.75 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -48342.14 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -51505.75 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -42972.33 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -39034.99 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -295981.7 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -180752.9 | 2019-06-12 01:08 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | AltAdjFactor | 1.0973 | 2019-06-12 01:09 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 7093.226 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 6427.112 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 8252.775 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 7557.405 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 1119.174 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 1437.76 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 357.1533 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 297.0639 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 406.7342 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 351.945 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 559.0461 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 465.6915 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 602.8699 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 540.6318 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 209.9614 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 159.6229 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 240.3073 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 238.7615 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 611.5963 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1246.472 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 886.0676 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1329.37 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1447.862 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 869.2761 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 641.7005 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 6418.908 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2607.694 | 2019-06-12 01:09 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 7883.184 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 6427.112 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 8252.775 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 7557.405 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 1119.174 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 1524.775 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 357.1533 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 297.0639 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 406.7342 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 351.945 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 559.0461 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 465.6915 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 602.8699 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 540.6318 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 209.9614 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 159.6229 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 240.3073 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 238.7615 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 611.5963 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1336.274 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 886.0676 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1329.37 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1447.862 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 1077.232 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 811.8117 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 6418.908 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2778.772 | 2019-06-12 01:09 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 7093.226 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 6427.112 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 8252.775 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 7557.405 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 1119.174 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 1437.76 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 357.1533 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 297.0639 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 406.7342 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 351.945 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 559.0461 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 465.6915 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 602.8699 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 540.6318 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 209.9614 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 159.6229 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 240.3073 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 238.7615 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 611.5963 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1246.472 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 886.0676 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1329.37 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1447.862 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 869.2761 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 641.7005 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 6418.908 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2607.694 | 2019-06-12 01:09 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 7093.226 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 6427.112 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 8252.775 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 7557.405 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 1119.174 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 1437.76 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 357.1533 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 297.0639 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 406.7342 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 351.945 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 559.0461 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 465.6915 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 602.8699 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 540.6318 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 209.9614 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 159.6229 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 240.3073 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 238.7615 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 611.5963 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1246.472 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 886.0676 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1329.37 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1447.862 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 869.2761 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 641.7005 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 6418.908 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2607.694 | 2019-06-12 01:09 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 282068.8 | 2019-06-12 01:09 | ClCap | 282068.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 255580.2 | 2019-06-12 01:09 | ClCap | 255580.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 328179.4 | 2019-06-12 01:09 | ClCap | 328179.4
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 300527.4 | 2019-06-12 01:09 | ClCap | 300527.4
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 34968.21 | 2019-06-12 01:09 | ClCap | 34968.21
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 44922.33 | 2019-06-12 01:09 | ClCap | 44922.33
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 14202.54 | 2019-06-12 01:09 | ClCap | 14202.54
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 11813.03 | 2019-06-12 01:09 | ClCap | 11813.03
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 16174.17 | 2019-06-12 01:09 | ClCap | 16174.17
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 13995.43 | 2019-06-12 01:09 | ClCap | 13995.43
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 17467.21 | 2019-06-12 01:09 | ClCap | 17467.21
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 14550.38 | 2019-06-12 01:09 | ClCap | 14550.38
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 18836.47 | 2019-06-12 01:09 | ClCap | 18836.47
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 16891.87 | 2019-06-12 01:09 | ClCap | 16891.87
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 6560.175 | 2019-06-12 01:09 | ClCap | 6560.175
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 4987.366 | 2019-06-12 01:09 | ClCap | 4987.366
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 7508.324 | 2019-06-12 01:09 | ClCap | 7508.324
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 7460.025 | 2019-06-12 01:09 | ClCap | 7460.025
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 19109.13 | 2019-06-12 01:09 | ClCap | 19109.13
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 38945.61 | 2019-06-12 01:09 | ClCap | 38945.61
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 27684.89 | 2019-06-12 01:09 | ClCap | 27684.89
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 41535.72 | 2019-06-12 01:09 | ClCap | 41535.72
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 45237.97 | 2019-06-12 01:09 | ClCap | 45237.97
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 27160.25 | 2019-06-12 01:09 | ClCap | 27160.25
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 20049.72 | 2019-06-12 01:09 | ClCap | 20049.72
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 200556.7 | 2019-06-12 01:09 | ClCap | 200556.7
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 135794.2 | 2019-06-12 01:09 | ClCap | 135794.2
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -387391.4 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -351753.1 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -411689.9 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -391695.3 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -43082 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -64864.08 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -19186.42 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -17931.99 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -21278.01 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -20006.71 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -22972.53 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -20472.31 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -25013.7 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -23034.4 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -9614.509 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -8533.983 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -11158.79 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -11054.9 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -27535.03 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -48461.86 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -36855.82 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -49339.91 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -53690.58 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -43637.81 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -40498.63 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -332588.7 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -192234.8 | 2019-06-12 01:09 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | AltAdjFactor | 1.0177 | 2019-06-12 01:11 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 9165.158 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 8699.054 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 9589.324 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 9536.808 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 1231.701 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 1904.279 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 484.1257 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 436.9853 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 484.8535 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 471.4514 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 670.538 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 593.1718 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 668.3721 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 658.6114 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 279.4684 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 238.1982 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 278.9823 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 309.1138 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 711.8712 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1446.656 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 1130.305 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1425.431 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1678.617 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 1070.903 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 855.0936 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 8446.675 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 3564.615 | 2019-06-12 01:11 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 9165.158 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 8699.054 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 9589.324 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 9536.808 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 1231.701 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 1904.279 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 484.1257 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 436.9854 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 484.8535 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 471.4514 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 670.538 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 593.1718 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 668.3721 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 658.6114 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 279.4684 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 238.1982 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 278.9823 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 309.1138 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 711.8712 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1446.656 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 1130.305 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1425.431 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1678.617 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 1070.903 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 855.0936 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 8446.675 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3564.615 | 2019-06-12 01:11 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 9165.158 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 8699.054 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 9589.324 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 9536.808 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 1231.701 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 1904.279 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 484.1257 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 436.9854 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 484.8535 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 471.4514 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 670.538 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 593.1718 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 668.3721 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 658.6114 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 279.4684 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 238.1982 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 278.9823 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 309.1138 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 711.8712 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1446.656 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 1130.305 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1425.431 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1678.617 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 1070.903 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 855.0936 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 8446.675 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 3564.615 | 2019-06-12 01:11 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 9165.158 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 8699.054 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 9589.324 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 9536.808 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 1231.701 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 1904.279 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 484.1257 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 436.9854 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 484.8535 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 471.4514 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 670.538 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 593.1718 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 668.3721 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 658.6114 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 279.4684 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 238.1982 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 278.9823 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 309.1138 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 711.8712 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1446.656 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 1130.305 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1425.431 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1678.617 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 1070.903 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 855.0936 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 8446.675 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 3564.615 | 2019-06-12 01:11 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 392991 | 2019-06-12 01:11 | ClCap | 392991
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 373005 | 2019-06-12 01:11 | ClCap | 373005
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 411178.7 | 2019-06-12 01:11 | ClCap | 411178.7
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 408926.8 | 2019-06-12 01:11 | ClCap | 408926.8
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 41496.6 | 2019-06-12 01:11 | ClCap | 41496.6
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 64156.06 | 2019-06-12 01:11 | ClCap | 64156.06
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 20758.73 | 2019-06-12 01:11 | ClCap | 20758.73
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 18737.41 | 2019-06-12 01:11 | ClCap | 18737.41
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 20789.94 | 2019-06-12 01:11 | ClCap | 20789.94
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 20215.27 | 2019-06-12 01:11 | ClCap | 20215.27
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 22590.75 | 2019-06-12 01:11 | ClCap | 22590.75
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 19984.24 | 2019-06-12 01:11 | ClCap | 19984.24
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 22517.78 | 2019-06-12 01:11 | ClCap | 22517.78
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 22188.94 | 2019-06-12 01:11 | ClCap | 22188.94
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 9415.427 | 2019-06-12 01:11 | ClCap | 9415.427
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 8025.012 | 2019-06-12 01:11 | ClCap | 8025.012
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 9399.048 | 2019-06-12 01:11 | ClCap | 9399.048
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 10414.19 | 2019-06-12 01:11 | ClCap | 10414.19
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 23983.28 | 2019-06-12 01:11 | ClCap | 23983.28
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 48738.53 | 2019-06-12 01:11 | ClCap | 48738.53
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 38080.52 | 2019-06-12 01:11 | ClCap | 38080.52
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 48023.47 | 2019-06-12 01:11 | ClCap | 48023.47
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 56553.42 | 2019-06-12 01:11 | ClCap | 56553.42
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 36079.25 | 2019-06-12 01:11 | ClCap | 36079.25
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 28808.52 | 2019-06-12 01:11 | ClCap | 28808.52
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 284572.6 | 2019-06-12 01:11 | ClCap | 284572.6
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 200156 | 2019-06-12 01:11 | ClCap | 200156
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -420351.3 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -428518.3 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -442000.9 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -454559.7 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -46660.51 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -76655.84 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -23475.3 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -22736.95 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -22543.84 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -23874.79 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -26600.79 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -24649.55 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -26656.45 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -26785.49 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -11999.99 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -11246.64 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -12063.66 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -13382.23 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -30479.87 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -52438.16 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -44820.01 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -50749.51 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -61138.69 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -42321.01 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -40471.5 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -390862.2 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -225088.1 | 2019-06-12 01:11 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | AltAdjFactor | 1.2145 | 2019-06-12 01:12 | AltAd | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_Clrm_EZn | 7687.553 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_Clrm_NZn | 4888.074 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_Clrm_SZn | 7475.697 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_Clrm_WZn | 6253.875 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_CompCL_CZn | 1105.453 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_Cordr_AZn | 1249.823 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_Din_EZn | 317.158 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_Din_NZn | 210.9218 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_Din_SZn | 347.8094 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_Din_WZn | 269.4037 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_LibRdg_EZn | 547.1755 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_LibRdg_NZn | 362.3394 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_LibRdg_SZn | 532.3702 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_LibRdg_WZn | 437.7047 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_LobWait_EZn | 183.8506 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_LobWait_NZn | 100.2317 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_LobWait_SZn | 177.493 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_LobWait_WZn | 172.5848 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_OffGen_CZn | 511.1941 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_OffGen_EZn | 1317.293 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_OffGen_NZn | 630.3771 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_OffGen_SZn | 1296.682 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_OffGen_WZn | 1290.506 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_Restrm_CZn | 1192.218 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_A_StorSm_CZn | 898.4663 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 3637.673 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 3075.385 | 2019-06-12 01:12 | CAssF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_E | 7687.553 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_N | 4888.074 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_S | 7475.697 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_Clrm_W | 6253.875 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_CompCL_C | 1105.453 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_Cordr_A | 1249.823 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_E | 317.158 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_N | 210.9218 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_S | 347.8094 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_Din_W | 269.4037 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_E | 547.1755 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_N | 362.3394 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_S | 532.3702 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_LibRdg_W | 437.7047 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_E | 183.8506 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_N | 100.2317 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_S | 177.493 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_LobWait_W | 172.5848 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_C | 511.1941 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_E | 1317.293 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_N | 630.3771 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_S | 1296.682 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_OffGen_W | 1290.506 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_Restrm_C | 1192.218 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_A_StorSm_C | 898.4663 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 3637.673 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3075.385 | 2019-06-12 01:12 | CHRtF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_E | 7687.553 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_N | 4888.074 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_S | 7475.697 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_Clrm_W | 6253.875 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_CompCL_C | 1105.453 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_Cordr_A | 1249.823 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_E | 317.158 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_N | 210.9218 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_S | 347.8094 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_Din_W | 269.4037 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_E | 547.1755 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_N | 362.3394 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_S | 532.3702 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_LibRdg_W | 437.7047 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_E | 183.8506 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_N | 100.2317 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_S | 177.493 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_LobWait_W | 172.5848 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_C | 511.1941 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_E | 1317.293 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_N | 630.3771 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_S | 1296.682 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_OffGen_W | 1290.506 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_Restrm_C | 1192.218 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_A_StorSm_C | 898.4663 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 3637.673 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 3075.385 | 2019-06-12 01:12 | CRtdF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_E | 7687.553 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_N | 4888.074 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_S | 7475.697 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_Clrm_W | 6253.875 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_CompCL_C | 1105.453 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_Cordr_A | 1249.823 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_E | 317.158 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_N | 210.9218 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_S | 347.8094 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_Din_W | 269.4037 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_E | 547.1755 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_N | 362.3394 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_S | 532.3702 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_LibRdg_W | 437.7047 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_E | 183.8506 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_N | 100.2317 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_S | 177.493 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_LobWait_W | 172.5848 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_C | 511.1941 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_E | 1317.293 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_N | 630.3771 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_S | 1296.682 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_OffGen_W | 1290.506 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_Restrm_C | 1192.218 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_A_StorSm_C | 898.4663 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 3637.673 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 3075.385 | 2019-06-12 01:12 | CSupF | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_E | 276218.7 | 2019-06-12 01:12 | ClCap | 276218.7
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_N | 175631.6 | 2019-06-12 01:12 | ClCap | 175631.6
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_S | 268606.5 | 2019-06-12 01:12 | ClCap | 268606.5
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_Clrm_W | 224705.7 | 2019-06-12 01:12 | ClCap | 224705.7
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_CompCL_C | 31208.27 | 2019-06-12 01:12 | ClCap | 31208.27
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_Cordr_A | 35284.02 | 2019-06-12 01:12 | ClCap | 35284.02
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_Din_E | 11395.69 | 2019-06-12 01:12 | ClCap | 11395.69
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_Din_N | 7578.554 | 2019-06-12 01:12 | ClCap | 7578.554
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_Din_S | 12497.01 | 2019-06-12 01:12 | ClCap | 12497.01
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_Din_W | 9679.844 | 2019-06-12 01:12 | ClCap | 9679.844
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_E | 15447.43 | 2019-06-12 01:12 | ClCap | 15447.43
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_N | 10229.28 | 2019-06-12 01:12 | ClCap | 10229.28
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_S | 15029.46 | 2019-06-12 01:12 | ClCap | 15029.46
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_LibRdg_W | 12356.93 | 2019-06-12 01:12 | ClCap | 12356.93
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_E | 5190.325 | 2019-06-12 01:12 | ClCap | 5190.325
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_N | 2829.661 | 2019-06-12 01:12 | ClCap | 2829.661
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_S | 5010.843 | 2019-06-12 01:12 | ClCap | 5010.843
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_LobWait_W | 4872.277 | 2019-06-12 01:12 | ClCap | 4872.277
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_C | 14431.63 | 2019-06-12 01:12 | ClCap | 14431.63
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_E | 37188.78 | 2019-06-12 01:12 | ClCap | 37188.78
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_N | 17796.31 | 2019-06-12 01:12 | ClCap | 17796.31
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_S | 36606.9 | 2019-06-12 01:12 | ClCap | 36606.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_OffGen_W | 36432.55 | 2019-06-12 01:12 | ClCap | 36432.55
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_Restrm_C | 33657.76 | 2019-06-12 01:12 | ClCap | 33657.76
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_A_StorSm_C | 25364.79 | 2019-06-12 01:12 | ClCap | 25364.79
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 102695.9 | 2019-06-12 01:12 | ClCap | 102695.9
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 144703 | 2019-06-12 01:12 | ClCap | 144703
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_E | -381378.3 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_N | -291227 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_S | -377524.8 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_Clrm_W | -336680.3 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_CompCL_C | -40923.64 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_Cordr_A | -55020.29 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_Din_E | -18050.8 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_Din_N | -14270.16 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_Din_S | -18980.57 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_Din_W | -16581.8 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_E | -22271.01 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_N | -16243.14 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_S | -21874.58 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_LibRdg_W | -18767.93 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_E | -8625.619 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_N | -5851.092 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_S | -8436.791 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_LobWait_W | -8262.487 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_C | -22623.25 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_E | -47288.82 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_N | -26998.92 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_S | -46882.34 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_OffGen_W | -46554.38 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_Restrm_C | -47036.88 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_A_StorSm_C | -43688.54 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -214210 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | EPr | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -208068.8 | 2019-06-12 01:12 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | AltAdjFactor | 1.0075 | 2019-06-12 01:14 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 6780.76 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2377.126 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 5857.883 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 3582.292 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 6734.376 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 4850.039 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5180.638 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1183.49 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2055.349 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 731.3856 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 761.7677 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 813.7145 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 709.97 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 1423.567 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 973.2864 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 1639.56 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 1503.364 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 1738.342 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 934.5781 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 1947.056 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 1477.701 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 334.2286 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 493.7218 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1138.539 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 627.3757 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1275.942 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1068.348 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1550.781 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 284.1241 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 284.1241 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 284.1241 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 284.1241 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1861.668 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 9641.861 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 6135.55 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 10436.78 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 7989.746 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2360.463 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 505.8294 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1114.91 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 521.286 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1287.443 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1039.689 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 664.6375 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 797.8511 | 2019-06-12 01:14 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 6780.76 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2377.126 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 5857.883 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 3582.292 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 6734.376 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 4850.039 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5180.638 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1183.49 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 2055.349 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 731.3856 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 761.7677 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 813.7145 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 709.97 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 1423.567 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 973.2864 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 1639.56 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 1503.364 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 1738.342 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 934.5781 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 1947.056 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 1477.701 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 334.2286 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 493.7218 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1138.539 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 627.3757 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1275.942 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1068.348 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1550.781 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 284.1241 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 284.1241 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 284.1241 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 284.1241 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1861.668 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 9641.861 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 6135.55 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 10436.78 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 7989.746 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 2360.463 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 505.8294 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1114.91 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 521.286 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1287.443 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1039.689 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 664.6375 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 797.8511 | 2019-06-12 01:14 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 6780.76 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2377.126 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 5857.883 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 3582.292 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 6734.376 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 4850.039 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5180.638 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1183.49 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2055.349 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 731.3856 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 761.7677 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 813.7145 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 709.97 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 1423.567 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 973.2863 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 1639.56 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 1503.364 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 1738.342 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 934.5781 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 1947.056 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 1477.701 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 334.2286 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 493.7218 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1138.539 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 627.3757 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1275.942 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1068.348 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1550.781 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 284.1241 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 284.1241 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 284.1241 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 284.1241 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1861.668 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 9641.861 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 6135.549 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 10436.78 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 7989.746 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2360.463 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 505.8294 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1114.91 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 521.286 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1287.443 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1039.689 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 664.6375 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 797.8511 | 2019-06-12 01:14 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 6780.76 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2377.126 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 5857.883 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 3582.292 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 6734.376 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 4850.039 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5180.638 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1183.49 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2055.349 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 731.3856 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 761.7677 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 813.7145 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 709.97 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 1423.567 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 973.2864 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 1639.56 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 1503.364 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 1738.342 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 934.5781 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 1947.056 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 1477.701 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 334.2286 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 493.7218 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1138.539 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 627.3757 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1275.942 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1068.348 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1550.781 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 284.1241 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 284.1241 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 284.1241 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 284.1241 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1861.668 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 9641.861 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 6135.55 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 10436.78 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 7989.746 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2360.463 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 505.8294 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1114.91 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 521.286 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1287.443 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1039.689 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 664.6375 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 797.8511 | 2019-06-12 01:14 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 230745.2 | 2019-06-12 01:14 | ClCap | 230745.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 134820.3 | 2019-06-12 01:14 | ClCap | 134820.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 253705.8 | 2019-06-12 01:14 | ClCap | 253705.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 155149.6 | 2019-06-12 01:14 | ClCap | 155149.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 291666.8 | 2019-06-12 01:14 | ClCap | 291666.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 210055.9 | 2019-06-12 01:14 | ClCap | 210055.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 176294 | 2019-06-12 01:14 | ClCap | 176294
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 51257.15 | 2019-06-12 01:14 | ClCap | 51257.15
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 69942.3 | 2019-06-12 01:14 | ClCap | 69942.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 24888.62 | 2019-06-12 01:14 | ClCap | 24888.62
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 25922.5 | 2019-06-12 01:14 | ClCap | 25922.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 27690.22 | 2019-06-12 01:14 | ClCap | 27690.22
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 24159.86 | 2019-06-12 01:14 | ClCap | 24159.86
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 61654.88 | 2019-06-12 01:14 | ClCap | 61654.88
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 42153.18 | 2019-06-12 01:14 | ClCap | 42153.18
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 71009.6 | 2019-06-12 01:14 | ClCap | 71009.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 65110.92 | 2019-06-12 01:14 | ClCap | 65110.92
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 59154.72 | 2019-06-12 01:14 | ClCap | 59154.72
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 31803.13 | 2019-06-12 01:14 | ClCap | 31803.13
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 66257.16 | 2019-06-12 01:14 | ClCap | 66257.16
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 50285.27 | 2019-06-12 01:14 | ClCap | 50285.27
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 11373.6 | 2019-06-12 01:14 | ClCap | 11373.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 16801.06 | 2019-06-12 01:14 | ClCap | 16801.06
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 38743.81 | 2019-06-12 01:14 | ClCap | 38743.81
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 21349.22 | 2019-06-12 01:14 | ClCap | 21349.22
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 43419.54 | 2019-06-12 01:14 | ClCap | 43419.54
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 36355.25 | 2019-06-12 01:14 | ClCap | 36355.25
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 52772.14 | 2019-06-12 01:14 | ClCap | 52772.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 9668.571 | 2019-06-12 01:14 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 9668.571 | 2019-06-12 01:14 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 9668.571 | 2019-06-12 01:14 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 9668.571 | 2019-06-12 01:14 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 63351.45 | 2019-06-12 01:14 | ClCap | 63351.45
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 417590.4 | 2019-06-12 01:14 | ClCap | 417590.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 265731.6 | 2019-06-12 01:14 | ClCap | 265731.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 452018.6 | 2019-06-12 01:14 | ClCap | 452018.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 346037.1 | 2019-06-12 01:14 | ClCap | 346037.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 80325.16 | 2019-06-12 01:14 | ClCap | 80325.16
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 17213.07 | 2019-06-12 01:14 | ClCap | 17213.07
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 37939.73 | 2019-06-12 01:14 | ClCap | 37939.73
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 17739.05 | 2019-06-12 01:14 | ClCap | 17739.05
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 43810.92 | 2019-06-12 01:14 | ClCap | 43810.92
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 35379.99 | 2019-06-12 01:14 | ClCap | 35379.99
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 22617.21 | 2019-06-12 01:14 | ClCap | 22617.21
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 27150.4 | 2019-06-12 01:14 | ClCap | 27150.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -477022.6 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -158570 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -311948.3 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -240405.9 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -336591.9 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -279919.6 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -187019.5 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -72263.19 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -100447.7 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -32978.72 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -33999.91 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -35305.91 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -32199.1 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -72113.71 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -57955.53 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -78199.84 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -74431.63 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -67863.24 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -42767.71 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -73185.53 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -59589.55 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -15476.97 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -22353.51 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -44897.41 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -28758.14 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -48195.81 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -42488.51 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -60074.91 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -19987.96 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -19987.96 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -19987.96 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -19987.96 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -89400.37 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -528931.3 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -394757.6 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -556836.4 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -466373.3 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -116923.2 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -24772.91 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -49961.91 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -27597.49 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -55201.12 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -47067.23 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -29522.95 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ01 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -42215.52 | 2019-06-12 01:14 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | AltAdjFactor | 1.0046 | 2019-06-12 01:15 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 10206.37 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2048.605 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 5755.568 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 4643.771 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 6059.492 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 5488.877 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 4868.4 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1260.992 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 1976.59 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 816.6377 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 464.1423 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 963.4216 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 918.5518 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 1451.8 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1085.657 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 1584.572 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 1645.916 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 1615.475 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1261.448 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 1812.773 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 1657.088 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 221.1569 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 539.3569 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1030.434 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 725.3027 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1213.792 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1190.548 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1171.277 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 418.1388 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 287.0487 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 426.9863 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 377.6758 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1319.105 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 8968.031 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 7429.445 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 8921.954 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 8164.776 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2094.081 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 526.1954 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1086.744 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 807.2985 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1298.29 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1220.378 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 434.6188 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 527.1891 | 2019-06-12 01:15 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 10206.37 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2789.662 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 7448.52 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 5096.386 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 7957.593 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 6292.735 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5382.815 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1349.853 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 2380.579 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1039.188 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 773.6851 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1072.043 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 970.7601 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 1826.527 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1085.657 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 1909.7 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 1875.646 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2033.046 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1332.857 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2163.309 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 1794.833 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 348.2756 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 599.5038 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1375.116 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 756.505 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1439.802 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1319.811 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1546.336 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 418.1388 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 287.0487 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 426.9863 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 377.6758 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1856.332 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 10427.37 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 7888.703 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 10967.94 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 8779.042 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 2859.736 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 543.1215 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1243.657 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 807.2985 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1380.077 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1220.378 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 662.7324 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 795.5642 | 2019-06-12 01:15 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 10206.37 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2048.605 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 5755.568 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 4643.771 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 6059.492 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 5488.877 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 4868.4 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1260.992 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 1976.59 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 816.6377 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 464.1423 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 963.4216 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 918.5518 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 1451.8 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1085.657 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 1584.572 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 1645.916 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 1615.475 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1261.448 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 1812.773 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 1657.088 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 221.1569 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 539.3569 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1030.434 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 725.3027 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1213.792 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1190.548 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1171.277 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 418.1388 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 287.0487 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 426.9863 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 377.6758 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1319.105 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 8968.031 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 7429.445 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 8921.954 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 8164.776 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2094.081 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 526.1954 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1086.744 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 807.2985 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1298.29 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1220.378 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 434.6187 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 527.1891 | 2019-06-12 01:15 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 10206.37 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2048.605 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 5755.568 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 4643.771 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 6059.492 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 5488.877 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 4868.4 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1260.992 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 1976.59 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 816.6377 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 464.1423 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 963.4216 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 918.5518 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 1451.8 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1085.657 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 1584.572 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 1645.916 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 1615.475 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1261.448 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 1812.773 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 1657.088 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 221.1569 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 539.3569 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1030.434 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 725.3027 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1213.792 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1190.548 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1171.277 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 418.1388 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 287.0487 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 426.9863 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 377.6758 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1319.105 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 8968.031 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 7429.445 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 8921.954 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 8164.776 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2094.081 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 526.1954 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1086.744 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 807.2985 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1298.29 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1220.378 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 434.6187 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 527.1891 | 2019-06-12 01:15 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 348314.9 | 2019-06-12 01:15 | ClCap | 348314.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 116522 | 2019-06-12 01:15 | ClCap | 116522
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 249991.1 | 2019-06-12 01:15 | ClCap | 249991.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 201700.5 | 2019-06-12 01:15 | ClCap | 201700.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 263191.9 | 2019-06-12 01:15 | ClCap | 263191.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 238407.4 | 2019-06-12 01:15 | ClCap | 238407.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 166145 | 2019-06-12 01:15 | ClCap | 166145
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 54770.74 | 2019-06-12 01:15 | ClCap | 54770.74
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 67455.52 | 2019-06-12 01:15 | ClCap | 67455.52
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 27869.57 | 2019-06-12 01:15 | ClCap | 27869.57
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 15839.89 | 2019-06-12 01:15 | ClCap | 15839.89
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 32878.9 | 2019-06-12 01:15 | ClCap | 32878.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 31347.62 | 2019-06-12 01:15 | ClCap | 31347.62
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 63058.42 | 2019-06-12 01:15 | ClCap | 63058.42
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 47155.14 | 2019-06-12 01:15 | ClCap | 47155.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 68825.33 | 2019-06-12 01:15 | ClCap | 68825.33
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 71489.77 | 2019-06-12 01:15 | ClCap | 71489.77
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 55131.68 | 2019-06-12 01:15 | ClCap | 55131.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 43049.71 | 2019-06-12 01:15 | ClCap | 43049.71
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 61864.9 | 2019-06-12 01:15 | ClCap | 61864.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 56551.8 | 2019-06-12 01:15 | ClCap | 56551.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 7547.472 | 2019-06-12 01:15 | ClCap | 7547.472
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 18406.75 | 2019-06-12 01:15 | ClCap | 18406.75
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 35165.84 | 2019-06-12 01:15 | ClCap | 35165.84
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 24752.56 | 2019-06-12 01:15 | ClCap | 24752.56
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 41423.34 | 2019-06-12 01:15 | ClCap | 41423.34
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 40630.11 | 2019-06-12 01:15 | ClCap | 40630.11
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 39972.43 | 2019-06-12 01:15 | ClCap | 39972.43
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 14269.92 | 2019-06-12 01:15 | ClCap | 14269.92
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 9796.174 | 2019-06-12 01:15 | ClCap | 9796.174
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 14571.86 | 2019-06-12 01:15 | ClCap | 14571.86
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 12889.02 | 2019-06-12 01:15 | ClCap | 12889.02
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 45017.38 | 2019-06-12 01:15 | ClCap | 45017.38
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 389523.3 | 2019-06-12 01:15 | ClCap | 389523.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 322695.3 | 2019-06-12 01:15 | ClCap | 322695.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 387521.9 | 2019-06-12 01:15 | ClCap | 387521.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 354634.2 | 2019-06-12 01:15 | ClCap | 354634.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 71465.18 | 2019-06-12 01:15 | ClCap | 71465.18
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 17957.59 | 2019-06-12 01:15 | ClCap | 17957.59
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 37087.56 | 2019-06-12 01:15 | ClCap | 37087.56
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 27550.85 | 2019-06-12 01:15 | ClCap | 27550.85
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 44307.04 | 2019-06-12 01:15 | ClCap | 44307.04
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 41648.11 | 2019-06-12 01:15 | ClCap | 41648.11
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 14832.33 | 2019-06-12 01:15 | ClCap | 14832.33
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 17991.5 | 2019-06-12 01:15 | ClCap | 17991.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -725434.8 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -179641.4 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -375680 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -303221.9 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -388261.6 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -339141.8 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -196901.1 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -81653.25 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -114956.6 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -43915.93 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -35488.6 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -44498.73 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -41604.01 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -87711.56 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -64708.88 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -89510.02 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -88980.9 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -78610.19 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -57089.24 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -81381.13 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -71002.98 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -16527.18 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -26553.64 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -53251.6 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -33986.43 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -54136.62 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -51254.99 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -61182.46 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -31285.57 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -21477.27 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -30909.2 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -28258.08 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -92950.68 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -580563.5 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -485304.3 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -598650.4 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -518170.8 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -139591.7 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -26808.53 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -55602.14 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -40312.93 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -59227.9 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -54782.16 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -29907.87 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ02 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -43702.16 | 2019-06-12 01:15 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | AltAdjFactor | 1.0003 | 2019-06-12 01:17 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 7047.869 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2656.259 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 8217.822 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 4607.464 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 8954.25 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 6502.595 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5317.911 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1318.379 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2228.564 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1230.032 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 778.1519 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1301.667 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1155.24 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 2111.992 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1002.624 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 2255.444 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2148.538 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2349.543 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1219.904 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2560.418 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2136.17 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 331.8143 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 573.3312 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1685.389 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 661.0617 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1781.15 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1612.584 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1539.579 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 319.6214 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 282.0717 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 354.8814 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 282.0717 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1848.22 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 11542.97 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 7344.323 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 12357.98 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 8834.22 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2775.147 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 527.3906 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1509.176 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 678.8804 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1705.708 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1461.236 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 659.8364 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 792.0878 | 2019-06-12 01:17 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 7047.869 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2656.259 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 8217.822 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 4607.464 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 8954.25 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 6502.595 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5317.911 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1318.379 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 2228.564 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1230.032 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 778.1519 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1301.667 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1155.24 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2111.992 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1002.624 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2255.444 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2148.538 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2349.543 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1219.904 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2560.418 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2136.17 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 331.8143 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 573.3312 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1685.389 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 661.0617 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1781.15 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1612.584 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1539.579 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 319.6214 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 282.0717 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 354.8814 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 282.0717 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1848.22 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 11542.97 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 7344.323 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 12357.98 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 8834.22 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 2775.147 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 527.3906 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1509.176 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 678.8804 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1705.708 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1461.236 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 659.8364 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 792.0878 | 2019-06-12 01:17 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 7047.869 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2656.258 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 8217.822 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 4607.464 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 8954.25 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 6502.595 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5317.911 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1318.379 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2228.564 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1230.032 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 778.1519 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1301.667 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1155.24 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 2111.992 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1002.624 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 2255.444 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2148.538 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2349.543 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1219.904 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2560.418 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2136.17 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 331.8143 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 573.3312 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1685.389 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 661.0617 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1781.15 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1612.584 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1539.579 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 319.6214 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 282.0717 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 354.8814 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 282.0717 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1848.22 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 11542.97 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 7344.323 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 12357.98 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 8834.22 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2775.147 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 527.3906 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1509.176 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 678.8804 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1705.708 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1461.236 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 659.8364 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 792.0878 | 2019-06-12 01:17 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 7047.869 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2656.259 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 8217.822 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 4607.464 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 8954.25 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 6502.595 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5317.911 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1318.379 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2228.564 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1230.032 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 778.1519 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1301.667 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1155.24 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 2111.992 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1002.624 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 2255.444 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2148.538 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2349.543 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1219.904 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2560.418 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2136.17 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 331.8143 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 573.3312 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1685.389 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 661.0617 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1781.15 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1612.584 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1539.579 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 319.6214 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 282.0717 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 354.8814 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 282.0717 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1848.22 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 11542.97 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 7344.323 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 12357.98 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 8834.22 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2775.147 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 527.3906 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1509.176 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 678.8804 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1705.708 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1461.236 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 659.8364 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 792.0878 | 2019-06-12 01:17 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 241579.8 | 2019-06-12 01:17 | ClCap | 241579.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 151747.6 | 2019-06-12 01:17 | ClCap | 151747.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 358504.8 | 2019-06-12 01:17 | ClCap | 358504.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 201001.9 | 2019-06-12 01:17 | ClCap | 201001.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 390631.7 | 2019-06-12 01:17 | ClCap | 390631.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 283677.5 | 2019-06-12 01:17 | ClCap | 283677.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 182282 | 2019-06-12 01:17 | ClCap | 182282
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 57514.67 | 2019-06-12 01:17 | ClCap | 57514.67
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 76388.49 | 2019-06-12 01:17 | ClCap | 76388.49
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 42161.81 | 2019-06-12 01:17 | ClCap | 42161.81
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 26672.71 | 2019-06-12 01:17 | ClCap | 26672.71
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 44617.23 | 2019-06-12 01:17 | ClCap | 44617.23
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 39598.18 | 2019-06-12 01:17 | ClCap | 39598.18
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 92136.25 | 2019-06-12 01:17 | ClCap | 92136.25
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 43739.75 | 2019-06-12 01:17 | ClCap | 43739.75
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 98394.35 | 2019-06-12 01:17 | ClCap | 98394.35
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 93730.57 | 2019-06-12 01:17 | ClCap | 93730.57
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 80535.29 | 2019-06-12 01:17 | ClCap | 80535.29
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 41814.64 | 2019-06-12 01:17 | ClCap | 41814.64
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 87763.47 | 2019-06-12 01:17 | ClCap | 87763.47
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 73221.5 | 2019-06-12 01:17 | ClCap | 73221.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 11373.6 | 2019-06-12 01:17 | ClCap | 11373.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 19652.08 | 2019-06-12 01:17 | ClCap | 19652.08
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 57770.08 | 2019-06-12 01:17 | ClCap | 57770.08
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 22659.21 | 2019-06-12 01:17 | ClCap | 22659.21
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 61052.5 | 2019-06-12 01:17 | ClCap | 61052.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 55274.56 | 2019-06-12 01:17 | ClCap | 55274.56
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 52772.14 | 2019-06-12 01:17 | ClCap | 52772.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 10955.66 | 2019-06-12 01:17 | ClCap | 10955.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 9668.571 | 2019-06-12 01:17 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 12164.27 | 2019-06-12 01:17 | ClCap | 12164.27
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 9668.571 | 2019-06-12 01:17 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 63351.45 | 2019-06-12 01:17 | ClCap | 63351.45
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 503565.2 | 2019-06-12 01:17 | ClCap | 503565.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 320398.2 | 2019-06-12 01:17 | ClCap | 320398.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 539120.1 | 2019-06-12 01:17 | ClCap | 539120.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 385395.3 | 2019-06-12 01:17 | ClCap | 385395.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 95123.73 | 2019-06-12 01:17 | ClCap | 95123.73
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 18077.37 | 2019-06-12 01:17 | ClCap | 18077.37
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 51730.01 | 2019-06-12 01:17 | ClCap | 51730.01
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 23269.99 | 2019-06-12 01:17 | ClCap | 23269.99
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 58466.54 | 2019-06-12 01:17 | ClCap | 58466.54
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 50086.79 | 2019-06-12 01:17 | ClCap | 50086.79
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 22617.21 | 2019-06-12 01:17 | ClCap | 22617.21
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 27150.39 | 2019-06-12 01:17 | ClCap | 27150.39
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -486855.8 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -164973.8 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -382434.7 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -271131.2 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -401489.8 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -328900.7 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -190715.3 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -76035.87 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -105259.5 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -48641.69 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -34348.64 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -50388.95 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -46137.98 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -92879.45 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -58461.34 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -96429.77 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -93724.27 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -86491.91 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -51756.44 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -91611 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -79673.66 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -15351.12 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -24814.53 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -61652.82 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -29776.82 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -63432.43 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -59120.91 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -59380.2 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -22355.97 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -19729.55 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -23550.26 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -19729.55 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -88262.53 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -596360.5 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -438961.3 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -624023.5 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -495123.9 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -131883.9 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -25151.68 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -63680.55 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -33552.63 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -68315.97 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -61793.72 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -29135.04 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ03 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -41690.51 | 2019-06-12 01:17 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | AltAdjFactor | 1.005 | 2019-06-12 01:19 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 11050.39 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2038.277 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 6040.152 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 4921.498 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 7437.731 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 6220.555 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 4957.91 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1263.925 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2072.639 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1040.95 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 552.8823 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1223.609 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1159.762 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 1524.278 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1170.119 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 1938.975 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 1917.5 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 1928.581 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1345.026 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2235.737 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2067.552 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 234.5513 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 540.6673 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1320.558 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 786.8466 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1512.75 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1523.29 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1230.311 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 426.0772 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 304.5459 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 465.8692 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 410.2831 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1345.482 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 9413.515 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 7671.6 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 10735.89 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 8830.763 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2261.056 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 521.7494 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1336.036 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 850.9808 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1623.885 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1543.327 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 472.0611 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 531.9474 | 2019-06-12 01:19 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 11050.39 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2840.055 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 8841.143 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 5556.944 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 9547.672 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 7216.616 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5436.272 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1382.301 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 2667.01 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1365.238 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 796.2442 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1429.185 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1302.456 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2257.11 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1188.638 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2395.321 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2331.664 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2478.562 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1442.434 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2692.082 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2310.747 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 402.0009 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 613.7925 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1783.347 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 844.6099 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1882.724 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1747.388 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1547.861 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 426.0772 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 304.5459 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 465.8692 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 410.2831 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1857.015 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 11958.74 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 8312.692 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 12733.35 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 9398.667 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 2930.59 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 549.4697 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1583.317 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 850.9808 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1782.933 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1573.214 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 662.9763 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 795.857 | 2019-06-12 01:19 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 11050.39 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2038.277 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 6040.152 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 4921.498 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 7437.732 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 6220.555 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 4957.91 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1263.925 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2072.639 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1040.95 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 552.8823 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1223.609 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1159.762 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 1524.278 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1170.119 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 1938.975 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 1917.5 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 1928.581 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1345.026 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2235.737 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2067.552 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 234.5513 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 540.6673 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1320.558 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 786.8466 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1512.75 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1523.29 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1230.311 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 426.0772 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 304.5459 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 465.8692 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 410.2831 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1345.482 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 9413.515 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 7671.6 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 10735.89 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 8830.763 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2261.056 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 521.7494 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1336.036 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 850.9808 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1623.885 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1543.327 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 472.0611 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 531.9474 | 2019-06-12 01:19 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 11050.39 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2038.277 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 6040.152 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 4921.498 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 7437.732 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 6220.555 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 4957.91 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1263.925 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2072.639 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1040.95 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 552.8823 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1223.609 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1159.762 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 1524.278 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1170.119 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 1938.975 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 1917.5 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 1928.581 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1345.026 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2235.737 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2067.552 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 234.5513 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 540.6673 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1320.558 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 786.8466 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1512.75 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1523.29 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1230.311 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 426.0772 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 304.5459 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 465.8692 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 410.2831 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1345.482 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 9413.515 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 7671.6 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 10735.89 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 8830.763 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2261.056 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 521.7494 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1336.036 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 850.9808 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1623.885 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1543.327 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 472.0611 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 531.9474 | 2019-06-12 01:19 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 376980.3 | 2019-06-12 01:19 | ClCap | 376980.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 115891.9 | 2019-06-12 01:19 | ClCap | 115891.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 262255.3 | 2019-06-12 01:19 | ClCap | 262255.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 213684.9 | 2019-06-12 01:19 | ClCap | 213684.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 322936.4 | 2019-06-12 01:19 | ClCap | 322936.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 270088.2 | 2019-06-12 01:19 | ClCap | 270088.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 169137.4 | 2019-06-12 01:19 | ClCap | 169137.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 54877.92 | 2019-06-12 01:19 | ClCap | 54877.92
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 70707.4 | 2019-06-12 01:19 | ClCap | 70707.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 35511.65 | 2019-06-12 01:19 | ClCap | 35511.65
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 18861.39 | 2019-06-12 01:19 | ClCap | 18861.39
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 41743.02 | 2019-06-12 01:19 | ClCap | 41743.02
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 39564.91 | 2019-06-12 01:19 | ClCap | 39564.91
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 66182.11 | 2019-06-12 01:19 | ClCap | 66182.11
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 50804.98 | 2019-06-12 01:19 | ClCap | 50804.98
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 84187.69 | 2019-06-12 01:19 | ClCap | 84187.69
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 83255.27 | 2019-06-12 01:19 | ClCap | 83255.27
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 65792.91 | 2019-06-12 01:19 | ClCap | 65792.91
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 45885.11 | 2019-06-12 01:19 | ClCap | 45885.11
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 76271.41 | 2019-06-12 01:19 | ClCap | 76271.41
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 70533.84 | 2019-06-12 01:19 | ClCap | 70533.84
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 8001.639 | 2019-06-12 01:19 | ClCap | 8001.639
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 18444.68 | 2019-06-12 01:19 | ClCap | 18444.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 45050.38 | 2019-06-12 01:19 | ClCap | 45050.38
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 26843.01 | 2019-06-12 01:19 | ClCap | 26843.01
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 51606.95 | 2019-06-12 01:19 | ClCap | 51606.95
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 51966.54 | 2019-06-12 01:19 | ClCap | 51966.54
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 41971.66 | 2019-06-12 01:19 | ClCap | 41971.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 14535.48 | 2019-06-12 01:19 | ClCap | 14535.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 10389.48 | 2019-06-12 01:19 | ClCap | 10389.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 15892.97 | 2019-06-12 01:19 | ClCap | 15892.97
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 13996.67 | 2019-06-12 01:19 | ClCap | 13996.67
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 45900.65 | 2019-06-12 01:19 | ClCap | 45900.65
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 408722.2 | 2019-06-12 01:19 | ClCap | 408722.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 333090.6 | 2019-06-12 01:19 | ClCap | 333090.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 466137.9 | 2019-06-12 01:19 | ClCap | 466137.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 383419.9 | 2019-06-12 01:19 | ClCap | 383419.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 77135.17 | 2019-06-12 01:19 | ClCap | 77135.17
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 17799.3 | 2019-06-12 01:19 | ClCap | 17799.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 45578.43 | 2019-06-12 01:19 | ClCap | 45578.43
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 29030.92 | 2019-06-12 01:19 | ClCap | 29030.92
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 55398.29 | 2019-06-12 01:19 | ClCap | 55398.29
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 52650.08 | 2019-06-12 01:19 | ClCap | 52650.08
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 16104.21 | 2019-06-12 01:19 | ClCap | 16104.21
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 18147.21 | 2019-06-12 01:19 | ClCap | 18147.21
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -736538.3 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -182638.5 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -418670.5 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -319310.2 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -436187.7 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -368436.4 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -196401.6 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -83034.63 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -123719.6 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -53850.86 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -36096.92 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -55259.89 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -51721.6 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -100837.7 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -68255.89 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -104089.5 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -102762.2 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -91628.14 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -60276.2 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -96661.13 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -86204.11 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -18128.13 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -26851.05 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -65377.67 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -36700.83 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -67112.23 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -63933.8 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -60398.41 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -30264.75 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -23008.86 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -31798.64 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -30997.45 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -92745.88 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -636396.6 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -502690.1 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -661736.1 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -542253.1 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -140985.8 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -26619.77 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -66930.95 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -41360 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -71062.13 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -66262.45 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -29448.86 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ04 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -43605.21 | 2019-06-12 01:19 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | AltAdjFactor | 1.0094 | 2019-06-12 01:21 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 6468.214 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2578.161 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 7756.675 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 4146.942 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 9223.933 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 6291.125 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5308.294 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1282.439 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2059.134 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1132.984 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 756.8575 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1356.899 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1102.104 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 2005.109 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 980.412 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 2309.025 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2096.354 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2253.125 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1122.834 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2612.371 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2101.42 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 334.8441 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 548.4993 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1621.894 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 640.745 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1813.633 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1587.86 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1553.637 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 291.3859 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 284.6473 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 363.6392 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 284.6473 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1865.097 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 11361.47 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 6907.721 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 12567.22 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 8835.894 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2616.145 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 520.3344 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1473.883 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 622.1314 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1742.01 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1458.632 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 665.8615 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 799.3204 | 2019-06-12 01:21 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 6468.214 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2578.161 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 7756.675 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 4146.942 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 9223.933 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 6291.125 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5308.294 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1282.439 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 2059.134 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1132.984 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 756.8575 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1356.899 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1102.104 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2005.109 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 980.412 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2309.025 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2096.354 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2253.125 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1122.834 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2612.371 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2101.42 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 334.8441 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 548.4993 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1621.894 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 640.745 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1813.633 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1587.86 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1553.637 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 291.3859 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 284.6473 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 363.6392 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 284.6473 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1865.097 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 11361.47 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 6907.721 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 12567.22 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 8835.894 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 2616.145 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 520.3344 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1473.883 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 622.1314 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1742.01 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1458.632 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 665.8615 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 799.3204 | 2019-06-12 01:21 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 6468.214 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2578.161 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 7756.675 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 4146.942 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 9223.933 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 6291.125 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5308.294 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1282.439 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2059.134 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1132.984 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 756.8575 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1356.899 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1102.104 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 2005.109 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 980.412 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 2309.025 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2096.354 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2253.125 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1122.834 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2612.371 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2101.42 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 334.8441 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 548.4993 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1621.894 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 640.745 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1813.633 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1587.86 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1553.637 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 291.3859 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 284.6473 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 363.6392 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 284.6473 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1865.097 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 11361.47 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 6907.721 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 12567.22 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 8835.894 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2616.145 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 520.3344 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1473.883 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 622.1314 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1742.01 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1458.632 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 665.8615 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 799.3204 | 2019-06-12 01:21 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 6468.214 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2578.161 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 7756.675 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 4146.942 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 9223.933 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 6291.125 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5308.294 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1282.439 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2059.134 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1132.984 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 756.8575 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1356.899 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1102.104 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 2005.109 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 980.412 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 2309.025 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2096.354 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2253.125 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1122.834 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2612.371 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2101.42 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 334.8441 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 548.4993 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1621.894 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 640.745 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1813.633 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1587.86 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1553.637 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 291.3859 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 284.6473 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 363.6392 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 284.6473 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1865.097 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 11361.47 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 6907.721 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 12567.22 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 8835.894 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2616.145 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 520.3344 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1473.883 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 622.1314 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1742.01 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1458.632 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 665.8615 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 799.3204 | 2019-06-12 01:21 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 219704.8 | 2019-06-12 01:21 | ClCap | 219704.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 145953.3 | 2019-06-12 01:21 | ClCap | 145953.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 335325.2 | 2019-06-12 01:21 | ClCap | 335325.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 179274.5 | 2019-06-12 01:21 | ClCap | 179274.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 398755.5 | 2019-06-12 01:21 | ClCap | 398755.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 271968.7 | 2019-06-12 01:21 | ClCap | 271968.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 180306 | 2019-06-12 01:21 | ClCap | 180306
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 55440.5 | 2019-06-12 01:21 | ClCap | 55440.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 69942.3 | 2019-06-12 01:21 | ClCap | 69942.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 38483.9 | 2019-06-12 01:21 | ClCap | 38483.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 25708.06 | 2019-06-12 01:21 | ClCap | 25708.06
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 46089.59 | 2019-06-12 01:21 | ClCap | 46089.59
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 37434.99 | 2019-06-12 01:21 | ClCap | 37434.99
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 86681.94 | 2019-06-12 01:21 | ClCap | 86681.94
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 42383.73 | 2019-06-12 01:21 | ClCap | 42383.73
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 99820.39 | 2019-06-12 01:21 | ClCap | 99820.39
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 90626.48 | 2019-06-12 01:21 | ClCap | 90626.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 76531.55 | 2019-06-12 01:21 | ClCap | 76531.55
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 38139.14 | 2019-06-12 01:21 | ClCap | 38139.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 88733.99 | 2019-06-12 01:21 | ClCap | 88733.99
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 71378.61 | 2019-06-12 01:21 | ClCap | 71378.61
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 11373.6 | 2019-06-12 01:21 | ClCap | 11373.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 18630.79 | 2019-06-12 01:21 | ClCap | 18630.79
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 55090.61 | 2019-06-12 01:21 | ClCap | 55090.61
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 21764.09 | 2019-06-12 01:21 | ClCap | 21764.09
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 61603.38 | 2019-06-12 01:21 | ClCap | 61603.38
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 53934.61 | 2019-06-12 01:21 | ClCap | 53934.61
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 52772.14 | 2019-06-12 01:21 | ClCap | 52772.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 9897.461 | 2019-06-12 01:21 | ClCap | 9897.461
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 9668.571 | 2019-06-12 01:21 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 12351.68 | 2019-06-12 01:21 | ClCap | 12351.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 9668.571 | 2019-06-12 01:21 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 63351.45 | 2019-06-12 01:21 | ClCap | 63351.45
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 491162.3 | 2019-06-12 01:21 | ClCap | 491162.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 298624.4 | 2019-06-12 01:21 | ClCap | 298624.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 543287.6 | 2019-06-12 01:21 | ClCap | 543287.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 381980.3 | 2019-06-12 01:21 | ClCap | 381980.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 88862.18 | 2019-06-12 01:21 | ClCap | 88862.18
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 17674.12 | 2019-06-12 01:21 | ClCap | 17674.12
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 50063.14 | 2019-06-12 01:21 | ClCap | 50063.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 21131.84 | 2019-06-12 01:21 | ClCap | 21131.84
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 59170.59 | 2019-06-12 01:21 | ClCap | 59170.59
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 49545.14 | 2019-06-12 01:21 | ClCap | 49545.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 22617.21 | 2019-06-12 01:21 | ClCap | 22617.21
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 27150.39 | 2019-06-12 01:21 | ClCap | 27150.39
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -460224.9 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -166113.5 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -370515.2 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -260830.5 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -410581.3 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -325150.6 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -186968.9 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -75829.27 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -100053.8 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -45222.5 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -33569.08 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -51557.16 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -44093.74 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -89813.19 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -58591.73 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -98006.01 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -92242.29 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -82531.8 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -48407.38 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -91879.72 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -77611.26 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -15617.06 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -23926.9 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -59178.1 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -29070.11 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -63592.31 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -57780.48 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -58605.43 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -20732.63 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -20253.16 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -24307.07 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -20253.16 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -88878.36 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -586765.4 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -425765.2 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -601582.1 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -496200.3 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -123924.3 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -24627.77 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -61332.54 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -31072.83 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -67284.32 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -60478.58 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -28478.82 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ05 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -41728.58 | 2019-06-12 01:21 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | AltAdjFactor | 1.0033 | 2019-06-12 01:23 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 9059.601 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 3121.562 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 8804.049 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 5447.999 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 9846.685 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 7322.727 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5421.403 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1373.734 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2619.988 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1376.326 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 640.1895 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1496.914 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1293.063 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 2273.603 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1150.68 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 2467.483 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2314.142 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2503.125 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1408.364 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2776.98 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2370.855 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 389.1382 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 606.597 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1818.947 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 812.2685 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1944.921 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1794.469 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1544.232 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 358.6382 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 282.9242 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 395.7923 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 318.0155 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1853.806 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 11998.48 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 8138.576 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 13062.93 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 9531.79 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2913.509 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 547.775 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1616.203 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 787.3654 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1841.966 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1611.152 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 661.8306 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 794.4817 | 2019-06-12 01:23 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 9059.601 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3121.562 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 8804.049 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 5447.999 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 9846.685 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 7322.727 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5421.403 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1373.734 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 2619.988 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1376.326 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 640.1895 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1496.914 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1293.063 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2273.603 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1150.68 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2467.483 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2314.142 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2503.125 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1408.364 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2776.98 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2370.855 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 389.1382 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 606.597 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1818.947 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 812.2685 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1944.921 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1794.469 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1544.232 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 358.6382 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 282.9242 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 395.7923 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 318.0155 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1853.806 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 11998.48 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 8138.576 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 13062.93 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 9531.79 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 2913.509 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 547.775 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1616.203 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 787.3654 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1841.966 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1611.152 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 661.8306 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 794.4817 | 2019-06-12 01:23 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 9059.601 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 3121.562 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 8804.049 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 5447.999 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 9846.685 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 7322.727 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5421.403 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1373.734 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2619.988 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1376.326 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 640.1895 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1496.914 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1293.063 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 2273.603 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1150.68 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 2467.483 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2314.142 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2503.125 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1408.364 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2776.98 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2370.855 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 389.1382 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 606.597 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1818.947 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 812.2685 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1944.921 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1794.469 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1544.232 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 358.6382 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 282.9242 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 395.7923 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 318.0155 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1853.806 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 11998.48 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 8138.576 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 13062.93 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 9531.79 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2913.509 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 547.775 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1616.203 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 787.3654 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1841.966 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1611.152 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 661.8306 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 794.4817 | 2019-06-12 01:23 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 9059.601 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 3121.562 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 8804.049 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 5447.999 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 9846.685 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 7322.727 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5421.403 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1373.734 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2619.988 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1376.326 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 640.1895 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1496.914 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1293.063 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 2273.603 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1150.68 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 2467.483 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2314.142 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2503.125 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1408.364 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2776.98 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2370.855 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 389.1382 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 606.597 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1818.947 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 812.2685 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1944.921 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1794.469 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1544.232 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 358.6382 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 282.9242 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 395.7923 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 318.0155 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1853.806 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 11998.48 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 8138.576 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 13062.93 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 9531.79 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2913.509 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 547.775 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1616.203 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 787.3654 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1841.966 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1611.152 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 661.8306 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 794.4817 | 2019-06-12 01:23 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 309600.3 | 2019-06-12 01:23 | ClCap | 309600.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 177792.3 | 2019-06-12 01:23 | ClCap | 177792.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 382921.8 | 2019-06-12 01:23 | ClCap | 382921.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 236954.3 | 2019-06-12 01:23 | ClCap | 236954.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 428270 | 2019-06-12 01:23 | ClCap | 428270
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 318493.4 | 2019-06-12 01:23 | ClCap | 318493.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 185269.5 | 2019-06-12 01:23 | ClCap | 185269.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 59748.93 | 2019-06-12 01:23 | ClCap | 59748.93
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 89534.73 | 2019-06-12 01:23 | ClCap | 89534.73
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 47034.18 | 2019-06-12 01:23 | ClCap | 47034.18
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 21877.66 | 2019-06-12 01:23 | ClCap | 21877.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 51155.12 | 2019-06-12 01:23 | ClCap | 51155.12
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 44188.79 | 2019-06-12 01:23 | ClCap | 44188.79
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 98887.68 | 2019-06-12 01:23 | ClCap | 98887.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 50047.49 | 2019-06-12 01:23 | ClCap | 50047.49
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 107320.3 | 2019-06-12 01:23 | ClCap | 107320.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 100650.9 | 2019-06-12 01:23 | ClCap | 100650.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 85541.12 | 2019-06-12 01:23 | ClCap | 85541.12
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 48129.03 | 2019-06-12 01:23 | ClCap | 48129.03
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 94899.74 | 2019-06-12 01:23 | ClCap | 94899.74
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 81020.94 | 2019-06-12 01:23 | ClCap | 81020.94
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 13298.3 | 2019-06-12 01:23 | ClCap | 13298.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 20729.68 | 2019-06-12 01:23 | ClCap | 20729.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 62160.18 | 2019-06-12 01:23 | ClCap | 62160.18
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 27758.24 | 2019-06-12 01:23 | ClCap | 27758.24
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 66465.19 | 2019-06-12 01:23 | ClCap | 66465.19
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 61323.68 | 2019-06-12 01:23 | ClCap | 61323.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 52772.14 | 2019-06-12 01:23 | ClCap | 52772.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 12256 | 2019-06-12 01:23 | ClCap | 12256
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 9668.571 | 2019-06-12 01:23 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 13525.7 | 2019-06-12 01:23 | ClCap | 13525.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 10867.77 | 2019-06-12 01:23 | ClCap | 10867.77
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 63351.45 | 2019-06-12 01:23 | ClCap | 63351.45
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 521859.9 | 2019-06-12 01:23 | ClCap | 521859.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 353977.8 | 2019-06-12 01:23 | ClCap | 353977.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 568157.1 | 2019-06-12 01:23 | ClCap | 568157.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 414574.1 | 2019-06-12 01:23 | ClCap | 414574.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 99565.45 | 2019-06-12 01:23 | ClCap | 99565.45
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 18719.51 | 2019-06-12 01:23 | ClCap | 18719.51
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 55231.66 | 2019-06-12 01:23 | ClCap | 55231.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 26907.21 | 2019-06-12 01:23 | ClCap | 26907.21
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 62946.84 | 2019-06-12 01:23 | ClCap | 62946.84
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 55059.07 | 2019-06-12 01:23 | ClCap | 55059.07
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 22617.21 | 2019-06-12 01:23 | ClCap | 22617.21
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 27150.4 | 2019-06-12 01:23 | ClCap | 27150.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -520548.5 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -170879.5 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -384576.9 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -284555 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -410374.6 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -338527.1 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -265036.7 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -74087.88 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -112286.6 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -51065.85 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -28521.17 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -54139.77 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -48330.9 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -94008.44 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -60357.91 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -98813.53 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -94878.73 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -87692.36 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -55219.71 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -93148.91 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -83326.7 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -16496.78 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -24764.31 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -63639.75 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -33346.95 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -65815.21 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -62482.14 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -56137.05 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -22565.42 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -18804.83 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -23614.54 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -21137.21 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -83786.36 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -587718.4 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -448489.4 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -596079.9 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -498482.1 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -131344.7 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -24745.01 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -64851.27 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -36177.6 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -68668.83 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -64298.81 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -27981.83 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ06 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -40094.66 | 2019-06-12 01:23 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | AltAdjFactor | 1.0005 | 2019-06-12 01:25 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 8684.777 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 3146.85 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 8750.953 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 5244.5 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 9637.064 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 7191.496 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5385.232 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1356.538 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2554.382 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1369.197 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 554.9838 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1451.061 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1278.615 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 2267.446 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1106.879 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 2409.471 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2297.94 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2493.193 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1360.903 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2708.101 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2339.712 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 377.6879 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 594.9379 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1811.231 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 773.6452 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1889.175 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1769.573 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1539.975 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 354.1612 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 282.1443 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 387.5277 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 312.7556 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1848.696 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 11952.17 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 7967.557 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 12826.93 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 9420.578 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2880.565 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 542.0142 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1616.698 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 760.0725 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1782.936 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1590.285 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 660.0064 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 792.2919 | 2019-06-12 01:25 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 8684.777 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3146.85 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 8750.953 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 5244.5 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 9637.064 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 7191.496 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5385.232 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1356.538 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 2554.382 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1369.197 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 554.9838 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1451.061 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1278.615 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2267.446 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1106.879 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2409.471 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2297.94 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2493.193 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1360.903 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2708.101 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2339.712 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 377.6879 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 594.9379 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1811.231 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 773.6452 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1889.175 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1769.573 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1539.975 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 354.1612 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 282.1443 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 387.5277 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 312.7556 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1848.696 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 11952.17 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 7967.557 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 12826.93 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 9420.578 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 2880.565 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 542.0142 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1616.698 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 760.0725 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1782.936 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1590.285 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 660.0064 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 792.2919 | 2019-06-12 01:25 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 8684.777 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 3146.851 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 8750.953 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 5244.5 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 9637.064 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 7191.497 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5385.232 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1356.538 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2554.382 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1369.197 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 554.9838 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1451.061 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1278.615 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 2267.446 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1106.879 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 2409.471 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2297.94 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2493.193 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1360.903 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2708.101 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2339.712 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 377.6879 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 594.9379 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1811.231 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 773.6452 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1889.175 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1769.573 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1539.975 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 354.1612 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 282.1443 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 387.5277 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 312.7556 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1848.696 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 11952.17 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 7967.558 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 12826.93 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 9420.578 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2880.565 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 542.0142 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1616.698 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 760.0725 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1782.936 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1590.285 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 660.0064 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 792.2919 | 2019-06-12 01:25 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 8684.777 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 3146.85 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 8750.953 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 5244.5 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 9637.064 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 7191.496 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5385.232 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1356.538 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2554.382 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1369.197 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 554.9838 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1451.061 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1278.615 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 2267.446 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1106.879 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 2409.471 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2297.94 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2493.193 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1360.903 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2708.101 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2339.712 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 377.6879 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 594.9379 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1811.231 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 773.6452 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1889.175 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1769.573 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1539.975 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 354.1612 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 282.1443 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 387.5277 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 312.7556 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1848.696 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 11952.17 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 7967.557 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 12826.93 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 9420.578 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2880.565 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 542.0142 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1616.698 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 760.0725 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1782.936 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1590.285 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 660.0064 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 792.2919 | 2019-06-12 01:25 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 297611.4 | 2019-06-12 01:25 | ClCap | 297611.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 179728 | 2019-06-12 01:25 | ClCap | 179728
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 381664.4 | 2019-06-12 01:25 | ClCap | 381664.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 228733.8 | 2019-06-12 01:25 | ClCap | 228733.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 420311.3 | 2019-06-12 01:25 | ClCap | 420311.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 313650.2 | 2019-06-12 01:25 | ClCap | 313650.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 184542.1 | 2019-06-12 01:25 | ClCap | 184542.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 59164.12 | 2019-06-12 01:25 | ClCap | 59164.12
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 87533.98 | 2019-06-12 01:25 | ClCap | 87533.98
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 46919.87 | 2019-06-12 01:25 | ClCap | 46919.87
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 19018.28 | 2019-06-12 01:25 | ClCap | 19018.28
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 49725.2 | 2019-06-12 01:25 | ClCap | 49725.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 43815.78 | 2019-06-12 01:25 | ClCap | 43815.78
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 98892.48 | 2019-06-12 01:25 | ClCap | 98892.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 48275.45 | 2019-06-12 01:25 | ClCap | 48275.45
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 105086.8 | 2019-06-12 01:25 | ClCap | 105086.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 100222.5 | 2019-06-12 01:25 | ClCap | 100222.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 85437.16 | 2019-06-12 01:25 | ClCap | 85437.16
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 46635.66 | 2019-06-12 01:25 | ClCap | 46635.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 92801.68 | 2019-06-12 01:25 | ClCap | 92801.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 80177.65 | 2019-06-12 01:25 | ClCap | 80177.65
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 12942.67 | 2019-06-12 01:25 | ClCap | 12942.67
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 20387.44 | 2019-06-12 01:25 | ClCap | 20387.44
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 62067.58 | 2019-06-12 01:25 | ClCap | 62067.58
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 26511.41 | 2019-06-12 01:25 | ClCap | 26511.41
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 64738.57 | 2019-06-12 01:25 | ClCap | 64738.57
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 60640.03 | 2019-06-12 01:25 | ClCap | 60640.03
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 52772.14 | 2019-06-12 01:25 | ClCap | 52772.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 12136.46 | 2019-06-12 01:25 | ClCap | 12136.46
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 9668.571 | 2019-06-12 01:25 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 13279.87 | 2019-06-12 01:25 | ClCap | 13279.87
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 10717.56 | 2019-06-12 01:25 | ClCap | 10717.56
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 63351.45 | 2019-06-12 01:25 | ClCap | 63351.45
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 521282.2 | 2019-06-12 01:25 | ClCap | 521282.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 347497.3 | 2019-06-12 01:25 | ClCap | 347497.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 559434.4 | 2019-06-12 01:25 | ClCap | 559434.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 410869.4 | 2019-06-12 01:25 | ClCap | 410869.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 98711.7 | 2019-06-12 01:25 | ClCap | 98711.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 18573.84 | 2019-06-12 01:25 | ClCap | 18573.84
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 55401.28 | 2019-06-12 01:25 | ClCap | 55401.28
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 26046.29 | 2019-06-12 01:25 | ClCap | 26046.29
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 61097.96 | 2019-06-12 01:25 | ClCap | 61097.96
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 54496.16 | 2019-06-12 01:25 | ClCap | 54496.16
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 22617.21 | 2019-06-12 01:25 | ClCap | 22617.21
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 27150.39 | 2019-06-12 01:25 | ClCap | 27150.39
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -458251.5 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -155396.1 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -357010.4 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -253214.5 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -375903.4 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -308410.8 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -264034.6 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -66693.22 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -102651.2 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -48586.7 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -23902.48 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -50455.91 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -45667.28 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -88149.67 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -53658.39 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -90735.12 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -88713.62 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -84115.8 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -50847.3 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -88138.18 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -79176.12 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -15077.78 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -22957.48 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -61339.79 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -30341.05 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -62175.92 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -59668.85 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -53242.3 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -20012.65 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -16674.53 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -20952.6 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -18483.63 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -76726.72 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -544205.8 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -403088.7 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -548601.9 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -455178.1 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -122486.8 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -23030.96 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -62274.06 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -33179.21 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -63907.71 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -61072.59 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -26602.1 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ07 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -37070.55 | 2019-06-12 01:25 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | AltAdjFactor | 1.0147 | 2019-06-12 01:27 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 13038.69 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2488.38 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 7032.273 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 5647.536 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 7656.761 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 6771.18 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5061.28 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1380.953 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2342.208 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1227.814 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 699.1893 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1293.729 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1274.335 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 1819.482 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1310.474 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 1944.687 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2093.836 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2187.451 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1482.822 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2336.295 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2194.674 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 331.0139 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 572.1281 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1519.354 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 875.1965 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1620.918 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1626.881 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1443.008 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 503.9737 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 366.9108 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 485.3681 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 481.4367 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1289.971 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 10671.6 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 8819.933 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 11230.47 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 9721.656 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2786.37 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 563.8099 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1521.875 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 943.9967 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1741.634 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1663.571 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 580.9842 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 674.0128 | 2019-06-12 01:27 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 13038.69 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3303.352 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 9204.432 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 5958.931 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 10224.41 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 7697.612 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5517.389 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1410.827 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 2782.474 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1458.131 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 699.1893 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1574.212 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1387.739 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2385.168 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1310.474 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2582.186 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2448.7 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2607.563 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1536.074 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2884.414 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2472.13 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 437.5555 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 629.3463 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1892.683 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 912.8666 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 2031.898 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1879.318 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1620.737 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 503.9737 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 366.9108 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 485.3681 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 481.4367 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1874.868 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 12307.39 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 8819.933 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 13493.39 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 9915.845 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 3022.003 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 563.8099 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1675.067 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 943.9968 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1918 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1685.543 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 669.3501 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 803.5084 | 2019-06-12 01:27 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 13038.69 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2488.38 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 7032.273 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 5647.536 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 7656.761 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 6771.18 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5061.28 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1380.953 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2342.208 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1227.814 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 699.1893 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1293.729 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1274.335 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 1819.482 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1310.474 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 1944.687 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2093.836 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2187.451 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1482.822 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2336.295 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2194.674 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 331.0139 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 572.1281 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1519.354 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 875.1965 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1620.918 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1626.881 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1443.008 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 503.9737 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 366.9108 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 485.3681 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 481.4367 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1289.971 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 10671.6 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 8819.933 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 11230.47 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 9721.656 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2786.37 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 563.8099 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1521.875 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 943.9968 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1741.634 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1663.571 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 580.9842 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 674.0128 | 2019-06-12 01:27 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 13038.69 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2488.38 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 7032.273 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 5647.536 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 7656.761 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 6771.18 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5061.28 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1380.953 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2342.208 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1227.814 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 699.1893 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1293.729 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1274.335 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 1819.482 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1310.474 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 1944.687 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2093.836 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2187.451 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1482.822 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2336.295 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2194.674 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 331.0139 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 572.1281 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1519.354 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 875.1965 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1620.918 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1626.881 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1443.008 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 503.9737 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 366.9108 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 485.3681 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 481.4367 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1289.971 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 10671.6 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 8819.933 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 11230.47 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 9721.656 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2786.37 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 563.8099 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1521.875 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 943.9968 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1741.634 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1663.571 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 580.9842 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 674.0128 | 2019-06-12 01:27 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 440574.7 | 2019-06-12 01:27 | ClCap | 440574.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 140136.5 | 2019-06-12 01:27 | ClCap | 140136.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 302424.4 | 2019-06-12 01:27 | ClCap | 302424.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 242873.5 | 2019-06-12 01:27 | ClCap | 242873.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 329280.7 | 2019-06-12 01:27 | ClCap | 329280.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 291196.1 | 2019-06-12 01:27 | ClCap | 291196.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 171019.7 | 2019-06-12 01:27 | ClCap | 171019.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 59388.2 | 2019-06-12 01:27 | ClCap | 59388.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 79142.77 | 2019-06-12 01:27 | ClCap | 79142.77
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 41487.62 | 2019-06-12 01:27 | ClCap | 41487.62
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 23625.47 | 2019-06-12 01:27 | ClCap | 23625.47
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 43714.86 | 2019-06-12 01:27 | ClCap | 43714.86
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 43059.53 | 2019-06-12 01:27 | ClCap | 43059.53
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 78247.2 | 2019-06-12 01:27 | ClCap | 78247.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 56357.24 | 2019-06-12 01:27 | ClCap | 56357.24
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 83631.7 | 2019-06-12 01:27 | ClCap | 83631.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 90045.85 | 2019-06-12 01:27 | ClCap | 90045.85
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 73913.57 | 2019-06-12 01:27 | ClCap | 73913.57
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 50104.28 | 2019-06-12 01:27 | ClCap | 50104.28
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 78942.97 | 2019-06-12 01:27 | ClCap | 78942.97
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 74157.61 | 2019-06-12 01:27 | ClCap | 74157.61
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 11184.9 | 2019-06-12 01:27 | ClCap | 11184.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 19332.1 | 2019-06-12 01:27 | ClCap | 19332.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 51338.68 | 2019-06-12 01:27 | ClCap | 51338.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 29572.73 | 2019-06-12 01:27 | ClCap | 29572.73
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 54770.52 | 2019-06-12 01:27 | ClCap | 54770.52
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 54972 | 2019-06-12 01:27 | ClCap | 54972
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 48758.98 | 2019-06-12 01:27 | ClCap | 48758.98
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 17029.18 | 2019-06-12 01:27 | ClCap | 17029.18
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 12397.85 | 2019-06-12 01:27 | ClCap | 12397.85
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 16400.5 | 2019-06-12 01:27 | ClCap | 16400.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 16267.66 | 2019-06-12 01:27 | ClCap | 16267.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 43587.88 | 2019-06-12 01:27 | ClCap | 43587.88
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 458934.5 | 2019-06-12 01:27 | ClCap | 458934.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 379303.1 | 2019-06-12 01:27 | ClCap | 379303.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 482968.7 | 2019-06-12 01:27 | ClCap | 482968.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 418081.9 | 2019-06-12 01:27 | ClCap | 418081.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 94150.92 | 2019-06-12 01:27 | ClCap | 94150.92
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 19051.03 | 2019-06-12 01:27 | ClCap | 19051.03
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 51423.85 | 2019-06-12 01:27 | ClCap | 51423.85
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 31897.47 | 2019-06-12 01:27 | ClCap | 31897.47
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 58849.48 | 2019-06-12 01:27 | ClCap | 58849.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 56211.74 | 2019-06-12 01:27 | ClCap | 56211.74
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 19631.35 | 2019-06-12 01:27 | ClCap | 19631.35
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 22774.76 | 2019-06-12 01:27 | ClCap | 22774.76
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -717740.7 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -175168.9 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -394204.4 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -298736.9 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -418784.9 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -347903.2 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -266576.9 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -74920.13 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -116557.3 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -53219.38 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -30676.7 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -56072.7 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -50885 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -96741.45 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -65274.93 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -101507.5 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -98258.73 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -90183.34 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -58804.45 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -96708.08 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -85771.11 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -17732.72 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -25312.13 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -65394.21 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -36306.47 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -67828.52 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -64548 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -58154.73 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -30602.29 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -24150.39 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -28013.57 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -31229.69 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -83965.86 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -597228.5 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -472771.9 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -607338 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -510994.9 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -134891 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -25203.06 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -66626.23 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -42475.98 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -70872.95 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -66618.28 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -28195.95 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ08 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -40328.38 | 2019-06-12 01:27 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | AltAdjFactor | 1.0277 | 2019-06-12 01:29 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 17535.03 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 3081.965 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 8331.301 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 7361.734 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 9620.271 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 8452.094 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5684.671 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1700.36 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2849.374 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1409.706 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 965.2324 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1547.959 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1538.606 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 2127.615 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1744.176 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 2449.556 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2502.401 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2457.619 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1838.453 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2702.065 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2610.527 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 419.508 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 676.5618 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1714.681 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 1126.097 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1826.144 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1934.803 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1675.298 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 647.4489 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 542.014 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 676.5267 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 633.9416 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1779.612 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 12913.34 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 11116.5 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 14115.5 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 12148.15 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 3199.031 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 659.4698 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1729.186 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 1197.511 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1996.187 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1994.5 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 676.8079 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 771.5061 | 2019-06-12 01:29 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 17535.03 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3452.382 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 9652.439 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 7361.734 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 10387.97 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 8452.094 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5684.671 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1700.36 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 3049.224 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1553.979 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 965.2324 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1594.321 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1538.606 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2523.487 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1744.176 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2611.171 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2584.56 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2742.944 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1838.453 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2919.131 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2642.307 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 523.2955 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 676.5618 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 2002.813 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 1126.097 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 2058.963 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 2018.41 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1806.251 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 647.4489 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 542.014 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 676.5267 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 633.9416 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1898.893 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 12913.34 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 11116.51 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 14115.5 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 12148.15 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 3212.755 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 659.4698 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1767.165 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 1197.511 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1996.187 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1994.5 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 677.9273 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 813.8047 | 2019-06-12 01:29 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 17535.03 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 3081.965 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 8331.301 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 7361.734 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 9620.271 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 8452.094 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5684.671 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1700.36 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2849.374 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1409.706 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 965.2324 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1547.959 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1538.606 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 2127.615 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1744.176 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 2449.556 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2502.401 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2457.619 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1838.453 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2702.065 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2610.527 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 419.508 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 676.5618 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1714.681 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 1126.097 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1826.144 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1934.803 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1675.298 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 647.4489 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 542.014 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 676.5267 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 633.9416 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1779.612 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 12913.34 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 11116.51 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 14115.5 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 12148.15 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 3199.031 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 659.4698 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1729.186 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 1197.511 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1996.187 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1994.5 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 676.8079 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 771.5061 | 2019-06-12 01:29 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 17535.03 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 3081.965 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 8331.301 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 7361.734 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 9620.271 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 8452.094 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5684.671 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1700.36 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2849.374 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1409.706 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 965.2324 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1547.959 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1538.606 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 2127.615 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1744.176 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 2449.556 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2502.401 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2457.619 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1838.453 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2702.065 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2610.527 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 419.508 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 676.5618 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1714.681 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 1126.097 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1826.144 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1934.803 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1675.298 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 647.4489 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 542.014 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 676.5267 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 633.9416 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1779.612 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 12913.34 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 11116.51 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 14115.5 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 12148.15 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 3199.031 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 659.4698 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1729.186 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 1197.511 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1996.187 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1994.5 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 676.8079 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 771.5061 | 2019-06-12 01:29 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 585008.8 | 2019-06-12 01:29 | ClCap | 585008.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 171369.1 | 2019-06-12 01:29 | ClCap | 171369.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 353756.3 | 2019-06-12 01:29 | ClCap | 353756.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 312587.4 | 2019-06-12 01:29 | ClCap | 312587.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 408487.4 | 2019-06-12 01:29 | ClCap | 408487.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 358885.3 | 2019-06-12 01:29 | ClCap | 358885.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 189653.7 | 2019-06-12 01:29 | ClCap | 189653.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 72199.17 | 2019-06-12 01:29 | ClCap | 72199.17
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 95061.65 | 2019-06-12 01:29 | ClCap | 95061.65
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 47031.03 | 2019-06-12 01:29 | ClCap | 47031.03
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 32202.37 | 2019-06-12 01:29 | ClCap | 32202.37
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 51643.48 | 2019-06-12 01:29 | ClCap | 51643.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 51331.44 | 2019-06-12 01:29 | ClCap | 51331.44
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 90340.92 | 2019-06-12 01:29 | ClCap | 90340.92
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 74059.63 | 2019-06-12 01:29 | ClCap | 74059.63
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 104010.9 | 2019-06-12 01:29 | ClCap | 104010.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 106254.7 | 2019-06-12 01:29 | ClCap | 106254.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 81991.82 | 2019-06-12 01:29 | ClCap | 81991.82
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 61335.03 | 2019-06-12 01:29 | ClCap | 61335.03
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 90147.12 | 2019-06-12 01:29 | ClCap | 90147.12
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 87093.2 | 2019-06-12 01:29 | ClCap | 87093.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 13995.75 | 2019-06-12 01:29 | ClCap | 13995.75
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 22571.66 | 2019-06-12 01:29 | ClCap | 22571.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 57205.71 | 2019-06-12 01:29 | ClCap | 57205.71
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 37569.19 | 2019-06-12 01:29 | ClCap | 37569.19
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 60924.37 | 2019-06-12 01:29 | ClCap | 60924.37
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 64549.48 | 2019-06-12 01:29 | ClCap | 64549.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 55891.8 | 2019-06-12 01:29 | ClCap | 55891.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 21600.38 | 2019-06-12 01:29 | ClCap | 21600.38
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 18082.83 | 2019-06-12 01:29 | ClCap | 18082.83
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 22570.48 | 2019-06-12 01:29 | ClCap | 22570.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 21149.75 | 2019-06-12 01:29 | ClCap | 21149.75
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 59371.95 | 2019-06-12 01:29 | ClCap | 59371.95
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 548314.9 | 2019-06-12 01:29 | ClCap | 548314.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 472019.2 | 2019-06-12 01:29 | ClCap | 472019.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 599359.6 | 2019-06-12 01:29 | ClCap | 599359.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 515824 | 2019-06-12 01:29 | ClCap | 515824
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 106727 | 2019-06-12 01:29 | ClCap | 106727
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 22001.43 | 2019-06-12 01:29 | ClCap | 22001.43
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 57689.61 | 2019-06-12 01:29 | ClCap | 57689.61
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 39951.71 | 2019-06-12 01:29 | ClCap | 39951.71
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 66597.38 | 2019-06-12 01:29 | ClCap | 66597.38
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 66541.1 | 2019-06-12 01:29 | ClCap | 66541.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 22579.87 | 2019-06-12 01:29 | ClCap | 22579.87
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 25739.22 | 2019-06-12 01:29 | ClCap | 25739.22
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -898365.2 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -178114.5 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -404072.5 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -346554.3 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -420354.9 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -370352.2 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -271119.8 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -88160.42 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -123626.2 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -55558.2 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -39348.26 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -56181.25 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -55221.54 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -99946.26 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -80682.45 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -101549.2 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -101360.9 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -93267.41 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -68025.81 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -96878.9 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -89901.03 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -19938.44 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -26691.4 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -67988.97 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -42964.11 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -68054.59 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -67975.95 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -63316.73 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -37550.27 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -35228.52 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -38260.86 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -38780.97 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -84140.54 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -615159 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -575660.8 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -653530.1 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -609413.5 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -140592.1 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -29058.57 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -69179.41 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -52122.81 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -73237.79 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -77315.83 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -28265.07 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ09 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -40394.89 | 2019-06-12 01:29 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | AltAdjFactor | 1.0314 | 2019-06-12 01:31 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 14549.91 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2692.955 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 7508.569 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 6628.816 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 8034.507 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 7286.861 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5528.523 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1581.149 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2625.687 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1081.593 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 852.1447 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1215.7 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1201.476 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 1864.661 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1587.424 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 2023.074 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2080.543 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 1969.025 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1686.231 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2207.333 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2074.993 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 350.0208 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 648.2646 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1295.278 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 1025.978 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1457.312 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1507.763 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1510.996 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 579.868 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 466.0363 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 567.6836 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 554.7115 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1661.45 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 11255.71 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 10046.64 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 11658.68 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 10506.03 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2822.969 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 625.5427 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1363.791 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 1074.031 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1565.104 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1544.448 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 595.9301 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 654.3343 | 2019-06-12 01:31 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 14549.91 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3148.722 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 8423.363 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 6628.815 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 9179.673 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 7416.337 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5646.826 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1581.149 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 2989.795 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1250.071 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 852.1447 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1319.965 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1201.476 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2093.796 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1587.424 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2223.197 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2149.227 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2243.571 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1686.231 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2455.112 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2084.797 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 502.835 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 662.6688 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1568.439 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 1025.978 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1667.317 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1551.633 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1805.488 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 579.868 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 466.0363 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 567.6836 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 554.7115 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1905.824 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 11255.71 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 10046.64 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 12078.2 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 10506.03 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 3175.729 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 625.5427 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1400.896 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 1074.031 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1565.104 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1544.448 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 680.4017 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 816.775 | 2019-06-12 01:31 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 14549.91 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2692.955 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 7508.569 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 6628.815 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 8034.507 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 7286.861 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5528.523 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1581.149 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2625.687 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1081.593 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 852.1447 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1215.7 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1201.476 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 1864.661 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1587.424 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 2023.074 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2080.543 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 1969.025 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1686.231 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2207.333 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2074.993 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 350.0208 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 648.2646 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1295.278 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 1025.978 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1457.312 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1507.763 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1510.996 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 579.868 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 466.0363 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 567.6836 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 554.7115 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1661.45 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 11251.91 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 10046.64 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 11658.68 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 10506.03 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2822.969 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 625.5427 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1363.791 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 1074.031 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1565.104 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1544.448 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 595.9301 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 654.3343 | 2019-06-12 01:31 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 14549.91 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2692.955 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 7508.569 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 6628.815 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 8034.507 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 7286.861 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5528.523 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1581.149 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2625.687 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1081.593 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 852.1447 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1215.7 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1201.476 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 1864.661 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1587.424 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 2023.074 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2080.543 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 1969.025 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1686.231 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2207.333 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2074.993 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 350.0208 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 648.2646 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1295.278 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 1025.978 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1457.312 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1507.763 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1510.996 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 579.868 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 466.0363 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 567.6836 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 554.7115 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1661.45 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 11251.91 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 10046.64 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 11658.68 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 10506.03 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2822.969 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 625.5427 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1363.791 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 1074.031 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1565.104 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1544.448 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 595.9301 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 654.3343 | 2019-06-12 01:31 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 483653.2 | 2019-06-12 01:31 | ClCap | 483653.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 149194.1 | 2019-06-12 01:31 | ClCap | 149194.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 317662.7 | 2019-06-12 01:31 | ClCap | 317662.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 280443.3 | 2019-06-12 01:31 | ClCap | 280443.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 339913.4 | 2019-06-12 01:31 | ClCap | 339913.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 308283 | 2019-06-12 01:31 | ClCap | 308283
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 183773.5 | 2019-06-12 01:31 | ClCap | 183773.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 66893.17 | 2019-06-12 01:31 | ClCap | 66893.17
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 87280.38 | 2019-06-12 01:31 | ClCap | 87280.38
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 35953.19 | 2019-06-12 01:31 | ClCap | 35953.19
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 28326.12 | 2019-06-12 01:31 | ClCap | 28326.12
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 40411.04 | 2019-06-12 01:31 | ClCap | 40411.04
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 39938.25 | 2019-06-12 01:31 | ClCap | 39938.25
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 78887.64 | 2019-06-12 01:31 | ClCap | 78887.64
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 67158.66 | 2019-06-12 01:31 | ClCap | 67158.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 85589.57 | 2019-06-12 01:31 | ClCap | 85589.57
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 88020.9 | 2019-06-12 01:31 | ClCap | 88020.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 65452.3 | 2019-06-12 01:31 | ClCap | 65452.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 56051.95 | 2019-06-12 01:31 | ClCap | 56051.95
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 73373.88 | 2019-06-12 01:31 | ClCap | 73373.88
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 68974.8 | 2019-06-12 01:31 | ClCap | 68974.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 11635.03 | 2019-06-12 01:31 | ClCap | 11635.03
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 21548.95 | 2019-06-12 01:31 | ClCap | 21548.95
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 43056.32 | 2019-06-12 01:31 | ClCap | 43056.32
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 34104.5 | 2019-06-12 01:31 | ClCap | 34104.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 48442.48 | 2019-06-12 01:31 | ClCap | 48442.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 50119.5 | 2019-06-12 01:31 | ClCap | 50119.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 50226.98 | 2019-06-12 01:31 | ClCap | 50226.98
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 19275.38 | 2019-06-12 01:31 | ClCap | 19275.38
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 15491.5 | 2019-06-12 01:31 | ClCap | 15491.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 18870.36 | 2019-06-12 01:31 | ClCap | 18870.36
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 18439.15 | 2019-06-12 01:31 | ClCap | 18439.15
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 55228.23 | 2019-06-12 01:31 | ClCap | 55228.23
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 476031.2 | 2019-06-12 01:31 | ClCap | 476031.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 425040 | 2019-06-12 01:31 | ClCap | 425040
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 493240.3 | 2019-06-12 01:31 | ClCap | 493240.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 444475.5 | 2019-06-12 01:31 | ClCap | 444475.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 93838.24 | 2019-06-12 01:31 | ClCap | 93838.24
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 20793.65 | 2019-06-12 01:31 | ClCap | 20793.65
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 45333.75 | 2019-06-12 01:31 | ClCap | 45333.75
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 35701.85 | 2019-06-12 01:31 | ClCap | 35701.85
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 52025.6 | 2019-06-12 01:31 | ClCap | 52025.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 51338.96 | 2019-06-12 01:31 | ClCap | 51338.96
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 19809.29 | 2019-06-12 01:31 | ClCap | 19809.29
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 21750.71 | 2019-06-12 01:31 | ClCap | 21750.71
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -815517.8 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -171805.3 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -373068.1 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -322020.4 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -391753.6 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -341905.3 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -191871.2 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -83432.14 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -124067.7 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -47320.68 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -36115.33 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -48920.43 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -45897.45 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -88614.1 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -76046.61 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -91646.31 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -89942.8 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -80012.63 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -64001.23 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -84994.48 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -74963.03 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -19486.64 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -26702.84 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -56028.7 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -40191.28 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -57841.43 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -55180.6 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -65098.17 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -35342.29 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -30676.63 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -33378.11 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -35401.38 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -86299.61 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -556114.4 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -527753.2 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -581814.3 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -541399.8 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -138987.9 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -28074.68 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -57383.95 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -47696.98 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -61479.75 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -63004.37 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -28128.24 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ10 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -40457.6 | 2019-06-12 01:31 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | AltAdjFactor | 1.0129 | 2019-06-12 01:34 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 14460.44 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2581.12 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 7417.807 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 6733.621 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 7774.251 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 7141.178 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5534.002 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1530.225 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2731.771 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1135.055 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 910.0332 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1189.534 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1231.903 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 1896.058 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1629.223 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 1962.989 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2089.838 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2007.229 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1743.274 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2144.501 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2094.389 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 365.5028 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 653.2569 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1324.35 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 1078.157 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1417.523 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1523.122 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1530.31 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 589.3936 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 520.4888 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 579.1238 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 562.0239 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1800.438 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 11107.79 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 9817.878 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 11199.75 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 10232.21 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2601.033 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 630.4247 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1450.144 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 1121.337 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1515.516 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1552.322 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 569.7278 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 716.3156 | 2019-06-12 01:34 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 14460.44 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3121.203 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 8644.249 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 6993.255 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 8772.024 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 7496.652 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5572.615 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1530.225 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 3078.054 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1294.337 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 910.0332 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1243.241 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1231.903 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2153.215 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1629.223 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2113.233 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2196.547 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2325.965 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1743.274 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2351.958 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2094.389 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 543.5146 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 660.4513 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1611.157 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 1078.157 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1591.173 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1549.557 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1828.012 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 589.3936 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 520.4888 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 579.1238 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 562.0239 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1871.628 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 11391.82 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 9817.878 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 11485.37 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 10232.21 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 3181.08 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 630.4247 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1450.144 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 1121.337 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1515.516 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1552.322 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 668.1934 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 802.1197 | 2019-06-12 01:34 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 14460.44 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2581.12 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 7417.806 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 6733.621 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 7774.25 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 7141.177 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5534.002 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1530.225 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2731.771 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1135.055 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 910.0332 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1189.534 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1231.903 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 1896.058 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1629.223 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 1962.989 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2089.838 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2007.229 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1743.274 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2144.501 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2094.389 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 365.5028 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 653.2569 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1324.35 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 1078.157 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1417.523 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1523.122 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1530.31 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 589.3936 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 520.4888 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 579.1238 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 562.0239 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1800.438 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 11107.79 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 9817.878 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 11199.75 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 10232.21 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2601.033 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 630.4247 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1450.144 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 1121.337 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1515.516 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1552.322 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 569.7278 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 716.3156 | 2019-06-12 01:34 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 14460.44 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2581.12 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 7417.806 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 6733.621 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 7774.25 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 7141.177 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5534.002 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1530.225 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2731.771 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1135.055 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 910.0332 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1189.534 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1231.903 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 1896.058 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1629.223 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 1962.989 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2089.838 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2007.229 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1743.274 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2144.501 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2094.389 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 365.5028 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 653.2569 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1324.35 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 1078.157 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1417.523 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1523.122 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1530.31 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 589.3936 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 520.4888 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 579.1238 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 562.0239 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1800.438 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 11107.79 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 9817.878 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 11199.75 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 10232.21 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2601.033 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 630.4247 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1450.144 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 1121.337 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1515.516 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1552.322 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 569.7278 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 716.3156 | 2019-06-12 01:34 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 489461.3 | 2019-06-12 01:34 | ClCap | 489461.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 145610.9 | 2019-06-12 01:34 | ClCap | 145610.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 319556.6 | 2019-06-12 01:34 | ClCap | 319556.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 290082.2 | 2019-06-12 01:34 | ClCap | 290082.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 334912.1 | 2019-06-12 01:34 | ClCap | 334912.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 307639.5 | 2019-06-12 01:34 | ClCap | 307639.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 187316.6 | 2019-06-12 01:34 | ClCap | 187316.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 65921.58 | 2019-06-12 01:34 | ClCap | 65921.58
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 92465.83 | 2019-06-12 01:34 | ClCap | 92465.83
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 38419.7 | 2019-06-12 01:34 | ClCap | 38419.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 30803.08 | 2019-06-12 01:34 | ClCap | 30803.08
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 40263.73 | 2019-06-12 01:34 | ClCap | 40263.73
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 41697.84 | 2019-06-12 01:34 | ClCap | 41697.84
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 81681.53 | 2019-06-12 01:34 | ClCap | 81681.53
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 70186.37 | 2019-06-12 01:34 | ClCap | 70186.37
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 84564.92 | 2019-06-12 01:34 | ClCap | 84564.92
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 90029.54 | 2019-06-12 01:34 | ClCap | 90029.54
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 67941.32 | 2019-06-12 01:34 | ClCap | 67941.32
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 59006.89 | 2019-06-12 01:34 | ClCap | 59006.89
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 72587.73 | 2019-06-12 01:34 | ClCap | 72587.73
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 70891.51 | 2019-06-12 01:34 | ClCap | 70891.51
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 12371.65 | 2019-06-12 01:34 | ClCap | 12371.65
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 22111.64 | 2019-06-12 01:34 | ClCap | 22111.64
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 44827 | 2019-06-12 01:34 | ClCap | 44827
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 36493.79 | 2019-06-12 01:34 | ClCap | 36493.79
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 47980.74 | 2019-06-12 01:34 | ClCap | 47980.74
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 51555.11 | 2019-06-12 01:34 | ClCap | 51555.11
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 51798.39 | 2019-06-12 01:34 | ClCap | 51798.39
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 19949.97 | 2019-06-12 01:34 | ClCap | 19949.97
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 17617.66 | 2019-06-12 01:34 | ClCap | 17617.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 19602.36 | 2019-06-12 01:34 | ClCap | 19602.36
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 19023.56 | 2019-06-12 01:34 | ClCap | 19023.56
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 60941.78 | 2019-06-12 01:34 | ClCap | 60941.78
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 478519.7 | 2019-06-12 01:34 | ClCap | 478519.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 422950.9 | 2019-06-12 01:34 | ClCap | 422950.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 482481.3 | 2019-06-12 01:34 | ClCap | 482481.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 440800 | 2019-06-12 01:34 | ClCap | 440800
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 88040.56 | 2019-06-12 01:34 | ClCap | 88040.56
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 21338.81 | 2019-06-12 01:34 | ClCap | 21338.81
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 49084.91 | 2019-06-12 01:34 | ClCap | 49084.91
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 37955.35 | 2019-06-12 01:34 | ClCap | 37955.35
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 51297.66 | 2019-06-12 01:34 | ClCap | 51297.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 52543.47 | 2019-06-12 01:34 | ClCap | 52543.47
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 19284.32 | 2019-06-12 01:34 | ClCap | 19284.32
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 24246.07 | 2019-06-12 01:34 | ClCap | 24246.07
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -839839.7 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -181911.3 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -401528.9 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -351557.8 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -403343.6 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -365810.9 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -201226.9 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -86222.04 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -134517.1 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -51132.1 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -39692.23 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -49166.79 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -49178.88 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -95421.58 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -80876.24 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -93654.73 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -96505.45 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -86583.28 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -69102 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -86457.37 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -79409.31 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -21465.29 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -27992.06 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -59803.03 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -43793.87 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -58416.06 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -57665.86 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -69889.09 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -37641.04 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -37118.3 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -37337.35 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -37505 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -91364.34 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -603249.6 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -550303.9 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -604243.1 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -567268.4 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -149586.8 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -30126.87 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -62330.98 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -52419 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -64416.36 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -66994.11 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -29801.53 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ11 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -43025.87 | 2019-06-12 01:34 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | AltAdjFactor | 1.0006 | 2019-06-12 01:36 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 12190.05 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2279.817 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 6535.46 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 5644.423 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 6809.839 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 6272.452 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5163.097 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1369.386 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2297.381 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 971.3654 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 706.9691 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1073.943 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1074.66 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 1647.405 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1363.571 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 1743.931 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 1845.28 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 1806.526 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1504.862 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 1987.95 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 1862.749 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 292.6913 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 585.6674 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1157.785 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 905.5703 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1320.486 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1350.82 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1360.716 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 479.7567 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 375.0464 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 474.6643 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 454.1259 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1471.319 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 9850.269 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 8662.572 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 9827.673 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 9052.916 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2435.157 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 563.8466 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1240.383 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 955.3943 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1402.402 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1382.789 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 521.3605 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 598.7783 | 2019-06-12 01:36 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 12190.05 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 2965.397 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 8139.691 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 6147.441 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 8444.613 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 6988.996 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5469.898 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1416.038 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 2840.135 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1182.02 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 776.7336 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1173.969 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1107.071 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 1989.163 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1363.571 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2030.752 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2043.86 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2172.73 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1558.004 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2270.439 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 1945.168 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 471.673 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 639.5211 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1495.626 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 933.1384 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1523.558 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1440.389 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1696.965 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 479.7567 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 375.0464 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 474.6643 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 454.1259 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1848.901 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 10837.18 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 8866.761 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 11210.26 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 9264.11 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 3068.723 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 563.8466 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1331.124 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 955.3943 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1429.181 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1382.789 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 660.0793 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 792.3794 | 2019-06-12 01:36 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 12190.05 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2279.817 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 6535.46 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 5644.423 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 6809.839 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 6272.452 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5163.097 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1369.386 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2297.381 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 971.3654 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 706.9691 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1073.943 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1074.66 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 1647.405 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1363.571 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 1743.931 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 1845.28 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 1806.526 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1504.862 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 1987.95 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 1862.749 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 292.6913 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 585.6674 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1157.786 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 905.5703 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1320.486 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1350.82 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1360.716 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 479.7567 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 375.0464 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 474.6643 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 454.1259 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1471.319 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 9850.269 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 8662.572 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 9827.673 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 9052.916 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2435.157 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 563.8466 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1240.383 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 955.3943 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1402.402 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1382.789 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 521.3605 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 598.7783 | 2019-06-12 01:36 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 12190.05 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2279.817 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 6535.46 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 5644.423 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 6809.839 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 6272.452 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5163.097 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1369.386 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2297.381 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 971.3654 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 706.9691 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1073.943 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1074.66 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 1647.405 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1363.571 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 1743.931 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 1845.28 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 1806.526 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1504.862 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 1987.95 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 1862.749 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 292.6913 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 585.6674 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1157.786 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 905.5703 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1320.486 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1350.82 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1360.716 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 479.7567 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 375.0464 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 474.6643 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 454.1259 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1471.319 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 9850.269 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 8662.572 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 9827.673 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 9052.916 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2435.157 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 563.8466 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1240.383 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 955.3943 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1402.402 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1382.789 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 521.3605 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 598.7783 | 2019-06-12 01:36 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 417684.6 | 2019-06-12 01:36 | ClCap | 417684.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 130194.2 | 2019-06-12 01:36 | ClCap | 130194.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 285006.3 | 2019-06-12 01:36 | ClCap | 285006.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 246148.9 | 2019-06-12 01:36 | ClCap | 246148.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 296971.8 | 2019-06-12 01:36 | ClCap | 296971.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 273536.8 | 2019-06-12 01:36 | ClCap | 273536.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 176910.3 | 2019-06-12 01:36 | ClCap | 176910.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 59717.87 | 2019-06-12 01:36 | ClCap | 59717.87
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 78718.35 | 2019-06-12 01:36 | ClCap | 78718.35
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 33283.24 | 2019-06-12 01:36 | ClCap | 33283.24
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 24223.86 | 2019-06-12 01:36 | ClCap | 24223.86
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 36798 | 2019-06-12 01:36 | ClCap | 36798
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 36822.56 | 2019-06-12 01:36 | ClCap | 36822.56
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 71842.05 | 2019-06-12 01:36 | ClCap | 71842.05
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 59464.27 | 2019-06-12 01:36 | ClCap | 59464.27
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 76051.47 | 2019-06-12 01:36 | ClCap | 76051.47
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 80471.2 | 2019-06-12 01:36 | ClCap | 80471.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 61899.52 | 2019-06-12 01:36 | ClCap | 61899.52
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 51563.17 | 2019-06-12 01:36 | ClCap | 51563.17
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 68115.89 | 2019-06-12 01:36 | ClCap | 68115.89
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 63825.95 | 2019-06-12 01:36 | ClCap | 63825.95
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 10028.89 | 2019-06-12 01:36 | ClCap | 10028.89
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 20067.54 | 2019-06-12 01:36 | ClCap | 20067.54
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 39670.81 | 2019-06-12 01:36 | ClCap | 39670.81
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 31028.81 | 2019-06-12 01:36 | ClCap | 31028.81
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 45245.66 | 2019-06-12 01:36 | ClCap | 45245.66
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 46285.02 | 2019-06-12 01:36 | ClCap | 46285.02
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 46624.09 | 2019-06-12 01:36 | ClCap | 46624.09
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 16438.57 | 2019-06-12 01:36 | ClCap | 16438.57
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 12850.74 | 2019-06-12 01:36 | ClCap | 12850.74
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 16264.08 | 2019-06-12 01:36 | ClCap | 16264.08
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 15560.35 | 2019-06-12 01:36 | ClCap | 15560.35
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 50413.84 | 2019-06-12 01:36 | ClCap | 50413.84
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 429562.6 | 2019-06-12 01:36 | ClCap | 429562.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 377768 | 2019-06-12 01:36 | ClCap | 377768
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 428577.2 | 2019-06-12 01:36 | ClCap | 428577.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 394790.6 | 2019-06-12 01:36 | ClCap | 394790.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 83439.16 | 2019-06-12 01:36 | ClCap | 83439.16
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 19319.86 | 2019-06-12 01:36 | ClCap | 19319.86
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 42500.97 | 2019-06-12 01:36 | ClCap | 42500.97
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 32736 | 2019-06-12 01:36 | ClCap | 32736
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 48052.44 | 2019-06-12 01:36 | ClCap | 48052.44
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 47380.42 | 2019-06-12 01:36 | ClCap | 47380.42
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 17864.1 | 2019-06-12 01:36 | ClCap | 17864.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 20516.77 | 2019-06-12 01:36 | ClCap | 20516.77
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -787885.3 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -184970.7 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -398249.4 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -337162.5 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -404819.2 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -361831.8 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -200849.4 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -84072.74 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -130287 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -48652.86 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -35730.21 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -47949.61 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -46126.35 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -93052.59 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -74141.78 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -93648.88 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -94480.09 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -83383.78 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -64504.17 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -85289.17 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -76082.94 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -20050.78 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -27964.31 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -57254.95 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -39842.36 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -57127.45 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -55253.13 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -66613.81 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -33643.99 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -28185.44 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -32776.03 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -33451.62 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -93263.93 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -599612.9 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -525605.4 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -612289.8 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -539605.3 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -148656.2 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -27764.09 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -59058 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -46600.36 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -61736.1 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -61514.92 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -30075.36 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ12 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -43856.39 | 2019-06-12 01:36 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | AltAdjFactor | 1.0124 | 2019-06-12 01:38 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 14289.72 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 2565.387 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 7284.25 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 6547.074 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 8206.22 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 7118.098 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 5441.505 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1548.833 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2587.304 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1111.774 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 886.8353 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1259.292 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1207.163 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 1828.707 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1568.85 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 2064.428 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2037.943 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2003.359 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1702.683 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2255.058 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2053.006 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 355.262 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 638.8652 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1315.662 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 1041.092 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1501.17 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1499.561 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1544.929 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 555.9219 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 469.5576 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 583.0595 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 534.967 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1641.517 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 10850.49 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 9714.179 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 11741.4 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 10193.12 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 2765.926 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 611.7651 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1377.858 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 1078.257 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1578.437 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1530.548 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 593.8828 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 659.2181 | 2019-06-12 01:38 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 14289.72 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3122.631 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 8570.564 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 6920.363 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 8746.989 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 7481.667 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 5566.011 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1548.833 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 3041.657 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1289.411 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 886.8354 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1259.292 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1207.163 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2139.592 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1568.85 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2098.204 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2183.452 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2295.209 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1702.683 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2311.553 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2084.052 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 534.6984 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 652.9144 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1603.833 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 1041.092 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1552.692 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1554.076 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1799.697 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 555.9219 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 469.5576 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 583.0595 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 534.967 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 1870.733 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 11314.6 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 9714.179 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 11741.4 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 10193.12 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 3164.542 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 611.7651 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1419.52 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 1078.257 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1578.437 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1530.548 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 667.8738 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 801.7361 | 2019-06-12 01:38 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 14289.72 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 2565.387 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 7284.25 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 6547.074 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 8206.22 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 7118.098 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 5441.505 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1548.833 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2587.304 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1111.774 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 886.8354 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1259.292 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1207.149 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 1828.707 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1568.85 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 2064.428 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2037.943 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2003.359 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1702.302 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2255.058 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2053.006 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 355.262 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 638.8652 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1315.662 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 1041.092 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1501.17 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1499.561 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1544.929 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 555.9219 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 469.5576 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 583.0595 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 534.967 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1641.517 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 10850.49 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 9714.179 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 11741.4 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 10193.12 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 2765.926 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 611.7651 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1377.858 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 1078.257 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1578.437 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1530.548 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 593.8828 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 659.2181 | 2019-06-12 01:38 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 14289.72 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 2565.387 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 7284.25 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 6547.074 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 8206.22 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 7118.098 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 5441.505 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1548.833 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2587.304 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1111.774 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 886.8354 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1259.292 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1207.149 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 1828.707 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1568.85 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 2064.428 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2037.943 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2003.359 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1702.302 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2255.058 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2053.006 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 355.262 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 638.8652 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1315.662 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 1041.092 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1501.17 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1499.561 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1544.929 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 555.9219 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 469.5576 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 583.0595 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 534.967 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1641.517 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 10850.49 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 9714.179 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 11741.4 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 10193.12 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 2765.926 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 611.7651 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1377.858 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 1078.257 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1578.437 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1530.548 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 593.8828 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 659.2181 | 2019-06-12 01:38 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 483914.4 | 2019-06-12 01:38 | ClCap | 483914.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 144792.6 | 2019-06-12 01:38 | ClCap | 144792.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 313953.2 | 2019-06-12 01:38 | ClCap | 313953.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 282180.7 | 2019-06-12 01:38 | ClCap | 282180.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 353690.3 | 2019-06-12 01:38 | ClCap | 353690.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 306792 | 2019-06-12 01:38 | ClCap | 306792
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 184273.9 | 2019-06-12 01:38 | ClCap | 184273.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 66755.13 | 2019-06-12 01:38 | ClCap | 66755.13
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 87617.76 | 2019-06-12 01:38 | ClCap | 87617.76
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 37649.68 | 2019-06-12 01:38 | ClCap | 37649.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 30032.24 | 2019-06-12 01:38 | ClCap | 30032.24
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 42645.29 | 2019-06-12 01:38 | ClCap | 42645.29
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 40879.5 | 2019-06-12 01:38 | ClCap | 40879.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 78817.77 | 2019-06-12 01:38 | ClCap | 78817.77
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 67617.86 | 2019-06-12 01:38 | ClCap | 67617.86
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 88977.44 | 2019-06-12 01:38 | ClCap | 88977.44
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 87835.91 | 2019-06-12 01:38 | ClCap | 87835.91
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 67842.77 | 2019-06-12 01:38 | ClCap | 67842.77
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 57647.59 | 2019-06-12 01:38 | ClCap | 57647.59
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 76366.43 | 2019-06-12 01:38 | ClCap | 76366.43
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 69524.02 | 2019-06-12 01:38 | ClCap | 69524.02
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 12030.77 | 2019-06-12 01:38 | ClCap | 12030.77
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 21634.85 | 2019-06-12 01:38 | ClCap | 21634.85
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 44554.25 | 2019-06-12 01:38 | ClCap | 44554.25
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 35256.07 | 2019-06-12 01:38 | ClCap | 35256.07
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 50836.36 | 2019-06-12 01:38 | ClCap | 50836.36
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 50781.87 | 2019-06-12 01:38 | ClCap | 50781.87
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 52318.25 | 2019-06-12 01:38 | ClCap | 52318.25
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 18826.02 | 2019-06-12 01:38 | ClCap | 18826.02
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 15901.33 | 2019-06-12 01:38 | ClCap | 15901.33
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 19745.02 | 2019-06-12 01:38 | ClCap | 19745.02
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 18116.39 | 2019-06-12 01:38 | ClCap | 18116.39
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 55589.16 | 2019-06-12 01:38 | ClCap | 55589.16
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 467658.9 | 2019-06-12 01:38 | ClCap | 467658.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 418683.8 | 2019-06-12 01:38 | ClCap | 418683.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 506057.6 | 2019-06-12 01:38 | ClCap | 506057.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 439326.2 | 2019-06-12 01:38 | ClCap | 439326.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 93666.71 | 2019-06-12 01:38 | ClCap | 93666.71
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 20717.12 | 2019-06-12 01:38 | ClCap | 20717.12
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 46660.48 | 2019-06-12 01:38 | ClCap | 46660.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 36514.63 | 2019-06-12 01:38 | ClCap | 36514.63
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 53452.96 | 2019-06-12 01:38 | ClCap | 53452.96
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 51831.25 | 2019-06-12 01:38 | ClCap | 51831.25
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 20111.54 | 2019-06-12 01:38 | ClCap | 20111.54
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 22324.09 | 2019-06-12 01:38 | ClCap | 22324.09
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -836636.6 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -181751.5 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -399042.5 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -349247.3 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -401380.2 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -364897.9 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -200726 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -87341.32 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -133142.7 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -50979.74 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -38888.69 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -49694.11 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -48235.55 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -94960 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -78158.91 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -92936.13 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -96011.23 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -85643.05 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -67729.75 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -84927.44 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -78894.92 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -21215.85 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -27722.68 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -59617.31 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -42549.43 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -57006 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -57768.48 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -68830.74 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -35632.24 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -33447.87 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -37335.87 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -35846.79 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -90936.99 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -599840.9 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -545477.4 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -619315.3 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -565078.3 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -148972.8 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -29238.78 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -61136.64 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -50755.54 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -66982.98 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -65976.03 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -29773.8 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ13 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -42974.17 | 2019-06-12 01:38 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | AltAdjFactor | 1.0973 | 2019-06-12 01:39 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 16806.32 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 3033.943 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 8410.707 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 7488.847 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 9389.111 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 8292.814 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 6077.231 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1800.378 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 2986.535 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1264.603 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 1003.25 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1410.78 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1350.664 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 2063.069 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1768.592 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 2324.62 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2302.658 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2264.929 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1915.094 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2505.077 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2300.176 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 424.2875 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 725.6729 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1506.675 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 1169.238 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1654.597 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1685.109 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1764.256 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 657.8629 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 562.6021 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 684.3359 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 634.4213 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 1860.471 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 12606.07 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 11349.3 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 13481.63 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 11925.76 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 3314.387 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 697.7764 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1559.528 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 1220.042 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1746.616 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1726.676 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 688.6298 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 777.4045 | 2019-06-12 01:39 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 16806.32 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3425 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 9351.021 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 7613.793 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 9389.111 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 8292.814 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 6077.231 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1800.378 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 3325.077 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1418.46 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 1003.25 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1410.78 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1350.664 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2352.451 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1768.592 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2324.62 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2390.231 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2503.128 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1915.094 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2505.077 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2300.176 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 591.6451 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 725.6729 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1762.672 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 1169.238 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1682.735 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1714.38 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1971.326 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 657.8629 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 562.6021 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 684.3359 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 634.4213 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 2027.592 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 12606.07 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 11349.3 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 13481.63 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 11925.76 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 3420.251 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 697.7764 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1569.437 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 1220.042 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1746.616 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1726.676 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 723.8742 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 868.9608 | 2019-06-12 01:39 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 16806.32 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 3033.943 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 8410.707 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 7488.847 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 9383.346 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 8292.814 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 6077.231 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1800.378 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 2986.535 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1264.603 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 1003.25 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1410.78 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1350.664 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 2063.069 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1768.592 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 2324.62 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2302.658 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2264.929 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1915.094 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2505.077 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2300.176 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 424.2875 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 725.6729 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1506.675 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 1169.238 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1654.597 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1685.109 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1764.256 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 657.8629 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 562.6021 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 684.3359 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 634.4213 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 1860.471 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 12606.07 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 11349.3 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 13481.63 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 11925.76 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 3314.387 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 697.7764 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1559.528 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 1220.042 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1746.616 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1726.676 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 688.6298 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 777.4045 | 2019-06-12 01:39 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 16806.32 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 3033.943 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 8410.707 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 7488.847 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 9383.346 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 8292.814 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 6077.231 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1800.378 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 2986.535 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1264.603 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 1003.25 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1410.78 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1350.664 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 2063.069 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1768.592 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 2324.62 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2302.658 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2264.929 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1915.094 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2505.077 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2300.176 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 424.2875 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 725.6729 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1506.675 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 1169.238 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1654.597 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1685.109 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1764.256 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 657.8629 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 562.6021 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 684.3359 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 634.4213 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 1860.471 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 12606.07 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 11349.3 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 13481.63 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 11925.76 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 3314.387 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 697.7764 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1559.528 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 1220.042 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1746.616 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1726.676 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 688.6298 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 777.4045 | 2019-06-12 01:39 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 525107.9 | 2019-06-12 01:39 | ClCap | 525107.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 157990.9 | 2019-06-12 01:39 | ClCap | 157990.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 334459.8 | 2019-06-12 01:39 | ClCap | 334459.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 297801.1 | 2019-06-12 01:39 | ClCap | 297801.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 373137.6 | 2019-06-12 01:39 | ClCap | 373137.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 329771.6 | 2019-06-12 01:39 | ClCap | 329771.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 189881.1 | 2019-06-12 01:39 | ClCap | 189881.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 71593.75 | 2019-06-12 01:39 | ClCap | 71593.75
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 93313.3 | 2019-06-12 01:39 | ClCap | 93313.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 39512.12 | 2019-06-12 01:39 | ClCap | 39512.12
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 31346.22 | 2019-06-12 01:39 | ClCap | 31346.22
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 44079.35 | 2019-06-12 01:39 | ClCap | 44079.35
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 42201.05 | 2019-06-12 01:39 | ClCap | 42201.05
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 82039.9 | 2019-06-12 01:39 | ClCap | 82039.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 70329.74 | 2019-06-12 01:39 | ClCap | 70329.74
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 92440.71 | 2019-06-12 01:39 | ClCap | 92440.71
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 91567.39 | 2019-06-12 01:39 | ClCap | 91567.39
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 70766.96 | 2019-06-12 01:39 | ClCap | 70766.96
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 59836.5 | 2019-06-12 01:39 | ClCap | 59836.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 78270.31 | 2019-06-12 01:39 | ClCap | 78270.31
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 71868.24 | 2019-06-12 01:39 | ClCap | 71868.24
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 13256.72 | 2019-06-12 01:39 | ClCap | 13256.72
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 22673.41 | 2019-06-12 01:39 | ClCap | 22673.41
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 47075.58 | 2019-06-12 01:39 | ClCap | 47075.58
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 36532.46 | 2019-06-12 01:39 | ClCap | 36532.46
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 51697.35 | 2019-06-12 01:39 | ClCap | 51697.35
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 52650.68 | 2019-06-12 01:39 | ClCap | 52650.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 55123.61 | 2019-06-12 01:39 | ClCap | 55123.61
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 20554.71 | 2019-06-12 01:39 | ClCap | 20554.71
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 17578.32 | 2019-06-12 01:39 | ClCap | 17578.32
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 21381.85 | 2019-06-12 01:39 | ClCap | 21381.85
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 19822.29 | 2019-06-12 01:39 | ClCap | 19822.29
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 58129.82 | 2019-06-12 01:39 | ClCap | 58129.82
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 501292.4 | 2019-06-12 01:39 | ClCap | 501292.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 451315.6 | 2019-06-12 01:39 | ClCap | 451315.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 536109.7 | 2019-06-12 01:39 | ClCap | 536109.7
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 474239.3 | 2019-06-12 01:39 | ClCap | 474239.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 103557 | 2019-06-12 01:39 | ClCap | 103557
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 21801.8 | 2019-06-12 01:39 | ClCap | 21801.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 48726.93 | 2019-06-12 01:39 | ClCap | 48726.93
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 38119.82 | 2019-06-12 01:39 | ClCap | 38119.82
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 54572.44 | 2019-06-12 01:39 | ClCap | 54572.44
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 53949.43 | 2019-06-12 01:39 | ClCap | 53949.43
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 21516.01 | 2019-06-12 01:39 | ClCap | 21516.01
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 24289.75 | 2019-06-12 01:39 | ClCap | 24289.75
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -962640.5 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -195743.3 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -419959.3 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -371659.3 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -418764.2 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -390854.8 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -205448.9 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -99548.79 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -139129.6 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -52905.05 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -41770.24 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -53067.21 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -51020.53 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -99942.73 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -84809.18 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -99765.87 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -100723.7 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -87825.24 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -71863.39 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -86946.8 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -81862.91 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -22350.19 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -29319.86 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -61391.01 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -44990.3 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -58334.24 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -59708.45 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -70685.97 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -41599.37 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -40045.64 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -43648.57 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -41984.76 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -95862.2 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -645804.9 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -621234.1 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -688247.4 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -640677.9 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -153581 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -31898.99 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -63490.31 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -54153.26 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -70354.09 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -70112.94 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -30463.14 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ14 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -45099.84 | 2019-06-12 01:39 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | AltAdjFactor | 1.0177 | 2019-06-12 01:41 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 22642.07 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 3847.718 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 10643.7 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 9910.194 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 10678.41 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 10397.63 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 6472.357 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 2173.598 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 3638.915 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1575.264 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 1352.795 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1556.639 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1696.955 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 2651.718 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 2364.978 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 2597.631 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2869.655 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2646.167 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 2354.982 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2666.259 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2748.723 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 547.0503 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 834.4747 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1786.281 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 1504.481 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1793.729 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 2015.166 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1959.727 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 889.8953 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 814.9747 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 854.3899 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 861.2818 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 2375.166 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 15678.76 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 14273.98 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 15399.87 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 14837.11 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 3837.186 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 799.4841 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1867.189 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 1539.053 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1878.962 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 2045.155 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 802.7207 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 1010.952 | 2019-06-12 01:41 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 22642.07 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3847.718 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 10643.7 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 9910.194 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 10678.41 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 10397.63 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 6472.357 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 2173.598 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 3638.914 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1575.264 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 1352.795 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1556.639 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1696.955 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2651.718 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 2364.978 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2597.631 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2869.655 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2646.167 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 2354.982 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2666.259 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2748.722 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 596.7002 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 834.4747 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1787.1 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 1504.481 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1793.729 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 2015.166 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1959.727 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 889.8954 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 814.9747 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 854.3899 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 861.2819 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 2375.166 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 15678.76 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 14273.98 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 15399.87 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 14837.11 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 3837.186 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 799.4841 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1867.189 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 1539.053 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1878.963 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 2045.155 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 802.7207 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 1010.952 | 2019-06-12 01:41 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 22642.07 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 3847.718 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 10643.7 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 9910.194 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 10678.41 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 10397.63 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 6472.357 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 2173.598 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 3638.914 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1575.264 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 1352.795 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1556.639 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1696.955 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 2651.718 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 2364.978 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 2597.631 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2869.655 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2646.167 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 2354.982 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2666.259 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2748.722 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 547.0503 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 834.4747 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1787.1 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 1504.481 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1793.729 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 2015.166 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1959.727 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 889.8954 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 814.9747 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 854.3899 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 861.2819 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 2375.166 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 15678.76 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 14273.98 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 15399.87 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 14837.11 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 3837.186 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 799.4841 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1867.189 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 1539.053 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1878.963 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 2045.155 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 802.7207 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 1010.952 | 2019-06-12 01:41 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 22642.07 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 3847.718 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 10643.7 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 9910.194 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 10678.41 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 10397.63 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 6472.357 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 2173.598 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 3638.914 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1575.264 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 1352.795 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1556.639 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1696.955 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 2651.718 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 2364.978 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 2597.631 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2869.655 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2646.167 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 2354.982 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2666.259 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2748.722 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 547.0503 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 834.4747 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1787.1 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 1504.481 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1793.729 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 2015.166 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1959.727 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 889.8954 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 814.9747 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 854.3899 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 861.2819 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 2375.166 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 15678.76 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 14273.98 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 15399.87 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 14837.11 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 3837.186 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 799.4841 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1867.189 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 1539.053 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1878.963 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 2045.155 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 802.7207 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 1010.952 | 2019-06-12 01:41 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 762822.4 | 2019-06-12 01:41 | ClCap | 762822.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 216052.5 | 2019-06-12 01:41 | ClCap | 216052.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 456389.1 | 2019-06-12 01:41 | ClCap | 456389.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 424937.2 | 2019-06-12 01:41 | ClCap | 424937.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 457877.2 | 2019-06-12 01:41 | ClCap | 457877.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 445837.8 | 2019-06-12 01:41 | ClCap | 445837.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 218056.8 | 2019-06-12 01:41 | ClCap | 218056.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 93201.26 | 2019-06-12 01:41 | ClCap | 93201.26
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 122596.8 | 2019-06-12 01:41 | ClCap | 122596.8
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 53071.4 | 2019-06-12 01:41 | ClCap | 53071.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 45576.3 | 2019-06-12 01:41 | ClCap | 45576.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 52443.91 | 2019-06-12 01:41 | ClCap | 52443.91
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 57171.23 | 2019-06-12 01:41 | ClCap | 57171.23
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 113702.5 | 2019-06-12 01:41 | ClCap | 113702.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 101407.4 | 2019-06-12 01:41 | ClCap | 101407.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 111383.3 | 2019-06-12 01:41 | ClCap | 111383.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 123047.3 | 2019-06-12 01:41 | ClCap | 123047.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 89150.64 | 2019-06-12 01:41 | ClCap | 89150.64
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 79340.47 | 2019-06-12 01:41 | ClCap | 79340.47
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 89827.55 | 2019-06-12 01:41 | ClCap | 89827.55
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 92605.78 | 2019-06-12 01:41 | ClCap | 92605.78
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 18430.39 | 2019-06-12 01:41 | ClCap | 18430.39
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 28113.86 | 2019-06-12 01:41 | ClCap | 28113.86
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 60208.27 | 2019-06-12 01:41 | ClCap | 60208.27
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 50686.68 | 2019-06-12 01:41 | ClCap | 50686.68
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 60431.58 | 2019-06-12 01:41 | ClCap | 60431.58
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 67891.9 | 2019-06-12 01:41 | ClCap | 67891.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 66024.14 | 2019-06-12 01:41 | ClCap | 66024.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 29981.01 | 2019-06-12 01:41 | ClCap | 29981.01
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 27456.89 | 2019-06-12 01:41 | ClCap | 27456.89
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 28784.81 | 2019-06-12 01:41 | ClCap | 28784.81
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 29017 | 2019-06-12 01:41 | ClCap | 29017
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 80020.48 | 2019-06-12 01:41 | ClCap | 80020.48
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 672286.5 | 2019-06-12 01:41 | ClCap | 672286.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 612051.2 | 2019-06-12 01:41 | ClCap | 612051.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 660328.1 | 2019-06-12 01:41 | ClCap | 660328.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 636197.3 | 2019-06-12 01:41 | ClCap | 636197.3
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 129276.6 | 2019-06-12 01:41 | ClCap | 129276.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 26935.01 | 2019-06-12 01:41 | ClCap | 26935.01
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 62906.5 | 2019-06-12 01:41 | ClCap | 62906.5
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 51851.44 | 2019-06-12 01:41 | ClCap | 51851.44
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 63303.16 | 2019-06-12 01:41 | ClCap | 63303.16
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 68902.24 | 2019-06-12 01:41 | ClCap | 68902.24
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 27044.05 | 2019-06-12 01:41 | ClCap | 27044.05
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 34059.47 | 2019-06-12 01:41 | ClCap | 34059.47
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -1135523 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -200510.9 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -449477.2 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -445529.6 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -443994.3 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -452482.6 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -311668.1 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -111660 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -144588.7 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -56748.48 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -52440.98 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -55936.64 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -61557.86 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -106383 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -103632.2 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -104154.9 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -114231.9 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -91247.54 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -85228.33 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -90544.02 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -95368.29 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -21938.44 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -32960.68 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -61819.25 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -55819.39 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -61065.88 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -69409.16 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -68019.72 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -49349.64 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -49242.68 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -47366.65 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -49504.91 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -105016.4 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -746347.2 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -718129.3 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -727320.7 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -732391.6 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -164233.8 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -35151.64 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -73716.75 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -65240.53 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -71938.66 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -80507.44 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -32530.29 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ15 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -49310.19 | 2019-06-12 01:41 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | AltAdjFactor | 1.2145 | 2019-06-12 01:43 | AltAd | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_GY_Gym_A1Zn | 10425.98 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_KT_Ktchn_CZn | 3397.943 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Clrm_EZn | 9428.109 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Clrm_NZn | 6549.981 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Clrm_SZn | 9449.492 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Clrm_WZn | 7979.559 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_CompCL_CZn | 6558.803 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Conf_CZn | 1675.575 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Cordr_CZn | 3167.378 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Cordr_EZn | 1355.786 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Cordr_NZn | 1125.745 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Cordr_SZn | 1269.565 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Cordr_WZn | 1216.035 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Din_EZn | 2316.965 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Din_NZn | 1460.892 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Din_SZn | 2237.965 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Din_WZn | 2311.553 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_LibRdg_EZn | 2534.693 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_LibRdg_NZn | 1688.075 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_LibRdg_SZn | 2535.371 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_LibRdg_WZn | 2219.145 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_MechElec_CZn | 492.7672 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_OffGen_CZn | 748.636 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_OffGen_EZn | 1752.342 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_OffGen_NZn | 970.1579 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_OffGen_SZn | 1667.643 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_OffGen_WZn | 1631.109 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Restrm_CZn | 1869.284 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Shop_EZn | 414.66 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Shop_NZn | 342.4781 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Shop_SZn | 413.8105 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_Shop_WZn | 379.2115 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_L_StorSm_CZn | 2244.022 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_Clrm_EZn | 12892.06 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_Clrm_NZn | 9996.57 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_Clrm_SZn | 12931.87 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_Clrm_WZn | 10859.68 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_Cordr_CZn | 3572.683 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_OffGen_CZn | 672.5115 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_OffGen_EZn | 1578.566 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_OffGen_NZn | 946.6583 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_OffGen_SZn | 1596.491 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_OffGen_WZn | 1476.905 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_Restrm_CZn | 801.1422 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CAssFlo_U_StorSm_CZn | 961.7156 | 2019-06-12 01:43 | CAssF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_GY_Gym_A1 | 10425.98 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_KT_Ktchn_C | 3397.943 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_E | 9428.109 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_N | 6549.981 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_S | 9449.492 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Clrm_W | 7979.559 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_CompCL_C | 6558.803 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Conf_C | 1675.575 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_C | 3167.378 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_E | 1355.786 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_N | 1125.745 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_S | 1269.565 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Cordr_W | 1216.035 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_E | 2316.965 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_N | 1460.892 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_S | 2237.965 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Din_W | 2311.553 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_E | 2534.693 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_N | 1688.075 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_S | 2535.371 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_LibRdg_W | 2219.145 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_MechElec_C | 492.7672 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_C | 748.636 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_E | 1752.342 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_N | 970.1579 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_S | 1667.643 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_OffGen_W | 1631.109 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Restrm_C | 1869.284 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_E | 414.66 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_N | 342.4781 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_S | 413.8105 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_Shop_W | 379.2115 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_L_StorSm_C | 2244.022 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_E | 12892.06 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_N | 9996.57 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_S | 12931.87 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_Clrm_W | 10859.68 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_Cordr_C | 3572.683 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_C | 672.5115 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_E | 1578.566 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_N | 946.6583 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_S | 1596.491 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_OffGen_W | 1476.905 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_Restrm_C | 801.1422 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CHRtFlo_Sys_U_StorSm_C | 961.7156 | 2019-06-12 01:43 | CHRtF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_GY_Gym_A1 | 10425.98 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_KT_Ktchn_C | 3397.943 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_E | 9428.109 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_N | 6549.981 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_S | 9449.492 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Clrm_W | 7979.559 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_CompCL_C | 6558.803 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Conf_C | 1675.575 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_C | 3167.378 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_E | 1355.786 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_N | 1125.745 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_S | 1269.565 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Cordr_W | 1216.035 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_E | 2316.965 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_N | 1460.892 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_S | 2237.965 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Din_W | 2311.553 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_E | 2534.693 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_N | 1688.075 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_S | 2535.371 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_LibRdg_W | 2219.145 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_MechElec_C | 492.7671 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_C | 748.636 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_E | 1752.342 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_N | 970.1579 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_S | 1667.643 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_OffGen_W | 1631.109 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Restrm_C | 1869.284 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_E | 414.66 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_N | 342.4781 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_S | 413.8105 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_Shop_W | 379.2115 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_L_StorSm_C | 2244.022 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_E | 12892.06 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_N | 9996.57 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_S | 12931.87 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_Clrm_W | 10859.68 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_Cordr_C | 3572.683 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_C | 672.5115 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_E | 1578.566 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_N | 946.6583 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_S | 1596.491 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_OffGen_W | 1476.905 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_Restrm_C | 801.1422 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CRtdFlo_Sys_U_StorSm_C | 961.7156 | 2019-06-12 01:43 | CRtdF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_GY_Gym_A1 | 10425.98 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_KT_Ktchn_C | 3397.943 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_E | 9428.109 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_N | 6549.981 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_S | 9449.492 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Clrm_W | 7979.559 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_CompCL_C | 6558.803 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Conf_C | 1675.575 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_C | 3167.378 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_E | 1355.786 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_N | 1125.745 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_S | 1269.565 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Cordr_W | 1216.035 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_E | 2316.965 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_N | 1460.892 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_S | 2237.965 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Din_W | 2311.553 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_E | 2534.693 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_N | 1688.075 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_S | 2535.371 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_LibRdg_W | 2219.145 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_MechElec_C | 492.7672 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_C | 748.636 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_E | 1752.342 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_N | 970.1579 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_S | 1667.643 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_OffGen_W | 1631.109 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Restrm_C | 1869.284 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_E | 414.66 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_N | 342.4781 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_S | 413.8105 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_Shop_W | 379.2115 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_L_StorSm_C | 2244.022 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_E | 12892.06 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_N | 9996.57 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_S | 12931.87 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_Clrm_W | 10859.68 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_Cordr_C | 3572.683 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_C | 672.5115 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_E | 1578.566 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_N | 946.6583 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_S | 1596.491 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_OffGen_W | 1476.905 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_Restrm_C | 801.1422 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | CSupFlo_Sys_U_StorSm_C | 961.7156 | 2019-06-12 01:43 | CSupF | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_GY_Gym_A1 | 294338.1 | 2019-06-12 01:43 | ClCap | 294338.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_KT_Ktchn_C | 159880.1 | 2019-06-12 01:43 | ClCap | 159880.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_E | 338757.9 | 2019-06-12 01:43 | ClCap | 338757.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_N | 235345 | 2019-06-12 01:43 | ClCap | 235345
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_S | 339526.2 | 2019-06-12 01:43 | ClCap | 339526.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Clrm_W | 286710.6 | 2019-06-12 01:43 | ClCap | 286710.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_CompCL_C | 185163 | 2019-06-12 01:43 | ClCap | 185163
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Conf_C | 60204.47 | 2019-06-12 01:43 | ClCap | 60204.47
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_C | 89418.91 | 2019-06-12 01:43 | ClCap | 89418.91
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_E | 38275.47 | 2019-06-12 01:43 | ClCap | 38275.47
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_N | 31781.13 | 2019-06-12 01:43 | ClCap | 31781.13
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_S | 35841.36 | 2019-06-12 01:43 | ClCap | 35841.36
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Cordr_W | 34330.14 | 2019-06-12 01:43 | ClCap | 34330.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Din_E | 83250.02 | 2019-06-12 01:43 | ClCap | 83250.02
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Din_N | 52490.77 | 2019-06-12 01:43 | ClCap | 52490.77
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Din_S | 80411.51 | 2019-06-12 01:43 | ClCap | 80411.51
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Din_W | 83055.58 | 2019-06-12 01:43 | ClCap | 83055.58
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_E | 71557.46 | 2019-06-12 01:43 | ClCap | 71557.46
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_N | 47656.4 | 2019-06-12 01:43 | ClCap | 47656.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_S | 71576.6 | 2019-06-12 01:43 | ClCap | 71576.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_LibRdg_W | 62649.14 | 2019-06-12 01:43 | ClCap | 62649.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_MechElec_C | 13911.41 | 2019-06-12 01:43 | ClCap | 13911.41
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_C | 21134.9 | 2019-06-12 01:43 | ClCap | 21134.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_E | 49470.73 | 2019-06-12 01:43 | ClCap | 49470.73
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_N | 27388.73 | 2019-06-12 01:43 | ClCap | 27388.73
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_S | 47079.59 | 2019-06-12 01:43 | ClCap | 47079.59
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_OffGen_W | 46048.18 | 2019-06-12 01:43 | ClCap | 46048.18
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Restrm_C | 52772.14 | 2019-06-12 01:43 | ClCap | 52772.14
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Shop_E | 11706.35 | 2019-06-12 01:43 | ClCap | 11706.35
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Shop_N | 9668.571 | 2019-06-12 01:43 | ClCap | 9668.571
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Shop_S | 11682.37 | 2019-06-12 01:43 | ClCap | 11682.37
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_Shop_W | 10705.6 | 2019-06-12 01:43 | ClCap | 10705.6
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_L_StorSm_C | 63351.45 | 2019-06-12 01:43 | ClCap | 63351.45
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_E | 463219.9 | 2019-06-12 01:43 | ClCap | 463219.9
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_N | 359183.1 | 2019-06-12 01:43 | ClCap | 359183.1
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_S | 464650.4 | 2019-06-12 01:43 | ClCap | 464650.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_Clrm_W | 390195 | 2019-06-12 01:43 | ClCap | 390195
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_Cordr_C | 100861.2 | 2019-06-12 01:43 | ClCap | 100861.2
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_C | 18985.81 | 2019-06-12 01:43 | ClCap | 18985.81
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_E | 44564.83 | 2019-06-12 01:43 | ClCap | 44564.83
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_N | 26725.31 | 2019-06-12 01:43 | ClCap | 26725.31
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_S | 45070.88 | 2019-06-12 01:43 | ClCap | 45070.88
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_OffGen_W | 41694.83 | 2019-06-12 01:43 | ClCap | 41694.83
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_Restrm_C | 22617.21 | 2019-06-12 01:43 | ClCap | 22617.21
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | ClCap_Sys_U_StorSm_C | 27150.4 | 2019-06-12 01:43 | ClCap | 27150.4
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_GY_Gym_A1 | -619572.3 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_KT_Ktchn_C | -196851.9 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_E | -415781.8 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_N | -340861.1 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_S | -415517.6 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Clrm_W | -377756 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_CompCL_C | -209481.6 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Conf_C | -90195.93 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_C | -131616.6 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_E | -49404.82 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_N | -43248.46 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_S | -46719.85 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Cordr_W | -45504.23 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Din_E | -97159.51 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Din_N | -74621.49 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Din_S | -94586.52 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Din_W | -96794.7 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_E | -85161.74 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_N | -63070.14 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_S | -84333.23 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_LibRdg_W | -76705.09 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_MechElec_C | -19264.82 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_C | -28989.98 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_E | -58748.93 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_N | -38073.48 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_S | -55771.71 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_OffGen_W | -55315.73 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Restrm_C | -64761.49 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Shop_E | -27371.69 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Shop_N | -23382.62 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Shop_S | -27351.9 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_Shop_W | -25890.59 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_L_StorSm_C | -101487.4 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_E | -639463.6 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_N | -545725.1 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_S | -645567.9 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_Clrm_W | -573829.9 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_Cordr_C | -154608 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_C | -29609.73 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_E | -62107.9 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_N | -42403.08 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_S | -62665 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_OffGen_W | -58818.4 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_Restrm_C | -32339.74 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgAC-lt55-PENo | ESe | 2007 | CZ16 | cDXGF | PkgAC | HtCap_Sys_U_StorSm_C | -47547.39 | 2019-06-12 01:43 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | PkgHP | AltAdjFactor | 1.0075 | 2019-06-12 01:44 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 1320.231 | 2019-06-12 01:44 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 1320.231 | 2019-06-12 01:44 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 1320.231 | 2019-06-12 01:44 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 1320.231 | 2019-06-12 01:44 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 57179.39 | 2019-06-12 01:44 | ClCap | 57179.39
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:44 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -56610.79 | 2019-06-12 01:44 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ01 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -50317.86 | 2019-06-12 01:44 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | PkgHP | AltAdjFactor | 1.0046 | 2019-06-12 01:45 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 1495.638 | 2019-06-12 01:45 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 1495.638 | 2019-06-12 01:45 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 1495.638 | 2019-06-12 01:45 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 1495.638 | 2019-06-12 01:45 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 64962.49 | 2019-06-12 01:45 | ClCap | 64962.49
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:45 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -64519.96 | 2019-06-12 01:45 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ02 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -57166.99 | 2019-06-12 01:45 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | PkgHP | AltAdjFactor | 1.0003 | 2019-06-12 01:45 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 1571.852 | 2019-06-12 01:45 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 1571.852 | 2019-06-12 01:45 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 1571.852 | 2019-06-12 01:45 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 1571.852 | 2019-06-12 01:45 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 68572.49 | 2019-06-12 01:45 | ClCap | 68572.49
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:45 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -58490.85 | 2019-06-12 01:45 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ03 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -60343.79 | 2019-06-12 01:45 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | PkgHP | AltAdjFactor | 1.005 | 2019-06-12 01:46 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 1660.282 | 2019-06-12 01:46 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 1660.282 | 2019-06-12 01:46 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 1660.282 | 2019-06-12 01:46 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 1660.282 | 2019-06-12 01:46 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 72087.23 | 2019-06-12 01:46 | ClCap | 72087.23
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:46 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -65926.85 | 2019-06-12 01:46 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ04 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -63436.76 | 2019-06-12 01:46 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | PkgHP | AltAdjFactor | 1.0094 | 2019-06-12 01:47 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 1493.275 | 2019-06-12 01:47 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 1493.275 | 2019-06-12 01:47 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 1493.275 | 2019-06-12 01:47 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 1493.275 | 2019-06-12 01:47 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 64555.07 | 2019-06-12 01:47 | ClCap | 64555.07
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:47 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -57543.16 | 2019-06-12 01:47 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ05 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -56808.46 | 2019-06-12 01:47 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | PkgHP | AltAdjFactor | 1.0033 | 2019-06-12 01:47 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 1710.566 | 2019-06-12 01:47 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 1710.566 | 2019-06-12 01:47 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 1710.566 | 2019-06-12 01:47 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 1710.566 | 2019-06-12 01:47 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 74399.09 | 2019-06-12 01:47 | ClCap | 74399.09
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:47 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -52127.81 | 2019-06-12 01:47 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ06 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -65471.2 | 2019-06-12 01:47 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | PkgHP | AltAdjFactor | 1.0005 | 2019-06-12 01:48 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 1643.939 | 2019-06-12 01:48 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 1643.939 | 2019-06-12 01:48 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 1643.939 | 2019-06-12 01:48 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 1643.939 | 2019-06-12 01:48 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 71698.84 | 2019-06-12 01:48 | ClCap | 71698.84
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:48 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -39549.41 | 2019-06-12 01:48 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ07 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -63094.98 | 2019-06-12 01:48 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | PkgHP | AltAdjFactor | 1.0147 | 2019-06-12 01:49 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 1767.237 | 2019-06-12 01:49 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 1767.237 | 2019-06-12 01:49 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 1767.237 | 2019-06-12 01:49 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 1767.237 | 2019-06-12 01:49 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 76000.4 | 2019-06-12 01:49 | ClCap | 76000.4
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:49 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -53459.93 | 2019-06-12 01:49 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ08 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -66880.35 | 2019-06-12 01:49 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | PkgHP | AltAdjFactor | 1.0277 | 2019-06-12 01:49 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 2327.615 | 2019-06-12 01:49 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 2327.615 | 2019-06-12 01:49 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 2327.615 | 2019-06-12 01:49 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 2327.615 | 2019-06-12 01:49 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 98833.13 | 2019-06-12 01:49 | ClCap | 98833.13
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:49 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -55210.33 | 2019-06-12 01:49 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ09 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -86973.16 | 2019-06-12 01:49 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | PkgHP | AltAdjFactor | 1.0314 | 2019-06-12 01:50 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 2046.163 | 2019-06-12 01:50 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 2046.163 | 2019-06-12 01:50 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 2046.163 | 2019-06-12 01:50 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 2046.163 | 2019-06-12 01:50 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 86566.4 | 2019-06-12 01:50 | ClCap | 86566.4
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:50 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -54453.71 | 2019-06-12 01:50 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ10 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -76178.43 | 2019-06-12 01:50 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | PkgHP | AltAdjFactor | 1.0129 | 2019-06-12 01:51 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 2067.05 | 2019-06-12 01:51 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 2067.05 | 2019-06-12 01:51 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 2067.05 | 2019-06-12 01:51 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 2067.05 | 2019-06-12 01:51 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 89047.83 | 2019-06-12 01:51 | ClCap | 89047.83
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:51 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -64185.38 | 2019-06-12 01:51 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ11 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -78362.09 | 2019-06-12 01:51 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | PkgHP | AltAdjFactor | 1.0006 | 2019-06-12 01:51 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 1761.554 | 2019-06-12 01:51 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 1761.554 | 2019-06-12 01:51 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 1761.554 | 2019-06-12 01:51 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 1761.554 | 2019-06-12 01:51 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 76820.01 | 2019-06-12 01:51 | ClCap | 76820.01
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:51 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -65615.84 | 2019-06-12 01:51 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ12 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -67601.61 | 2019-06-12 01:51 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | PkgHP | AltAdjFactor | 1.0124 | 2019-06-12 01:52 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 2053.419 | 2019-06-12 01:52 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 2053.419 | 2019-06-12 01:52 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 2053.419 | 2019-06-12 01:52 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 2053.419 | 2019-06-12 01:52 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 88502.91 | 2019-06-12 01:52 | ClCap | 88502.91
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:52 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -63780.09 | 2019-06-12 01:52 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ13 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -77882.56 | 2019-06-12 01:52 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | PkgHP | AltAdjFactor | 1.0973 | 2019-06-12 01:53 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 2368.876 | 2019-06-12 01:53 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 2368.876 | 2019-06-12 01:53 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 2368.876 | 2019-06-12 01:53 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 2368.876 | 2019-06-12 01:53 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 94200.61 | 2019-06-12 01:53 | ClCap | 94200.61
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:53 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -66895.52 | 2019-06-12 01:53 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ14 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -82896.54 | 2019-06-12 01:53 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | PkgHP | AltAdjFactor | 1.0177 | 2019-06-12 01:53 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 2949.385 | 2019-06-12 01:53 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 2949.385 | 2019-06-12 01:53 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 2949.385 | 2019-06-12 01:53 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 2949.385 | 2019-06-12 01:53 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 126466.1 | 2019-06-12 01:53 | ClCap | 126466.1
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:53 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -55645.09 | 2019-06-12 01:53 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ15 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -111290.2 | 2019-06-12 01:53 | HtCap | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | PkgHP | AltAdjFactor | 1.2145 | 2019-06-12 01:54 | AltAd | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | PkgHP | CAssFlo_A_Clrm_A1Zn | 1933.553 | 2019-06-12 01:54 | CAssF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | PkgHP | CHRtFlo_Sys_A_Clrm_A1 | 1933.553 | 2019-06-12 01:54 | CHRtF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | PkgHP | CRtdFlo_Sys_A_Clrm_A1 | 1933.553 | 2019-06-12 01:54 | CRtdF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | PkgHP | CSupFlo_Sys_A_Clrm_A1 | 1933.553 | 2019-06-12 01:54 | CSupF | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | PkgHP | ClCap_Sys_A_Clrm_A1 | 69473.77 | 2019-06-12 01:54 | ClCap | 69473.77
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | PkgHP | HRtECT_Sys_A_Clrm_A1 | 47 | 2019-06-12 01:54 | HRtEC | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | PkgHP | HSpCap_Sys_A_Clrm_A1 | -74696 | 2019-06-12 01:54 | HSpCa | 0
PreNResPkgHP-lt55-PENo | ERC | 2007 | CZ16 | cDXHP | PkgHP | HtCap_Sys_A_Clrm_A1 | -61136.92 | 2019-06-12 01:54 | HtCap | 0

## Cost Anaysis
Thermostat Unit Cost
| GMC | Base | IMC
Material | 349 | 169 | 180
Labor | 156 | 156 | 0
BldgType | # of AC units | Avg_ton/Bldg | Avg_ton/unit | Basecase Material/Ton | Basecase Labor/Ton | Measure case Material/Ton | Measure case Labor/Ton | HVAC Type
ESe | 45 | 452 | 10 | 16.9 | 15.6 | 34.9 | 15.6 | cDXAC
EPr | 27 | 144 | 5 | 33.8 | 31.2 | 69.8 | 31.2 | cDXAC
ERC | 1 | 7 | 7 | 24.14 | 22.29 | 49.86 | 22.29 | cDXHP
|  |  |  | Basecase Material/Ton | Basecase Labor/Ton | Measure case Material/Ton | Measure case Labor/Ton
ESe and EPr avg |  |  |  | 25.35 | 23.4 | 52.35 | 23.4
ERC |  |  |  | 24.14 | 22.29 | 49.86 | 22.29