## SWHC020-01 Air-Cooled Chiller-M
currentbp database tables: Measure
This file created on 2/10/2019 11:43:23 AM while connected to AmazonWS-RDS as sptviewer.
Program/Database Description: READI v.2.5.1 (Preliminary Ex Ante Review data) options: include Non-DEER and Proposed data; 1/1/2017 - 1/1/2021
Index | MeasureID | Description | Version | UpdateYear | VersionSource | LastMod | SourceDesc | MeasID_PGE | MeasID_SCE | MeasID_SDG | MeasID_SCG | SupportedAppType | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | StdCostID | EUL_ID | RUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | LegacyID | MeasQualifierGroup | QualVersion | MsrNormUnits | MsrEULCode | PreEULCode | MsScaleBas | MsScaleVal | ExScaleBas | ExScaleVal | CdScaleBas | CdScaleVal | UseCatName | UseSubCatName | TechGroupName | TechTypeName | MeasType | StartDate | ExpiryDate | Status | ReviewStatus | ReviewComment | Comment | List of all Measure Versions, Qualifiers
2020 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | DEER2020 | 2020 | D20 v1 | 2018-11-18 16:35 | DEER2020 Proposed Update |  |  |  |  | ErRobNc | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | Chiller | AirCldScrewChlr |  |  | HVAC-Chlr | HVAC-Chlr | Air cooled constant speed screw chillers, efficiency based on vintage | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | AirCldScrewChlr-gte150tons-10.1EER-14IPLV | AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV |  | None | DEER2020 | [9 empty] | HVAC | Space Cooling | Liquid Chilling Equipment | Air-cooled Screw Chiller | Standard | 2020-01-01 |  | Available | NotInEA
2020 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | DEER2020 | 2020 | D20 v1 | 2018-11-18 16:35 | DEER2020 Proposed Update |  |  |  |  | ErRobNc | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | Chiller | AirCldScrewChlr |  |  | HVAC-Chlr | HVAC-Chlr | Air cooled constant speed screw chillers, efficiency based on vintage | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | AirCldScrewChlr-gte150tons-10.1EER-14IPLV | AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV |  | None | DEER2020 | [9 empty] | HVAC | Space Cooling | Liquid Chilling Equipment | Air-cooled Screw Chiller | Standard | 2020-01-01 |  | Available | NotInEA
2020 | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | DEER2020 | 2020 | D20 v1 | 2018-11-18 16:35 | DEER2020 Proposed Update |  |  |  |  | ErRobNc | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | Chiller | AirCldScrewChlr |  |  | HVAC-Chlr | HVAC-Chlr | Air cooled constant speed screw chillers, efficiency based on vintage | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | AirCldScrewChlr-lt150tons-10.1EER-13.7IPLV | AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV |  | None | DEER2020 | [9 empty] | HVAC | Space Cooling | Liquid Chilling Equipment | Air-cooled Screw Chiller | Standard | 2020-01-01 |  | Available | NotInEA
2020 | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | DEER2020 | 2020 | D20 v1 | 2018-11-18 16:35 | DEER2020 Proposed Update |  |  |  |  | ErRobNc | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | Chiller | AirCldScrewChlr |  |  | HVAC-Chlr | HVAC-Chlr | Air cooled constant speed screw chillers, efficiency based on vintage | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | AirCldScrewChlr-lt150tons-10.1EER-13.7IPLV | AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV |  | None | DEER2020 | [9 empty] | HVAC | Space Cooling | Liquid Chilling Equipment | Air-cooled Screw Chiller | Standard | 2020-01-01 |  | Available | NotInEA
| Title-24-2019 |  |  | Title-24 2019 |  | Measure 1 |  | Measure 2 |  | Measure 1 |  | Measure 2
|  |  |  | EER | IPLV | EER | IPLV | EER | IPLV | % improvement EER | % improvement IPLV | % improvement EER | % improvement IPLV
|  |  | <150 | 10.1 | 13.7 | 11.1 | 15.1 | 12.1 | 16.6 | 9.901% | 10.22% | 19.8% | 21.17% |  | 9.009% | 9.272% | 16.53% | 17.47%
|  |  | >=150 | 10.1 | 14 | 11.1 | 15.4 | 12.1 | 16.9 | 9.901% | 10% | 19.8% | 20.71% |  | 9.009% | 9.091% | 16.53% | 17.16%