## Measures
[10 empty] | * | * | *
EnergyImpactID | Version | VersionSource | LastMod | PA | BldgType | BldgVint | BldgHVAC | BldgLoc | NormUnit | AStdWBkWh | AStdWBkW | AStdWBtherm | ElecImpactProfileID | GasImpactProfileID | Flag | BldgType_desc | Lead IOUname | MeasureID | Qualifier | MeasureDesc | MeasImpactType | MeasTechEUL_ID | MeasTechDesc | StdTechDesc | BaseTechDesc | QualifierDesc
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ01 | Cap-Tons | 15.56 | 0.02 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ02 | Cap-Tons | 65.39 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ03 | Cap-Tons | 45.07 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ04 | Cap-Tons | 71.98 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ05 | Cap-Tons | 54.14 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ06 | Cap-Tons | 84.38 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ07 | Cap-Tons | 80.17 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SDG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ08 | Cap-Tons | 90.57 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ09 | Cap-Tons | 86.75 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ10 | Cap-Tons | 95.37 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ11 | Cap-Tons | 97.57 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ12 | Cap-Tons | 80.07 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ13 | Cap-Tons | 98.78 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ14 | Cap-Tons | 92.92 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ15 | Cap-Tons | 150.47 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ16 | Cap-Tons | 60.79 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ01 | Cap-Tons | 28.52 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ02 | Cap-Tons | 120.09 | 0.1 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ03 | Cap-Tons | 82.7 | 0.07 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ04 | Cap-Tons | 131.85 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ05 | Cap-Tons | 99.35 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ06 | Cap-Tons | 154.75 | 0.08 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ07 | Cap-Tons | 147.24 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SDG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ08 | Cap-Tons | 166.28 | 0.07 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ09 | Cap-Tons | 159.05 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ10 | Cap-Tons | 175 | 0.1 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ11 | Cap-Tons | 178.96 | 0.12 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ12 | Cap-Tons | 147.08 | 0.11 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ13 | Cap-Tons | 181.17 | 0.1 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ14 | Cap-Tons | 170.52 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ15 | Cap-Tons | 275.99 | 0.1 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ16 | Cap-Tons | 111.57 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ01 | Cap-Tons | 15.56 | 0.02 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ02 | Cap-Tons | 65.39 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ03 | Cap-Tons | 45.07 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ04 | Cap-Tons | 71.98 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ05 | Cap-Tons | 54.14 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ06 | Cap-Tons | 84.38 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ07 | Cap-Tons | 80.17 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SDG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ08 | Cap-Tons | 90.57 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ09 | Cap-Tons | 86.75 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ10 | Cap-Tons | 95.37 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ11 | Cap-Tons | 97.57 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ12 | Cap-Tons | 80.07 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ13 | Cap-Tons | 98.78 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ14 | Cap-Tons | 92.92 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ15 | Cap-Tons | 150.47 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ16 | Cap-Tons | 60.79 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ01 | Cap-Tons | 28.52 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ02 | Cap-Tons | 120.09 | 0.1 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ03 | Cap-Tons | 82.7 | 0.07 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ04 | Cap-Tons | 131.85 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ05 | Cap-Tons | 99.35 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ06 | Cap-Tons | 154.75 | 0.08 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ07 | Cap-Tons | 147.24 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SDG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ08 | Cap-Tons | 166.28 | 0.07 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ09 | Cap-Tons | 159.05 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ10 | Cap-Tons | 175 | 0.1 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ11 | Cap-Tons | 178.96 | 0.12 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ12 | Cap-Tons | 147.08 | 0.11 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ13 | Cap-Tons | 181.17 | 0.1 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ14 | Cap-Tons | 170.52 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ15 | Cap-Tons | 275.99 | 0.1 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | Ex | Any | CZ16 | Cap-Tons | 111.57 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ01 | Cap-Tons | 16.48 | 0.02 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ02 | Cap-Tons | 54.01 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ03 | Cap-Tons | 40.97 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ04 | Cap-Tons | 60.91 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ05 | Cap-Tons | 46.6 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ06 | Cap-Tons | 73.32 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ07 | Cap-Tons | 72.02 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SDG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ08 | Cap-Tons | 78.69 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ09 | Cap-Tons | 73.12 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ10 | Cap-Tons | 84.33 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ11 | Cap-Tons | 83 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ12 | Cap-Tons | 68.39 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ13 | Cap-Tons | 84.26 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ14 | Cap-Tons | 81.5 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ15 | Cap-Tons | 130.6 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ16 | Cap-Tons | 52.09 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 Min EER, 15.4 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ01 | Cap-Tons | 30.24 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ02 | Cap-Tons | 99.11 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ03 | Cap-Tons | 75.12 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ04 | Cap-Tons | 111.75 | 0.07 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ05 | Cap-Tons | 85.48 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ06 | Cap-Tons | 134.25 | 0.07 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ07 | Cap-Tons | 132.19 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SDG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ08 | Cap-Tons | 144.4 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ09 | Cap-Tons | 134.08 | 0.08 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ10 | Cap-Tons | 154.94 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ11 | Cap-Tons | 152.34 | 0.1 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ12 | Cap-Tons | 125.39 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ13 | Cap-Tons | 154.52 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ14 | Cap-Tons | 149.62 | 0.08 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ15 | Cap-Tons | 239.6 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ16 | Cap-Tons | 95.5 | 0.08 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | None | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 Min EER, 16.9 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 10.1 EER, 14 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ01 | Cap-Tons | 16.48 | 0.02 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ02 | Cap-Tons | 54.01 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ03 | Cap-Tons | 40.97 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ04 | Cap-Tons | 60.91 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ05 | Cap-Tons | 46.6 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ06 | Cap-Tons | 73.32 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ07 | Cap-Tons | 72.02 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SDG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ08 | Cap-Tons | 78.69 | 0.03 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ09 | Cap-Tons | 73.12 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ10 | Cap-Tons | 84.33 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ11 | Cap-Tons | 83 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ12 | Cap-Tons | 68.39 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ13 | Cap-Tons | 84.26 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ14 | Cap-Tons | 81.5 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ15 | Cap-Tons | 130.6 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ16 | Cap-Tons | 52.09 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 Min EER, 15.1 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ01 | Cap-Tons | 30.24 | 0.04 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ02 | Cap-Tons | 99.11 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ03 | Cap-Tons | 75.12 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ04 | Cap-Tons | 111.75 | 0.07 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ05 | Cap-Tons | 85.48 | 0.05 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ06 | Cap-Tons | 134.25 | 0.07 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ07 | Cap-Tons | 132.19 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SDG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ08 | Cap-Tons | 144.4 | 0.06 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ09 | Cap-Tons | 134.08 | 0.08 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ10 | Cap-Tons | 154.94 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ11 | Cap-Tons | 152.34 | 0.1 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ12 | Cap-Tons | 125.39 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | PG&E | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ13 | Cap-Tons | 154.52 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ14 | Cap-Tons | 149.62 | 0.08 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ15 | Cap-Tons | 239.6 | 0.09 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | Any | Com | New | Any | CZ16 | Cap-Tons | 95.5 | 0.08 | 0 | DEER:HVAC_Chillers | Annual | 2020 | Commercial - Weighted Average | SCE | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | None | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 Min EER, 16.6 Min IPLV) | Standard | HVAC-Chlr | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 10.1 EER, 13.7 IPLV) | Air cooled constant speed screw chillers, efficiency based on vintage | Measure Definition does not have Energy Impact Qualifiers

## Pivot table (hidden)
BldgVint | Ex
|  |  | Values | PA
|  |  | Count of Original index |  |  | Sum of AStdWBkWh
BldgLoc | MeasureID | BldgType | PGE | SCE | SDG | PGE | SCE | SDG
CZ01 |  |  | 40 |  |  | 1009.2
CZ02 |  |  | 40 |  |  | 3361
CZ03 |  |  | 40 |  |  | 2548.8
CZ04 |  |  | 40 |  |  | 3802.6
CZ05 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC | 1 | 1 |  | 48.4 | 48.4
|  | ESe | 1 | 1 |  | 41.3 | 41.3
|  | EUn | 1 | 1 |  | 40.9 | 40.7
|  | Hsp | 1 | 1 |  | 23.4 | 23.5
|  | Htl | 1 | 1 |  | 84.1 | 84.7
|  | MBT | 1 | 1 |  | 49.9 | 49.7
|  | Nrs | 1 | 1 |  | 54.9 | 57
|  | OfL | 1 | 1 |  | 47.9 | 48
|  | OfS | 1 | 1 |  | 55.6 | 55.5
|  | Rt3 | 1 | 1 |  | 52.6 | 52.4
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC | 1 | 1 |  | 88.8 | 88.8
|  | ESe | 1 | 1 |  | 75.8 | 75.7
|  | EUn | 1 | 1 |  | 75 | 74.6
|  | Hsp | 1 | 1 |  | 42.9 | 43
|  | Htl | 1 | 1 |  | 154 | 155
|  | MBT | 1 | 1 |  | 91.5 | 91.3
|  | Nrs | 1 | 1 |  | 101 | 105
|  | OfL | 1 | 1 |  | 87.9 | 88
|  | OfS | 1 | 1 |  | 102 | 102
|  | Rt3 | 1 | 1 |  | 96.5 | 96.2
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC | 1 | 1 |  | 48.4 | 48.4
|  | ESe | 1 | 1 |  | 41.3 | 41.3
|  | EUn | 1 | 1 |  | 40.9 | 40.7
|  | Hsp | 1 | 1 |  | 23.4 | 23.5
|  | Htl | 1 | 1 |  | 84.1 | 84.7
|  | MBT | 1 | 1 |  | 49.9 | 49.7
|  | Nrs | 1 | 1 |  | 54.9 | 57
|  | OfL | 1 | 1 |  | 47.9 | 48
|  | OfS | 1 | 1 |  | 55.6 | 55.5
|  | Rt3 | 1 | 1 |  | 52.6 | 52.4
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC | 1 | 1 |  | 88.8 | 88.8
|  | ESe | 1 | 1 |  | 75.8 | 75.7
|  | EUn | 1 | 1 |  | 75 | 74.6
|  | Hsp | 1 | 1 |  | 42.9 | 43
|  | Htl | 1 | 1 |  | 154 | 155
|  | MBT | 1 | 1 |  | 91.5 | 91.3
|  | Nrs | 1 | 1 |  | 101 | 105
|  | OfL | 1 | 1 |  | 87.9 | 88
|  | OfS | 1 | 1 |  | 102 | 102
|  | Rt3 | 1 | 1 |  | 96.5 | 96.2
CZ06 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC |  | 1 | 1 |  | 76 | 76.1
|  | ESe |  | 1 | 1 |  | 56.8 | 57.2
|  | EUn |  | 1 | 1 |  | 62.8 | 62.8
|  | Hsp |  | 1 | 1 |  | 50.3 | 50.3
|  | Htl |  | 1 | 1 |  | 108 | 108
|  | MBT |  | 1 | 1 |  | 77.2 | 77.3
|  | Nrs |  | 1 | 1 |  | 96.1 | 95.5
|  | OfL |  | 1 | 1 |  | 78 | 78
|  | OfS |  | 1 | 1 |  | 81.6 | 81.9
|  | Rt3 |  | 1 | 1 |  | 88.1 | 88.2
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC |  | 1 | 1 |  | 139 | 140
|  | ESe |  | 1 | 1 |  | 104 | 105
|  | EUn |  | 1 | 1 |  | 115 | 115
|  | Hsp |  | 1 | 1 |  | 92.4 | 92.2
|  | Htl |  | 1 | 1 |  | 199 | 198
|  | MBT |  | 1 | 1 |  | 142 | 142
|  | Nrs |  | 1 | 1 |  | 176 | 175
|  | OfL |  | 1 | 1 |  | 143 | 143
|  | OfS |  | 1 | 1 |  | 150 | 150
|  | Rt3 |  | 1 | 1 |  | 162 | 162
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC |  | 1 | 1 |  | 76 | 76.1
|  | ESe |  | 1 | 1 |  | 56.8 | 57.2
|  | EUn |  | 1 | 1 |  | 62.8 | 62.8
|  | Hsp |  | 1 | 1 |  | 50.3 | 50.3
|  | Htl |  | 1 | 1 |  | 108 | 108
|  | MBT |  | 1 | 1 |  | 77.2 | 77.3
|  | Nrs |  | 1 | 1 |  | 96.1 | 95.5
|  | OfL |  | 1 | 1 |  | 78 | 78
|  | OfS |  | 1 | 1 |  | 81.6 | 81.9
|  | Rt3 |  | 1 | 1 |  | 88.1 | 88.2
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC |  | 1 | 1 |  | 139 | 140
|  | ESe |  | 1 | 1 |  | 104 | 105
|  | EUn |  | 1 | 1 |  | 115 | 115
|  | Hsp |  | 1 | 1 |  | 92.4 | 92.2
|  | Htl |  | 1 | 1 |  | 199 | 198
|  | MBT |  | 1 | 1 |  | 142 | 142
|  | Nrs |  | 1 | 1 |  | 176 | 175
|  | OfL |  | 1 | 1 |  | 143 | 143
|  | OfS |  | 1 | 1 |  | 150 | 150
|  | Rt3 |  | 1 | 1 |  | 162 | 162
CZ07 |  |  |  |  | 40 |  |  | 4287.8
CZ08 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC |  | 1 | 1 |  | 83 | 83.1
|  | ESe |  | 1 | 1 |  | 66 | 66.6
|  | EUn |  | 1 | 1 |  | 69.6 | 69.8
|  | Hsp |  | 1 | 1 |  | 56.3 | 56.3
|  | Htl |  | 1 | 1 |  | 119 | 119
|  | MBT |  | 1 | 1 |  | 81.5 | 81.6
|  | Nrs |  | 1 | 1 |  | 111 | 111
|  | OfL |  | 1 | 1 |  | 79.6 | 79.6
|  | OfS |  | 1 | 1 |  | 89.6 | 89.9
|  | Rt3 |  | 1 | 1 |  | 99.5 | 99.7
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC |  | 1 | 1 |  | 152 | 153
|  | ESe |  | 1 | 1 |  | 121 | 122
|  | EUn |  | 1 | 1 |  | 128 | 128
|  | Hsp |  | 1 | 1 |  | 103 | 103
|  | Htl |  | 1 | 1 |  | 219 | 218
|  | MBT |  | 1 | 1 |  | 150 | 150
|  | Nrs |  | 1 | 1 |  | 204 | 203
|  | OfL |  | 1 | 1 |  | 146 | 146
|  | OfS |  | 1 | 1 |  | 164 | 165
|  | Rt3 |  | 1 | 1 |  | 183 | 183
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC |  | 1 | 1 |  | 83 | 83.1
|  | ESe |  | 1 | 1 |  | 66 | 66.6
|  | EUn |  | 1 | 1 |  | 69.6 | 69.8
|  | Hsp |  | 1 | 1 |  | 56.3 | 56.3
|  | Htl |  | 1 | 1 |  | 119 | 119
|  | MBT |  | 1 | 1 |  | 81.5 | 81.6
|  | Nrs |  | 1 | 1 |  | 111 | 111
|  | OfL |  | 1 | 1 |  | 79.6 | 79.6
|  | OfS |  | 1 | 1 |  | 89.6 | 89.9
|  | Rt3 |  | 1 | 1 |  | 99.5 | 99.7
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC |  | 1 | 1 |  | 152 | 153
|  | ESe |  | 1 | 1 |  | 121 | 122
|  | EUn |  | 1 | 1 |  | 128 | 128
|  | Hsp |  | 1 | 1 |  | 103 | 103
|  | Htl |  | 1 | 1 |  | 219 | 218
|  | MBT |  | 1 | 1 |  | 150 | 150
|  | Nrs |  | 1 | 1 |  | 204 | 203
|  | OfL |  | 1 | 1 |  | 146 | 146
|  | OfS |  | 1 | 1 |  | 164 | 165
|  | Rt3 |  | 1 | 1 |  | 183 | 183
CZ09 |  |  |  | 40 |  |  | 4485.4
CZ10 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC |  | 1 | 1 |  | 87.7 | 87.8
|  | ESe |  | 1 | 1 |  | 66.5 | 66.7
|  | EUn |  | 1 | 1 |  | 76.3 | 76.3
|  | Hsp |  | 1 | 1 |  | 57.8 | 57.9
|  | Htl |  | 1 | 1 |  | 118 | 118
|  | MBT |  | 1 | 1 |  | 83 | 83
|  | Nrs |  | 1 | 1 |  | 114 | 118
|  | OfL |  | 1 | 1 |  | 83.9 | 84
|  | OfS |  | 1 | 1 |  | 91.1 | 91.1
|  | Rt3 |  | 1 | 1 |  | 102 | 102
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC |  | 1 | 1 |  | 161 | 161
|  | ESe |  | 1 | 1 |  | 122 | 122
|  | EUn |  | 1 | 1 |  | 140 | 140
|  | Hsp |  | 1 | 1 |  | 106 | 106
|  | Htl |  | 1 | 1 |  | 217 | 217
|  | MBT |  | 1 | 1 |  | 152 | 152
|  | Nrs |  | 1 | 1 |  | 209 | 216
|  | OfL |  | 1 | 1 |  | 154 | 154
|  | OfS |  | 1 | 1 |  | 167 | 167
|  | Rt3 |  | 1 | 1 |  | 187 | 187
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC |  | 1 | 1 |  | 87.7 | 87.8
|  | ESe |  | 1 | 1 |  | 66.5 | 66.7
|  | EUn |  | 1 | 1 |  | 76.3 | 76.3
|  | Hsp |  | 1 | 1 |  | 57.8 | 57.9
|  | Htl |  | 1 | 1 |  | 118 | 118
|  | MBT |  | 1 | 1 |  | 83 | 83
|  | Nrs |  | 1 | 1 |  | 114 | 118
|  | OfL |  | 1 | 1 |  | 83.9 | 84
|  | OfS |  | 1 | 1 |  | 91.1 | 91.1
|  | Rt3 |  | 1 | 1 |  | 102 | 102
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC |  | 1 | 1 |  | 161 | 161
|  | ESe |  | 1 | 1 |  | 122 | 122
|  | EUn |  | 1 | 1 |  | 140 | 140
|  | Hsp |  | 1 | 1 |  | 106 | 106
|  | Htl |  | 1 | 1 |  | 217 | 217
|  | MBT |  | 1 | 1 |  | 152 | 152
|  | Nrs |  | 1 | 1 |  | 209 | 216
|  | OfL |  | 1 | 1 |  | 154 | 154
|  | OfS |  | 1 | 1 |  | 167 | 167
|  | Rt3 |  | 1 | 1 |  | 187 | 187
CZ11 |  |  | 40 |  |  | 5098.4
CZ12 |  |  | 40 |  |  | 4253.4
CZ13 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC | 1 | 1 |  | 92.9 | 92.8
|  | ESe | 1 | 1 |  | 66.9 | 66.8
|  | EUn | 1 | 1 |  | 84.8 | 84.7
|  | Hsp | 1 | 1 |  | 64.4 | 63.9
|  | Htl | 1 | 1 |  | 127 | 126
|  | MBT | 1 | 1 |  | 80.9 | 80.9
|  | Nrs | 1 | 1 |  | 128 | 125
|  | OfL | 1 | 1 |  | 83 | 82.7
|  | OfS | 1 | 1 |  | 89.6 | 89.5
|  | Rt3 | 1 | 1 |  | 97.7 | 97.7
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC | 1 | 1 |  | 171 | 170
|  | ESe | 1 | 1 |  | 123 | 123
|  | EUn | 1 | 1 |  | 156 | 155
|  | Hsp | 1 | 1 |  | 118 | 117
|  | Htl | 1 | 1 |  | 232 | 231
|  | MBT | 1 | 1 |  | 148 | 148
|  | Nrs | 1 | 1 |  | 235 | 229
|  | OfL | 1 | 1 |  | 152 | 152
|  | OfS | 1 | 1 |  | 164 | 164
|  | Rt3 | 1 | 1 |  | 179 | 179
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC | 1 | 1 |  | 92.9 | 92.8
|  | ESe | 1 | 1 |  | 66.9 | 66.8
|  | EUn | 1 | 1 |  | 84.8 | 84.7
|  | Hsp | 1 | 1 |  | 64.4 | 63.9
|  | Htl | 1 | 1 |  | 127 | 126
|  | MBT | 1 | 1 |  | 80.9 | 80.9
|  | Nrs | 1 | 1 |  | 128 | 125
|  | OfL | 1 | 1 |  | 83 | 82.7
|  | OfS | 1 | 1 |  | 89.6 | 89.5
|  | Rt3 | 1 | 1 |  | 97.7 | 97.7
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC | 1 | 1 |  | 171 | 170
|  | ESe | 1 | 1 |  | 123 | 123
|  | EUn | 1 | 1 |  | 156 | 155
|  | Hsp | 1 | 1 |  | 118 | 117
|  | Htl | 1 | 1 |  | 232 | 231
|  | MBT | 1 | 1 |  | 148 | 148
|  | Nrs | 1 | 1 |  | 235 | 229
|  | OfL | 1 | 1 |  | 152 | 152
|  | OfS | 1 | 1 |  | 164 | 164
|  | Rt3 | 1 | 1 |  | 179 | 179
CZ14 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC |  | 1 | 1 |  | 85.2 | 85.3
|  | ESe |  | 1 | 1 |  | 62.4 | 62.8
|  | EUn |  | 1 | 1 |  | 78 | 77.9
|  | Hsp |  | 1 | 1 |  | 59.4 | 58.9
|  | Htl |  | 1 | 1 |  | 117 | 117
|  | MBT |  | 1 | 1 |  | 79.2 | 79.2
|  | Nrs |  | 1 | 1 |  | 125 | 123
|  | OfL |  | 1 | 1 |  | 82 | 82.3
|  | OfS |  | 1 | 1 |  | 87.9 | 87.7
|  | Rt3 |  | 1 | 1 |  | 94.2 | 94.3
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC |  | 1 | 1 |  | 156 | 156
|  | ESe |  | 1 | 1 |  | 115 | 115
|  | EUn |  | 1 | 1 |  | 143 | 143
|  | Hsp |  | 1 | 1 |  | 109 | 108
|  | Htl |  | 1 | 1 |  | 215 | 215
|  | MBT |  | 1 | 1 |  | 145 | 145
|  | Nrs |  | 1 | 1 |  | 230 | 225
|  | OfL |  | 1 | 1 |  | 151 | 151
|  | OfS |  | 1 | 1 |  | 161 | 161
|  | Rt3 |  | 1 | 1 |  | 173 | 173
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC |  | 1 | 1 |  | 85.2 | 85.3
|  | ESe |  | 1 | 1 |  | 62.4 | 62.8
|  | EUn |  | 1 | 1 |  | 78 | 77.9
|  | Hsp |  | 1 | 1 |  | 59.4 | 58.9
|  | Htl |  | 1 | 1 |  | 117 | 117
|  | MBT |  | 1 | 1 |  | 79.2 | 79.2
|  | Nrs |  | 1 | 1 |  | 125 | 123
|  | OfL |  | 1 | 1 |  | 82 | 82.3
|  | OfS |  | 1 | 1 |  | 87.9 | 87.7
|  | Rt3 |  | 1 | 1 |  | 94.2 | 94.3
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC |  | 1 | 1 |  | 156 | 156
|  | ESe |  | 1 | 1 |  | 115 | 115
|  | EUn |  | 1 | 1 |  | 143 | 143
|  | Hsp |  | 1 | 1 |  | 109 | 108
|  | Htl |  | 1 | 1 |  | 215 | 215
|  | MBT |  | 1 | 1 |  | 145 | 145
|  | Nrs |  | 1 | 1 |  | 230 | 225
|  | OfL |  | 1 | 1 |  | 151 | 151
|  | OfS |  | 1 | 1 |  | 161 | 161
|  | Rt3 |  | 1 | 1 |  | 173 | 173
CZ15 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC |  | 1 |  |  | 133
|  | ESe |  | 1 | 1 |  | 102 | 102
|  | EUn |  | 1 |  |  | 120
|  | Hsp |  | 1 |  |  | 102
|  | Htl |  | 1 | 1 |  | 172 | 172
|  | MBT |  | 1 | 1 |  | 123 | 123
|  | Nrs |  | 1 |  |  | 190
|  | OfL |  | 1 | 1 |  | 121 | 121
|  | OfS |  | 1 | 1 |  | 136 | 136
|  | Rt3 |  | 1 | 1 |  | 146 | 146
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC |  | 1 |  |  | 244
|  | ESe |  | 1 | 1 |  | 187 | 186
|  | EUn |  | 1 |  |  | 219
|  | Hsp |  | 1 |  |  | 187
|  | Htl |  | 1 | 1 |  | 315 | 315
|  | MBT |  | 1 | 1 |  | 226 | 226
|  | Nrs |  | 1 |  |  | 349
|  | OfL |  | 1 | 1 |  | 222 | 222
|  | OfS |  | 1 | 1 |  | 249 | 249
|  | Rt3 |  | 1 | 1 |  | 269 | 267
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC |  | 1 |  |  | 133
|  | ESe |  | 1 | 1 |  | 102 | 102
|  | EUn |  | 1 |  |  | 120
|  | Hsp |  | 1 |  |  | 102
|  | Htl |  | 1 | 1 |  | 172 | 172
|  | MBT |  | 1 | 1 |  | 123 | 123
|  | Nrs |  | 1 |  |  | 190
|  | OfL |  | 1 | 1 |  | 121 | 121
|  | OfS |  | 1 | 1 |  | 136 | 136
|  | Rt3 |  | 1 | 1 |  | 146 | 146
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC |  | 1 |  |  | 244
|  | ESe |  | 1 | 1 |  | 187 | 186
|  | EUn |  | 1 |  |  | 219
|  | Hsp |  | 1 |  |  | 187
|  | Htl |  | 1 | 1 |  | 315 | 315
|  | MBT |  | 1 | 1 |  | 226 | 226
|  | Nrs |  | 1 |  |  | 349
|  | OfL |  | 1 | 1 |  | 222 | 222
|  | OfS |  | 1 | 1 |  | 249 | 249
|  | Rt3 |  | 1 | 1 |  | 269 | 267
CZ16 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC | 1 | 1 |  | 56.1 | 56.1
|  | ESe | 1 | 1 |  | 38.4 | 38.6
|  | EUn | 1 | 1 |  | 52.2 | 52.3
|  | Hsp | 1 | 1 |  | 34.8 | 34.5
|  | Htl | 1 | 1 |  | 98.8 | 97.3
|  | MBT | 1 | 1 |  | 46.8 | 46.8
|  | Nrs | 1 | 1 |  | 73.2 | 70.1
|  | OfL | 1 | 1 |  | 50.2 | 49.9
|  | OfS | 1 | 1 |  | 56.3 | 56.2
|  | Rt3 | 1 | 1 |  | 55.1 | 55.1
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC | 1 | 1 |  | 103 | 103
|  | ESe | 1 | 1 |  | 70.4 | 70.8
|  | EUn | 1 | 1 |  | 95.8 | 95.9
|  | Hsp | 1 | 1 |  | 63.8 | 63.3
|  | Htl | 1 | 1 |  | 181 | 178
|  | MBT | 1 | 1 |  | 85.9 | 85.9
|  | Nrs | 1 | 1 |  | 134 | 129
|  | OfL | 1 | 1 |  | 92 | 91.6
|  | OfS | 1 | 1 |  | 103 | 103
|  | Rt3 | 1 | 1 |  | 101 | 101
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC | 1 | 1 |  | 56.1 | 56.1
|  | ESe | 1 | 1 |  | 38.4 | 38.6
|  | EUn | 1 | 1 |  | 52.2 | 52.3
|  | Hsp | 1 | 1 |  | 34.8 | 34.5
|  | Htl | 1 | 1 |  | 98.8 | 97.3
|  | MBT | 1 | 1 |  | 46.8 | 46.8
|  | Nrs | 1 | 1 |  | 73.2 | 70.1
|  | OfL | 1 | 1 |  | 50.2 | 49.9
|  | OfS | 1 | 1 |  | 56.3 | 56.2
|  | Rt3 | 1 | 1 |  | 55.1 | 55.1
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC | 1 | 1 |  | 103 | 103
|  | ESe | 1 | 1 |  | 70.4 | 70.8
|  | EUn | 1 | 1 |  | 95.8 | 95.9
|  | Hsp | 1 | 1 |  | 63.8 | 63.3
|  | Htl | 1 | 1 |  | 181 | 178
|  | MBT | 1 | 1 |  | 85.9 | 85.9
|  | Nrs | 1 | 1 |  | 134 | 129
|  | OfL | 1 | 1 |  | 92 | 91.6
|  | OfS | 1 | 1 |  | 103 | 103
|  | Rt3 | 1 | 1 |  | 101 | 101

## DEER2020EnergyImpact
Ex Ante Source Tables Export
EnergyImpact Table (exante.EnergyImpact)
This file created on 5/23/2019 6:24:23 AM while connected to AmazonWS-RDS as sptviewer.
Program/Database Description: READI v.2.5.1 (Preliminary Ex Ante Review data) options: include Non-DEER and Proposed data; 1/1/2013 - 1/1/2021
EnergyImpactID | Version | VersionSource | LastMod | PA | BldgType | BldgVint | BldgVintOut | BldgLoc | BldgHVAC | NormUnit | NumUnit | MeasArea | ScaleBasis | APreWBkWh | APreWBkW | APreWBtherm | AStdWBkWh | AStdWBkW | AStdWBtherm | APreEUkWh | APreEUkW | APreEUtherm | AStdEUkWh | AStdEUkW | AStdEUtherm | ElecImpactProfileID | GasImpactProfileID | Flag | wts
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ06 | Any | Cap-Tons | 463 | 0 | None | 169 | 0.0686 | 0 | 82.7 | 0.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.864
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ10 | Any | Cap-Tons | 455 | 0 | None | 161 | 0.113 | 0 | 78.9 | 0.0552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.978
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ06 | Any | Cap-Tons | 267 | 0 | None | 351 | 0.154 | 0 | 224 | 0.0982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.76
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ10 | Any | Cap-Tons | 156 | 0 | None | 385 | 0.23 | 0 | 246 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.912
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ06 | Any | Cap-Tons | 393 | 0 | None | 121 | 0.076 | 0 | 59.2 | 0.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.595
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ07 | Any | Cap-Tons | 30.5 | 0 | None | 176 | 0.0625 | 0 | 86 | 0.0306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 37.463
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ10 | Any | Cap-Tons | 415 | 0 | None | 181 | 0.106 | 0 | 88.3 | 0.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.6
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ10 | Any | Cap-Tons | 323 | 0 | None | 390 | 0.194 | 0 | 248 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.493
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ01 | Any | Cap-Tons | 343 | 0 | None | 19.5 | 0.0346 | 0 | 9.6 | 0.0169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.322
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ05 | Any | Cap-Tons | 247 | 0 | None | 81.5 | 0.0519 | 0 | 39.9 | 0.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.209
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ13 | Any | Cap-Tons | 431 | 0 | None | 179 | 0.111 | 0 | 87.6 | 0.0544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.196
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ02 | Any | Cap-Tons | 256 | 0 | None | 199 | 0.19 | 0 | 127 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.537
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ11 | Any | Cap-Tons | 888 | 0 | None | 231 | 0.134 | 0 | 147 | 0.0857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.449
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ16 | Any | Cap-Tons | 402 | 0 | None | 157 | 0.131 | 0 | 100 | 0.0832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.673
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ08 | Any | Cap-Tons | 813 | 0 | None | 188 | 0.114 | 0 | 92 | 0.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.447
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ13 | Any | Cap-Tons | 317 | 0 | None | 298 | 0.151 | 0 | 145 | 0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.474
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ16 | Any | Cap-Tons | 25.7 | 0 | None | 132 | 0.104 | 0 | 64.6 | 0.0507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.728
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ09 | Any | Cap-Tons | 3310 | 0 | None | 226 | 0.191 | 0 | 144 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.959
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ14 | Any | Cap-Tons | 162 | 0 | None | 419 | 0.22 | 0 | 267 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ06 | Any | Cap-Tons | 2240 | 0 | None | 105 | 0.0896 | 0 | 62.8 | 0.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ06 | Any | Cap-Tons | 811 | 0 | None | 84 | 0.0471 | 0 | 50.3 | 0.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ06 | Any | Cap-Tons | 182 | 0 | None | 180 | 0.0883 | 0 | 108 | 0.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.341
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ06 | Any | Cap-Tons | 334 | 0 | None | 129 | 0.0634 | 0 | 77.3 | 0.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.262
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ06 | Any | Cap-Tons | 114 | 0 | None | 160 | 0.0944 | 0 | 95.5 | 0.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ06 | Any | Cap-Tons | 389 | 0 | None | 130 | 0.0445 | 0 | 78 | 0.0266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.428
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ06 | Any | Cap-Tons | 25.6 | 0 | None | 137 | 0.0465 | 0 | 81.9 | 0.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ06 | Any | Cap-Tons | 256 | 0 | None | 147 | 0.0916 | 0 | 88.2 | 0.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.259
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ07 | Any | Cap-Tons | 623 | 0 | None | 126 | 0.0901 | 0 | 75.3 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.885
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ07 | Any | Cap-Tons | 348 | 0 | None | 95 | 0.0486 | 0 | 56.9 | 0.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.407
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ07 | Any | Cap-Tons | 2170 | 0 | None | 97 | 0.0744 | 0 | 58.1 | 0.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.885
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ07 | Any | Cap-Tons | 837 | 0 | None | 83 | 0.0364 | 0 | 49.6 | 0.0218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.846
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ07 | Any | Cap-Tons | 167 | 0 | None | 189 | 0.0725 | 0 | 113 | 0.0433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.897
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ07 | Any | Cap-Tons | 328 | 0 | None | 123 | 0.0531 | 0 | 73.4 | 0.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ07 | Any | Cap-Tons | 107 | 0 | None | 160 | 0.0753 | 0 | 95.8 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.846
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ07 | Any | Cap-Tons | 385 | 0 | None | 119 | 0.036 | 0 | 71.2 | 0.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.353
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ07 | Any | Cap-Tons | 24.4 | 0 | None | 130 | 0.0371 | 0 | 77.8 | 0.0222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.963
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ07 | Any | Cap-Tons | 250 | 0 | None | 142 | 0.0805 | 0 | 84.7 | 0.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.042
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ08 | Any | Cap-Tons | 721 | 0 | None | 139 | 0.0897 | 0 | 83.1 | 0.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ08 | Any | Cap-Tons | 392 | 0 | None | 111 | 0.0563 | 0 | 66.6 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.138
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ08 | Any | Cap-Tons | 2450 | 0 | None | 117 | 0.0797 | 0 | 69.8 | 0.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ08 | Any | Cap-Tons | 902 | 0 | None | 94 | 0.0402 | 0 | 56.3 | 0.0241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ08 | Any | Cap-Tons | 194 | 0 | None | 198 | 0.0815 | 0 | 119 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ08 | Any | Cap-Tons | 368 | 0 | None | 136 | 0.0555 | 0 | 81.6 | 0.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.16
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ08 | Any | Cap-Tons | 123 | 0 | None | 185 | 0.088 | 0 | 111 | 0.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ08 | Any | Cap-Tons | 428 | 0 | None | 133 | 0.0372 | 0 | 79.6 | 0.0223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.401
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ08 | Any | Cap-Tons | 26.6 | 0 | None | 150 | 0.0406 | 0 | 89.9 | 0.0243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ08 | Any | Cap-Tons | 275 | 0 | None | 167 | 0.0872 | 0 | 99.7 | 0.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ10 | Any | Cap-Tons | 752 | 0 | None | 147 | 0.13 | 0 | 87.8 | 0.0778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.909
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ10 | Any | Cap-Tons | 393 | 0 | None | 111 | 0.0837 | 0 | 66.7 | 0.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.82
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ10 | Any | Cap-Tons | 2550 | 0 | None | 128 | 0.113 | 0 | 76.3 | 0.0676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.909
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ10 | Any | Cap-Tons | 925 | 0 | None | 96.8 | 0.0574 | 0 | 57.9 | 0.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.328
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ10 | Any | Cap-Tons | 217 | 0 | None | 197 | 0.109 | 0 | 118 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.67
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ10 | Any | Cap-Tons | 371 | 0 | None | 139 | 0.0796 | 0 | 83 | 0.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.44
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ10 | Any | Cap-Tons | 123 | 0 | None | 197 | 0.128 | 0 | 118 | 0.0763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.328
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ10 | Any | Cap-Tons | 427 | 0 | None | 140 | 0.0551 | 0 | 84 | 0.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.417
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ10 | Any | Cap-Tons | 27.6 | 0 | None | 152 | 0.0591 | 0 | 91.1 | 0.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.327
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ10 | Any | Cap-Tons | 293 | 0 | None | 171 | 0.114 | 0 | 102 | 0.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.878
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ14 | Any | Cap-Tons | 815 | 0 | None | 143 | 0.107 | 0 | 85.3 | 0.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ14 | Any | Cap-Tons | 434 | 0 | None | 105 | 0.0677 | 0 | 62.8 | 0.0405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.022
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ14 | Any | Cap-Tons | 2680 | 0 | None | 130 | 0.1 | 0 | 77.9 | 0.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ14 | Any | Cap-Tons | 988 | 0 | None | 98.5 | 0.0508 | 0 | 58.9 | 0.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ14 | Any | Cap-Tons | 236 | 0 | None | 196 | 0.0992 | 0 | 117 | 0.0593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.068
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ14 | Any | Cap-Tons | 400 | 0 | None | 132 | 0.0739 | 0 | 79.2 | 0.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.076
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ14 | Any | Cap-Tons | 129 | 0 | None | 205 | 0.116 | 0 | 123 | 0.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 138 | 0.0569 | 0 | 82.3 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ06 | Any | Cap-Tons | 664 | 0 | None | 191 | 0.148 | 0 | 140 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ06 | Any | Cap-Tons | 366 | 0 | None | 143 | 0.0872 | 0 | 105 | 0.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ06 | Any | Cap-Tons | 2240 | 0 | None | 157 | 0.134 | 0 | 115 | 0.0983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ06 | Any | Cap-Tons | 811 | 0 | None | 126 | 0.0707 | 0 | 92.2 | 0.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ06 | Any | Cap-Tons | 182 | 0 | None | 270 | 0.132 | 0 | 198 | 0.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.341
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ06 | Any | Cap-Tons | 334 | 0 | None | 194 | 0.095 | 0 | 142 | 0.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.262
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ06 | Any | Cap-Tons | 114 | 0 | None | 239 | 0.142 | 0 | 175 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ06 | Any | Cap-Tons | 389 | 0 | None | 195 | 0.0667 | 0 | 143 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.428
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ06 | Any | Cap-Tons | 25.6 | 0 | None | 205 | 0.0698 | 0 | 150 | 0.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ06 | Any | Cap-Tons | 256 | 0 | None | 221 | 0.137 | 0 | 162 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.259
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ07 | Any | Cap-Tons | 623 | 0 | None | 189 | 0.135 | 0 | 138 | 0.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.885
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ07 | Any | Cap-Tons | 348 | 0 | None | 143 | 0.0729 | 0 | 104 | 0.0534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.407
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ07 | Any | Cap-Tons | 2170 | 0 | None | 145 | 0.112 | 0 | 107 | 0.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.885
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ07 | Any | Cap-Tons | 837 | 0 | None | 124 | 0.0545 | 0 | 91.1 | 0.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.846
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ07 | Any | Cap-Tons | 167 | 0 | None | 284 | 0.109 | 0 | 208 | 0.0795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.897
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ07 | Any | Cap-Tons | 328 | 0 | None | 184 | 0.0796 | 0 | 135 | 0.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ07 | Any | Cap-Tons | 107 | 0 | None | 240 | 0.113 | 0 | 176 | 0.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.846
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ07 | Any | Cap-Tons | 385 | 0 | None | 178 | 0.0539 | 0 | 131 | 0.0395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.353
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ07 | Any | Cap-Tons | 24.4 | 0 | None | 195 | 0.0557 | 0 | 143 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.963
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ07 | Any | Cap-Tons | 250 | 0 | None | 212 | 0.121 | 0 | 155 | 0.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.042
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ08 | Any | Cap-Tons | 721 | 0 | None | 208 | 0.135 | 0 | 153 | 0.0985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ08 | Any | Cap-Tons | 392 | 0 | None | 167 | 0.0843 | 0 | 122 | 0.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.138
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ08 | Any | Cap-Tons | 2450 | 0 | None | 175 | 0.119 | 0 | 128 | 0.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ08 | Any | Cap-Tons | 902 | 0 | None | 141 | 0.0603 | 0 | 103 | 0.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ08 | Any | Cap-Tons | 194 | 0 | None | 297 | 0.122 | 0 | 218 | 0.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ08 | Any | Cap-Tons | 368 | 0 | None | 204 | 0.0833 | 0 | 150 | 0.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.16
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ08 | Any | Cap-Tons | 123 | 0 | None | 277 | 0.132 | 0 | 203 | 0.0966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ08 | Any | Cap-Tons | 428 | 0 | None | 200 | 0.0558 | 0 | 146 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.401
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ08 | Any | Cap-Tons | 26.6 | 0 | None | 225 | 0.0608 | 0 | 165 | 0.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ08 | Any | Cap-Tons | 275 | 0 | None | 250 | 0.131 | 0 | 183 | 0.0957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ10 | Any | Cap-Tons | 752 | 0 | None | 220 | 0.195 | 0 | 161 | 0.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.909
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ10 | Any | Cap-Tons | 393 | 0 | None | 167 | 0.125 | 0 | 122 | 0.0919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.82
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ10 | Any | Cap-Tons | 2550 | 0 | None | 191 | 0.17 | 0 | 140 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.909
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ10 | Any | Cap-Tons | 925 | 0 | None | 145 | 0.086 | 0 | 106 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.328
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ10 | Any | Cap-Tons | 217 | 0 | None | 296 | 0.163 | 0 | 217 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.67
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ10 | Any | Cap-Tons | 371 | 0 | None | 208 | 0.119 | 0 | 152 | 0.0873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.44
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ10 | Any | Cap-Tons | 123 | 0 | None | 295 | 0.191 | 0 | 216 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.328
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ10 | Any | Cap-Tons | 427 | 0 | None | 211 | 0.0827 | 0 | 154 | 0.0605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.417
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ10 | Any | Cap-Tons | 27.6 | 0 | None | 228 | 0.0886 | 0 | 167 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.327
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ10 | Any | Cap-Tons | 293 | 0 | None | 256 | 0.17 | 0 | 187 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.878
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ14 | Any | Cap-Tons | 815 | 0 | None | 214 | 0.161 | 0 | 156 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ14 | Any | Cap-Tons | 434 | 0 | None | 157 | 0.102 | 0 | 115 | 0.0743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.022
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ14 | Any | Cap-Tons | 2680 | 0 | None | 195 | 0.15 | 0 | 143 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ14 | Any | Cap-Tons | 988 | 0 | None | 148 | 0.0762 | 0 | 108 | 0.0558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ14 | Any | Cap-Tons | 236 | 0 | None | 294 | 0.149 | 0 | 215 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.068
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ06 | Any | Cap-Tons | 664 | 0 | None | 127 | 0.099 | 0 | 76.1 | 0.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ06 | Any | Cap-Tons | 366 | 0 | None | 95.6 | 0.0582 | 0 | 57.2 | 0.0348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ06 | Any | Cap-Tons | 2240 | 0 | None | 105 | 0.0896 | 0 | 62.8 | 0.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ06 | Any | Cap-Tons | 811 | 0 | None | 84 | 0.0471 | 0 | 50.3 | 0.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ06 | Any | Cap-Tons | 182 | 0 | None | 180 | 0.0883 | 0 | 108 | 0.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.341
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ06 | Any | Cap-Tons | 334 | 0 | None | 129 | 0.0634 | 0 | 77.3 | 0.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.262
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ06 | Any | Cap-Tons | 114 | 0 | None | 160 | 0.0944 | 0 | 95.5 | 0.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ06 | Any | Cap-Tons | 389 | 0 | None | 130 | 0.0445 | 0 | 78 | 0.0266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.428
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ06 | Any | Cap-Tons | 25.6 | 0 | None | 137 | 0.0465 | 0 | 81.9 | 0.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ06 | Any | Cap-Tons | 256 | 0 | None | 147 | 0.0916 | 0 | 88.2 | 0.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.259
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ07 | Any | Cap-Tons | 623 | 0 | None | 126 | 0.0901 | 0 | 75.3 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.885
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ07 | Any | Cap-Tons | 348 | 0 | None | 95 | 0.0486 | 0 | 56.9 | 0.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.407
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ07 | Any | Cap-Tons | 2170 | 0 | None | 97 | 0.0744 | 0 | 58.1 | 0.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.885
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ07 | Any | Cap-Tons | 837 | 0 | None | 83 | 0.0364 | 0 | 49.6 | 0.0218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.846
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ07 | Any | Cap-Tons | 167 | 0 | None | 189 | 0.0725 | 0 | 113 | 0.0433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.897
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ07 | Any | Cap-Tons | 328 | 0 | None | 123 | 0.0531 | 0 | 73.4 | 0.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ07 | Any | Cap-Tons | 107 | 0 | None | 160 | 0.0753 | 0 | 95.8 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.846
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ07 | Any | Cap-Tons | 385 | 0 | None | 119 | 0.036 | 0 | 71.2 | 0.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.353
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ07 | Any | Cap-Tons | 24.4 | 0 | None | 130 | 0.0371 | 0 | 77.8 | 0.0222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.963
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ07 | Any | Cap-Tons | 250 | 0 | None | 142 | 0.0805 | 0 | 84.7 | 0.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.042
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ08 | Any | Cap-Tons | 721 | 0 | None | 139 | 0.0897 | 0 | 83.1 | 0.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ08 | Any | Cap-Tons | 392 | 0 | None | 111 | 0.0563 | 0 | 66.6 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.138
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ08 | Any | Cap-Tons | 2450 | 0 | None | 117 | 0.0797 | 0 | 69.8 | 0.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ08 | Any | Cap-Tons | 902 | 0 | None | 94 | 0.0402 | 0 | 56.3 | 0.0241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ08 | Any | Cap-Tons | 194 | 0 | None | 198 | 0.0815 | 0 | 119 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ08 | Any | Cap-Tons | 368 | 0 | None | 136 | 0.0555 | 0 | 81.6 | 0.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.16
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ08 | Any | Cap-Tons | 123 | 0 | None | 185 | 0.088 | 0 | 111 | 0.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ08 | Any | Cap-Tons | 428 | 0 | None | 133 | 0.0372 | 0 | 79.6 | 0.0223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.401
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ08 | Any | Cap-Tons | 26.6 | 0 | None | 150 | 0.0406 | 0 | 89.9 | 0.0243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ08 | Any | Cap-Tons | 275 | 0 | None | 167 | 0.0872 | 0 | 99.7 | 0.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ10 | Any | Cap-Tons | 752 | 0 | None | 147 | 0.13 | 0 | 87.8 | 0.0778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.909
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ10 | Any | Cap-Tons | 393 | 0 | None | 111 | 0.0837 | 0 | 66.7 | 0.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.82
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ10 | Any | Cap-Tons | 2550 | 0 | None | 128 | 0.113 | 0 | 76.3 | 0.0676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.909
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ10 | Any | Cap-Tons | 925 | 0 | None | 96.8 | 0.0574 | 0 | 57.9 | 0.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.328
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ10 | Any | Cap-Tons | 217 | 0 | None | 197 | 0.109 | 0 | 118 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.67
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ10 | Any | Cap-Tons | 371 | 0 | None | 139 | 0.0796 | 0 | 83 | 0.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.44
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ10 | Any | Cap-Tons | 123 | 0 | None | 197 | 0.128 | 0 | 118 | 0.0763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.328
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ10 | Any | Cap-Tons | 427 | 0 | None | 140 | 0.0551 | 0 | 84 | 0.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.417
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ10 | Any | Cap-Tons | 27.6 | 0 | None | 152 | 0.0591 | 0 | 91.1 | 0.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.327
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ10 | Any | Cap-Tons | 293 | 0 | None | 171 | 0.114 | 0 | 102 | 0.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.878
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ14 | Any | Cap-Tons | 815 | 0 | None | 143 | 0.107 | 0 | 85.3 | 0.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ14 | Any | Cap-Tons | 434 | 0 | None | 105 | 0.0677 | 0 | 62.8 | 0.0405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.022
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ14 | Any | Cap-Tons | 2680 | 0 | None | 130 | 0.1 | 0 | 77.9 | 0.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ14 | Any | Cap-Tons | 129 | 0 | None | 205 | 0.116 | 0 | 123 | 0.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 138 | 0.0569 | 0 | 82.3 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ14 | Any | Cap-Tons | 29.4 | 0 | None | 147 | 0.0599 | 0 | 87.7 | 0.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ14 | Any | Cap-Tons | 316 | 0 | None | 158 | 0.094 | 0 | 94.3 | 0.0562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ15 | Any | Cap-Tons | 559 | 0 | None | 170 | 0.0733 | 0 | 102 | 0.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.007
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ06 | Any | Cap-Tons | 366 | 0 | None | 143 | 0.0872 | 0 | 105 | 0.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ06 | Any | Cap-Tons | 2240 | 0 | None | 157 | 0.134 | 0 | 115 | 0.0983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ06 | Any | Cap-Tons | 811 | 0 | None | 126 | 0.0707 | 0 | 92.2 | 0.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ06 | Any | Cap-Tons | 182 | 0 | None | 270 | 0.132 | 0 | 198 | 0.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.341
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ06 | Any | Cap-Tons | 334 | 0 | None | 194 | 0.095 | 0 | 142 | 0.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.262
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ06 | Any | Cap-Tons | 114 | 0 | None | 239 | 0.142 | 0 | 175 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ06 | Any | Cap-Tons | 389 | 0 | None | 195 | 0.0667 | 0 | 143 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.428
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ06 | Any | Cap-Tons | 25.6 | 0 | None | 205 | 0.0698 | 0 | 150 | 0.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ06 | Any | Cap-Tons | 256 | 0 | None | 221 | 0.137 | 0 | 162 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.259
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ07 | Any | Cap-Tons | 623 | 0 | None | 189 | 0.135 | 0 | 138 | 0.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.885
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ07 | Any | Cap-Tons | 348 | 0 | None | 143 | 0.0729 | 0 | 104 | 0.0534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.407
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ07 | Any | Cap-Tons | 2170 | 0 | None | 145 | 0.112 | 0 | 107 | 0.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.885
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ07 | Any | Cap-Tons | 837 | 0 | None | 124 | 0.0545 | 0 | 91.1 | 0.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.846
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ07 | Any | Cap-Tons | 167 | 0 | None | 284 | 0.109 | 0 | 208 | 0.0795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.897
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ07 | Any | Cap-Tons | 328 | 0 | None | 184 | 0.0796 | 0 | 135 | 0.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ07 | Any | Cap-Tons | 107 | 0 | None | 240 | 0.113 | 0 | 176 | 0.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.846
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ07 | Any | Cap-Tons | 385 | 0 | None | 178 | 0.0539 | 0 | 131 | 0.0395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.353
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ07 | Any | Cap-Tons | 24.4 | 0 | None | 195 | 0.0557 | 0 | 143 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.963
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ07 | Any | Cap-Tons | 250 | 0 | None | 212 | 0.121 | 0 | 155 | 0.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.042
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ08 | Any | Cap-Tons | 721 | 0 | None | 208 | 0.135 | 0 | 153 | 0.0985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ08 | Any | Cap-Tons | 392 | 0 | None | 167 | 0.0843 | 0 | 122 | 0.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.138
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ08 | Any | Cap-Tons | 2450 | 0 | None | 175 | 0.119 | 0 | 128 | 0.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ08 | Any | Cap-Tons | 902 | 0 | None | 141 | 0.0603 | 0 | 103 | 0.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ08 | Any | Cap-Tons | 194 | 0 | None | 297 | 0.122 | 0 | 218 | 0.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ08 | Any | Cap-Tons | 368 | 0 | None | 204 | 0.0833 | 0 | 150 | 0.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.16
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ08 | Any | Cap-Tons | 123 | 0 | None | 277 | 0.132 | 0 | 203 | 0.0966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ08 | Any | Cap-Tons | 428 | 0 | None | 200 | 0.0558 | 0 | 146 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.401
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ08 | Any | Cap-Tons | 26.6 | 0 | None | 225 | 0.0608 | 0 | 165 | 0.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ08 | Any | Cap-Tons | 275 | 0 | None | 250 | 0.131 | 0 | 183 | 0.0957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ10 | Any | Cap-Tons | 752 | 0 | None | 220 | 0.195 | 0 | 161 | 0.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.909
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ10 | Any | Cap-Tons | 393 | 0 | None | 167 | 0.125 | 0 | 122 | 0.0919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.82
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ10 | Any | Cap-Tons | 2550 | 0 | None | 191 | 0.17 | 0 | 140 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.909
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ10 | Any | Cap-Tons | 925 | 0 | None | 145 | 0.086 | 0 | 106 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.328
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ10 | Any | Cap-Tons | 217 | 0 | None | 296 | 0.163 | 0 | 217 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.67
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ10 | Any | Cap-Tons | 371 | 0 | None | 208 | 0.119 | 0 | 152 | 0.0873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.44
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ10 | Any | Cap-Tons | 123 | 0 | None | 295 | 0.191 | 0 | 216 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.328
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ10 | Any | Cap-Tons | 427 | 0 | None | 211 | 0.0827 | 0 | 154 | 0.0605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.417
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ10 | Any | Cap-Tons | 27.6 | 0 | None | 228 | 0.0886 | 0 | 167 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.327
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ10 | Any | Cap-Tons | 293 | 0 | None | 256 | 0.17 | 0 | 187 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.878
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ14 | Any | Cap-Tons | 815 | 0 | None | 214 | 0.161 | 0 | 156 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ14 | Any | Cap-Tons | 434 | 0 | None | 157 | 0.102 | 0 | 115 | 0.0743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.022
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | EUn | Ex | Ex | CZ14 | Any | Cap-Tons | 2680 | 0 | None | 195 | 0.15 | 0 | 143 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ14 | Any | Cap-Tons | 129 | 0 | None | 308 | 0.174 | 0 | 225 | 0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 206 | 0.0853 | 0 | 151 | 0.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ14 | Any | Cap-Tons | 29.4 | 0 | None | 220 | 0.0897 | 0 | 161 | 0.0657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ14 | Any | Cap-Tons | 316 | 0 | None | 236 | 0.141 | 0 | 173 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ06 | Any | Cap-Tons | 664 | 0 | None | 127 | 0.099 | 0 | 76.1 | 0.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ06 | Any | Cap-Tons | 366 | 0 | None | 95.6 | 0.0582 | 0 | 57.2 | 0.0348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ06 | Any | Cap-Tons | 763 | 0 | None | 164 | 0.123 | 0 | 80.1 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ06 | Any | Cap-Tons | 393 | 0 | None | 121 | 0.076 | 0 | 59.2 | 0.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.595
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ06 | Any | Cap-Tons | 2600 | 0 | None | 147 | 0.112 | 0 | 72.1 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ06 | Any | Cap-Tons | 809 | 0 | None | 131 | 0.0662 | 0 | 63.9 | 0.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.334
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ06 | Any | Cap-Tons | 267 | 0 | None | 249 | 0.109 | 0 | 122 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.76
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ06 | Any | Cap-Tons | 354 | 0 | None | 157 | 0.0832 | 0 | 77 | 0.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.709
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ06 | Any | Cap-Tons | 128 | 0 | None | 225 | 0.126 | 0 | 110 | 0.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.334
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ06 | Any | Cap-Tons | 31.9 | 0 | None | 191 | 0.0768 | 0 | 93.4 | 0.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.044
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ06 | Any | Cap-Tons | 266 | 0 | None | 180 | 0.113 | 0 | 88 | 0.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.949
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ07 | Any | Cap-Tons | 720 | 0 | None | 156 | 0.108 | 0 | 76.4 | 0.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.56
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ07 | Any | Cap-Tons | 372 | 0 | None | 120 | 0.0669 | 0 | 58.5 | 0.0327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.829
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ07 | Any | Cap-Tons | 2520 | 0 | None | 134 | 0.0937 | 0 | 65.4 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.56
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ07 | Any | Cap-Tons | 821 | 0 | None | 127 | 0.0533 | 0 | 62.3 | 0.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.755
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ07 | Any | Cap-Tons | 250 | 0 | None | 258 | 0.0899 | 0 | 126 | 0.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.165
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ07 | Any | Cap-Tons | 337 | 0 | None | 154 | 0.0769 | 0 | 75.4 | 0.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.736
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ07 | Any | Cap-Tons | 119 | 0 | None | 226 | 0.103 | 0 | 111 | 0.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.755
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ07 | Any | Cap-Tons | 458 | 0 | None | 149 | 0.0528 | 0 | 72.8 | 0.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 66.908
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ07 | Any | Cap-Tons | 30.5 | 0 | None | 176 | 0.0625 | 0 | 86 | 0.0306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 37.463
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ07 | Any | Cap-Tons | 260 | 0 | None | 165 | 0.0998 | 0 | 80.8 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.511
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ08 | Any | Cap-Tons | 812 | 0 | None | 187 | 0.114 | 0 | 91.7 | 0.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.102
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ08 | Any | Cap-Tons | 422 | 0 | None | 147 | 0.0752 | 0 | 71.8 | 0.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.671
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ08 | Any | Cap-Tons | 2830 | 0 | None | 165 | 0.102 | 0 | 80.9 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.102
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ08 | Any | Cap-Tons | 883 | 0 | None | 143 | 0.0584 | 0 | 70.1 | 0.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.604
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ08 | Any | Cap-Tons | 283 | 0 | None | 271 | 0.102 | 0 | 132 | 0.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.049
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ08 | Any | Cap-Tons | 388 | 0 | None | 173 | 0.0749 | 0 | 84.4 | 0.0366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ08 | Any | Cap-Tons | 138 | 0 | None | 258 | 0.119 | 0 | 126 | 0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.604
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ08 | Any | Cap-Tons | 507 | 0 | None | 178 | 0.0589 | 0 | 86.9 | 0.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.743
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ08 | Any | Cap-Tons | 33.1 | 0 | None | 211 | 0.0746 | 0 | 103 | 0.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.976
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ08 | Any | Cap-Tons | 285 | 0 | None | 214 | 0.113 | 0 | 105 | 0.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.703
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ10 | Any | Cap-Tons | 876 | 0 | None | 200 | 0.163 | 0 | 98 | 0.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.698
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ10 | Any | Cap-Tons | 3050 | 0 | None | 184 | 0.143 | 0 | 90 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.698
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ10 | Any | Cap-Tons | 896 | 0 | None | 154 | 0.0841 | 0 | 75.3 | 0.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.912
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ10 | Any | Cap-Tons | 323 | 0 | None | 277 | 0.138 | 0 | 135 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.493
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ10 | Any | Cap-Tons | 415 | 0 | None | 181 | 0.106 | 0 | 88.3 | 0.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.6
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ10 | Any | Cap-Tons | 156 | 0 | None | 274 | 0.163 | 0 | 134 | 0.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.912
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ10 | Any | Cap-Tons | 513 | 0 | None | 197 | 0.0933 | 0 | 96.3 | 0.0456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.894
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ10 | Any | Cap-Tons | 37 | 0 | None | 218 | 0.109 | 0 | 107 | 0.0532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.339
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ10 | Any | Cap-Tons | 307 | 0 | None | 215 | 0.139 | 0 | 105 | 0.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.894
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ14 | Any | Cap-Tons | 951 | 0 | None | 192 | 0.133 | 0 | 94 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ14 | Any | Cap-Tons | 491 | 0 | None | 149 | 0.0953 | 0 | 73.1 | 0.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.109
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ14 | Any | Cap-Tons | 3170 | 0 | None | 188 | 0.131 | 0 | 91.8 | 0.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ14 | Any | Cap-Tons | 941 | 0 | None | 153 | 0.075 | 0 | 74.9 | 0.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ14 | Any | Cap-Tons | 322 | 0 | None | 291 | 0.131 | 0 | 142 | 0.0643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 175 | 0.095 | 0 | 85.8 | 0.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.208
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ14 | Any | Cap-Tons | 163 | 0 | None | 298 | 0.157 | 0 | 146 | 0.0766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ14 | Any | Cap-Tons | 532 | 0 | None | 194 | 0.0979 | 0 | 94.8 | 0.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.361
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ14 | Any | Cap-Tons | 38.4 | 0 | None | 218 | 0.105 | 0 | 106 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.202
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ14 | Any | Cap-Tons | 336 | 0 | None | 198 | 0.117 | 0 | 96.7 | 0.0574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ14 | Any | Cap-Tons | 29.4 | 0 | None | 147 | 0.0599 | 0 | 87.7 | 0.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ14 | Any | Cap-Tons | 316 | 0 | None | 158 | 0.094 | 0 | 94.3 | 0.0562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ15 | Any | Cap-Tons | 559 | 0 | None | 170 | 0.0733 | 0 | 102 | 0.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.007
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ15 | Any | Cap-Tons | 633 | 0 | None | 240 | 0.0983 | 0 | 117 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ15 | Any | Cap-Tons | 304 | 0 | None | 287 | 0.104 | 0 | 172 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ15 | Any | Cap-Tons | 494 | 0 | None | 205 | 0.0805 | 0 | 123 | 0.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ15 | Any | Cap-Tons | 385 | 0 | None | 410 | 0.138 | 0 | 200 | 0.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ15 | Any | Cap-Tons | 534 | 0 | None | 280 | 0.109 | 0 | 137 | 0.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ15 | Any | Cap-Tons | 534 | 0 | None | 202 | 0.0577 | 0 | 121 | 0.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ15 | Any | Cap-Tons | 35 | 0 | None | 227 | 0.0695 | 0 | 136 | 0.0416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ15 | Any | Cap-Tons | 387 | 0 | None | 244 | 0.105 | 0 | 146 | 0.0627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ15 | Any | Cap-Tons | 631 | 0 | None | 291 | 0.0979 | 0 | 142 | 0.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ15 | Any | Cap-Tons | 44.3 | 0 | None | 346 | 0.113 | 0 | 169 | 0.0552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ15 | Any | Cap-Tons | 411 | 0 | None | 312 | 0.131 | 0 | 152 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ06 | Any | Cap-Tons | 763 | 0 | None | 231 | 0.173 | 0 | 147 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ06 | Any | Cap-Tons | 393 | 0 | None | 171 | 0.107 | 0 | 109 | 0.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.595
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ06 | Any | Cap-Tons | 2600 | 0 | None | 208 | 0.158 | 0 | 132 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ06 | Any | Cap-Tons | 809 | 0 | None | 184 | 0.0933 | 0 | 117 | 0.0594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.334
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ06 | Any | Cap-Tons | 354 | 0 | None | 222 | 0.117 | 0 | 141 | 0.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.709
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ06 | Any | Cap-Tons | 128 | 0 | None | 317 | 0.177 | 0 | 202 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.334
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ06 | Any | Cap-Tons | 463 | 0 | None | 238 | 0.0966 | 0 | 152 | 0.0615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.864
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ06 | Any | Cap-Tons | 31.9 | 0 | None | 269 | 0.108 | 0 | 171 | 0.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.044
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ06 | Any | Cap-Tons | 266 | 0 | None | 253 | 0.159 | 0 | 161 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.949
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ07 | Any | Cap-Tons | 720 | 0 | None | 220 | 0.152 | 0 | 140 | 0.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.56
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ07 | Any | Cap-Tons | 372 | 0 | None | 169 | 0.0942 | 0 | 107 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.829
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ07 | Any | Cap-Tons | 2520 | 0 | None | 188 | 0.132 | 0 | 120 | 0.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.56
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ07 | Any | Cap-Tons | 821 | 0 | None | 179 | 0.075 | 0 | 114 | 0.0478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.755
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ07 | Any | Cap-Tons | 250 | 0 | None | 363 | 0.127 | 0 | 232 | 0.0806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.165
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ07 | Any | Cap-Tons | 337 | 0 | None | 217 | 0.108 | 0 | 138 | 0.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.736
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ07 | Any | Cap-Tons | 119 | 0 | None | 319 | 0.144 | 0 | 203 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.755
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ07 | Any | Cap-Tons | 458 | 0 | None | 210 | 0.0743 | 0 | 134 | 0.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 66.908
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ07 | Any | Cap-Tons | 30.5 | 0 | None | 248 | 0.088 | 0 | 158 | 0.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 37.463
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ07 | Any | Cap-Tons | 260 | 0 | None | 233 | 0.141 | 0 | 148 | 0.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.511
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ08 | Any | Cap-Tons | 812 | 0 | None | 264 | 0.16 | 0 | 168 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.102
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ08 | Any | Cap-Tons | 422 | 0 | None | 207 | 0.106 | 0 | 132 | 0.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.671
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ08 | Any | Cap-Tons | 2830 | 0 | None | 233 | 0.144 | 0 | 148 | 0.0918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.102
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ08 | Any | Cap-Tons | 883 | 0 | None | 202 | 0.0823 | 0 | 129 | 0.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.604
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ08 | Any | Cap-Tons | 283 | 0 | None | 382 | 0.143 | 0 | 243 | 0.0914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.049
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ08 | Any | Cap-Tons | 388 | 0 | None | 243 | 0.105 | 0 | 155 | 0.0672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ08 | Any | Cap-Tons | 138 | 0 | None | 363 | 0.167 | 0 | 232 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.604
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ08 | Any | Cap-Tons | 507 | 0 | None | 250 | 0.0829 | 0 | 159 | 0.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.743
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ08 | Any | Cap-Tons | 33.1 | 0 | None | 298 | 0.105 | 0 | 190 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.976
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ08 | Any | Cap-Tons | 285 | 0 | None | 302 | 0.159 | 0 | 192 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.703
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ10 | Any | Cap-Tons | 876 | 0 | None | 282 | 0.229 | 0 | 180 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.698
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ10 | Any | Cap-Tons | 455 | 0 | None | 227 | 0.159 | 0 | 145 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.978
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ10 | Any | Cap-Tons | 3050 | 0 | None | 259 | 0.202 | 0 | 165 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.698
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ10 | Any | Cap-Tons | 896 | 0 | None | 217 | 0.118 | 0 | 138 | 0.0754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.912
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ10 | Any | Cap-Tons | 323 | 0 | None | 390 | 0.194 | 0 | 248 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.493
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ10 | Any | Cap-Tons | 415 | 0 | None | 254 | 0.15 | 0 | 162 | 0.0955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.6
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ10 | Any | Cap-Tons | 513 | 0 | None | 277 | 0.131 | 0 | 177 | 0.0837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.894
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ10 | Any | Cap-Tons | 37 | 0 | None | 307 | 0.153 | 0 | 196 | 0.0976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.339
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ10 | Any | Cap-Tons | 307 | 0 | None | 303 | 0.196 | 0 | 193 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.894
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ14 | Any | Cap-Tons | 951 | 0 | None | 271 | 0.188 | 0 | 172 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ14 | Any | Cap-Tons | 491 | 0 | None | 210 | 0.134 | 0 | 134 | 0.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.109
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ14 | Any | Cap-Tons | 3170 | 0 | None | 264 | 0.184 | 0 | 168 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ14 | Any | Cap-Tons | 941 | 0 | None | 216 | 0.106 | 0 | 137 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ14 | Any | Cap-Tons | 322 | 0 | None | 410 | 0.185 | 0 | 261 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 247 | 0.134 | 0 | 157 | 0.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.208
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ14 | Any | Cap-Tons | 163 | 0 | None | 420 | 0.22 | 0 | 267 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ14 | Any | Cap-Tons | 532 | 0 | None | 273 | 0.138 | 0 | 174 | 0.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.361
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ14 | Any | Cap-Tons | 38.4 | 0 | None | 306 | 0.148 | 0 | 195 | 0.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.202
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ14 | Any | Cap-Tons | 336 | 0 | None | 278 | 0.165 | 0 | 177 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ14 | Any | Cap-Tons | 400 | 0 | None | 198 | 0.111 | 0 | 145 | 0.0812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.076
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Nrs | Ex | Ex | CZ14 | Any | Cap-Tons | 129 | 0 | None | 308 | 0.174 | 0 | 225 | 0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 206 | 0.0853 | 0 | 151 | 0.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ15 | Any | Cap-Tons | 633 | 0 | None | 338 | 0.138 | 0 | 215 | 0.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ14 | Any | Cap-Tons | 29.4 | 0 | None | 220 | 0.0897 | 0 | 161 | 0.0657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ14 | Any | Cap-Tons | 316 | 0 | None | 236 | 0.141 | 0 | 173 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ15 | Any | Cap-Tons | 559 | 0 | None | 255 | 0.11 | 0 | 186 | 0.0805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.007
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ15 | Any | Cap-Tons | 304 | 0 | None | 430 | 0.156 | 0 | 315 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ15 | Any | Cap-Tons | 494 | 0 | None | 308 | 0.121 | 0 | 226 | 0.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ15 | Any | Cap-Tons | 385 | 0 | None | 577 | 0.194 | 0 | 368 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ15 | Any | Cap-Tons | 534 | 0 | None | 395 | 0.153 | 0 | 252 | 0.0974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ15 | Any | Cap-Tons | 534 | 0 | None | 303 | 0.0865 | 0 | 222 | 0.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ15 | Any | Cap-Tons | 35 | 0 | None | 340 | 0.104 | 0 | 249 | 0.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ15 | Any | Cap-Tons | 387 | 0 | None | 365 | 0.157 | 0 | 267 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ15 | Any | Cap-Tons | 631 | 0 | None | 410 | 0.138 | 0 | 261 | 0.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ15 | Any | Cap-Tons | 44.3 | 0 | None | 487 | 0.159 | 0 | 310 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ15 | Any | Cap-Tons | 411 | 0 | None | 439 | 0.185 | 0 | 280 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ06 | Any | Cap-Tons | 763 | 0 | None | 164 | 0.123 | 0 | 80.1 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ06 | Any | Cap-Tons | 2600 | 0 | None | 147 | 0.112 | 0 | 72.1 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ06 | Any | Cap-Tons | 809 | 0 | None | 131 | 0.0662 | 0 | 63.9 | 0.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.334
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ06 | Any | Cap-Tons | 267 | 0 | None | 249 | 0.109 | 0 | 122 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.76
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ06 | Any | Cap-Tons | 354 | 0 | None | 157 | 0.0832 | 0 | 77 | 0.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.709
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ06 | Any | Cap-Tons | 128 | 0 | None | 225 | 0.126 | 0 | 110 | 0.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.334
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ06 | Any | Cap-Tons | 463 | 0 | None | 169 | 0.0686 | 0 | 82.7 | 0.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.864
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ06 | Any | Cap-Tons | 31.9 | 0 | None | 191 | 0.0768 | 0 | 93.4 | 0.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.044
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ06 | Any | Cap-Tons | 266 | 0 | None | 180 | 0.113 | 0 | 88 | 0.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.949
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ07 | Any | Cap-Tons | 720 | 0 | None | 156 | 0.108 | 0 | 76.4 | 0.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.56
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ07 | Any | Cap-Tons | 372 | 0 | None | 120 | 0.0669 | 0 | 58.5 | 0.0327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.829
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ07 | Any | Cap-Tons | 2520 | 0 | None | 134 | 0.0937 | 0 | 65.4 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.56
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ07 | Any | Cap-Tons | 821 | 0 | None | 127 | 0.0533 | 0 | 62.3 | 0.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.755
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ07 | Any | Cap-Tons | 250 | 0 | None | 258 | 0.0899 | 0 | 126 | 0.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.165
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ07 | Any | Cap-Tons | 337 | 0 | None | 154 | 0.0769 | 0 | 75.4 | 0.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.736
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ07 | Any | Cap-Tons | 119 | 0 | None | 226 | 0.103 | 0 | 111 | 0.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.755
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ07 | Any | Cap-Tons | 458 | 0 | None | 149 | 0.0528 | 0 | 72.8 | 0.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 66.908
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ07 | Any | Cap-Tons | 260 | 0 | None | 165 | 0.0998 | 0 | 80.8 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.511
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ08 | Any | Cap-Tons | 812 | 0 | None | 187 | 0.114 | 0 | 91.7 | 0.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.102
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ08 | Any | Cap-Tons | 422 | 0 | None | 147 | 0.0752 | 0 | 71.8 | 0.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.671
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ08 | Any | Cap-Tons | 2830 | 0 | None | 165 | 0.102 | 0 | 80.9 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.102
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ08 | Any | Cap-Tons | 883 | 0 | None | 143 | 0.0584 | 0 | 70.1 | 0.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.604
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ08 | Any | Cap-Tons | 283 | 0 | None | 271 | 0.102 | 0 | 132 | 0.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.049
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ08 | Any | Cap-Tons | 388 | 0 | None | 173 | 0.0749 | 0 | 84.4 | 0.0366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ08 | Any | Cap-Tons | 138 | 0 | None | 258 | 0.119 | 0 | 126 | 0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.604
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ08 | Any | Cap-Tons | 507 | 0 | None | 178 | 0.0589 | 0 | 86.9 | 0.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.743
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ08 | Any | Cap-Tons | 33.1 | 0 | None | 211 | 0.0746 | 0 | 103 | 0.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.976
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ08 | Any | Cap-Tons | 285 | 0 | None | 214 | 0.113 | 0 | 105 | 0.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.703
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ10 | Any | Cap-Tons | 876 | 0 | None | 200 | 0.163 | 0 | 98 | 0.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.698
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ10 | Any | Cap-Tons | 455 | 0 | None | 161 | 0.113 | 0 | 78.9 | 0.0552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.978
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ10 | Any | Cap-Tons | 3050 | 0 | None | 184 | 0.143 | 0 | 90 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.698
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ10 | Any | Cap-Tons | 896 | 0 | None | 154 | 0.0841 | 0 | 75.3 | 0.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.912
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ10 | Any | Cap-Tons | 323 | 0 | None | 277 | 0.138 | 0 | 135 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.493
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ10 | Any | Cap-Tons | 156 | 0 | None | 274 | 0.163 | 0 | 134 | 0.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.912
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ10 | Any | Cap-Tons | 513 | 0 | None | 197 | 0.0933 | 0 | 96.3 | 0.0456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.894
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ10 | Any | Cap-Tons | 37 | 0 | None | 218 | 0.109 | 0 | 107 | 0.0532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.339
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ10 | Any | Cap-Tons | 307 | 0 | None | 215 | 0.139 | 0 | 105 | 0.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.894
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ14 | Any | Cap-Tons | 951 | 0 | None | 192 | 0.133 | 0 | 94 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ14 | Any | Cap-Tons | 491 | 0 | None | 149 | 0.0953 | 0 | 73.1 | 0.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.109
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ14 | Any | Cap-Tons | 3170 | 0 | None | 188 | 0.131 | 0 | 91.8 | 0.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ14 | Any | Cap-Tons | 941 | 0 | None | 153 | 0.075 | 0 | 74.9 | 0.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ14 | Any | Cap-Tons | 322 | 0 | None | 291 | 0.131 | 0 | 142 | 0.0643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 175 | 0.095 | 0 | 85.8 | 0.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.208
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ14 | Any | Cap-Tons | 163 | 0 | None | 298 | 0.157 | 0 | 146 | 0.0766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ14 | Any | Cap-Tons | 532 | 0 | None | 194 | 0.0979 | 0 | 94.8 | 0.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.361
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ14 | Any | Cap-Tons | 38.4 | 0 | None | 218 | 0.105 | 0 | 106 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.202
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ14 | Any | Cap-Tons | 336 | 0 | None | 198 | 0.117 | 0 | 96.7 | 0.0574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ15 | Any | Cap-Tons | 633 | 0 | None | 240 | 0.0983 | 0 | 117 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ14 | Any | Cap-Tons | 988 | 0 | None | 98.5 | 0.0508 | 0 | 58.9 | 0.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ14 | Any | Cap-Tons | 236 | 0 | None | 196 | 0.0992 | 0 | 117 | 0.0593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.068
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ14 | Any | Cap-Tons | 400 | 0 | None | 132 | 0.0739 | 0 | 79.2 | 0.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.076
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ15 | Any | Cap-Tons | 304 | 0 | None | 287 | 0.104 | 0 | 172 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ15 | Any | Cap-Tons | 494 | 0 | None | 205 | 0.0805 | 0 | 123 | 0.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ15 | Any | Cap-Tons | 534 | 0 | None | 202 | 0.0577 | 0 | 121 | 0.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ15 | Any | Cap-Tons | 35 | 0 | None | 227 | 0.0695 | 0 | 136 | 0.0416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ15 | Any | Cap-Tons | 387 | 0 | None | 244 | 0.105 | 0 | 146 | 0.0627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ECC | Ex | Ex | CZ06 | Any | Cap-Tons | 664 | 0 | None | 191 | 0.148 | 0 | 140 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.02
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ15 | Any | Cap-Tons | 385 | 0 | None | 410 | 0.138 | 0 | 200 | 0.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ15 | Any | Cap-Tons | 534 | 0 | None | 280 | 0.109 | 0 | 137 | 0.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ15 | Any | Cap-Tons | 631 | 0 | None | 291 | 0.0979 | 0 | 142 | 0.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ15 | Any | Cap-Tons | 44.3 | 0 | None | 346 | 0.113 | 0 | 169 | 0.0552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ15 | Any | Cap-Tons | 411 | 0 | None | 312 | 0.131 | 0 | 152 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ06 | Any | Cap-Tons | 763 | 0 | None | 231 | 0.173 | 0 | 147 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ06 | Any | Cap-Tons | 393 | 0 | None | 171 | 0.107 | 0 | 109 | 0.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.595
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ06 | Any | Cap-Tons | 2600 | 0 | None | 208 | 0.158 | 0 | 132 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ06 | Any | Cap-Tons | 809 | 0 | None | 184 | 0.0933 | 0 | 117 | 0.0594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.334
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ06 | Any | Cap-Tons | 267 | 0 | None | 351 | 0.154 | 0 | 224 | 0.0982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.76
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ06 | Any | Cap-Tons | 354 | 0 | None | 222 | 0.117 | 0 | 141 | 0.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.709
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ06 | Any | Cap-Tons | 128 | 0 | None | 317 | 0.177 | 0 | 202 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.334
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ06 | Any | Cap-Tons | 463 | 0 | None | 238 | 0.0966 | 0 | 152 | 0.0615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.864
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ06 | Any | Cap-Tons | 31.9 | 0 | None | 269 | 0.108 | 0 | 171 | 0.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.044
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ06 | Any | Cap-Tons | 266 | 0 | None | 253 | 0.159 | 0 | 161 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.949
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ07 | Any | Cap-Tons | 720 | 0 | None | 220 | 0.152 | 0 | 140 | 0.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.56
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ07 | Any | Cap-Tons | 372 | 0 | None | 169 | 0.0942 | 0 | 107 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.829
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ07 | Any | Cap-Tons | 2520 | 0 | None | 188 | 0.132 | 0 | 120 | 0.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.56
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ07 | Any | Cap-Tons | 821 | 0 | None | 179 | 0.075 | 0 | 114 | 0.0478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.755
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ07 | Any | Cap-Tons | 250 | 0 | None | 363 | 0.127 | 0 | 232 | 0.0806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.165
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ07 | Any | Cap-Tons | 337 | 0 | None | 217 | 0.108 | 0 | 138 | 0.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.736
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ07 | Any | Cap-Tons | 119 | 0 | None | 319 | 0.144 | 0 | 203 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.755
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ07 | Any | Cap-Tons | 458 | 0 | None | 210 | 0.0743 | 0 | 134 | 0.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 66.908
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ07 | Any | Cap-Tons | 30.5 | 0 | None | 248 | 0.088 | 0 | 158 | 0.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 37.463
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ07 | Any | Cap-Tons | 260 | 0 | None | 233 | 0.141 | 0 | 148 | 0.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.511
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ08 | Any | Cap-Tons | 812 | 0 | None | 264 | 0.16 | 0 | 168 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.102
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ08 | Any | Cap-Tons | 422 | 0 | None | 207 | 0.106 | 0 | 132 | 0.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.671
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ08 | Any | Cap-Tons | 2830 | 0 | None | 233 | 0.144 | 0 | 148 | 0.0918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.102
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ08 | Any | Cap-Tons | 883 | 0 | None | 202 | 0.0823 | 0 | 129 | 0.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.604
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ08 | Any | Cap-Tons | 283 | 0 | None | 382 | 0.143 | 0 | 243 | 0.0914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.049
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ08 | Any | Cap-Tons | 388 | 0 | None | 243 | 0.105 | 0 | 155 | 0.0672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ08 | Any | Cap-Tons | 138 | 0 | None | 363 | 0.167 | 0 | 232 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.604
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ08 | Any | Cap-Tons | 507 | 0 | None | 250 | 0.0829 | 0 | 159 | 0.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.743
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ08 | Any | Cap-Tons | 33.1 | 0 | None | 298 | 0.105 | 0 | 190 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.976
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ08 | Any | Cap-Tons | 285 | 0 | None | 302 | 0.159 | 0 | 192 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.703
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ10 | Any | Cap-Tons | 876 | 0 | None | 282 | 0.229 | 0 | 180 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.698
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ10 | Any | Cap-Tons | 455 | 0 | None | 227 | 0.159 | 0 | 145 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.978
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ10 | Any | Cap-Tons | 3050 | 0 | None | 259 | 0.202 | 0 | 165 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.698
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ10 | Any | Cap-Tons | 896 | 0 | None | 217 | 0.118 | 0 | 138 | 0.0754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.912
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ10 | Any | Cap-Tons | 415 | 0 | None | 254 | 0.15 | 0 | 162 | 0.0955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.6
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ10 | Any | Cap-Tons | 156 | 0 | None | 385 | 0.23 | 0 | 246 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.912
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ10 | Any | Cap-Tons | 513 | 0 | None | 277 | 0.131 | 0 | 177 | 0.0837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.894
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ10 | Any | Cap-Tons | 37 | 0 | None | 307 | 0.153 | 0 | 196 | 0.0976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.339
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ10 | Any | Cap-Tons | 307 | 0 | None | 303 | 0.196 | 0 | 193 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.894
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Old | Ex | CZ14 | Any | Cap-Tons | 951 | 0 | None | 271 | 0.188 | 0 | 172 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ14 | Any | Cap-Tons | 491 | 0 | None | 210 | 0.134 | 0 | 134 | 0.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.109
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Old | Ex | CZ14 | Any | Cap-Tons | 3170 | 0 | None | 264 | 0.184 | 0 | 168 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Old | Ex | CZ14 | Any | Cap-Tons | 941 | 0 | None | 216 | 0.106 | 0 | 137 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ14 | Any | Cap-Tons | 322 | 0 | None | 410 | 0.185 | 0 | 261 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 247 | 0.134 | 0 | 157 | 0.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.208
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Old | Ex | CZ14 | Any | Cap-Tons | 163 | 0 | None | 420 | 0.22 | 0 | 267 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ14 | Any | Cap-Tons | 532 | 0 | None | 273 | 0.138 | 0 | 174 | 0.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.361
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ14 | Any | Cap-Tons | 38.4 | 0 | None | 306 | 0.148 | 0 | 195 | 0.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.202
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ14 | Any | Cap-Tons | 336 | 0 | None | 278 | 0.165 | 0 | 177 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Hsp | Ex | Ex | CZ14 | Any | Cap-Tons | 988 | 0 | None | 148 | 0.0762 | 0 | 108 | 0.0558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ14 | Any | Cap-Tons | 236 | 0 | None | 294 | 0.149 | 0 | 215 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.068
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ14 | Any | Cap-Tons | 400 | 0 | None | 198 | 0.111 | 0 | 145 | 0.0812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.076
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Old | Ex | CZ15 | Any | Cap-Tons | 633 | 0 | None | 338 | 0.138 | 0 | 215 | 0.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | ESe | Ex | Ex | CZ15 | Any | Cap-Tons | 559 | 0 | None | 255 | 0.11 | 0 | 186 | 0.0805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.007
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Htl | Ex | Ex | CZ15 | Any | Cap-Tons | 304 | 0 | None | 430 | 0.156 | 0 | 315 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | MBT | Ex | Ex | CZ15 | Any | Cap-Tons | 494 | 0 | None | 308 | 0.121 | 0 | 226 | 0.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfL | Ex | Ex | CZ15 | Any | Cap-Tons | 534 | 0 | None | 303 | 0.0865 | 0 | 222 | 0.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | OfS | Ex | Ex | CZ15 | Any | Cap-Tons | 35 | 0 | None | 340 | 0.104 | 0 | 249 | 0.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SDG | Rt3 | Ex | Ex | CZ15 | Any | Cap-Tons | 387 | 0 | None | 365 | 0.157 | 0 | 267 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Old | Ex | CZ15 | Any | Cap-Tons | 385 | 0 | None | 577 | 0.194 | 0 | 368 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Old | Ex | CZ15 | Any | Cap-Tons | 534 | 0 | None | 395 | 0.153 | 0 | 252 | 0.0974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Old | Ex | CZ15 | Any | Cap-Tons | 631 | 0 | None | 410 | 0.138 | 0 | 261 | 0.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Old | Ex | CZ15 | Any | Cap-Tons | 44.3 | 0 | None | 487 | 0.159 | 0 | 310 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Old | Ex | CZ15 | Any | Cap-Tons | 411 | 0 | None | 439 | 0.185 | 0 | 280 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ01 | Any | Cap-Tons | 344 | 0 | None | 25.5 | 0.0644 | 0 | 15.3 | 0.0385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ01 | Any | Cap-Tons | 169 | 0 | None | 18.4 | 0.0297 | 0 | 11 | 0.0178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ01 | Any | Cap-Tons | 1310 | 0 | None | 25 | 0.0491 | 0 | 14.9 | 0.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ01 | Any | Cap-Tons | 533 | 0 | None | 8.1 | 0.0187 | 0 | 4.9 | 0.0112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ01 | Any | Cap-Tons | 109 | 0 | None | 79.5 | 0.0454 | 0 | 47.6 | 0.0272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.224
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ01 | Any | Cap-Tons | 191 | 0 | None | 28.9 | 0.0337 | 0 | 17.3 | 0.0202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ01 | Any | Cap-Tons | 64.1 | 0 | None | 19.4 | 0.0355 | 0 | 11.6 | 0.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ01 | Any | Cap-Tons | 261 | 0 | None | 28.9 | 0.0267 | 0 | 17.3 | 0.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.353
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ01 | Any | Cap-Tons | 15.6 | 0 | None | 32.4 | 0.0261 | 0 | 19.4 | 0.0156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.325
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ01 | Any | Cap-Tons | 147 | 0 | None | 31.4 | 0.05 | 0 | 18.8 | 0.0299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ02 | Any | Cap-Tons | 607 | 0 | None | 97.4 | 0.0894 | 0 | 58.3 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.802
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ02 | Any | Cap-Tons | 311 | 0 | None | 71.7 | 0.0398 | 0 | 42.9 | 0.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.622
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ02 | Any | Cap-Tons | 2140 | 0 | None | 87 | 0.0953 | 0 | 52.1 | 0.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.802
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ02 | Any | Cap-Tons | 823 | 0 | None | 55.2 | 0.0545 | 0 | 33 | 0.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ02 | Any | Cap-Tons | 177 | 0 | None | 149 | 0.121 | 0 | 89.3 | 0.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.824
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ02 | Any | Cap-Tons | 312 | 0 | None | 91.7 | 0.0839 | 0 | 54.9 | 0.0502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.337
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ02 | Any | Cap-Tons | 102 | 0 | None | 120 | 0.132 | 0 | 71.6 | 0.0788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ02 | Any | Cap-Tons | 370 | 0 | None | 95.3 | 0.0681 | 0 | 57 | 0.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.833
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ02 | Any | Cap-Tons | 22.7 | 0 | None | 108 | 0.0793 | 0 | 64.5 | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.847
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ02 | Any | Cap-Tons | 243 | 0 | None | 115 | 0.11 | 0 | 69.1 | 0.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.284
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ03 | Any | Cap-Tons | 487 | 0 | None | 71.8 | 0.0541 | 0 | 42.9 | 0.0323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.221
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ03 | Any | Cap-Tons | 258 | 0 | None | 56.4 | 0.027 | 0 | 33.7 | 0.0162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.819
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ03 | Any | Cap-Tons | 1740 | 0 | None | 60.4 | 0.0609 | 0 | 36.2 | 0.0364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.221
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ03 | Any | Cap-Tons | 624 | 0 | None | 40.9 | 0.0406 | 0 | 24.4 | 0.0243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.179
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ03 | Any | Cap-Tons | 146 | 0 | None | 128 | 0.0824 | 0 | 76.6 | 0.0493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.374
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ03 | Any | Cap-Tons | 249 | 0 | None | 75.9 | 0.0594 | 0 | 45.4 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.908
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ03 | Any | Cap-Tons | 86.6 | 0 | None | 81.6 | 0.0818 | 0 | 48.8 | 0.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.179
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ03 | Any | Cap-Tons | 317 | 0 | None | 73.7 | 0.0489 | 0 | 44.1 | 0.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 34.557
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ03 | Any | Cap-Tons | 20.6 | 0 | None | 79.2 | 0.0513 | 0 | 47.4 | 0.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.797
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ03 | Any | Cap-Tons | 194 | 0 | None | 83.4 | 0.0804 | 0 | 49.9 | 0.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.258
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ04 | Any | Cap-Tons | 625 | 0 | None | 107 | 0.115 | 0 | 64.1 | 0.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.088
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ04 | Any | Cap-Tons | 327 | 0 | None | 89.2 | 0.0764 | 0 | 53.4 | 0.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.301
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ04 | Any | Cap-Tons | 2160 | 0 | None | 95.8 | 0.103 | 0 | 57.3 | 0.0615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.088
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ04 | Any | Cap-Tons | 785 | 0 | None | 70 | 0.0527 | 0 | 41.9 | 0.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.448
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ04 | Any | Cap-Tons | 188 | 0 | None | 158 | 0.0984 | 0 | 94.7 | 0.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.722
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ04 | Any | Cap-Tons | 308 | 0 | None | 112 | 0.0785 | 0 | 66.7 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.753
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ04 | Any | Cap-Tons | 113 | 0 | None | 140 | 0.109 | 0 | 84 | 0.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.448
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ04 | Any | Cap-Tons | 378 | 0 | None | 106 | 0.055 | 0 | 63.6 | 0.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 19.239
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ04 | Any | Cap-Tons | 25.1 | 0 | None | 115 | 0.0584 | 0 | 68.7 | 0.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.129
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ04 | Any | Cap-Tons | 244 | 0 | None | 127 | 0.102 | 0 | 76.1 | 0.0608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.747
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ05 | Any | Cap-Tons | 426 | 0 | None | 80.9 | 0.0672 | 0 | 48.4 | 0.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.821
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ05 | Any | Cap-Tons | 224 | 0 | None | 69.1 | 0.0399 | 0 | 41.3 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ05 | Any | Cap-Tons | 1540 | 0 | None | 68.3 | 0.0573 | 0 | 40.9 | 0.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.821
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ05 | Any | Cap-Tons | 634 | 0 | None | 39.1 | 0.0281 | 0 | 23.4 | 0.0168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.22
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ05 | Any | Cap-Tons | 124 | 0 | None | 141 | 0.0585 | 0 | 84.1 | 0.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.721
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ05 | Any | Cap-Tons | 242 | 0 | None | 83.4 | 0.044 | 0 | 49.9 | 0.0263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.448
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ05 | Any | Cap-Tons | 80.1 | 0 | None | 91.8 | 0.0598 | 0 | 54.9 | 0.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.22
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ05 | Any | Cap-Tons | 318 | 0 | None | 80.1 | 0.0303 | 0 | 47.9 | 0.0181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.353
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ05 | Any | Cap-Tons | 18.5 | 0 | None | 93 | 0.0324 | 0 | 55.6 | 0.0194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.29
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ05 | Any | Cap-Tons | 186 | 0 | None | 87.9 | 0.0536 | 0 | 52.6 | 0.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.476
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ11 | Any | Cap-Tons | 709 | 0 | None | 157 | 0.111 | 0 | 93.8 | 0.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.197
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ11 | Any | Cap-Tons | 361 | 0 | None | 113 | 0.0468 | 0 | 67.8 | 0.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.941
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ11 | Any | Cap-Tons | 2390 | 0 | None | 141 | 0.12 | 0 | 84.6 | 0.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.197
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ11 | Any | Cap-Tons | 920 | 0 | None | 106 | 0.068 | 0 | 63.2 | 0.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.918
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ11 | Any | Cap-Tons | 227 | 0 | None | 205 | 0.131 | 0 | 122 | 0.0786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.508
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ11 | Any | Cap-Tons | 383 | 0 | None | 132 | 0.095 | 0 | 79 | 0.0568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.473
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ11 | Any | Cap-Tons | 132 | 0 | None | 207 | 0.15 | 0 | 124 | 0.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.918
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ11 | Any | Cap-Tons | 427 | 0 | None | 134 | 0.0767 | 0 | 80.4 | 0.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.943
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ11 | Any | Cap-Tons | 28 | 0 | None | 149 | 0.0868 | 0 | 89.1 | 0.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.408
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ11 | Any | Cap-Tons | 306 | 0 | None | 159 | 0.115 | 0 | 95.3 | 0.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.474
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ12 | Any | Cap-Tons | 643 | 0 | None | 132 | 0.109 | 0 | 79.2 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.674
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ12 | Any | Cap-Tons | 330 | 0 | None | 97.6 | 0.0469 | 0 | 58.4 | 0.0281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.103
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ12 | Any | Cap-Tons | 2200 | 0 | None | 119 | 0.116 | 0 | 71 | 0.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.674
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ12 | Any | Cap-Tons | 880 | 0 | None | 80.1 | 0.0638 | 0 | 47.9 | 0.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.681
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ12 | Any | Cap-Tons | 205 | 0 | None | 176 | 0.136 | 0 | 106 | 0.0814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.914
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ12 | Any | Cap-Tons | 359 | 0 | None | 110 | 0.0908 | 0 | 66.1 | 0.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.929
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ12 | Any | Cap-Tons | 119 | 0 | None | 161 | 0.144 | 0 | 96.3 | 0.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.681
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ12 | Any | Cap-Tons | 406 | 0 | None | 114 | 0.0726 | 0 | 68.3 | 0.0434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 17.611
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ12 | Any | Cap-Tons | 26.1 | 0 | None | 126 | 0.0824 | 0 | 75.4 | 0.0493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.65
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ12 | Any | Cap-Tons | 287 | 0 | None | 137 | 0.115 | 0 | 82.1 | 0.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.103
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ13 | Any | Cap-Tons | 754 | 0 | None | 155 | 0.0878 | 0 | 92.9 | 0.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.809
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ13 | Any | Cap-Tons | 395 | 0 | None | 112 | 0.037 | 0 | 66.9 | 0.0221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.178
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ13 | Any | Cap-Tons | 2480 | 0 | None | 142 | 0.103 | 0 | 84.8 | 0.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.809
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ13 | Any | Cap-Tons | 934 | 0 | None | 108 | 0.0602 | 0 | 64.4 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.404
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ13 | Any | Cap-Tons | 226 | 0 | None | 212 | 0.117 | 0 | 127 | 0.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.052
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ13 | Any | Cap-Tons | 388 | 0 | None | 135 | 0.0854 | 0 | 80.9 | 0.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.331
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ13 | Any | Cap-Tons | 132 | 0 | None | 214 | 0.13 | 0 | 128 | 0.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.404
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ13 | Any | Cap-Tons | 421 | 0 | None | 139 | 0.0611 | 0 | 83 | 0.0366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.978
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ13 | Any | Cap-Tons | 28.1 | 0 | None | 150 | 0.0682 | 0 | 89.6 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ13 | Any | Cap-Tons | 311 | 0 | None | 163 | 0.11 | 0 | 97.7 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.701
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ16 | Any | Cap-Tons | 436 | 0 | None | 93.8 | 0.0798 | 0 | 56.1 | 0.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ16 | Any | Cap-Tons | 228 | 0 | None | 64.2 | 0.0399 | 0 | 38.4 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ16 | Any | Cap-Tons | 1550 | 0 | None | 87.3 | 0.0901 | 0 | 52.2 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ16 | Any | Cap-Tons | 644 | 0 | None | 58.1 | 0.0477 | 0 | 34.8 | 0.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ16 | Any | Cap-Tons | 137 | 0 | None | 165 | 0.111 | 0 | 98.8 | 0.0663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.236
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ16 | Any | Cap-Tons | 250 | 0 | None | 78.2 | 0.0682 | 0 | 46.8 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.286
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ16 | Any | Cap-Tons | 80.3 | 0 | None | 122 | 0.112 | 0 | 73.2 | 0.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ16 | Any | Cap-Tons | 313 | 0 | None | 83.8 | 0.0602 | 0 | 50.2 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.208
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ16 | Any | Cap-Tons | 19.2 | 0 | None | 94 | 0.0686 | 0 | 56.3 | 0.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.173
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ16 | Any | Cap-Tons | 207 | 0 | None | 92.1 | 0.0863 | 0 | 55.1 | 0.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.069
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ01 | Any | Cap-Tons | 344 | 0 | None | 38.3 | 0.0965 | 0 | 28 | 0.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ01 | Any | Cap-Tons | 169 | 0 | None | 27.7 | 0.0445 | 0 | 20.2 | 0.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ01 | Any | Cap-Tons | 1310 | 0 | None | 37.4 | 0.0735 | 0 | 27.4 | 0.0538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ01 | Any | Cap-Tons | 533 | 0 | None | 12.2 | 0.028 | 0 | 8.9 | 0.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ01 | Any | Cap-Tons | 109 | 0 | None | 119 | 0.0681 | 0 | 87.3 | 0.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.224
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ01 | Any | Cap-Tons | 191 | 0 | None | 43.3 | 0.0505 | 0 | 31.7 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ01 | Any | Cap-Tons | 64.1 | 0 | None | 29.1 | 0.0533 | 0 | 21.3 | 0.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ01 | Any | Cap-Tons | 261 | 0 | None | 43.3 | 0.04 | 0 | 31.7 | 0.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.353
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ01 | Any | Cap-Tons | 15.6 | 0 | None | 48.6 | 0.0392 | 0 | 35.6 | 0.0287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.325
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ01 | Any | Cap-Tons | 147 | 0 | None | 47 | 0.0749 | 0 | 34.4 | 0.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ02 | Any | Cap-Tons | 607 | 0 | None | 146 | 0.134 | 0 | 107 | 0.0982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.802
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ02 | Any | Cap-Tons | 311 | 0 | None | 107 | 0.0596 | 0 | 78.7 | 0.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.622
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ02 | Any | Cap-Tons | 2140 | 0 | None | 130 | 0.143 | 0 | 95.5 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.802
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ02 | Any | Cap-Tons | 823 | 0 | None | 82.8 | 0.0817 | 0 | 60.6 | 0.0598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ02 | Any | Cap-Tons | 177 | 0 | None | 224 | 0.181 | 0 | 164 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.824
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ02 | Any | Cap-Tons | 312 | 0 | None | 138 | 0.126 | 0 | 101 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.337
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ02 | Any | Cap-Tons | 102 | 0 | None | 179 | 0.197 | 0 | 131 | 0.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ02 | Any | Cap-Tons | 370 | 0 | None | 143 | 0.102 | 0 | 105 | 0.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.833
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ02 | Any | Cap-Tons | 22.7 | 0 | None | 162 | 0.119 | 0 | 118 | 0.0871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.847
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ02 | Any | Cap-Tons | 243 | 0 | None | 173 | 0.165 | 0 | 127 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.284
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ03 | Any | Cap-Tons | 487 | 0 | None | 108 | 0.0811 | 0 | 78.8 | 0.0593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.221
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ03 | Any | Cap-Tons | 258 | 0 | None | 84.5 | 0.0405 | 0 | 61.9 | 0.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.819
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ03 | Any | Cap-Tons | 1740 | 0 | None | 90.6 | 0.0913 | 0 | 66.3 | 0.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.221
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ03 | Any | Cap-Tons | 624 | 0 | None | 61.3 | 0.0608 | 0 | 44.8 | 0.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.179
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ03 | Any | Cap-Tons | 146 | 0 | None | 192 | 0.124 | 0 | 141 | 0.0905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.374
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ03 | Any | Cap-Tons | 249 | 0 | None | 114 | 0.0891 | 0 | 83.3 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.908
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ03 | Any | Cap-Tons | 86.6 | 0 | None | 122 | 0.123 | 0 | 89.6 | 0.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.179
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ03 | Any | Cap-Tons | 317 | 0 | None | 111 | 0.0734 | 0 | 80.9 | 0.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 34.557
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ03 | Any | Cap-Tons | 20.6 | 0 | None | 119 | 0.0768 | 0 | 86.9 | 0.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.797
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ03 | Any | Cap-Tons | 194 | 0 | None | 125 | 0.121 | 0 | 91.5 | 0.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.258
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ04 | Any | Cap-Tons | 625 | 0 | None | 161 | 0.172 | 0 | 118 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.088
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ04 | Any | Cap-Tons | 327 | 0 | None | 134 | 0.114 | 0 | 97.9 | 0.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.301
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ04 | Any | Cap-Tons | 2160 | 0 | None | 144 | 0.154 | 0 | 105 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.088
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ04 | Any | Cap-Tons | 785 | 0 | None | 105 | 0.079 | 0 | 76.9 | 0.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.448
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ04 | Any | Cap-Tons | 188 | 0 | None | 237 | 0.148 | 0 | 174 | 0.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.722
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ04 | Any | Cap-Tons | 308 | 0 | None | 167 | 0.118 | 0 | 122 | 0.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.753
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ04 | Any | Cap-Tons | 113 | 0 | None | 211 | 0.164 | 0 | 154 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.448
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ04 | Any | Cap-Tons | 378 | 0 | None | 159 | 0.0824 | 0 | 117 | 0.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 19.239
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ04 | Any | Cap-Tons | 25.1 | 0 | None | 172 | 0.0876 | 0 | 126 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.129
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ04 | Any | Cap-Tons | 244 | 0 | None | 191 | 0.152 | 0 | 140 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.747
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ05 | Any | Cap-Tons | 426 | 0 | None | 121 | 0.101 | 0 | 88.8 | 0.0737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.821
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ05 | Any | Cap-Tons | 224 | 0 | None | 104 | 0.0598 | 0 | 75.8 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ05 | Any | Cap-Tons | 1540 | 0 | None | 102 | 0.086 | 0 | 75 | 0.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.821
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ05 | Any | Cap-Tons | 634 | 0 | None | 58.6 | 0.0422 | 0 | 42.9 | 0.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.22
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ05 | Any | Cap-Tons | 124 | 0 | None | 211 | 0.0877 | 0 | 154 | 0.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.721
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ05 | Any | Cap-Tons | 242 | 0 | None | 125 | 0.066 | 0 | 91.5 | 0.0483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.448
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ05 | Any | Cap-Tons | 80.1 | 0 | None | 138 | 0.0896 | 0 | 101 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.22
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ05 | Any | Cap-Tons | 318 | 0 | None | 120 | 0.0455 | 0 | 87.9 | 0.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.353
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ05 | Any | Cap-Tons | 18.5 | 0 | None | 139 | 0.0486 | 0 | 102 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.29
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ05 | Any | Cap-Tons | 186 | 0 | None | 132 | 0.0804 | 0 | 96.5 | 0.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.476
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ11 | Any | Cap-Tons | 709 | 0 | None | 235 | 0.166 | 0 | 172 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.197
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ11 | Any | Cap-Tons | 361 | 0 | None | 170 | 0.0702 | 0 | 124 | 0.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.941
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ11 | Any | Cap-Tons | 2390 | 0 | None | 212 | 0.18 | 0 | 155 | 0.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.197
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ11 | Any | Cap-Tons | 920 | 0 | None | 158 | 0.102 | 0 | 116 | 0.0747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.918
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ11 | Any | Cap-Tons | 227 | 0 | None | 307 | 0.197 | 0 | 225 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.508
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ11 | Any | Cap-Tons | 383 | 0 | None | 198 | 0.142 | 0 | 145 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.473
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ11 | Any | Cap-Tons | 132 | 0 | None | 310 | 0.225 | 0 | 227 | 0.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.918
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ11 | Any | Cap-Tons | 427 | 0 | None | 201 | 0.115 | 0 | 147 | 0.0842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.943
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ11 | Any | Cap-Tons | 28 | 0 | None | 223 | 0.13 | 0 | 164 | 0.0952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.408
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ11 | Any | Cap-Tons | 306 | 0 | None | 239 | 0.172 | 0 | 175 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.474
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ12 | Any | Cap-Tons | 643 | 0 | None | 198 | 0.163 | 0 | 145 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.674
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ12 | Any | Cap-Tons | 330 | 0 | None | 146 | 0.0704 | 0 | 107 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.103
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ12 | Any | Cap-Tons | 2200 | 0 | None | 178 | 0.174 | 0 | 130 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.674
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ12 | Any | Cap-Tons | 880 | 0 | None | 120 | 0.0957 | 0 | 88 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.681
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ12 | Any | Cap-Tons | 205 | 0 | None | 264 | 0.204 | 0 | 194 | 0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.914
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ12 | Any | Cap-Tons | 359 | 0 | None | 166 | 0.136 | 0 | 121 | 0.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.929
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ12 | Any | Cap-Tons | 119 | 0 | None | 241 | 0.216 | 0 | 177 | 0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.681
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ12 | Any | Cap-Tons | 406 | 0 | None | 171 | 0.109 | 0 | 125 | 0.0797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 17.611
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ12 | Any | Cap-Tons | 26.1 | 0 | None | 189 | 0.124 | 0 | 138 | 0.0904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.65
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ12 | Any | Cap-Tons | 287 | 0 | None | 206 | 0.173 | 0 | 151 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.103
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ13 | Any | Cap-Tons | 754 | 0 | None | 233 | 0.132 | 0 | 171 | 0.0964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.809
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ13 | Any | Cap-Tons | 395 | 0 | None | 168 | 0.0555 | 0 | 123 | 0.0406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.178
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ13 | Any | Cap-Tons | 2480 | 0 | None | 213 | 0.154 | 0 | 156 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.809
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ13 | Any | Cap-Tons | 934 | 0 | None | 161 | 0.0903 | 0 | 118 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.404
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ13 | Any | Cap-Tons | 226 | 0 | None | 318 | 0.175 | 0 | 232 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.052
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ13 | Any | Cap-Tons | 388 | 0 | None | 203 | 0.128 | 0 | 148 | 0.0938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.331
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ13 | Any | Cap-Tons | 132 | 0 | None | 321 | 0.195 | 0 | 235 | 0.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.404
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ13 | Any | Cap-Tons | 421 | 0 | None | 208 | 0.0917 | 0 | 152 | 0.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.978
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ13 | Any | Cap-Tons | 28.1 | 0 | None | 224 | 0.102 | 0 | 164 | 0.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ13 | Any | Cap-Tons | 311 | 0 | None | 245 | 0.166 | 0 | 179 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.701
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ16 | Any | Cap-Tons | 436 | 0 | None | 141 | 0.12 | 0 | 103 | 0.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ16 | Any | Cap-Tons | 228 | 0 | None | 96.2 | 0.0598 | 0 | 70.4 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ16 | Any | Cap-Tons | 1550 | 0 | None | 131 | 0.135 | 0 | 95.8 | 0.0988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ16 | Any | Cap-Tons | 644 | 0 | None | 87.1 | 0.0716 | 0 | 63.8 | 0.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ16 | Any | Cap-Tons | 137 | 0 | None | 248 | 0.166 | 0 | 181 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.236
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ16 | Any | Cap-Tons | 250 | 0 | None | 117 | 0.102 | 0 | 85.9 | 0.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.286
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ16 | Any | Cap-Tons | 80.3 | 0 | None | 183 | 0.168 | 0 | 134 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ16 | Any | Cap-Tons | 313 | 0 | None | 126 | 0.0903 | 0 | 92 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.208
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ16 | Any | Cap-Tons | 19.2 | 0 | None | 141 | 0.103 | 0 | 103 | 0.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.173
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ16 | Any | Cap-Tons | 207 | 0 | None | 138 | 0.129 | 0 | 101 | 0.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.069
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ01 | Any | Cap-Tons | 344 | 0 | None | 25.5 | 0.0644 | 0 | 15.3 | 0.0385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ01 | Any | Cap-Tons | 169 | 0 | None | 18.4 | 0.0297 | 0 | 11 | 0.0178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ01 | Any | Cap-Tons | 1310 | 0 | None | 25 | 0.0491 | 0 | 14.9 | 0.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ01 | Any | Cap-Tons | 533 | 0 | None | 8.1 | 0.0187 | 0 | 4.9 | 0.0112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ01 | Any | Cap-Tons | 109 | 0 | None | 79.5 | 0.0454 | 0 | 47.6 | 0.0272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.224
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ01 | Any | Cap-Tons | 191 | 0 | None | 28.9 | 0.0337 | 0 | 17.3 | 0.0202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ01 | Any | Cap-Tons | 64.1 | 0 | None | 19.4 | 0.0355 | 0 | 11.6 | 0.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ01 | Any | Cap-Tons | 261 | 0 | None | 28.9 | 0.0267 | 0 | 17.3 | 0.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.353
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ01 | Any | Cap-Tons | 15.6 | 0 | None | 32.4 | 0.0261 | 0 | 19.4 | 0.0156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.325
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ01 | Any | Cap-Tons | 147 | 0 | None | 31.4 | 0.05 | 0 | 18.8 | 0.0299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ02 | Any | Cap-Tons | 607 | 0 | None | 97.4 | 0.0894 | 0 | 58.3 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.802
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ02 | Any | Cap-Tons | 311 | 0 | None | 71.7 | 0.0398 | 0 | 42.9 | 0.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.622
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ02 | Any | Cap-Tons | 2140 | 0 | None | 87 | 0.0953 | 0 | 52.1 | 0.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.802
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ02 | Any | Cap-Tons | 823 | 0 | None | 55.2 | 0.0545 | 0 | 33 | 0.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ02 | Any | Cap-Tons | 177 | 0 | None | 149 | 0.121 | 0 | 89.3 | 0.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.824
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ02 | Any | Cap-Tons | 312 | 0 | None | 91.7 | 0.0839 | 0 | 54.9 | 0.0502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.337
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ02 | Any | Cap-Tons | 102 | 0 | None | 120 | 0.132 | 0 | 71.6 | 0.0788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ02 | Any | Cap-Tons | 370 | 0 | None | 95.3 | 0.0681 | 0 | 57 | 0.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.833
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ02 | Any | Cap-Tons | 22.7 | 0 | None | 108 | 0.0793 | 0 | 64.5 | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.847
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ02 | Any | Cap-Tons | 243 | 0 | None | 115 | 0.11 | 0 | 69.1 | 0.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.284
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ03 | Any | Cap-Tons | 487 | 0 | None | 71.8 | 0.0541 | 0 | 42.9 | 0.0323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.221
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ03 | Any | Cap-Tons | 258 | 0 | None | 56.4 | 0.027 | 0 | 33.7 | 0.0162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.819
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ03 | Any | Cap-Tons | 1740 | 0 | None | 60.4 | 0.0609 | 0 | 36.2 | 0.0364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.221
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ03 | Any | Cap-Tons | 624 | 0 | None | 40.9 | 0.0406 | 0 | 24.4 | 0.0243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.179
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ03 | Any | Cap-Tons | 146 | 0 | None | 128 | 0.0824 | 0 | 76.6 | 0.0493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.374
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ03 | Any | Cap-Tons | 249 | 0 | None | 75.9 | 0.0594 | 0 | 45.4 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.908
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ03 | Any | Cap-Tons | 86.6 | 0 | None | 81.6 | 0.0818 | 0 | 48.8 | 0.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.179
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ03 | Any | Cap-Tons | 317 | 0 | None | 73.7 | 0.0489 | 0 | 44.1 | 0.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 34.557
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ03 | Any | Cap-Tons | 20.6 | 0 | None | 79.2 | 0.0513 | 0 | 47.4 | 0.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.797
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ03 | Any | Cap-Tons | 194 | 0 | None | 83.4 | 0.0804 | 0 | 49.9 | 0.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.258
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ04 | Any | Cap-Tons | 625 | 0 | None | 107 | 0.115 | 0 | 64.1 | 0.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.088
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ04 | Any | Cap-Tons | 327 | 0 | None | 89.2 | 0.0764 | 0 | 53.4 | 0.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.301
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ04 | Any | Cap-Tons | 2160 | 0 | None | 95.8 | 0.103 | 0 | 57.3 | 0.0615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.088
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ04 | Any | Cap-Tons | 785 | 0 | None | 70 | 0.0527 | 0 | 41.9 | 0.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.448
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ04 | Any | Cap-Tons | 188 | 0 | None | 158 | 0.0984 | 0 | 94.7 | 0.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.722
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ04 | Any | Cap-Tons | 308 | 0 | None | 112 | 0.0785 | 0 | 66.7 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.753
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ04 | Any | Cap-Tons | 113 | 0 | None | 140 | 0.109 | 0 | 84 | 0.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.448
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ04 | Any | Cap-Tons | 378 | 0 | None | 106 | 0.055 | 0 | 63.6 | 0.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 19.239
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ04 | Any | Cap-Tons | 25.1 | 0 | None | 115 | 0.0584 | 0 | 68.7 | 0.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.129
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ04 | Any | Cap-Tons | 244 | 0 | None | 127 | 0.102 | 0 | 76.1 | 0.0608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.747
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ05 | Any | Cap-Tons | 426 | 0 | None | 80.9 | 0.0672 | 0 | 48.4 | 0.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.821
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ05 | Any | Cap-Tons | 224 | 0 | None | 69.1 | 0.0399 | 0 | 41.3 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ05 | Any | Cap-Tons | 1540 | 0 | None | 68.3 | 0.0573 | 0 | 40.9 | 0.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.821
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ05 | Any | Cap-Tons | 634 | 0 | None | 39.1 | 0.0281 | 0 | 23.4 | 0.0168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.22
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ05 | Any | Cap-Tons | 124 | 0 | None | 141 | 0.0585 | 0 | 84.1 | 0.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.721
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ05 | Any | Cap-Tons | 242 | 0 | None | 83.4 | 0.044 | 0 | 49.9 | 0.0263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.448
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ05 | Any | Cap-Tons | 80.1 | 0 | None | 91.8 | 0.0598 | 0 | 54.9 | 0.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.22
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ05 | Any | Cap-Tons | 318 | 0 | None | 80.1 | 0.0303 | 0 | 47.9 | 0.0181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.353
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ05 | Any | Cap-Tons | 18.5 | 0 | None | 93 | 0.0324 | 0 | 55.6 | 0.0194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.29
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ05 | Any | Cap-Tons | 186 | 0 | None | 87.9 | 0.0536 | 0 | 52.6 | 0.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.476
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ11 | Any | Cap-Tons | 709 | 0 | None | 157 | 0.111 | 0 | 93.8 | 0.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.197
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ11 | Any | Cap-Tons | 361 | 0 | None | 113 | 0.0468 | 0 | 67.8 | 0.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.941
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ11 | Any | Cap-Tons | 2390 | 0 | None | 141 | 0.12 | 0 | 84.6 | 0.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.197
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ11 | Any | Cap-Tons | 920 | 0 | None | 106 | 0.068 | 0 | 63.2 | 0.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.918
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ11 | Any | Cap-Tons | 227 | 0 | None | 205 | 0.131 | 0 | 122 | 0.0786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.508
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ11 | Any | Cap-Tons | 383 | 0 | None | 132 | 0.095 | 0 | 79 | 0.0568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.473
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ11 | Any | Cap-Tons | 132 | 0 | None | 207 | 0.15 | 0 | 124 | 0.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.918
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ11 | Any | Cap-Tons | 427 | 0 | None | 134 | 0.0767 | 0 | 80.4 | 0.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.943
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ11 | Any | Cap-Tons | 28 | 0 | None | 149 | 0.0868 | 0 | 89.1 | 0.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.408
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ11 | Any | Cap-Tons | 306 | 0 | None | 159 | 0.115 | 0 | 95.3 | 0.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.474
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ12 | Any | Cap-Tons | 643 | 0 | None | 132 | 0.109 | 0 | 79.2 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.674
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ12 | Any | Cap-Tons | 330 | 0 | None | 97.6 | 0.0469 | 0 | 58.4 | 0.0281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.103
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ12 | Any | Cap-Tons | 2200 | 0 | None | 119 | 0.116 | 0 | 71 | 0.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.674
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ12 | Any | Cap-Tons | 880 | 0 | None | 80.1 | 0.0638 | 0 | 47.9 | 0.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.681
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ12 | Any | Cap-Tons | 205 | 0 | None | 176 | 0.136 | 0 | 106 | 0.0814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.914
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ12 | Any | Cap-Tons | 359 | 0 | None | 110 | 0.0908 | 0 | 66.1 | 0.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.929
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ12 | Any | Cap-Tons | 119 | 0 | None | 161 | 0.144 | 0 | 96.3 | 0.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.681
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ12 | Any | Cap-Tons | 406 | 0 | None | 114 | 0.0726 | 0 | 68.3 | 0.0434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 17.611
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ12 | Any | Cap-Tons | 26.1 | 0 | None | 126 | 0.0824 | 0 | 75.4 | 0.0493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.65
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ12 | Any | Cap-Tons | 287 | 0 | None | 137 | 0.115 | 0 | 82.1 | 0.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.103
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ13 | Any | Cap-Tons | 754 | 0 | None | 155 | 0.0878 | 0 | 92.9 | 0.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.809
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ13 | Any | Cap-Tons | 395 | 0 | None | 112 | 0.037 | 0 | 66.9 | 0.0221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.178
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ13 | Any | Cap-Tons | 2480 | 0 | None | 142 | 0.103 | 0 | 84.8 | 0.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.809
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ13 | Any | Cap-Tons | 934 | 0 | None | 108 | 0.0602 | 0 | 64.4 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.404
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ13 | Any | Cap-Tons | 226 | 0 | None | 212 | 0.117 | 0 | 127 | 0.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.052
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ13 | Any | Cap-Tons | 388 | 0 | None | 135 | 0.0854 | 0 | 80.9 | 0.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.331
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ13 | Any | Cap-Tons | 132 | 0 | None | 214 | 0.13 | 0 | 128 | 0.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.404
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ13 | Any | Cap-Tons | 421 | 0 | None | 139 | 0.0611 | 0 | 83 | 0.0366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.978
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ13 | Any | Cap-Tons | 28.1 | 0 | None | 150 | 0.0682 | 0 | 89.6 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ13 | Any | Cap-Tons | 311 | 0 | None | 163 | 0.11 | 0 | 97.7 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.701
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ16 | Any | Cap-Tons | 436 | 0 | None | 93.8 | 0.0798 | 0 | 56.1 | 0.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ16 | Any | Cap-Tons | 228 | 0 | None | 64.2 | 0.0399 | 0 | 38.4 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ16 | Any | Cap-Tons | 1550 | 0 | None | 87.3 | 0.0901 | 0 | 52.2 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ16 | Any | Cap-Tons | 644 | 0 | None | 58.1 | 0.0477 | 0 | 34.8 | 0.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ16 | Any | Cap-Tons | 137 | 0 | None | 165 | 0.111 | 0 | 98.8 | 0.0663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.236
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ16 | Any | Cap-Tons | 250 | 0 | None | 78.2 | 0.0682 | 0 | 46.8 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.286
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ16 | Any | Cap-Tons | 80.3 | 0 | None | 122 | 0.112 | 0 | 73.2 | 0.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ16 | Any | Cap-Tons | 313 | 0 | None | 83.8 | 0.0602 | 0 | 50.2 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.208
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ16 | Any | Cap-Tons | 19.2 | 0 | None | 94 | 0.0686 | 0 | 56.3 | 0.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.173
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ16 | Any | Cap-Tons | 207 | 0 | None | 92.1 | 0.0863 | 0 | 55.1 | 0.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.069
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ01 | Any | Cap-Tons | 344 | 0 | None | 38.3 | 0.0965 | 0 | 28 | 0.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ01 | Any | Cap-Tons | 169 | 0 | None | 27.7 | 0.0445 | 0 | 20.2 | 0.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ01 | Any | Cap-Tons | 1310 | 0 | None | 37.4 | 0.0735 | 0 | 27.4 | 0.0538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ01 | Any | Cap-Tons | 533 | 0 | None | 12.2 | 0.028 | 0 | 8.9 | 0.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ01 | Any | Cap-Tons | 109 | 0 | None | 119 | 0.0681 | 0 | 87.3 | 0.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.224
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ01 | Any | Cap-Tons | 191 | 0 | None | 43.3 | 0.0505 | 0 | 31.7 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ01 | Any | Cap-Tons | 64.1 | 0 | None | 29.1 | 0.0533 | 0 | 21.3 | 0.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ01 | Any | Cap-Tons | 261 | 0 | None | 43.3 | 0.04 | 0 | 31.7 | 0.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.353
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ01 | Any | Cap-Tons | 15.6 | 0 | None | 48.6 | 0.0392 | 0 | 35.6 | 0.0287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.325
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ01 | Any | Cap-Tons | 147 | 0 | None | 47 | 0.0749 | 0 | 34.4 | 0.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ02 | Any | Cap-Tons | 607 | 0 | None | 146 | 0.134 | 0 | 107 | 0.0982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.802
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ02 | Any | Cap-Tons | 311 | 0 | None | 107 | 0.0596 | 0 | 78.7 | 0.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.622
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ02 | Any | Cap-Tons | 2140 | 0 | None | 130 | 0.143 | 0 | 95.5 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.802
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ02 | Any | Cap-Tons | 823 | 0 | None | 82.8 | 0.0817 | 0 | 60.6 | 0.0598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ02 | Any | Cap-Tons | 177 | 0 | None | 224 | 0.181 | 0 | 164 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.824
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ02 | Any | Cap-Tons | 312 | 0 | None | 138 | 0.126 | 0 | 101 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.337
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ02 | Any | Cap-Tons | 102 | 0 | None | 179 | 0.197 | 0 | 131 | 0.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ02 | Any | Cap-Tons | 370 | 0 | None | 143 | 0.102 | 0 | 105 | 0.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.833
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ02 | Any | Cap-Tons | 22.7 | 0 | None | 162 | 0.119 | 0 | 118 | 0.0871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.847
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ02 | Any | Cap-Tons | 243 | 0 | None | 173 | 0.165 | 0 | 127 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.284
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ03 | Any | Cap-Tons | 487 | 0 | None | 108 | 0.0811 | 0 | 78.8 | 0.0593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.221
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ03 | Any | Cap-Tons | 258 | 0 | None | 84.5 | 0.0405 | 0 | 61.9 | 0.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.819
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ03 | Any | Cap-Tons | 1740 | 0 | None | 90.6 | 0.0913 | 0 | 66.3 | 0.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.221
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ03 | Any | Cap-Tons | 624 | 0 | None | 61.3 | 0.0608 | 0 | 44.8 | 0.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.179
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ03 | Any | Cap-Tons | 146 | 0 | None | 192 | 0.124 | 0 | 141 | 0.0905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.374
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ03 | Any | Cap-Tons | 249 | 0 | None | 114 | 0.0891 | 0 | 83.3 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.908
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ03 | Any | Cap-Tons | 86.6 | 0 | None | 122 | 0.123 | 0 | 89.6 | 0.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.179
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ03 | Any | Cap-Tons | 317 | 0 | None | 111 | 0.0734 | 0 | 80.9 | 0.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 34.557
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ03 | Any | Cap-Tons | 20.6 | 0 | None | 119 | 0.0768 | 0 | 86.9 | 0.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.797
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ03 | Any | Cap-Tons | 194 | 0 | None | 125 | 0.121 | 0 | 91.5 | 0.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.258
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ04 | Any | Cap-Tons | 625 | 0 | None | 161 | 0.172 | 0 | 118 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.088
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ04 | Any | Cap-Tons | 327 | 0 | None | 134 | 0.114 | 0 | 97.9 | 0.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.301
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ04 | Any | Cap-Tons | 2160 | 0 | None | 144 | 0.154 | 0 | 105 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.088
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ04 | Any | Cap-Tons | 785 | 0 | None | 105 | 0.079 | 0 | 76.9 | 0.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.448
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ04 | Any | Cap-Tons | 188 | 0 | None | 237 | 0.148 | 0 | 174 | 0.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.722
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ04 | Any | Cap-Tons | 308 | 0 | None | 167 | 0.118 | 0 | 122 | 0.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.753
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ04 | Any | Cap-Tons | 113 | 0 | None | 211 | 0.164 | 0 | 154 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.448
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ04 | Any | Cap-Tons | 378 | 0 | None | 159 | 0.0824 | 0 | 117 | 0.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 19.239
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ04 | Any | Cap-Tons | 25.1 | 0 | None | 172 | 0.0876 | 0 | 126 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.129
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ04 | Any | Cap-Tons | 244 | 0 | None | 191 | 0.152 | 0 | 140 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.747
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ05 | Any | Cap-Tons | 426 | 0 | None | 121 | 0.101 | 0 | 88.8 | 0.0737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.821
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ05 | Any | Cap-Tons | 224 | 0 | None | 104 | 0.0598 | 0 | 75.8 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ05 | Any | Cap-Tons | 1540 | 0 | None | 102 | 0.086 | 0 | 75 | 0.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.821
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ05 | Any | Cap-Tons | 634 | 0 | None | 58.6 | 0.0422 | 0 | 42.9 | 0.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.22
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ05 | Any | Cap-Tons | 124 | 0 | None | 211 | 0.0877 | 0 | 154 | 0.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.721
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ05 | Any | Cap-Tons | 242 | 0 | None | 125 | 0.066 | 0 | 91.5 | 0.0483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.448
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ05 | Any | Cap-Tons | 80.1 | 0 | None | 138 | 0.0896 | 0 | 101 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.22
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ05 | Any | Cap-Tons | 318 | 0 | None | 120 | 0.0455 | 0 | 87.9 | 0.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.353
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ05 | Any | Cap-Tons | 18.5 | 0 | None | 139 | 0.0486 | 0 | 102 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.29
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ05 | Any | Cap-Tons | 186 | 0 | None | 132 | 0.0804 | 0 | 96.5 | 0.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.476
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ11 | Any | Cap-Tons | 709 | 0 | None | 235 | 0.166 | 0 | 172 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.197
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ11 | Any | Cap-Tons | 361 | 0 | None | 170 | 0.0702 | 0 | 124 | 0.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.941
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ11 | Any | Cap-Tons | 2390 | 0 | None | 212 | 0.18 | 0 | 155 | 0.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.197
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ11 | Any | Cap-Tons | 920 | 0 | None | 158 | 0.102 | 0 | 116 | 0.0747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.918
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ11 | Any | Cap-Tons | 227 | 0 | None | 307 | 0.197 | 0 | 225 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.508
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ11 | Any | Cap-Tons | 383 | 0 | None | 198 | 0.142 | 0 | 145 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.473
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ11 | Any | Cap-Tons | 132 | 0 | None | 310 | 0.225 | 0 | 227 | 0.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.918
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ11 | Any | Cap-Tons | 427 | 0 | None | 201 | 0.115 | 0 | 147 | 0.0842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.943
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ11 | Any | Cap-Tons | 28 | 0 | None | 223 | 0.13 | 0 | 164 | 0.0952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.408
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ11 | Any | Cap-Tons | 306 | 0 | None | 239 | 0.172 | 0 | 175 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.474
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ12 | Any | Cap-Tons | 643 | 0 | None | 198 | 0.163 | 0 | 145 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.674
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ12 | Any | Cap-Tons | 330 | 0 | None | 146 | 0.0704 | 0 | 107 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.103
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ12 | Any | Cap-Tons | 2200 | 0 | None | 178 | 0.174 | 0 | 130 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.674
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ12 | Any | Cap-Tons | 880 | 0 | None | 120 | 0.0957 | 0 | 88 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.681
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ12 | Any | Cap-Tons | 205 | 0 | None | 264 | 0.204 | 0 | 194 | 0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.914
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ12 | Any | Cap-Tons | 359 | 0 | None | 166 | 0.136 | 0 | 121 | 0.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.929
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ12 | Any | Cap-Tons | 119 | 0 | None | 241 | 0.216 | 0 | 177 | 0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.681
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ12 | Any | Cap-Tons | 406 | 0 | None | 171 | 0.109 | 0 | 125 | 0.0797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 17.611
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ12 | Any | Cap-Tons | 26.1 | 0 | None | 189 | 0.124 | 0 | 138 | 0.0904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.65
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ12 | Any | Cap-Tons | 287 | 0 | None | 206 | 0.173 | 0 | 151 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.103
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ13 | Any | Cap-Tons | 754 | 0 | None | 233 | 0.132 | 0 | 171 | 0.0964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.809
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ13 | Any | Cap-Tons | 395 | 0 | None | 168 | 0.0555 | 0 | 123 | 0.0406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.178
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ13 | Any | Cap-Tons | 2480 | 0 | None | 213 | 0.154 | 0 | 156 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.809
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ13 | Any | Cap-Tons | 934 | 0 | None | 161 | 0.0903 | 0 | 118 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.404
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ13 | Any | Cap-Tons | 226 | 0 | None | 318 | 0.175 | 0 | 232 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.052
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ13 | Any | Cap-Tons | 388 | 0 | None | 203 | 0.128 | 0 | 148 | 0.0938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.331
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ13 | Any | Cap-Tons | 132 | 0 | None | 321 | 0.195 | 0 | 235 | 0.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.404
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ13 | Any | Cap-Tons | 421 | 0 | None | 208 | 0.0917 | 0 | 152 | 0.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.978
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ13 | Any | Cap-Tons | 28.1 | 0 | None | 224 | 0.102 | 0 | 164 | 0.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ13 | Any | Cap-Tons | 311 | 0 | None | 245 | 0.166 | 0 | 179 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.701
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ECC | Ex | Ex | CZ16 | Any | Cap-Tons | 436 | 0 | None | 141 | 0.12 | 0 | 103 | 0.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | ESe | Ex | Ex | CZ16 | Any | Cap-Tons | 228 | 0 | None | 96.2 | 0.0598 | 0 | 70.4 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.131
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | EUn | Ex | Ex | CZ16 | Any | Cap-Tons | 1550 | 0 | None | 131 | 0.135 | 0 | 95.8 | 0.0988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Hsp | Ex | Ex | CZ16 | Any | Cap-Tons | 644 | 0 | None | 87.1 | 0.0716 | 0 | 63.8 | 0.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Htl | Ex | Ex | CZ16 | Any | Cap-Tons | 137 | 0 | None | 248 | 0.166 | 0 | 181 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.236
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | MBT | Ex | Ex | CZ16 | Any | Cap-Tons | 250 | 0 | None | 117 | 0.102 | 0 | 85.9 | 0.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.286
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Nrs | Ex | Ex | CZ16 | Any | Cap-Tons | 80.3 | 0 | None | 183 | 0.168 | 0 | 134 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfL | Ex | Ex | CZ16 | Any | Cap-Tons | 313 | 0 | None | 126 | 0.0903 | 0 | 92 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.208
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | OfS | Ex | Ex | CZ16 | Any | Cap-Tons | 19.2 | 0 | None | 141 | 0.103 | 0 | 103 | 0.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.173
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | PGE | Rt3 | Ex | Ex | CZ16 | Any | Cap-Tons | 207 | 0 | None | 138 | 0.129 | 0 | 101 | 0.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.069
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ05 | Any | Cap-Tons | 1520 | 0 | None | 68 | 0.0573 | 0 | 40.7 | 0.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ05 | Any | Cap-Tons | 634 | 0 | None | 39.2 | 0.0282 | 0 | 23.5 | 0.0169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.152
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ05 | Any | Cap-Tons | 125 | 0 | None | 142 | 0.0586 | 0 | 84.7 | 0.0351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.021
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ05 | Any | Cap-Tons | 241 | 0 | None | 83.1 | 0.0438 | 0 | 49.7 | 0.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.077
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ05 | Any | Cap-Tons | 80.3 | 0 | None | 95.3 | 0.0613 | 0 | 57 | 0.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.152
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ05 | Any | Cap-Tons | 319 | 0 | None | 80.2 | 0.0303 | 0 | 48 | 0.0181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.12
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ05 | Any | Cap-Tons | 18.4 | 0 | None | 92.8 | 0.0325 | 0 | 55.5 | 0.0194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.046
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ05 | Any | Cap-Tons | 186 | 0 | None | 87.6 | 0.0536 | 0 | 52.4 | 0.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.124
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ06 | Any | Cap-Tons | 664 | 0 | None | 127 | 0.0989 | 0 | 76 | 0.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ06 | Any | Cap-Tons | 365 | 0 | None | 95 | 0.058 | 0 | 56.8 | 0.0347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.241
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ06 | Any | Cap-Tons | 2230 | 0 | None | 105 | 0.0895 | 0 | 62.8 | 0.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ06 | Any | Cap-Tons | 811 | 0 | None | 84.1 | 0.0472 | 0 | 50.3 | 0.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.322
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ06 | Any | Cap-Tons | 184 | 0 | None | 181 | 0.0885 | 0 | 108 | 0.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.464
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ06 | Any | Cap-Tons | 334 | 0 | None | 129 | 0.0633 | 0 | 77.2 | 0.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.365
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ06 | Any | Cap-Tons | 114 | 0 | None | 161 | 0.0948 | 0 | 96.1 | 0.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.322
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ06 | Any | Cap-Tons | 389 | 0 | None | 130 | 0.0445 | 0 | 78 | 0.0266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.459
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ06 | Any | Cap-Tons | 25.5 | 0 | None | 136 | 0.0464 | 0 | 81.6 | 0.0277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.067
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ06 | Any | Cap-Tons | 255 | 0 | None | 147 | 0.0917 | 0 | 88.1 | 0.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.932
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ08 | Any | Cap-Tons | 719 | 0 | None | 139 | 0.0897 | 0 | 83 | 0.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.438
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ08 | Any | Cap-Tons | 391 | 0 | None | 110 | 0.0557 | 0 | 66 | 0.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.23
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ08 | Any | Cap-Tons | 2440 | 0 | None | 116 | 0.0796 | 0 | 69.6 | 0.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.438
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ08 | Any | Cap-Tons | 902 | 0 | None | 94.1 | 0.0403 | 0 | 56.3 | 0.0241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.496
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ08 | Any | Cap-Tons | 195 | 0 | None | 199 | 0.0817 | 0 | 119 | 0.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.576
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ08 | Any | Cap-Tons | 368 | 0 | None | 136 | 0.0555 | 0 | 81.5 | 0.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.289
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ08 | Any | Cap-Tons | 124 | 0 | None | 186 | 0.0884 | 0 | 111 | 0.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.496
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ08 | Any | Cap-Tons | 428 | 0 | None | 133 | 0.0372 | 0 | 79.6 | 0.0223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.09
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ08 | Any | Cap-Tons | 26.5 | 0 | None | 150 | 0.0405 | 0 | 89.6 | 0.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.921
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ08 | Any | Cap-Tons | 275 | 0 | None | 166 | 0.0871 | 0 | 99.5 | 0.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.981
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ09 | Any | Cap-Tons | 866 | 0 | None | 127 | 0.123 | 0 | 76.2 | 0.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.895
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ09 | Any | Cap-Tons | 469 | 0 | None | 101 | 0.0773 | 0 | 60.2 | 0.0462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.305
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ09 | Any | Cap-Tons | 2870 | 0 | None | 110 | 0.108 | 0 | 66 | 0.0648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.895
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ09 | Any | Cap-Tons | 1030 | 0 | None | 93.2 | 0.0576 | 0 | 55.8 | 0.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.43
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ09 | Any | Cap-Tons | 250 | 0 | None | 176 | 0.103 | 0 | 105 | 0.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.299
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ09 | Any | Cap-Tons | 416 | 0 | None | 133 | 0.0835 | 0 | 79.6 | 0.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.334
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ09 | Any | Cap-Tons | 150 | 0 | None | 174 | 0.11 | 0 | 104 | 0.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.43
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ09 | Any | Cap-Tons | 469 | 0 | None | 127 | 0.057 | 0 | 76 | 0.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.412
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ09 | Any | Cap-Tons | 32 | 0 | None | 135 | 0.0592 | 0 | 80.9 | 0.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.721
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ09 | Any | Cap-Tons | 334 | 0 | None | 147 | 0.106 | 0 | 88 | 0.0635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.496
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ10 | Any | Cap-Tons | 751 | 0 | None | 147 | 0.13 | 0 | 87.7 | 0.0778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.169
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ10 | Any | Cap-Tons | 392 | 0 | None | 111 | 0.0835 | 0 | 66.5 | 0.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.815
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ10 | Any | Cap-Tons | 2540 | 0 | None | 127 | 0.113 | 0 | 76.3 | 0.0677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.169
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ10 | Any | Cap-Tons | 926 | 0 | None | 96.6 | 0.0572 | 0 | 57.8 | 0.0342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.862
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ10 | Any | Cap-Tons | 217 | 0 | None | 198 | 0.109 | 0 | 118 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.986
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ10 | Any | Cap-Tons | 372 | 0 | None | 139 | 0.0796 | 0 | 83 | 0.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.368
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ10 | Any | Cap-Tons | 122 | 0 | None | 190 | 0.125 | 0 | 114 | 0.0745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.862
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ10 | Any | Cap-Tons | 427 | 0 | None | 140 | 0.0551 | 0 | 83.9 | 0.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.408
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ10 | Any | Cap-Tons | 27.6 | 0 | None | 152 | 0.0591 | 0 | 91.1 | 0.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.388
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ10 | Any | Cap-Tons | 293 | 0 | None | 171 | 0.114 | 0 | 102 | 0.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.825
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ13 | Any | Cap-Tons | 753 | 0 | None | 155 | 0.0877 | 0 | 92.8 | 0.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.516
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ13 | Any | Cap-Tons | 395 | 0 | None | 112 | 0.0369 | 0 | 66.8 | 0.0221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.624
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ13 | Any | Cap-Tons | 2480 | 0 | None | 142 | 0.102 | 0 | 84.7 | 0.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.516
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ13 | Any | Cap-Tons | 937 | 0 | None | 107 | 0.0595 | 0 | 63.9 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.272
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ13 | Any | Cap-Tons | 224 | 0 | None | 210 | 0.116 | 0 | 126 | 0.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.113
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ13 | Any | Cap-Tons | 388 | 0 | None | 135 | 0.0854 | 0 | 80.9 | 0.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.962
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ13 | Any | Cap-Tons | 130 | 0 | None | 208 | 0.127 | 0 | 125 | 0.0763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.272
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ13 | Any | Cap-Tons | 420 | 0 | None | 138 | 0.061 | 0 | 82.7 | 0.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.706
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ13 | Any | Cap-Tons | 28.1 | 0 | None | 150 | 0.0681 | 0 | 89.5 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.055
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ13 | Any | Cap-Tons | 311 | 0 | None | 163 | 0.11 | 0 | 97.7 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.314
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ14 | Any | Cap-Tons | 814 | 0 | None | 142 | 0.107 | 0 | 85.2 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.724
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ14 | Any | Cap-Tons | 433 | 0 | None | 104 | 0.0674 | 0 | 62.4 | 0.0403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.85
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ14 | Any | Cap-Tons | 2670 | 0 | None | 130 | 0.1 | 0 | 78 | 0.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.724
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ14 | Any | Cap-Tons | 984 | 0 | None | 99.3 | 0.0515 | 0 | 59.4 | 0.0308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.317
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ14 | Any | Cap-Tons | 235 | 0 | None | 196 | 0.099 | 0 | 117 | 0.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.405
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ14 | Any | Cap-Tons | 400 | 0 | None | 132 | 0.074 | 0 | 79.2 | 0.0443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.213
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ14 | Any | Cap-Tons | 130 | 0 | None | 209 | 0.118 | 0 | 125 | 0.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.317
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 137 | 0.0568 | 0 | 82 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.707
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ14 | Any | Cap-Tons | 29.4 | 0 | None | 147 | 0.06 | 0 | 87.9 | 0.0359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.941
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ14 | Any | Cap-Tons | 316 | 0 | None | 158 | 0.0939 | 0 | 94.2 | 0.0562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.98
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ15 | Any | Cap-Tons | 1050 | 0 | None | 222 | 0.112 | 0 | 133 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.632
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ15 | Any | Cap-Tons | 560 | 0 | None | 170 | 0.0736 | 0 | 102 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.34
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ15 | Any | Cap-Tons | 3380 | 0 | None | 200 | 0.106 | 0 | 120 | 0.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.632
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ15 | Any | Cap-Tons | 1160 | 0 | None | 170 | 0.0594 | 0 | 102 | 0.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.386
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ15 | Any | Cap-Tons | 304 | 0 | None | 287 | 0.104 | 0 | 172 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.519
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ15 | Any | Cap-Tons | 494 | 0 | None | 205 | 0.0805 | 0 | 123 | 0.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.84
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ15 | Any | Cap-Tons | 172 | 0 | None | 318 | 0.119 | 0 | 190 | 0.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.386
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ15 | Any | Cap-Tons | 533 | 0 | None | 202 | 0.0576 | 0 | 121 | 0.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.844
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ15 | Any | Cap-Tons | 35.1 | 0 | None | 227 | 0.0699 | 0 | 136 | 0.0418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ15 | Any | Cap-Tons | 390 | 0 | None | 245 | 0.105 | 0 | 146 | 0.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.791
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ16 | Any | Cap-Tons | 437 | 0 | None | 93.8 | 0.0799 | 0 | 56.1 | 0.0478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.415
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ16 | Any | Cap-Tons | 229 | 0 | None | 64.5 | 0.0401 | 0 | 38.6 | 0.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.422
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ16 | Any | Cap-Tons | 1550 | 0 | None | 87.3 | 0.0902 | 0 | 52.3 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.415
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ16 | Any | Cap-Tons | 645 | 0 | None | 57.7 | 0.0472 | 0 | 34.5 | 0.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ16 | Any | Cap-Tons | 134 | 0 | None | 163 | 0.11 | 0 | 97.3 | 0.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.422
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ16 | Any | Cap-Tons | 250 | 0 | None | 78.2 | 0.0682 | 0 | 46.8 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.377
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ16 | Any | Cap-Tons | 79.7 | 0 | None | 117 | 0.108 | 0 | 70.1 | 0.0647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ16 | Any | Cap-Tons | 312 | 0 | None | 83.4 | 0.0598 | 0 | 49.9 | 0.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.736
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ16 | Any | Cap-Tons | 19.2 | 0 | None | 94 | 0.0686 | 0 | 56.2 | 0.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.471
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ16 | Any | Cap-Tons | 207 | 0 | None | 92.1 | 0.0863 | 0 | 55.1 | 0.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.415
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ05 | Any | Cap-Tons | 421 | 0 | None | 121 | 0.101 | 0 | 88.8 | 0.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ05 | Any | Cap-Tons | 224 | 0 | None | 103 | 0.0598 | 0 | 75.7 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.007
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ05 | Any | Cap-Tons | 1520 | 0 | None | 102 | 0.086 | 0 | 74.6 | 0.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ05 | Any | Cap-Tons | 634 | 0 | None | 58.8 | 0.0423 | 0 | 43 | 0.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.152
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ05 | Any | Cap-Tons | 125 | 0 | None | 212 | 0.0879 | 0 | 155 | 0.0644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.021
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ05 | Any | Cap-Tons | 241 | 0 | None | 125 | 0.0657 | 0 | 91.3 | 0.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.077
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ05 | Any | Cap-Tons | 80.3 | 0 | None | 143 | 0.0919 | 0 | 105 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.152
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ05 | Any | Cap-Tons | 319 | 0 | None | 120 | 0.0455 | 0 | 88 | 0.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.12
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ05 | Any | Cap-Tons | 18.4 | 0 | None | 139 | 0.0487 | 0 | 102 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.046
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ05 | Any | Cap-Tons | 186 | 0 | None | 131 | 0.0803 | 0 | 96.2 | 0.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.124
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ06 | Any | Cap-Tons | 664 | 0 | None | 191 | 0.148 | 0 | 139 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ06 | Any | Cap-Tons | 365 | 0 | None | 142 | 0.0869 | 0 | 104 | 0.0636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.241
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ06 | Any | Cap-Tons | 2230 | 0 | None | 157 | 0.134 | 0 | 115 | 0.0983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ06 | Any | Cap-Tons | 811 | 0 | None | 126 | 0.0708 | 0 | 92.4 | 0.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.322
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ06 | Any | Cap-Tons | 184 | 0 | None | 271 | 0.133 | 0 | 199 | 0.0971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.464
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ06 | Any | Cap-Tons | 334 | 0 | None | 194 | 0.095 | 0 | 142 | 0.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.365
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ06 | Any | Cap-Tons | 114 | 0 | None | 241 | 0.142 | 0 | 176 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.322
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ06 | Any | Cap-Tons | 389 | 0 | None | 196 | 0.0667 | 0 | 143 | 0.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.459
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ06 | Any | Cap-Tons | 25.5 | 0 | None | 204 | 0.0695 | 0 | 150 | 0.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.067
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ06 | Any | Cap-Tons | 255 | 0 | None | 221 | 0.137 | 0 | 162 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.932
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ08 | Any | Cap-Tons | 719 | 0 | None | 208 | 0.135 | 0 | 152 | 0.0985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.438
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ08 | Any | Cap-Tons | 391 | 0 | None | 165 | 0.0835 | 0 | 121 | 0.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.23
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ08 | Any | Cap-Tons | 2440 | 0 | None | 174 | 0.119 | 0 | 128 | 0.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.438
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ08 | Any | Cap-Tons | 902 | 0 | None | 141 | 0.0604 | 0 | 103 | 0.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.496
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ08 | Any | Cap-Tons | 195 | 0 | None | 299 | 0.123 | 0 | 219 | 0.0897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.576
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ08 | Any | Cap-Tons | 368 | 0 | None | 204 | 0.0832 | 0 | 150 | 0.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.289
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ08 | Any | Cap-Tons | 124 | 0 | None | 279 | 0.133 | 0 | 204 | 0.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.496
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ08 | Any | Cap-Tons | 428 | 0 | None | 200 | 0.0558 | 0 | 146 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.09
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ08 | Any | Cap-Tons | 26.5 | 0 | None | 225 | 0.0608 | 0 | 164 | 0.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.921
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ08 | Any | Cap-Tons | 275 | 0 | None | 249 | 0.131 | 0 | 183 | 0.0956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.981
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ09 | Any | Cap-Tons | 866 | 0 | None | 191 | 0.184 | 0 | 140 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.895
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ09 | Any | Cap-Tons | 469 | 0 | None | 151 | 0.116 | 0 | 110 | 0.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.305
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ09 | Any | Cap-Tons | 2870 | 0 | None | 165 | 0.162 | 0 | 121 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.895
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ09 | Any | Cap-Tons | 1030 | 0 | None | 140 | 0.0863 | 0 | 102 | 0.0632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.43
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ09 | Any | Cap-Tons | 250 | 0 | None | 263 | 0.154 | 0 | 193 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.299
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ09 | Any | Cap-Tons | 416 | 0 | None | 200 | 0.125 | 0 | 146 | 0.0916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.334
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ09 | Any | Cap-Tons | 150 | 0 | None | 261 | 0.165 | 0 | 191 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.43
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ09 | Any | Cap-Tons | 469 | 0 | None | 190 | 0.0855 | 0 | 139 | 0.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.412
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ09 | Any | Cap-Tons | 32 | 0 | None | 203 | 0.0888 | 0 | 148 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.721
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ09 | Any | Cap-Tons | 334 | 0 | None | 221 | 0.159 | 0 | 161 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.496
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ10 | Any | Cap-Tons | 751 | 0 | None | 220 | 0.195 | 0 | 161 | 0.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.169
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ10 | Any | Cap-Tons | 392 | 0 | None | 167 | 0.125 | 0 | 122 | 0.0916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.815
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ10 | Any | Cap-Tons | 2540 | 0 | None | 191 | 0.17 | 0 | 140 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.169
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ10 | Any | Cap-Tons | 926 | 0 | None | 145 | 0.0858 | 0 | 106 | 0.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.862
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ10 | Any | Cap-Tons | 217 | 0 | None | 296 | 0.163 | 0 | 217 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.986
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ10 | Any | Cap-Tons | 372 | 0 | None | 208 | 0.119 | 0 | 152 | 0.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.368
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ10 | Any | Cap-Tons | 122 | 0 | None | 285 | 0.187 | 0 | 209 | 0.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.862
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ10 | Any | Cap-Tons | 427 | 0 | None | 210 | 0.0826 | 0 | 154 | 0.0605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.408
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ10 | Any | Cap-Tons | 27.6 | 0 | None | 228 | 0.0887 | 0 | 167 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.388
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ10 | Any | Cap-Tons | 293 | 0 | None | 256 | 0.17 | 0 | 187 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.825
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ13 | Any | Cap-Tons | 753 | 0 | None | 233 | 0.131 | 0 | 170 | 0.0962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.516
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ13 | Any | Cap-Tons | 395 | 0 | None | 168 | 0.0554 | 0 | 123 | 0.0405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.624
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ13 | Any | Cap-Tons | 2480 | 0 | None | 212 | 0.154 | 0 | 155 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.516
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ13 | Any | Cap-Tons | 937 | 0 | None | 160 | 0.0892 | 0 | 117 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.272
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ13 | Any | Cap-Tons | 224 | 0 | None | 315 | 0.174 | 0 | 231 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.113
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ13 | Any | Cap-Tons | 388 | 0 | None | 203 | 0.128 | 0 | 148 | 0.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.962
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ13 | Any | Cap-Tons | 130 | 0 | None | 312 | 0.191 | 0 | 229 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.272
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ13 | Any | Cap-Tons | 420 | 0 | None | 207 | 0.0914 | 0 | 152 | 0.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.706
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ13 | Any | Cap-Tons | 28.1 | 0 | None | 224 | 0.102 | 0 | 164 | 0.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.055
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ13 | Any | Cap-Tons | 311 | 0 | None | 245 | 0.166 | 0 | 179 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.314
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ14 | Any | Cap-Tons | 814 | 0 | None | 214 | 0.161 | 0 | 156 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.724
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ14 | Any | Cap-Tons | 433 | 0 | None | 157 | 0.101 | 0 | 115 | 0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.85
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ14 | Any | Cap-Tons | 2670 | 0 | None | 195 | 0.15 | 0 | 143 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.724
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ14 | Any | Cap-Tons | 984 | 0 | None | 149 | 0.0772 | 0 | 109 | 0.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.317
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ14 | Any | Cap-Tons | 235 | 0 | None | 293 | 0.148 | 0 | 215 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.405
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ14 | Any | Cap-Tons | 400 | 0 | None | 199 | 0.111 | 0 | 145 | 0.0812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.213
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ14 | Any | Cap-Tons | 130 | 0 | None | 314 | 0.177 | 0 | 230 | 0.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.317
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 206 | 0.0852 | 0 | 151 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.707
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ14 | Any | Cap-Tons | 29.4 | 0 | None | 220 | 0.09 | 0 | 161 | 0.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.941
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ14 | Any | Cap-Tons | 316 | 0 | None | 236 | 0.141 | 0 | 173 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.98
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ15 | Any | Cap-Tons | 1050 | 0 | None | 333 | 0.169 | 0 | 244 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.632
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ15 | Any | Cap-Tons | 560 | 0 | None | 255 | 0.11 | 0 | 187 | 0.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.34
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ15 | Any | Cap-Tons | 3380 | 0 | None | 300 | 0.16 | 0 | 219 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.632
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ15 | Any | Cap-Tons | 1160 | 0 | None | 255 | 0.0891 | 0 | 187 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.386
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ15 | Any | Cap-Tons | 304 | 0 | None | 430 | 0.156 | 0 | 315 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.519
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ15 | Any | Cap-Tons | 494 | 0 | None | 308 | 0.121 | 0 | 226 | 0.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.84
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ15 | Any | Cap-Tons | 172 | 0 | None | 476 | 0.178 | 0 | 349 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.386
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ15 | Any | Cap-Tons | 533 | 0 | None | 303 | 0.0864 | 0 | 222 | 0.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.844
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ15 | Any | Cap-Tons | 35.1 | 0 | None | 340 | 0.105 | 0 | 249 | 0.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ15 | Any | Cap-Tons | 390 | 0 | None | 367 | 0.158 | 0 | 269 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.791
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ16 | Any | Cap-Tons | 437 | 0 | None | 141 | 0.12 | 0 | 103 | 0.0877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.415
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ16 | Any | Cap-Tons | 229 | 0 | None | 96.7 | 0.0602 | 0 | 70.8 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.422
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ16 | Any | Cap-Tons | 1550 | 0 | None | 131 | 0.135 | 0 | 95.9 | 0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.415
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ16 | Any | Cap-Tons | 645 | 0 | None | 86.5 | 0.0708 | 0 | 63.3 | 0.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ16 | Any | Cap-Tons | 134 | 0 | None | 244 | 0.165 | 0 | 178 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.422
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ16 | Any | Cap-Tons | 250 | 0 | None | 117 | 0.102 | 0 | 85.9 | 0.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.377
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ16 | Any | Cap-Tons | 79.7 | 0 | None | 176 | 0.162 | 0 | 129 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ16 | Any | Cap-Tons | 312 | 0 | None | 125 | 0.0896 | 0 | 91.6 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.736
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ16 | Any | Cap-Tons | 19.2 | 0 | None | 141 | 0.103 | 0 | 103 | 0.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.471
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ16 | Any | Cap-Tons | 207 | 0 | None | 138 | 0.129 | 0 | 101 | 0.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.415
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ05 | Any | Cap-Tons | 421 | 0 | None | 80.9 | 0.0673 | 0 | 48.4 | 0.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ05 | Any | Cap-Tons | 224 | 0 | None | 69 | 0.0399 | 0 | 41.3 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.007
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ05 | Any | Cap-Tons | 1520 | 0 | None | 68 | 0.0573 | 0 | 40.7 | 0.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ05 | Any | Cap-Tons | 634 | 0 | None | 39.2 | 0.0282 | 0 | 23.5 | 0.0169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.152
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ05 | Any | Cap-Tons | 125 | 0 | None | 142 | 0.0586 | 0 | 84.7 | 0.0351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.021
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ05 | Any | Cap-Tons | 241 | 0 | None | 83.1 | 0.0438 | 0 | 49.7 | 0.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.077
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ05 | Any | Cap-Tons | 80.3 | 0 | None | 95.3 | 0.0613 | 0 | 57 | 0.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.152
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ05 | Any | Cap-Tons | 319 | 0 | None | 80.2 | 0.0303 | 0 | 48 | 0.0181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.12
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ05 | Any | Cap-Tons | 18.4 | 0 | None | 92.8 | 0.0325 | 0 | 55.5 | 0.0194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.046
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ05 | Any | Cap-Tons | 186 | 0 | None | 87.6 | 0.0536 | 0 | 52.4 | 0.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.124
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ06 | Any | Cap-Tons | 664 | 0 | None | 127 | 0.0989 | 0 | 76 | 0.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ06 | Any | Cap-Tons | 365 | 0 | None | 95 | 0.058 | 0 | 56.8 | 0.0347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.241
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ06 | Any | Cap-Tons | 2230 | 0 | None | 105 | 0.0895 | 0 | 62.8 | 0.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ06 | Any | Cap-Tons | 811 | 0 | None | 84.1 | 0.0472 | 0 | 50.3 | 0.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.322
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ06 | Any | Cap-Tons | 184 | 0 | None | 181 | 0.0885 | 0 | 108 | 0.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.464
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ06 | Any | Cap-Tons | 334 | 0 | None | 129 | 0.0633 | 0 | 77.2 | 0.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.365
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ06 | Any | Cap-Tons | 114 | 0 | None | 161 | 0.0948 | 0 | 96.1 | 0.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.322
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ06 | Any | Cap-Tons | 389 | 0 | None | 130 | 0.0445 | 0 | 78 | 0.0266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.459
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ06 | Any | Cap-Tons | 25.5 | 0 | None | 136 | 0.0464 | 0 | 81.6 | 0.0277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.067
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ06 | Any | Cap-Tons | 255 | 0 | None | 147 | 0.0917 | 0 | 88.1 | 0.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.932
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ08 | Any | Cap-Tons | 719 | 0 | None | 139 | 0.0897 | 0 | 83 | 0.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.438
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ08 | Any | Cap-Tons | 391 | 0 | None | 110 | 0.0557 | 0 | 66 | 0.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.23
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ08 | Any | Cap-Tons | 2440 | 0 | None | 116 | 0.0796 | 0 | 69.6 | 0.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.438
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ08 | Any | Cap-Tons | 902 | 0 | None | 94.1 | 0.0403 | 0 | 56.3 | 0.0241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.496
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ08 | Any | Cap-Tons | 195 | 0 | None | 199 | 0.0817 | 0 | 119 | 0.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.576
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ08 | Any | Cap-Tons | 368 | 0 | None | 136 | 0.0555 | 0 | 81.5 | 0.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.289
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ08 | Any | Cap-Tons | 124 | 0 | None | 186 | 0.0884 | 0 | 111 | 0.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.496
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ08 | Any | Cap-Tons | 428 | 0 | None | 133 | 0.0372 | 0 | 79.6 | 0.0223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.09
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ08 | Any | Cap-Tons | 26.5 | 0 | None | 150 | 0.0405 | 0 | 89.6 | 0.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.921
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ08 | Any | Cap-Tons | 275 | 0 | None | 166 | 0.0871 | 0 | 99.5 | 0.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.981
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ09 | Any | Cap-Tons | 866 | 0 | None | 127 | 0.123 | 0 | 76.2 | 0.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.895
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ09 | Any | Cap-Tons | 469 | 0 | None | 101 | 0.0773 | 0 | 60.2 | 0.0462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.305
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ09 | Any | Cap-Tons | 2870 | 0 | None | 110 | 0.108 | 0 | 66 | 0.0648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.895
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ09 | Any | Cap-Tons | 1030 | 0 | None | 93.2 | 0.0576 | 0 | 55.8 | 0.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.43
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ09 | Any | Cap-Tons | 250 | 0 | None | 176 | 0.103 | 0 | 105 | 0.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.299
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ09 | Any | Cap-Tons | 416 | 0 | None | 133 | 0.0835 | 0 | 79.6 | 0.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.334
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ09 | Any | Cap-Tons | 150 | 0 | None | 174 | 0.11 | 0 | 104 | 0.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.43
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ09 | Any | Cap-Tons | 469 | 0 | None | 127 | 0.057 | 0 | 76 | 0.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.412
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ09 | Any | Cap-Tons | 32 | 0 | None | 135 | 0.0592 | 0 | 80.9 | 0.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.721
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ09 | Any | Cap-Tons | 334 | 0 | None | 147 | 0.106 | 0 | 88 | 0.0635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.496
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ10 | Any | Cap-Tons | 751 | 0 | None | 147 | 0.13 | 0 | 87.7 | 0.0778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.169
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ10 | Any | Cap-Tons | 392 | 0 | None | 111 | 0.0835 | 0 | 66.5 | 0.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.815
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ10 | Any | Cap-Tons | 2540 | 0 | None | 127 | 0.113 | 0 | 76.3 | 0.0677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.169
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ10 | Any | Cap-Tons | 926 | 0 | None | 96.6 | 0.0572 | 0 | 57.8 | 0.0342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.862
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ10 | Any | Cap-Tons | 217 | 0 | None | 198 | 0.109 | 0 | 118 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.986
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ10 | Any | Cap-Tons | 372 | 0 | None | 139 | 0.0796 | 0 | 83 | 0.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.368
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ10 | Any | Cap-Tons | 122 | 0 | None | 190 | 0.125 | 0 | 114 | 0.0745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.862
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ10 | Any | Cap-Tons | 427 | 0 | None | 140 | 0.0551 | 0 | 83.9 | 0.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.408
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ10 | Any | Cap-Tons | 27.6 | 0 | None | 152 | 0.0591 | 0 | 91.1 | 0.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.388
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ10 | Any | Cap-Tons | 293 | 0 | None | 171 | 0.114 | 0 | 102 | 0.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.825
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ13 | Any | Cap-Tons | 753 | 0 | None | 155 | 0.0877 | 0 | 92.8 | 0.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.516
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ13 | Any | Cap-Tons | 395 | 0 | None | 112 | 0.0369 | 0 | 66.8 | 0.0221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.624
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ13 | Any | Cap-Tons | 2480 | 0 | None | 142 | 0.102 | 0 | 84.7 | 0.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.516
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ13 | Any | Cap-Tons | 937 | 0 | None | 107 | 0.0595 | 0 | 63.9 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.272
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ13 | Any | Cap-Tons | 224 | 0 | None | 210 | 0.116 | 0 | 126 | 0.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.113
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ13 | Any | Cap-Tons | 388 | 0 | None | 135 | 0.0854 | 0 | 80.9 | 0.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.962
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ13 | Any | Cap-Tons | 130 | 0 | None | 208 | 0.127 | 0 | 125 | 0.0763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.272
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ13 | Any | Cap-Tons | 420 | 0 | None | 138 | 0.061 | 0 | 82.7 | 0.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.706
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ13 | Any | Cap-Tons | 28.1 | 0 | None | 150 | 0.0681 | 0 | 89.5 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.055
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ13 | Any | Cap-Tons | 311 | 0 | None | 163 | 0.11 | 0 | 97.7 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.314
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ14 | Any | Cap-Tons | 814 | 0 | None | 142 | 0.107 | 0 | 85.2 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.724
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ14 | Any | Cap-Tons | 433 | 0 | None | 104 | 0.0674 | 0 | 62.4 | 0.0403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.85
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ14 | Any | Cap-Tons | 2670 | 0 | None | 130 | 0.1 | 0 | 78 | 0.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.724
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ14 | Any | Cap-Tons | 984 | 0 | None | 99.3 | 0.0515 | 0 | 59.4 | 0.0308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.317
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ14 | Any | Cap-Tons | 235 | 0 | None | 196 | 0.099 | 0 | 117 | 0.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.405
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ14 | Any | Cap-Tons | 400 | 0 | None | 132 | 0.074 | 0 | 79.2 | 0.0443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.213
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ14 | Any | Cap-Tons | 130 | 0 | None | 209 | 0.118 | 0 | 125 | 0.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.317
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 137 | 0.0568 | 0 | 82 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.707
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ14 | Any | Cap-Tons | 29.4 | 0 | None | 147 | 0.06 | 0 | 87.9 | 0.0359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.941
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ14 | Any | Cap-Tons | 316 | 0 | None | 158 | 0.0939 | 0 | 94.2 | 0.0562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.98
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ15 | Any | Cap-Tons | 1050 | 0 | None | 222 | 0.112 | 0 | 133 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.632
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ15 | Any | Cap-Tons | 560 | 0 | None | 170 | 0.0736 | 0 | 102 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.34
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ15 | Any | Cap-Tons | 3380 | 0 | None | 200 | 0.106 | 0 | 120 | 0.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.632
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ15 | Any | Cap-Tons | 1160 | 0 | None | 170 | 0.0594 | 0 | 102 | 0.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.386
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ15 | Any | Cap-Tons | 304 | 0 | None | 287 | 0.104 | 0 | 172 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.519
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ15 | Any | Cap-Tons | 494 | 0 | None | 205 | 0.0805 | 0 | 123 | 0.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.84
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ15 | Any | Cap-Tons | 172 | 0 | None | 318 | 0.119 | 0 | 190 | 0.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.386
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ15 | Any | Cap-Tons | 533 | 0 | None | 202 | 0.0576 | 0 | 121 | 0.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.844
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ15 | Any | Cap-Tons | 35.1 | 0 | None | 227 | 0.0699 | 0 | 136 | 0.0418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ15 | Any | Cap-Tons | 390 | 0 | None | 245 | 0.105 | 0 | 146 | 0.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.791
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ16 | Any | Cap-Tons | 437 | 0 | None | 93.8 | 0.0799 | 0 | 56.1 | 0.0478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.415
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ16 | Any | Cap-Tons | 229 | 0 | None | 64.5 | 0.0401 | 0 | 38.6 | 0.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.422
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ16 | Any | Cap-Tons | 1550 | 0 | None | 87.3 | 0.0902 | 0 | 52.3 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.415
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ16 | Any | Cap-Tons | 645 | 0 | None | 57.7 | 0.0472 | 0 | 34.5 | 0.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ16 | Any | Cap-Tons | 134 | 0 | None | 163 | 0.11 | 0 | 97.3 | 0.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.422
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ16 | Any | Cap-Tons | 250 | 0 | None | 78.2 | 0.0682 | 0 | 46.8 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.377
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ16 | Any | Cap-Tons | 79.7 | 0 | None | 117 | 0.108 | 0 | 70.1 | 0.0647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ16 | Any | Cap-Tons | 312 | 0 | None | 83.4 | 0.0598 | 0 | 49.9 | 0.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.736
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ16 | Any | Cap-Tons | 19.2 | 0 | None | 94 | 0.0686 | 0 | 56.2 | 0.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.471
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ16 | Any | Cap-Tons | 207 | 0 | None | 92.1 | 0.0863 | 0 | 55.1 | 0.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.415
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ05 | Any | Cap-Tons | 421 | 0 | None | 121 | 0.101 | 0 | 88.8 | 0.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ05 | Any | Cap-Tons | 224 | 0 | None | 103 | 0.0598 | 0 | 75.7 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.007
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ05 | Any | Cap-Tons | 1520 | 0 | None | 102 | 0.086 | 0 | 74.6 | 0.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ05 | Any | Cap-Tons | 634 | 0 | None | 58.8 | 0.0423 | 0 | 43 | 0.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.152
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ05 | Any | Cap-Tons | 125 | 0 | None | 212 | 0.0879 | 0 | 155 | 0.0644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.021
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ05 | Any | Cap-Tons | 241 | 0 | None | 125 | 0.0657 | 0 | 91.3 | 0.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.077
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ05 | Any | Cap-Tons | 80.3 | 0 | None | 143 | 0.0919 | 0 | 105 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.152
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ05 | Any | Cap-Tons | 319 | 0 | None | 120 | 0.0455 | 0 | 88 | 0.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.12
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ05 | Any | Cap-Tons | 18.4 | 0 | None | 139 | 0.0487 | 0 | 102 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.046
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ05 | Any | Cap-Tons | 186 | 0 | None | 131 | 0.0803 | 0 | 96.2 | 0.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.124
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ06 | Any | Cap-Tons | 664 | 0 | None | 191 | 0.148 | 0 | 139 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ06 | Any | Cap-Tons | 365 | 0 | None | 142 | 0.0869 | 0 | 104 | 0.0636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.241
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ06 | Any | Cap-Tons | 2230 | 0 | None | 157 | 0.134 | 0 | 115 | 0.0983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ06 | Any | Cap-Tons | 811 | 0 | None | 126 | 0.0708 | 0 | 92.4 | 0.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.322
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ06 | Any | Cap-Tons | 184 | 0 | None | 271 | 0.133 | 0 | 199 | 0.0971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.464
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ06 | Any | Cap-Tons | 334 | 0 | None | 194 | 0.095 | 0 | 142 | 0.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.365
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ06 | Any | Cap-Tons | 114 | 0 | None | 241 | 0.142 | 0 | 176 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.322
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ06 | Any | Cap-Tons | 389 | 0 | None | 196 | 0.0667 | 0 | 143 | 0.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.459
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ06 | Any | Cap-Tons | 25.5 | 0 | None | 204 | 0.0695 | 0 | 150 | 0.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.067
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ06 | Any | Cap-Tons | 255 | 0 | None | 221 | 0.137 | 0 | 162 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.932
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ08 | Any | Cap-Tons | 719 | 0 | None | 208 | 0.135 | 0 | 152 | 0.0985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.438
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ08 | Any | Cap-Tons | 391 | 0 | None | 165 | 0.0835 | 0 | 121 | 0.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.23
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ08 | Any | Cap-Tons | 2440 | 0 | None | 174 | 0.119 | 0 | 128 | 0.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.438
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ08 | Any | Cap-Tons | 902 | 0 | None | 141 | 0.0604 | 0 | 103 | 0.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.496
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ08 | Any | Cap-Tons | 195 | 0 | None | 299 | 0.123 | 0 | 219 | 0.0897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.576
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ08 | Any | Cap-Tons | 368 | 0 | None | 204 | 0.0832 | 0 | 150 | 0.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.289
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ08 | Any | Cap-Tons | 124 | 0 | None | 279 | 0.133 | 0 | 204 | 0.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.496
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ08 | Any | Cap-Tons | 428 | 0 | None | 200 | 0.0558 | 0 | 146 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.09
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ08 | Any | Cap-Tons | 26.5 | 0 | None | 225 | 0.0608 | 0 | 164 | 0.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.921
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ08 | Any | Cap-Tons | 275 | 0 | None | 249 | 0.131 | 0 | 183 | 0.0956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.981
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ09 | Any | Cap-Tons | 866 | 0 | None | 191 | 0.184 | 0 | 140 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.895
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ09 | Any | Cap-Tons | 469 | 0 | None | 151 | 0.116 | 0 | 110 | 0.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.305
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ09 | Any | Cap-Tons | 2870 | 0 | None | 165 | 0.162 | 0 | 121 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.895
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ09 | Any | Cap-Tons | 1030 | 0 | None | 140 | 0.0863 | 0 | 102 | 0.0632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.43
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ09 | Any | Cap-Tons | 250 | 0 | None | 263 | 0.154 | 0 | 193 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.299
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ09 | Any | Cap-Tons | 416 | 0 | None | 200 | 0.125 | 0 | 146 | 0.0916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.334
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ09 | Any | Cap-Tons | 150 | 0 | None | 261 | 0.165 | 0 | 191 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.43
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ09 | Any | Cap-Tons | 469 | 0 | None | 190 | 0.0855 | 0 | 139 | 0.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.412
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ09 | Any | Cap-Tons | 32 | 0 | None | 203 | 0.0888 | 0 | 148 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.721
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ09 | Any | Cap-Tons | 334 | 0 | None | 221 | 0.159 | 0 | 161 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.496
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ10 | Any | Cap-Tons | 751 | 0 | None | 220 | 0.195 | 0 | 161 | 0.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.169
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ10 | Any | Cap-Tons | 392 | 0 | None | 167 | 0.125 | 0 | 122 | 0.0916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.815
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ10 | Any | Cap-Tons | 2540 | 0 | None | 191 | 0.17 | 0 | 140 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.169
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ10 | Any | Cap-Tons | 926 | 0 | None | 145 | 0.0858 | 0 | 106 | 0.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.862
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ10 | Any | Cap-Tons | 217 | 0 | None | 296 | 0.163 | 0 | 217 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.986
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ10 | Any | Cap-Tons | 372 | 0 | None | 208 | 0.119 | 0 | 152 | 0.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.368
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ10 | Any | Cap-Tons | 122 | 0 | None | 285 | 0.187 | 0 | 209 | 0.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.862
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ10 | Any | Cap-Tons | 427 | 0 | None | 210 | 0.0826 | 0 | 154 | 0.0605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.408
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ10 | Any | Cap-Tons | 27.6 | 0 | None | 228 | 0.0887 | 0 | 167 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.388
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ10 | Any | Cap-Tons | 293 | 0 | None | 256 | 0.17 | 0 | 187 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.825
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ13 | Any | Cap-Tons | 753 | 0 | None | 233 | 0.131 | 0 | 170 | 0.0962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.516
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ13 | Any | Cap-Tons | 395 | 0 | None | 168 | 0.0554 | 0 | 123 | 0.0405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.624
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ13 | Any | Cap-Tons | 2480 | 0 | None | 212 | 0.154 | 0 | 155 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.516
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ13 | Any | Cap-Tons | 937 | 0 | None | 160 | 0.0892 | 0 | 117 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.272
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ13 | Any | Cap-Tons | 224 | 0 | None | 315 | 0.174 | 0 | 231 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.113
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ13 | Any | Cap-Tons | 388 | 0 | None | 203 | 0.128 | 0 | 148 | 0.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.962
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ13 | Any | Cap-Tons | 130 | 0 | None | 312 | 0.191 | 0 | 229 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.272
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ13 | Any | Cap-Tons | 420 | 0 | None | 207 | 0.0914 | 0 | 152 | 0.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.706
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ13 | Any | Cap-Tons | 28.1 | 0 | None | 224 | 0.102 | 0 | 164 | 0.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.055
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ13 | Any | Cap-Tons | 311 | 0 | None | 245 | 0.166 | 0 | 179 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.314
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ14 | Any | Cap-Tons | 814 | 0 | None | 214 | 0.161 | 0 | 156 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.724
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ14 | Any | Cap-Tons | 433 | 0 | None | 157 | 0.101 | 0 | 115 | 0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.85
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ14 | Any | Cap-Tons | 2670 | 0 | None | 195 | 0.15 | 0 | 143 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.724
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ14 | Any | Cap-Tons | 984 | 0 | None | 149 | 0.0772 | 0 | 109 | 0.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.317
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ14 | Any | Cap-Tons | 235 | 0 | None | 293 | 0.148 | 0 | 215 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.405
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ14 | Any | Cap-Tons | 400 | 0 | None | 199 | 0.111 | 0 | 145 | 0.0812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.213
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ14 | Any | Cap-Tons | 130 | 0 | None | 314 | 0.177 | 0 | 230 | 0.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.317
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ14 | Any | Cap-Tons | 438 | 0 | None | 206 | 0.0852 | 0 | 151 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.707
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ14 | Any | Cap-Tons | 29.4 | 0 | None | 220 | 0.09 | 0 | 161 | 0.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.941
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ14 | Any | Cap-Tons | 316 | 0 | None | 236 | 0.141 | 0 | 173 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.98
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ15 | Any | Cap-Tons | 1050 | 0 | None | 333 | 0.169 | 0 | 244 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.632
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ15 | Any | Cap-Tons | 560 | 0 | None | 255 | 0.11 | 0 | 187 | 0.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.34
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ15 | Any | Cap-Tons | 3380 | 0 | None | 300 | 0.16 | 0 | 219 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.632
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ15 | Any | Cap-Tons | 1160 | 0 | None | 255 | 0.0891 | 0 | 187 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.386
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ15 | Any | Cap-Tons | 304 | 0 | None | 430 | 0.156 | 0 | 315 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.519
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ15 | Any | Cap-Tons | 494 | 0 | None | 308 | 0.121 | 0 | 226 | 0.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.84
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ15 | Any | Cap-Tons | 172 | 0 | None | 476 | 0.178 | 0 | 349 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.386
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ15 | Any | Cap-Tons | 533 | 0 | None | 303 | 0.0864 | 0 | 222 | 0.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.844
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ15 | Any | Cap-Tons | 35.1 | 0 | None | 340 | 0.105 | 0 | 249 | 0.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ15 | Any | Cap-Tons | 390 | 0 | None | 367 | 0.158 | 0 | 269 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.791
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ16 | Any | Cap-Tons | 437 | 0 | None | 141 | 0.12 | 0 | 103 | 0.0877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.415
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ16 | Any | Cap-Tons | 229 | 0 | None | 96.7 | 0.0602 | 0 | 70.8 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.422
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | EUn | Ex | Ex | CZ16 | Any | Cap-Tons | 1550 | 0 | None | 131 | 0.135 | 0 | 95.9 | 0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.415
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Hsp | Ex | Ex | CZ16 | Any | Cap-Tons | 645 | 0 | None | 86.5 | 0.0708 | 0 | 63.3 | 0.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Htl | Ex | Ex | CZ16 | Any | Cap-Tons | 134 | 0 | None | 244 | 0.165 | 0 | 178 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.422
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | MBT | Ex | Ex | CZ16 | Any | Cap-Tons | 250 | 0 | None | 117 | 0.102 | 0 | 85.9 | 0.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.377
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Nrs | Ex | Ex | CZ16 | Any | Cap-Tons | 79.7 | 0 | None | 176 | 0.162 | 0 | 129 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfL | Ex | Ex | CZ16 | Any | Cap-Tons | 312 | 0 | None | 125 | 0.0896 | 0 | 91.6 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.736
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | OfS | Ex | Ex | CZ16 | Any | Cap-Tons | 19.2 | 0 | None | 141 | 0.103 | 0 | 103 | 0.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.471
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | Rt3 | Ex | Ex | CZ16 | Any | Cap-Tons | 207 | 0 | None | 138 | 0.129 | 0 | 101 | 0.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.415
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ01 | Any | Cap-Tons | 435 | 0 | None | 18.1 | 0.0582 | 0 | 8.8 | 0.0285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ01 | Any | Cap-Tons | 205 | 0 | None | 15.4 | 0.039 | 0 | 7.5 | 0.0191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.602
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ01 | Any | Cap-Tons | 1700 | 0 | None | 31.8 | 0.05 | 0 | 15.6 | 0.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ01 | Any | Cap-Tons | 533 | 0 | None | 13.9 | 0.0303 | 0 | 6.8 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.614
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ01 | Any | Cap-Tons | 175 | 0 | None | 133 | 0.0613 | 0 | 64.9 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.705
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ01 | Any | Cap-Tons | 211 | 0 | None | 20.8 | 0.044 | 0 | 10.2 | 0.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.882
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ01 | Any | Cap-Tons | 79.7 | 0 | None | 44.8 | 0.0535 | 0 | 21.9 | 0.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.614
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ01 | Any | Cap-Tons | 343 | 0 | None | 19.5 | 0.0346 | 0 | 9.6 | 0.0169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.322
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ01 | Any | Cap-Tons | 21.9 | 0 | None | 25.2 | 0.0396 | 0 | 12.3 | 0.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.898
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ01 | Any | Cap-Tons | 160 | 0 | None | 21.3 | 0.0514 | 0 | 10.4 | 0.0251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.136
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ02 | Any | Cap-Tons | 735 | 0 | None | 129 | 0.126 | 0 | 63.1 | 0.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.935
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ02 | Any | Cap-Tons | 362 | 0 | None | 108 | 0.0621 | 0 | 52.7 | 0.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.515
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ02 | Any | Cap-Tons | 2650 | 0 | None | 126 | 0.127 | 0 | 61.8 | 0.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.935
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ02 | Any | Cap-Tons | 794 | 0 | None | 89.7 | 0.08 | 0 | 43.9 | 0.0391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.289
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ02 | Any | Cap-Tons | 272 | 0 | None | 219 | 0.153 | 0 | 107 | 0.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.489
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ02 | Any | Cap-Tons | 345 | 0 | None | 126 | 0.121 | 0 | 61.6 | 0.0593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.734
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ02 | Any | Cap-Tons | 127 | 0 | None | 183 | 0.176 | 0 | 89.3 | 0.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.289
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ02 | Any | Cap-Tons | 466 | 0 | None | 129 | 0.105 | 0 | 63 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.845
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ02 | Any | Cap-Tons | 30.4 | 0 | None | 154 | 0.119 | 0 | 75.2 | 0.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.572
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ02 | Any | Cap-Tons | 256 | 0 | None | 141 | 0.135 | 0 | 69.1 | 0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.537
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ03 | Any | Cap-Tons | 589 | 0 | None | 83.8 | 0.0842 | 0 | 41 | 0.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.346
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ03 | Any | Cap-Tons | 288 | 0 | None | 66.3 | 0.0444 | 0 | 32.4 | 0.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 17.783
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ03 | Any | Cap-Tons | 2130 | 0 | None | 84.7 | 0.0863 | 0 | 41.4 | 0.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.346
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ03 | Any | Cap-Tons | 640 | 0 | None | 62.2 | 0.0586 | 0 | 30.4 | 0.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.544
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ03 | Any | Cap-Tons | 228 | 0 | None | 186 | 0.105 | 0 | 90.9 | 0.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 23.105
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ03 | Any | Cap-Tons | 277 | 0 | None | 79.4 | 0.0766 | 0 | 38.8 | 0.0374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 44.501
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ03 | Any | Cap-Tons | 104 | 0 | None | 124 | 0.112 | 0 | 60.6 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.544
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ03 | Any | Cap-Tons | 392 | 0 | None | 85.8 | 0.077 | 0 | 41.9 | 0.0377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 174.648
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ03 | Any | Cap-Tons | 27.2 | 0 | None | 102 | 0.0882 | 0 | 50 | 0.0431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 27.509
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ03 | Any | Cap-Tons | 207 | 0 | None | 91.4 | 0.102 | 0 | 44.7 | 0.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 35.701
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ04 | Any | Cap-Tons | 739 | 0 | None | 143 | 0.143 | 0 | 69.9 | 0.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.805
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ04 | Any | Cap-Tons | 364 | 0 | None | 114 | 0.0968 | 0 | 55.7 | 0.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.74
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ04 | Any | Cap-Tons | 2600 | 0 | None | 139 | 0.129 | 0 | 67.7 | 0.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.805
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ04 | Any | Cap-Tons | 769 | 0 | None | 108 | 0.0754 | 0 | 52.6 | 0.0369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.099
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ04 | Any | Cap-Tons | 282 | 0 | None | 228 | 0.127 | 0 | 112 | 0.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.366
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ04 | Any | Cap-Tons | 340 | 0 | None | 141 | 0.106 | 0 | 68.7 | 0.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 23.473
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ04 | Any | Cap-Tons | 133 | 0 | None | 196 | 0.144 | 0 | 95.9 | 0.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.099
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ04 | Any | Cap-Tons | 455 | 0 | None | 144 | 0.0916 | 0 | 70.6 | 0.0448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 69.341
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ04 | Any | Cap-Tons | 32.3 | 0 | None | 163 | 0.0996 | 0 | 79.7 | 0.0487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 21.136
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ04 | Any | Cap-Tons | 257 | 0 | None | 157 | 0.125 | 0 | 76.9 | 0.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.221
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ05 | Any | Cap-Tons | 518 | 0 | None | 94.6 | 0.0818 | 0 | 46.2 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.633
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ05 | Any | Cap-Tons | 247 | 0 | None | 81.5 | 0.0519 | 0 | 39.9 | 0.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.209
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ05 | Any | Cap-Tons | 1910 | 0 | None | 95.7 | 0.0742 | 0 | 46.8 | 0.0363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.633
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ05 | Any | Cap-Tons | 626 | 0 | None | 60.3 | 0.0401 | 0 | 29.5 | 0.0196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ05 | Any | Cap-Tons | 203 | 0 | None | 211 | 0.0801 | 0 | 103 | 0.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.074
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ05 | Any | Cap-Tons | 264 | 0 | None | 94 | 0.0597 | 0 | 45.9 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.802
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ05 | Any | Cap-Tons | 90.4 | 0 | None | 135 | 0.0854 | 0 | 66.1 | 0.0418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ05 | Any | Cap-Tons | 362 | 0 | None | 107 | 0.0529 | 0 | 52.1 | 0.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.865
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ05 | Any | Cap-Tons | 24.7 | 0 | None | 122 | 0.0619 | 0 | 59.5 | 0.0303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.488
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ05 | Any | Cap-Tons | 194 | 0 | None | 104 | 0.0728 | 0 | 50.6 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.617
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ11 | Any | Cap-Tons | 852 | 0 | None | 212 | 0.146 | 0 | 104 | 0.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.639
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ11 | Any | Cap-Tons | 422 | 0 | None | 162 | 0.069 | 0 | 79.2 | 0.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.527
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ11 | Any | Cap-Tons | 2920 | 0 | None | 202 | 0.157 | 0 | 98.8 | 0.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.639
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ11 | Any | Cap-Tons | 888 | 0 | None | 164 | 0.0955 | 0 | 80.3 | 0.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.449
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ11 | Any | Cap-Tons | 326 | 0 | None | 291 | 0.177 | 0 | 142 | 0.0865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.924
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ11 | Any | Cap-Tons | 426 | 0 | None | 175 | 0.125 | 0 | 85.7 | 0.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.029
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ11 | Any | Cap-Tons | 162 | 0 | None | 289 | 0.193 | 0 | 141 | 0.0944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.449
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ11 | Any | Cap-Tons | 531 | 0 | None | 190 | 0.115 | 0 | 92.9 | 0.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.743
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ11 | Any | Cap-Tons | 36.3 | 0 | None | 221 | 0.126 | 0 | 108 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.587
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ11 | Any | Cap-Tons | 326 | 0 | None | 200 | 0.142 | 0 | 97.9 | 0.0693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.724
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ12 | Any | Cap-Tons | 776 | 0 | None | 178 | 0.149 | 0 | 87.2 | 0.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.613
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ12 | Any | Cap-Tons | 387 | 0 | None | 137 | 0.067 | 0 | 66.9 | 0.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.518
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ12 | Any | Cap-Tons | 2720 | 0 | None | 169 | 0.15 | 0 | 82.5 | 0.0733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.613
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ12 | Any | Cap-Tons | 851 | 0 | None | 127 | 0.0929 | 0 | 62.3 | 0.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.659
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ12 | Any | Cap-Tons | 298 | 0 | None | 252 | 0.173 | 0 | 123 | 0.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.437
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ12 | Any | Cap-Tons | 398 | 0 | None | 144 | 0.122 | 0 | 70.6 | 0.0596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ12 | Any | Cap-Tons | 149 | 0 | None | 234 | 0.186 | 0 | 114 | 0.0908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.659
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ12 | Any | Cap-Tons | 500 | 0 | None | 158 | 0.111 | 0 | 77.1 | 0.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 47.841
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ12 | Any | Cap-Tons | 33.8 | 0 | None | 185 | 0.125 | 0 | 90.6 | 0.0612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 25.803
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ12 | Any | Cap-Tons | 303 | 0 | None | 172 | 0.143 | 0 | 84.3 | 0.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.052
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ13 | Any | Cap-Tons | 896 | 0 | None | 209 | 0.126 | 0 | 102 | 0.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.046
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ13 | Any | Cap-Tons | 450 | 0 | None | 166 | 0.0614 | 0 | 81.2 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.743
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ13 | Any | Cap-Tons | 2980 | 0 | None | 202 | 0.137 | 0 | 98.7 | 0.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.046
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ13 | Any | Cap-Tons | 903 | 0 | None | 167 | 0.0895 | 0 | 81.5 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.773
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ13 | Any | Cap-Tons | 324 | 0 | None | 297 | 0.151 | 0 | 145 | 0.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.253
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ13 | Any | Cap-Tons | 431 | 0 | None | 179 | 0.111 | 0 | 87.6 | 0.0544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.196
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ13 | Any | Cap-Tons | 162 | 0 | None | 299 | 0.171 | 0 | 146 | 0.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.773
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ13 | Any | Cap-Tons | 517 | 0 | None | 196 | 0.106 | 0 | 96 | 0.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 21.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ13 | Any | Cap-Tons | 36.3 | 0 | None | 221 | 0.116 | 0 | 108 | 0.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.844
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ13 | Any | Cap-Tons | 330 | 0 | None | 206 | 0.138 | 0 | 101 | 0.0676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.777
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ16 | Any | Cap-Tons | 549 | 0 | None | 125 | 0.111 | 0 | 61.1 | 0.0542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ16 | Any | Cap-Tons | 269 | 0 | None | 95.7 | 0.061 | 0 | 46.8 | 0.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.548
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ16 | Any | Cap-Tons | 1950 | 0 | None | 123 | 0.117 | 0 | 60.3 | 0.0574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ16 | Any | Cap-Tons | 634 | 0 | None | 90.2 | 0.0698 | 0 | 44.1 | 0.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.2
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ16 | Any | Cap-Tons | 209 | 0 | None | 236 | 0.137 | 0 | 115 | 0.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.78
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ16 | Any | Cap-Tons | 281 | 0 | None | 102 | 0.0883 | 0 | 50.1 | 0.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.351
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ16 | Any | Cap-Tons | 103 | 0 | None | 180 | 0.146 | 0 | 88 | 0.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.2
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ16 | Any | Cap-Tons | 402 | 0 | None | 112 | 0.0927 | 0 | 54.6 | 0.0453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.673
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ16 | Any | Cap-Tons | 25.8 | 0 | None | 132 | 0.104 | 0 | 64.6 | 0.0507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.939
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ16 | Any | Cap-Tons | 226 | 0 | None | 112 | 0.107 | 0 | 54.8 | 0.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.338
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ01 | Any | Cap-Tons | 435 | 0 | None | 25.4 | 0.082 | 0 | 16.2 | 0.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ01 | Any | Cap-Tons | 205 | 0 | None | 21.6 | 0.0549 | 0 | 13.8 | 0.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.602
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ01 | Any | Cap-Tons | 1700 | 0 | None | 44.8 | 0.0704 | 0 | 28.5 | 0.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ01 | Any | Cap-Tons | 533 | 0 | None | 19.5 | 0.0427 | 0 | 12.4 | 0.0272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.614
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ01 | Any | Cap-Tons | 175 | 0 | None | 187 | 0.0863 | 0 | 119 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.705
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ01 | Any | Cap-Tons | 211 | 0 | None | 29.3 | 0.0619 | 0 | 18.7 | 0.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.882
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ01 | Any | Cap-Tons | 79.7 | 0 | None | 63.1 | 0.0753 | 0 | 40.2 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.614
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ01 | Any | Cap-Tons | 343 | 0 | None | 27.5 | 0.0488 | 0 | 17.5 | 0.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.322
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ01 | Any | Cap-Tons | 21.9 | 0 | None | 35.5 | 0.0557 | 0 | 22.6 | 0.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.898
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ01 | Any | Cap-Tons | 160 | 0 | None | 29.9 | 0.0724 | 0 | 19.1 | 0.0461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.136
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ02 | Any | Cap-Tons | 735 | 0 | None | 182 | 0.177 | 0 | 116 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.935
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ02 | Any | Cap-Tons | 362 | 0 | None | 152 | 0.0874 | 0 | 96.8 | 0.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.515
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ02 | Any | Cap-Tons | 2650 | 0 | None | 178 | 0.179 | 0 | 113 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.935
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ02 | Any | Cap-Tons | 794 | 0 | None | 126 | 0.113 | 0 | 80.5 | 0.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.289
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ02 | Any | Cap-Tons | 272 | 0 | None | 308 | 0.216 | 0 | 196 | 0.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.489
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ02 | Any | Cap-Tons | 345 | 0 | None | 177 | 0.171 | 0 | 113 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.734
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ02 | Any | Cap-Tons | 127 | 0 | None | 257 | 0.248 | 0 | 164 | 0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.289
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ02 | Any | Cap-Tons | 466 | 0 | None | 181 | 0.148 | 0 | 116 | 0.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.845
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ02 | Any | Cap-Tons | 30.4 | 0 | None | 216 | 0.168 | 0 | 138 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.572
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ02 | Any | Cap-Tons | 256 | 0 | None | 199 | 0.19 | 0 | 127 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.537
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ03 | Any | Cap-Tons | 589 | 0 | None | 118 | 0.119 | 0 | 75.2 | 0.0756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.346
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ03 | Any | Cap-Tons | 288 | 0 | None | 93.4 | 0.0625 | 0 | 59.5 | 0.0398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 17.783
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ03 | Any | Cap-Tons | 2130 | 0 | None | 119 | 0.121 | 0 | 76 | 0.0774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.346
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ03 | Any | Cap-Tons | 640 | 0 | None | 87.5 | 0.0825 | 0 | 55.8 | 0.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.544
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ03 | Any | Cap-Tons | 228 | 0 | None | 262 | 0.148 | 0 | 167 | 0.0942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 23.105
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ03 | Any | Cap-Tons | 277 | 0 | None | 112 | 0.108 | 0 | 71.2 | 0.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 44.501
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ03 | Any | Cap-Tons | 104 | 0 | None | 175 | 0.158 | 0 | 111 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.544
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ03 | Any | Cap-Tons | 392 | 0 | None | 121 | 0.108 | 0 | 76.9 | 0.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 174.648
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ03 | Any | Cap-Tons | 27.2 | 0 | None | 144 | 0.124 | 0 | 91.7 | 0.0791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 27.509
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ03 | Any | Cap-Tons | 207 | 0 | None | 129 | 0.144 | 0 | 82 | 0.0915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 35.701
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ04 | Any | Cap-Tons | 739 | 0 | None | 201 | 0.201 | 0 | 128 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.805
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ04 | Any | Cap-Tons | 364 | 0 | None | 160 | 0.136 | 0 | 102 | 0.0868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.74
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ04 | Any | Cap-Tons | 2600 | 0 | None | 195 | 0.182 | 0 | 124 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.805
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ04 | Any | Cap-Tons | 769 | 0 | None | 152 | 0.106 | 0 | 96.6 | 0.0677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.099
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ04 | Any | Cap-Tons | 282 | 0 | None | 321 | 0.178 | 0 | 205 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.366
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ04 | Any | Cap-Tons | 340 | 0 | None | 198 | 0.149 | 0 | 126 | 0.0952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 23.473
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ04 | Any | Cap-Tons | 133 | 0 | None | 276 | 0.203 | 0 | 176 | 0.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.099
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ04 | Any | Cap-Tons | 455 | 0 | None | 203 | 0.129 | 0 | 129 | 0.0821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 69.341
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ04 | Any | Cap-Tons | 32.3 | 0 | None | 229 | 0.14 | 0 | 146 | 0.0894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 21.136
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ04 | Any | Cap-Tons | 257 | 0 | None | 222 | 0.175 | 0 | 141 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.221
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ05 | Any | Cap-Tons | 518 | 0 | None | 133 | 0.115 | 0 | 84.8 | 0.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.633
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ05 | Any | Cap-Tons | 247 | 0 | None | 115 | 0.0731 | 0 | 73.1 | 0.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.209
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ05 | Any | Cap-Tons | 1910 | 0 | None | 135 | 0.104 | 0 | 85.8 | 0.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.633
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ05 | Any | Cap-Tons | 626 | 0 | None | 84.9 | 0.0565 | 0 | 54.1 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ05 | Any | Cap-Tons | 203 | 0 | None | 297 | 0.113 | 0 | 189 | 0.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.074
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ05 | Any | Cap-Tons | 264 | 0 | None | 132 | 0.084 | 0 | 84.3 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.802
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ05 | Any | Cap-Tons | 90.4 | 0 | None | 190 | 0.12 | 0 | 121 | 0.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ05 | Any | Cap-Tons | 362 | 0 | None | 150 | 0.0745 | 0 | 95.7 | 0.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.865
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ05 | Any | Cap-Tons | 24.7 | 0 | None | 171 | 0.0871 | 0 | 109 | 0.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.488
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ05 | Any | Cap-Tons | 194 | 0 | None | 146 | 0.102 | 0 | 92.9 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.617
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ11 | Any | Cap-Tons | 852 | 0 | None | 299 | 0.205 | 0 | 190 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.639
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ11 | Any | Cap-Tons | 422 | 0 | None | 228 | 0.0972 | 0 | 145 | 0.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.527
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ11 | Any | Cap-Tons | 2920 | 0 | None | 284 | 0.22 | 0 | 181 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.639
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ11 | Any | Cap-Tons | 888 | 0 | None | 231 | 0.134 | 0 | 147 | 0.0857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.449
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ11 | Any | Cap-Tons | 326 | 0 | None | 410 | 0.249 | 0 | 261 | 0.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.924
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ11 | Any | Cap-Tons | 426 | 0 | None | 247 | 0.176 | 0 | 157 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.029
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ11 | Any | Cap-Tons | 162 | 0 | None | 407 | 0.272 | 0 | 259 | 0.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.449
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ11 | Any | Cap-Tons | 531 | 0 | None | 268 | 0.163 | 0 | 171 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.743
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ11 | Any | Cap-Tons | 36.3 | 0 | None | 311 | 0.178 | 0 | 198 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.587
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ11 | Any | Cap-Tons | 326 | 0 | None | 282 | 0.2 | 0 | 180 | 0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.724
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ12 | Any | Cap-Tons | 776 | 0 | None | 251 | 0.21 | 0 | 160 | 0.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.613
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ12 | Any | Cap-Tons | 387 | 0 | None | 193 | 0.0944 | 0 | 123 | 0.0601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.518
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ12 | Any | Cap-Tons | 2720 | 0 | None | 238 | 0.211 | 0 | 151 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.613
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ12 | Any | Cap-Tons | 851 | 0 | None | 179 | 0.131 | 0 | 114 | 0.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.659
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ12 | Any | Cap-Tons | 298 | 0 | None | 354 | 0.244 | 0 | 226 | 0.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.437
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ12 | Any | Cap-Tons | 398 | 0 | None | 203 | 0.172 | 0 | 130 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ12 | Any | Cap-Tons | 149 | 0 | None | 330 | 0.262 | 0 | 210 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.659
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ12 | Any | Cap-Tons | 500 | 0 | None | 222 | 0.157 | 0 | 142 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 47.841
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ12 | Any | Cap-Tons | 33.8 | 0 | None | 261 | 0.176 | 0 | 166 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 25.803
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ12 | Any | Cap-Tons | 303 | 0 | None | 243 | 0.201 | 0 | 155 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.052
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ13 | Any | Cap-Tons | 896 | 0 | None | 294 | 0.178 | 0 | 187 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.046
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ13 | Any | Cap-Tons | 450 | 0 | None | 234 | 0.0865 | 0 | 149 | 0.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.743
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ13 | Any | Cap-Tons | 2980 | 0 | None | 284 | 0.193 | 0 | 181 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.046
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ13 | Any | Cap-Tons | 903 | 0 | None | 235 | 0.126 | 0 | 150 | 0.0803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.773
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ13 | Any | Cap-Tons | 324 | 0 | None | 419 | 0.213 | 0 | 267 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.253
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ13 | Any | Cap-Tons | 431 | 0 | None | 252 | 0.157 | 0 | 161 | 0.0997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.196
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ13 | Any | Cap-Tons | 162 | 0 | None | 420 | 0.24 | 0 | 268 | 0.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.773
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ13 | Any | Cap-Tons | 517 | 0 | None | 276 | 0.15 | 0 | 176 | 0.0954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 21.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ13 | Any | Cap-Tons | 36.3 | 0 | None | 312 | 0.163 | 0 | 198 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.844
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ13 | Any | Cap-Tons | 330 | 0 | None | 290 | 0.195 | 0 | 185 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.777
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ16 | Any | Cap-Tons | 549 | 0 | None | 176 | 0.156 | 0 | 112 | 0.0994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ16 | Any | Cap-Tons | 269 | 0 | None | 135 | 0.0859 | 0 | 85.8 | 0.0547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.548
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ16 | Any | Cap-Tons | 1950 | 0 | None | 174 | 0.165 | 0 | 111 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ16 | Any | Cap-Tons | 634 | 0 | None | 127 | 0.0983 | 0 | 81 | 0.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.2
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ16 | Any | Cap-Tons | 209 | 0 | None | 332 | 0.192 | 0 | 212 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.78
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ16 | Any | Cap-Tons | 281 | 0 | None | 144 | 0.124 | 0 | 91.9 | 0.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.351
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ16 | Any | Cap-Tons | 103 | 0 | None | 254 | 0.206 | 0 | 162 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.2
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ16 | Any | Cap-Tons | 402 | 0 | None | 157 | 0.131 | 0 | 100 | 0.0832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.673
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ16 | Any | Cap-Tons | 25.8 | 0 | None | 186 | 0.146 | 0 | 119 | 0.0929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.939
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ16 | Any | Cap-Tons | 226 | 0 | None | 158 | 0.15 | 0 | 100 | 0.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.338
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ01 | Any | Cap-Tons | 435 | 0 | None | 18.1 | 0.0582 | 0 | 8.8 | 0.0285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ01 | Any | Cap-Tons | 205 | 0 | None | 15.4 | 0.039 | 0 | 7.5 | 0.0191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.602
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ01 | Any | Cap-Tons | 1700 | 0 | None | 31.8 | 0.05 | 0 | 15.6 | 0.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ01 | Any | Cap-Tons | 533 | 0 | None | 13.9 | 0.0303 | 0 | 6.8 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.614
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ01 | Any | Cap-Tons | 175 | 0 | None | 133 | 0.0613 | 0 | 64.9 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.705
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ01 | Any | Cap-Tons | 211 | 0 | None | 20.8 | 0.044 | 0 | 10.2 | 0.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.882
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ01 | Any | Cap-Tons | 79.7 | 0 | None | 44.8 | 0.0535 | 0 | 21.9 | 0.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.614
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ01 | Any | Cap-Tons | 21.9 | 0 | None | 25.2 | 0.0396 | 0 | 12.3 | 0.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.898
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ01 | Any | Cap-Tons | 160 | 0 | None | 21.3 | 0.0514 | 0 | 10.4 | 0.0251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.136
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ02 | Any | Cap-Tons | 735 | 0 | None | 129 | 0.126 | 0 | 63.1 | 0.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.935
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ02 | Any | Cap-Tons | 362 | 0 | None | 108 | 0.0621 | 0 | 52.7 | 0.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.515
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ02 | Any | Cap-Tons | 2650 | 0 | None | 126 | 0.127 | 0 | 61.8 | 0.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.935
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ02 | Any | Cap-Tons | 794 | 0 | None | 89.7 | 0.08 | 0 | 43.9 | 0.0391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.289
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ02 | Any | Cap-Tons | 272 | 0 | None | 219 | 0.153 | 0 | 107 | 0.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.489
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ02 | Any | Cap-Tons | 345 | 0 | None | 126 | 0.121 | 0 | 61.6 | 0.0593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.734
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ02 | Any | Cap-Tons | 127 | 0 | None | 183 | 0.176 | 0 | 89.3 | 0.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.289
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ02 | Any | Cap-Tons | 466 | 0 | None | 129 | 0.105 | 0 | 63 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.845
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ02 | Any | Cap-Tons | 30.4 | 0 | None | 154 | 0.119 | 0 | 75.2 | 0.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.572
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ02 | Any | Cap-Tons | 256 | 0 | None | 141 | 0.135 | 0 | 69.1 | 0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.537
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ03 | Any | Cap-Tons | 589 | 0 | None | 83.8 | 0.0842 | 0 | 41 | 0.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.346
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ03 | Any | Cap-Tons | 288 | 0 | None | 66.3 | 0.0444 | 0 | 32.4 | 0.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 17.783
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ03 | Any | Cap-Tons | 2130 | 0 | None | 84.7 | 0.0863 | 0 | 41.4 | 0.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.346
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ03 | Any | Cap-Tons | 640 | 0 | None | 62.2 | 0.0586 | 0 | 30.4 | 0.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.544
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ03 | Any | Cap-Tons | 228 | 0 | None | 186 | 0.105 | 0 | 90.9 | 0.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 23.105
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ03 | Any | Cap-Tons | 277 | 0 | None | 79.4 | 0.0766 | 0 | 38.8 | 0.0374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 44.501
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ03 | Any | Cap-Tons | 104 | 0 | None | 124 | 0.112 | 0 | 60.6 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.544
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ03 | Any | Cap-Tons | 392 | 0 | None | 85.8 | 0.077 | 0 | 41.9 | 0.0377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 174.648
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ03 | Any | Cap-Tons | 27.2 | 0 | None | 102 | 0.0882 | 0 | 50 | 0.0431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 27.509
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ03 | Any | Cap-Tons | 207 | 0 | None | 91.4 | 0.102 | 0 | 44.7 | 0.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 35.701
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ04 | Any | Cap-Tons | 739 | 0 | None | 143 | 0.143 | 0 | 69.9 | 0.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.805
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ04 | Any | Cap-Tons | 364 | 0 | None | 114 | 0.0968 | 0 | 55.7 | 0.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.74
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ04 | Any | Cap-Tons | 2600 | 0 | None | 139 | 0.129 | 0 | 67.7 | 0.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.805
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ04 | Any | Cap-Tons | 769 | 0 | None | 108 | 0.0754 | 0 | 52.6 | 0.0369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.099
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ04 | Any | Cap-Tons | 282 | 0 | None | 228 | 0.127 | 0 | 112 | 0.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.366
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ04 | Any | Cap-Tons | 340 | 0 | None | 141 | 0.106 | 0 | 68.7 | 0.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 23.473
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ04 | Any | Cap-Tons | 133 | 0 | None | 196 | 0.144 | 0 | 95.9 | 0.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.099
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ04 | Any | Cap-Tons | 455 | 0 | None | 144 | 0.0916 | 0 | 70.6 | 0.0448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 69.341
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ04 | Any | Cap-Tons | 32.3 | 0 | None | 163 | 0.0996 | 0 | 79.7 | 0.0487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 21.136
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ04 | Any | Cap-Tons | 257 | 0 | None | 157 | 0.125 | 0 | 76.9 | 0.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.221
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ05 | Any | Cap-Tons | 518 | 0 | None | 94.6 | 0.0818 | 0 | 46.2 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.633
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ05 | Any | Cap-Tons | 1910 | 0 | None | 95.7 | 0.0742 | 0 | 46.8 | 0.0363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.633
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ05 | Any | Cap-Tons | 626 | 0 | None | 60.3 | 0.0401 | 0 | 29.5 | 0.0196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ05 | Any | Cap-Tons | 203 | 0 | None | 211 | 0.0801 | 0 | 103 | 0.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.074
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ05 | Any | Cap-Tons | 264 | 0 | None | 94 | 0.0597 | 0 | 45.9 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.802
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ05 | Any | Cap-Tons | 90.4 | 0 | None | 135 | 0.0854 | 0 | 66.1 | 0.0418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ05 | Any | Cap-Tons | 362 | 0 | None | 107 | 0.0529 | 0 | 52.1 | 0.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.865
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ05 | Any | Cap-Tons | 24.7 | 0 | None | 122 | 0.0619 | 0 | 59.5 | 0.0303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.488
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ05 | Any | Cap-Tons | 194 | 0 | None | 104 | 0.0728 | 0 | 50.6 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.617
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ11 | Any | Cap-Tons | 852 | 0 | None | 212 | 0.146 | 0 | 104 | 0.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.639
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ11 | Any | Cap-Tons | 422 | 0 | None | 162 | 0.069 | 0 | 79.2 | 0.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.527
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ11 | Any | Cap-Tons | 2920 | 0 | None | 202 | 0.157 | 0 | 98.8 | 0.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.639
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ11 | Any | Cap-Tons | 888 | 0 | None | 164 | 0.0955 | 0 | 80.3 | 0.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.449
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ11 | Any | Cap-Tons | 326 | 0 | None | 291 | 0.177 | 0 | 142 | 0.0865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.924
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ11 | Any | Cap-Tons | 426 | 0 | None | 175 | 0.125 | 0 | 85.7 | 0.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.029
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ11 | Any | Cap-Tons | 162 | 0 | None | 289 | 0.193 | 0 | 141 | 0.0944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.449
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ11 | Any | Cap-Tons | 531 | 0 | None | 190 | 0.115 | 0 | 92.9 | 0.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.743
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ11 | Any | Cap-Tons | 36.3 | 0 | None | 221 | 0.126 | 0 | 108 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.587
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ11 | Any | Cap-Tons | 326 | 0 | None | 200 | 0.142 | 0 | 97.9 | 0.0693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.724
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ12 | Any | Cap-Tons | 776 | 0 | None | 178 | 0.149 | 0 | 87.2 | 0.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.613
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ12 | Any | Cap-Tons | 387 | 0 | None | 137 | 0.067 | 0 | 66.9 | 0.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.518
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ12 | Any | Cap-Tons | 2720 | 0 | None | 169 | 0.15 | 0 | 82.5 | 0.0733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.613
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ12 | Any | Cap-Tons | 851 | 0 | None | 127 | 0.0929 | 0 | 62.3 | 0.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.659
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ12 | Any | Cap-Tons | 298 | 0 | None | 252 | 0.173 | 0 | 123 | 0.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.437
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ12 | Any | Cap-Tons | 398 | 0 | None | 144 | 0.122 | 0 | 70.6 | 0.0596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ12 | Any | Cap-Tons | 149 | 0 | None | 234 | 0.186 | 0 | 114 | 0.0908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.659
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ12 | Any | Cap-Tons | 500 | 0 | None | 158 | 0.111 | 0 | 77.1 | 0.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 47.841
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ12 | Any | Cap-Tons | 33.8 | 0 | None | 185 | 0.125 | 0 | 90.6 | 0.0612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 25.803
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ12 | Any | Cap-Tons | 303 | 0 | None | 172 | 0.143 | 0 | 84.3 | 0.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.052
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ13 | Any | Cap-Tons | 896 | 0 | None | 209 | 0.126 | 0 | 102 | 0.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.046
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ13 | Any | Cap-Tons | 450 | 0 | None | 166 | 0.0614 | 0 | 81.2 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.743
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ13 | Any | Cap-Tons | 2980 | 0 | None | 202 | 0.137 | 0 | 98.7 | 0.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.046
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ13 | Any | Cap-Tons | 903 | 0 | None | 167 | 0.0895 | 0 | 81.5 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.773
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ13 | Any | Cap-Tons | 324 | 0 | None | 297 | 0.151 | 0 | 145 | 0.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.253
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ13 | Any | Cap-Tons | 162 | 0 | None | 299 | 0.171 | 0 | 146 | 0.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.773
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ13 | Any | Cap-Tons | 517 | 0 | None | 196 | 0.106 | 0 | 96 | 0.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 21.008
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ13 | Any | Cap-Tons | 36.3 | 0 | None | 221 | 0.116 | 0 | 108 | 0.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.844
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ13 | Any | Cap-Tons | 330 | 0 | None | 206 | 0.138 | 0 | 101 | 0.0676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.777
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ16 | Any | Cap-Tons | 549 | 0 | None | 125 | 0.111 | 0 | 61.1 | 0.0542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ16 | Any | Cap-Tons | 269 | 0 | None | 95.7 | 0.061 | 0 | 46.8 | 0.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.548
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ16 | Any | Cap-Tons | 1950 | 0 | None | 123 | 0.117 | 0 | 60.3 | 0.0574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ16 | Any | Cap-Tons | 634 | 0 | None | 90.2 | 0.0698 | 0 | 44.1 | 0.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.2
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ16 | Any | Cap-Tons | 209 | 0 | None | 236 | 0.137 | 0 | 115 | 0.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.78
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ16 | Any | Cap-Tons | 281 | 0 | None | 102 | 0.0883 | 0 | 50.1 | 0.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.351
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ16 | Any | Cap-Tons | 103 | 0 | None | 180 | 0.146 | 0 | 88 | 0.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.2
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ16 | Any | Cap-Tons | 402 | 0 | None | 112 | 0.0927 | 0 | 54.6 | 0.0453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.673
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ16 | Any | Cap-Tons | 25.8 | 0 | None | 132 | 0.104 | 0 | 64.6 | 0.0507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.939
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ16 | Any | Cap-Tons | 226 | 0 | None | 112 | 0.107 | 0 | 54.8 | 0.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.338
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ01 | Any | Cap-Tons | 435 | 0 | None | 25.4 | 0.082 | 0 | 16.2 | 0.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ01 | Any | Cap-Tons | 205 | 0 | None | 21.6 | 0.0549 | 0 | 13.8 | 0.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.602
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ01 | Any | Cap-Tons | 1700 | 0 | None | 44.8 | 0.0704 | 0 | 28.5 | 0.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ01 | Any | Cap-Tons | 533 | 0 | None | 19.5 | 0.0427 | 0 | 12.4 | 0.0272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.614
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ01 | Any | Cap-Tons | 175 | 0 | None | 187 | 0.0863 | 0 | 119 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.705
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ01 | Any | Cap-Tons | 211 | 0 | None | 29.3 | 0.0619 | 0 | 18.7 | 0.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.882
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ01 | Any | Cap-Tons | 79.7 | 0 | None | 63.1 | 0.0753 | 0 | 40.2 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.614
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ01 | Any | Cap-Tons | 343 | 0 | None | 27.5 | 0.0488 | 0 | 17.5 | 0.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.322
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ01 | Any | Cap-Tons | 21.9 | 0 | None | 35.5 | 0.0557 | 0 | 22.6 | 0.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.898
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ01 | Any | Cap-Tons | 160 | 0 | None | 29.9 | 0.0724 | 0 | 19.1 | 0.0461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.136
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ02 | Any | Cap-Tons | 735 | 0 | None | 182 | 0.177 | 0 | 116 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.935
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ02 | Any | Cap-Tons | 362 | 0 | None | 152 | 0.0874 | 0 | 96.8 | 0.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.515
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ02 | Any | Cap-Tons | 2650 | 0 | None | 178 | 0.179 | 0 | 113 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.935
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ02 | Any | Cap-Tons | 794 | 0 | None | 126 | 0.113 | 0 | 80.5 | 0.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.289
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ02 | Any | Cap-Tons | 272 | 0 | None | 308 | 0.216 | 0 | 196 | 0.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.489
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ02 | Any | Cap-Tons | 345 | 0 | None | 177 | 0.171 | 0 | 113 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.734
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ02 | Any | Cap-Tons | 127 | 0 | None | 257 | 0.248 | 0 | 164 | 0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.289
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ02 | Any | Cap-Tons | 466 | 0 | None | 181 | 0.148 | 0 | 116 | 0.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.845
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ02 | Any | Cap-Tons | 30.4 | 0 | None | 216 | 0.168 | 0 | 138 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.572
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ03 | Any | Cap-Tons | 589 | 0 | None | 118 | 0.119 | 0 | 75.2 | 0.0756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.346
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ03 | Any | Cap-Tons | 288 | 0 | None | 93.4 | 0.0625 | 0 | 59.5 | 0.0398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 17.783
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ03 | Any | Cap-Tons | 2130 | 0 | None | 119 | 0.121 | 0 | 76 | 0.0774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.346
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ03 | Any | Cap-Tons | 640 | 0 | None | 87.5 | 0.0825 | 0 | 55.8 | 0.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.544
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ03 | Any | Cap-Tons | 228 | 0 | None | 262 | 0.148 | 0 | 167 | 0.0942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 23.105
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ03 | Any | Cap-Tons | 277 | 0 | None | 112 | 0.108 | 0 | 71.2 | 0.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 44.501
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ03 | Any | Cap-Tons | 104 | 0 | None | 175 | 0.158 | 0 | 111 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.544
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ03 | Any | Cap-Tons | 392 | 0 | None | 121 | 0.108 | 0 | 76.9 | 0.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 174.648
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ03 | Any | Cap-Tons | 27.2 | 0 | None | 144 | 0.124 | 0 | 91.7 | 0.0791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 27.509
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ03 | Any | Cap-Tons | 207 | 0 | None | 129 | 0.144 | 0 | 82 | 0.0915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 35.701
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ04 | Any | Cap-Tons | 739 | 0 | None | 201 | 0.201 | 0 | 128 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.805
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ04 | Any | Cap-Tons | 364 | 0 | None | 160 | 0.136 | 0 | 102 | 0.0868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.74
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ04 | Any | Cap-Tons | 2600 | 0 | None | 195 | 0.182 | 0 | 124 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.805
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ04 | Any | Cap-Tons | 769 | 0 | None | 152 | 0.106 | 0 | 96.6 | 0.0677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.099
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ04 | Any | Cap-Tons | 282 | 0 | None | 321 | 0.178 | 0 | 205 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.366
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ04 | Any | Cap-Tons | 340 | 0 | None | 198 | 0.149 | 0 | 126 | 0.0952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 23.473
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ04 | Any | Cap-Tons | 133 | 0 | None | 276 | 0.203 | 0 | 176 | 0.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.099
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ04 | Any | Cap-Tons | 455 | 0 | None | 203 | 0.129 | 0 | 129 | 0.0821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 69.341
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ04 | Any | Cap-Tons | 32.3 | 0 | None | 229 | 0.14 | 0 | 146 | 0.0894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 21.136
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ04 | Any | Cap-Tons | 257 | 0 | None | 222 | 0.175 | 0 | 141 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.221
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ05 | Any | Cap-Tons | 518 | 0 | None | 133 | 0.115 | 0 | 84.8 | 0.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.633
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ05 | Any | Cap-Tons | 247 | 0 | None | 115 | 0.0731 | 0 | 73.1 | 0.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.209
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ05 | Any | Cap-Tons | 1910 | 0 | None | 135 | 0.104 | 0 | 85.8 | 0.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.633
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ05 | Any | Cap-Tons | 626 | 0 | None | 84.9 | 0.0565 | 0 | 54.1 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ05 | Any | Cap-Tons | 203 | 0 | None | 297 | 0.113 | 0 | 189 | 0.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.074
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ05 | Any | Cap-Tons | 264 | 0 | None | 132 | 0.084 | 0 | 84.3 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.802
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ05 | Any | Cap-Tons | 90.4 | 0 | None | 190 | 0.12 | 0 | 121 | 0.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ05 | Any | Cap-Tons | 362 | 0 | None | 150 | 0.0745 | 0 | 95.7 | 0.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.865
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ05 | Any | Cap-Tons | 24.7 | 0 | None | 171 | 0.0871 | 0 | 109 | 0.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.488
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ05 | Any | Cap-Tons | 194 | 0 | None | 146 | 0.102 | 0 | 92.9 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.617
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ11 | Any | Cap-Tons | 852 | 0 | None | 299 | 0.205 | 0 | 190 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.639
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ11 | Any | Cap-Tons | 422 | 0 | None | 228 | 0.0972 | 0 | 145 | 0.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.527
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ11 | Any | Cap-Tons | 2920 | 0 | None | 284 | 0.22 | 0 | 181 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.639
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ11 | Any | Cap-Tons | 326 | 0 | None | 410 | 0.249 | 0 | 261 | 0.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.924
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ11 | Any | Cap-Tons | 426 | 0 | None | 247 | 0.176 | 0 | 157 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.029
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ11 | Any | Cap-Tons | 162 | 0 | None | 407 | 0.272 | 0 | 259 | 0.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.449
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ11 | Any | Cap-Tons | 531 | 0 | None | 268 | 0.163 | 0 | 171 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.743
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ11 | Any | Cap-Tons | 36.3 | 0 | None | 311 | 0.178 | 0 | 198 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.587
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ11 | Any | Cap-Tons | 326 | 0 | None | 282 | 0.2 | 0 | 180 | 0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.724
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ12 | Any | Cap-Tons | 776 | 0 | None | 251 | 0.21 | 0 | 160 | 0.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.613
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ12 | Any | Cap-Tons | 387 | 0 | None | 193 | 0.0944 | 0 | 123 | 0.0601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.518
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ12 | Any | Cap-Tons | 2720 | 0 | None | 238 | 0.211 | 0 | 151 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.613
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ12 | Any | Cap-Tons | 851 | 0 | None | 179 | 0.131 | 0 | 114 | 0.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.659
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ12 | Any | Cap-Tons | 298 | 0 | None | 354 | 0.244 | 0 | 226 | 0.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.437
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ12 | Any | Cap-Tons | 398 | 0 | None | 203 | 0.172 | 0 | 130 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ12 | Any | Cap-Tons | 149 | 0 | None | 330 | 0.262 | 0 | 210 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.659
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ12 | Any | Cap-Tons | 500 | 0 | None | 222 | 0.157 | 0 | 142 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 47.841
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ12 | Any | Cap-Tons | 33.8 | 0 | None | 261 | 0.176 | 0 | 166 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 25.803
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ12 | Any | Cap-Tons | 303 | 0 | None | 243 | 0.201 | 0 | 155 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.052
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ13 | Any | Cap-Tons | 896 | 0 | None | 294 | 0.178 | 0 | 187 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.046
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ13 | Any | Cap-Tons | 450 | 0 | None | 234 | 0.0865 | 0 | 149 | 0.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.743
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ13 | Any | Cap-Tons | 2980 | 0 | None | 284 | 0.193 | 0 | 181 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.046
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ13 | Any | Cap-Tons | 903 | 0 | None | 235 | 0.126 | 0 | 150 | 0.0803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.773
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ13 | Any | Cap-Tons | 324 | 0 | None | 419 | 0.213 | 0 | 267 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.253
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ13 | Any | Cap-Tons | 431 | 0 | None | 252 | 0.157 | 0 | 161 | 0.0997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.196
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ13 | Any | Cap-Tons | 162 | 0 | None | 420 | 0.24 | 0 | 268 | 0.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 8.773
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Old | Ex | CZ13 | Any | Cap-Tons | 517 | 0 | None | 276 | 0.15 | 0 | 176 | 0.0954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 21.008
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ13 | Any | Cap-Tons | 36.3 | 0 | None | 312 | 0.163 | 0 | 198 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.844
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ13 | Any | Cap-Tons | 330 | 0 | None | 290 | 0.195 | 0 | 185 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 14.777
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Old | Ex | CZ16 | Any | Cap-Tons | 549 | 0 | None | 176 | 0.156 | 0 | 112 | 0.0994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Old | Ex | CZ16 | Any | Cap-Tons | 269 | 0 | None | 135 | 0.0859 | 0 | 85.8 | 0.0547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.548
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Old | Ex | CZ16 | Any | Cap-Tons | 1950 | 0 | None | 174 | 0.165 | 0 | 111 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.155
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Old | Ex | CZ16 | Any | Cap-Tons | 634 | 0 | None | 127 | 0.0983 | 0 | 81 | 0.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.2
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Old | Ex | CZ16 | Any | Cap-Tons | 209 | 0 | None | 332 | 0.192 | 0 | 212 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.78
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Old | Ex | CZ16 | Any | Cap-Tons | 281 | 0 | None | 144 | 0.124 | 0 | 91.9 | 0.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.351
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Old | Ex | CZ16 | Any | Cap-Tons | 103 | 0 | None | 254 | 0.206 | 0 | 162 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.2
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Old | Ex | CZ16 | Any | Cap-Tons | 25.8 | 0 | None | 186 | 0.146 | 0 | 119 | 0.0929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.939
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Old | Ex | CZ16 | Any | Cap-Tons | 226 | 0 | None | 158 | 0.15 | 0 | 100 | 0.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.338
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ01 | Any | Cap-Tons | 298 | 0 | None | 15 | 0.0399 | 0 | 15 | 0.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ01 | Any | Cap-Tons | 145 | 0 | None | 9.8 | 0.0181 | 0 | 9.8 | 0.0181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ01 | Any | Cap-Tons | 1120 | 0 | None | 12.4 | 0.0298 | 0 | 12.4 | 0.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ01 | Any | Cap-Tons | 528 | 0 | None | 4.7 | 0.0102 | 0 | 4.7 | 0.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.006
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ01 | Any | Cap-Tons | 88.3 | 0 | None | 40.2 | 0.0252 | 0 | 40.2 | 0.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ01 | Any | Cap-Tons | 170 | 0 | None | 17.9 | 0.0201 | 0 | 17.9 | 0.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ01 | Any | Cap-Tons | 61.8 | 0 | None | 5.7 | 0.0161 | 0 | 5.7 | 0.0161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.006
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ01 | Any | Cap-Tons | 243 | 0 | None | 14.1 | 0.0134 | 0 | 14.1 | 0.0134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.012
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ01 | Any | Cap-Tons | 13.4 | 0 | None | 16.2 | 0.0137 | 0 | 16.2 | 0.0137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.018
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ01 | Any | Cap-Tons | 125 | 0 | None | 15.5 | 0.0288 | 0 | 15.5 | 0.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ02 | Any | Cap-Tons | 549 | 0 | None | 56.3 | 0.0517 | 0 | 56.3 | 0.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.038
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ02 | Any | Cap-Tons | 282 | 0 | None | 38.2 | 0.0212 | 0 | 38.2 | 0.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ02 | Any | Cap-Tons | 1920 | 0 | None | 49.9 | 0.0569 | 0 | 49.9 | 0.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.038
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ02 | Any | Cap-Tons | 849 | 0 | None | 30 | 0.029 | 0 | 30 | 0.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ02 | Any | Cap-Tons | 156 | 0 | None | 83 | 0.0716 | 0 | 83 | 0.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.042
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ02 | Any | Cap-Tons | 285 | 0 | None | 53.5 | 0.0475 | 0 | 53.5 | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ02 | Any | Cap-Tons | 100 | 0 | None | 54.5 | 0.0659 | 0 | 54.5 | 0.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ02 | Any | Cap-Tons | 362 | 0 | None | 51.1 | 0.0368 | 0 | 51.1 | 0.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.178
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ02 | Any | Cap-Tons | 20.4 | 0 | None | 59.3 | 0.0422 | 0 | 59.3 | 0.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.05
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ02 | Any | Cap-Tons | 222 | 0 | None | 65.2 | 0.0682 | 0 | 65.2 | 0.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ03 | Any | Cap-Tons | 421 | 0 | None | 42.7 | 0.0305 | 0 | 42.7 | 0.0305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.143
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ03 | Any | Cap-Tons | 214 | 0 | None | 27.1 | 0.0061 | 0 | 27.1 | 0.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.078
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ03 | Any | Cap-Tons | 1490 | 0 | None | 34.9 | 0.0337 | 0 | 34.9 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.143
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ03 | Any | Cap-Tons | 582 | 0 | None | 22.9 | 0.0212 | 0 | 22.9 | 0.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.146
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ03 | Any | Cap-Tons | 121 | 0 | None | 67.8 | 0.0466 | 0 | 67.8 | 0.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.125
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ03 | Any | Cap-Tons | 221 | 0 | None | 45 | 0.0319 | 0 | 45 | 0.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.261
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ03 | Any | Cap-Tons | 77.9 | 0 | None | 31.3 | 0.04 | 0 | 31.3 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.146
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ03 | Any | Cap-Tons | 285 | 0 | None | 40.7 | 0.0254 | 0 | 40.7 | 0.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.623
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ03 | Any | Cap-Tons | 17.3 | 0 | None | 43.6 | 0.0267 | 0 | 43.6 | 0.0267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.301
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ03 | Any | Cap-Tons | 174 | 0 | None | 44.2 | 0.0477 | 0 | 44.2 | 0.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.305
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ04 | Any | Cap-Tons | 542 | 0 | None | 63.9 | 0.0732 | 0 | 63.9 | 0.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ04 | Any | Cap-Tons | 281 | 0 | None | 42.8 | 0.0407 | 0 | 42.8 | 0.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ04 | Any | Cap-Tons | 1880 | 0 | None | 55.3 | 0.063 | 0 | 55.3 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ04 | Any | Cap-Tons | 816 | 0 | None | 36.1 | 0.0258 | 0 | 36.1 | 0.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ04 | Any | Cap-Tons | 163 | 0 | None | 87.6 | 0.0578 | 0 | 87.6 | 0.0578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.093
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ04 | Any | Cap-Tons | 277 | 0 | None | 61.2 | 0.0426 | 0 | 61.2 | 0.0426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.199
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ04 | Any | Cap-Tons | 95.5 | 0 | None | 64.3 | 0.0592 | 0 | 64.3 | 0.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ04 | Any | Cap-Tons | 351 | 0 | None | 58.3 | 0.0289 | 0 | 58.3 | 0.0289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.903
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ04 | Any | Cap-Tons | 20.9 | 0 | None | 64.8 | 0.0321 | 0 | 64.8 | 0.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.243
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ04 | Any | Cap-Tons | 222 | 0 | None | 71.4 | 0.0618 | 0 | 71.4 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.15
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ05 | Any | Cap-Tons | 360 | 0 | None | 48.8 | 0.0419 | 0 | 48.8 | 0.0419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ05 | Any | Cap-Tons | 180 | 0 | None | 34.9 | 0.0238 | 0 | 34.9 | 0.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ05 | Any | Cap-Tons | 1300 | 0 | None | 39.2 | 0.0347 | 0 | 39.2 | 0.0347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ05 | Any | Cap-Tons | 644 | 0 | None | 20.4 | 0.0141 | 0 | 20.4 | 0.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ05 | Any | Cap-Tons | 102 | 0 | None | 76.5 | 0.0344 | 0 | 76.5 | 0.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.041
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ05 | Any | Cap-Tons | 215 | 0 | None | 48.8 | 0.0245 | 0 | 48.8 | 0.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ05 | Any | Cap-Tons | 77.4 | 0 | None | 30.4 | 0.0256 | 0 | 30.4 | 0.0256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ05 | Any | Cap-Tons | 278 | 0 | None | 45.3 | 0.0185 | 0 | 45.3 | 0.0185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.074
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ05 | Any | Cap-Tons | 15.2 | 0 | None | 51.2 | 0.0193 | 0 | 51.2 | 0.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ05 | Any | Cap-Tons | 164 | 0 | None | 46.2 | 0.0313 | 0 | 46.2 | 0.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ06 | Any | Cap-Tons | 585 | 0 | None | 74.1 | 0.0618 | 0 | 74.1 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.228
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ06 | Any | Cap-Tons | 318 | 0 | None | 45.6 | 0.031 | 0 | 45.6 | 0.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.111
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ06 | Any | Cap-Tons | 1960 | 0 | None | 59.6 | 0.0539 | 0 | 59.6 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.228
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ06 | Any | Cap-Tons | 842 | 0 | None | 43.2 | 0.023 | 0 | 43.2 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.214
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ06 | Any | Cap-Tons | 154 | 0 | None | 100 | 0.0515 | 0 | 100 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.28
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ06 | Any | Cap-Tons | 298 | 0 | None | 74.4 | 0.0361 | 0 | 74.4 | 0.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.781
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ06 | Any | Cap-Tons | 102 | 0 | None | 67.7 | 0.0471 | 0 | 67.7 | 0.0471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.214
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ06 | Any | Cap-Tons | 369 | 0 | None | 71.1 | 0.0239 | 0 | 71.1 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.273
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ06 | Any | Cap-Tons | 21.8 | 0 | None | 75.7 | 0.0249 | 0 | 75.7 | 0.0249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.553
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ06 | Any | Cap-Tons | 233 | 0 | None | 81.3 | 0.0556 | 0 | 81.3 | 0.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.861
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ07 | Any | Cap-Tons | 550 | 0 | None | 73.9 | 0.0554 | 0 | 73.9 | 0.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.118
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ07 | Any | Cap-Tons | 303 | 0 | None | 44.3 | 0.0257 | 0 | 44.3 | 0.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ07 | Any | Cap-Tons | 1900 | 0 | None | 55.6 | 0.0457 | 0 | 55.6 | 0.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.118
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ07 | Any | Cap-Tons | 874 | 0 | None | 42.2 | 0.0179 | 0 | 42.2 | 0.0179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ07 | Any | Cap-Tons | 141 | 0 | None | 105 | 0.0421 | 0 | 105 | 0.0421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.323
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ07 | Any | Cap-Tons | 297 | 0 | None | 68.6 | 0.0295 | 0 | 68.6 | 0.0295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.286
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ07 | Any | Cap-Tons | 104 | 0 | None | 62.3 | 0.0339 | 0 | 62.3 | 0.0339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ07 | Any | Cap-Tons | 357 | 0 | None | 65.5 | 0.0207 | 0 | 65.5 | 0.0207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.734
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ07 | Any | Cap-Tons | 20.8 | 0 | None | 71.9 | 0.0213 | 0 | 71.9 | 0.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.336
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ07 | Any | Cap-Tons | 228 | 0 | None | 77.3 | 0.0475 | 0 | 77.3 | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.281
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ08 | Any | Cap-Tons | 641 | 0 | None | 80.6 | 0.0542 | 0 | 80.6 | 0.0542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ08 | Any | Cap-Tons | 344 | 0 | None | 53 | 0.0275 | 0 | 53 | 0.0275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.197
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ08 | Any | Cap-Tons | 2190 | 0 | None | 65.3 | 0.0468 | 0 | 65.3 | 0.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ08 | Any | Cap-Tons | 945 | 0 | None | 47.8 | 0.0196 | 0 | 47.8 | 0.0196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ08 | Any | Cap-Tons | 164 | 0 | None | 112 | 0.0477 | 0 | 112 | 0.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.195
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ08 | Any | Cap-Tons | 332 | 0 | None | 76.6 | 0.0312 | 0 | 76.6 | 0.0312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.142
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ08 | Any | Cap-Tons | 113 | 0 | None | 81.7 | 0.0438 | 0 | 81.7 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ08 | Any | Cap-Tons | 391 | 0 | None | 75.8 | 0.0217 | 0 | 75.8 | 0.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.712
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ08 | Any | Cap-Tons | 22.6 | 0 | None | 84.4 | 0.023 | 0 | 84.4 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.685
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ08 | Any | Cap-Tons | 254 | 0 | None | 91.3 | 0.0502 | 0 | 91.3 | 0.0502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.032
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ09 | Any | Cap-Tons | 772 | 0 | None | 74.7 | 0.0751 | 0 | 74.7 | 0.0751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.163
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ09 | Any | Cap-Tons | 409 | 0 | None | 50.5 | 0.0432 | 0 | 50.5 | 0.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.14
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ09 | Any | Cap-Tons | 2540 | 0 | None | 63 | 0.0654 | 0 | 63 | 0.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.163
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ09 | Any | Cap-Tons | 1080 | 0 | None | 47.5 | 0.0281 | 0 | 47.5 | 0.0281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.255
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ09 | Any | Cap-Tons | 216 | 0 | None | 100 | 0.0603 | 0 | 100 | 0.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.29
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ09 | Any | Cap-Tons | 364 | 0 | None | 74.8 | 0.0477 | 0 | 74.8 | 0.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.74
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ09 | Any | Cap-Tons | 129 | 0 | None | 82.2 | 0.0575 | 0 | 82.2 | 0.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.255
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ09 | Any | Cap-Tons | 458 | 0 | None | 68.2 | 0.0296 | 0 | 68.2 | 0.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.078
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ09 | Any | Cap-Tons | 27.1 | 0 | None | 77.5 | 0.0324 | 0 | 77.5 | 0.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.526
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ09 | Any | Cap-Tons | 312 | 0 | None | 82.2 | 0.0638 | 0 | 82.2 | 0.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.845
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ10 | Any | Cap-Tons | 687 | 0 | None | 85.3 | 0.0782 | 0 | 85.3 | 0.0782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ10 | Any | Cap-Tons | 360 | 0 | None | 59.4 | 0.0456 | 0 | 59.4 | 0.0456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.312
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ10 | Any | Cap-Tons | 2310 | 0 | None | 73.2 | 0.0684 | 0 | 73.2 | 0.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ10 | Any | Cap-Tons | 954 | 0 | None | 52.6 | 0.0296 | 0 | 52.6 | 0.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ10 | Any | Cap-Tons | 194 | 0 | None | 113 | 0.0651 | 0 | 113 | 0.0651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.145
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ10 | Any | Cap-Tons | 338 | 0 | None | 81.2 | 0.0465 | 0 | 81.2 | 0.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.607
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ10 | Any | Cap-Tons | 115 | 0 | None | 97.9 | 0.0669 | 0 | 97.9 | 0.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ10 | Any | Cap-Tons | 406 | 0 | None | 79.3 | 0.0318 | 0 | 79.3 | 0.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.227
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ10 | Any | Cap-Tons | 24.6 | 0 | None | 87 | 0.034 | 0 | 87 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.865
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ10 | Any | Cap-Tons | 273 | 0 | None | 97.4 | 0.0696 | 0 | 97.4 | 0.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.493
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ11 | Any | Cap-Tons | 635 | 0 | None | 90.7 | 0.0619 | 0 | 90.7 | 0.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.058
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ11 | Any | Cap-Tons | 330 | 0 | None | 59.9 | 0.025 | 0 | 59.9 | 0.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.044
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ11 | Any | Cap-Tons | 2120 | 0 | None | 82.5 | 0.0709 | 0 | 82.5 | 0.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.058
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ11 | Any | Cap-Tons | 967 | 0 | None | 55.2 | 0.0342 | 0 | 55.2 | 0.0342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ11 | Any | Cap-Tons | 202 | 0 | None | 118 | 0.0775 | 0 | 118 | 0.0775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.027
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ11 | Any | Cap-Tons | 346 | 0 | None | 76.7 | 0.0549 | 0 | 76.7 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ11 | Any | Cap-Tons | 118 | 0 | None | 109 | 0.0823 | 0 | 109 | 0.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ11 | Any | Cap-Tons | 409 | 0 | None | 76.4 | 0.0447 | 0 | 76.4 | 0.0447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ11 | Any | Cap-Tons | 25 | 0 | None | 84.4 | 0.0489 | 0 | 84.4 | 0.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ11 | Any | Cap-Tons | 275 | 0 | None | 93.1 | 0.0694 | 0 | 93.1 | 0.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ12 | Any | Cap-Tons | 576 | 0 | None | 77.9 | 0.0626 | 0 | 77.9 | 0.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.08
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ12 | Any | Cap-Tons | 301 | 0 | None | 51.5 | 0.0239 | 0 | 51.5 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.134
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ12 | Any | Cap-Tons | 1980 | 0 | None | 68.8 | 0.0694 | 0 | 68.8 | 0.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.08
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ12 | Any | Cap-Tons | 912 | 0 | None | 43.2 | 0.0328 | 0 | 43.2 | 0.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ12 | Any | Cap-Tons | 183 | 0 | None | 101 | 0.0794 | 0 | 101 | 0.0794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.105
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ12 | Any | Cap-Tons | 323 | 0 | None | 64.7 | 0.0531 | 0 | 64.7 | 0.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.26
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ12 | Any | Cap-Tons | 110 | 0 | None | 82.4 | 0.0794 | 0 | 82.4 | 0.0794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ12 | Any | Cap-Tons | 386 | 0 | None | 64.4 | 0.0422 | 0 | 64.4 | 0.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.847
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ12 | Any | Cap-Tons | 23.4 | 0 | None | 71.1 | 0.0468 | 0 | 71.1 | 0.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.312
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ12 | Any | Cap-Tons | 263 | 0 | None | 78.7 | 0.0707 | 0 | 78.7 | 0.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.309
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ13 | Any | Cap-Tons | 678 | 0 | None | 90.1 | 0.0508 | 0 | 90.1 | 0.0508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.144
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ13 | Any | Cap-Tons | 362 | 0 | None | 60.4 | 0.0183 | 0 | 60.4 | 0.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ13 | Any | Cap-Tons | 2260 | 0 | None | 81.2 | 0.0597 | 0 | 81.2 | 0.0597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.144
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ13 | Any | Cap-Tons | 978 | 0 | None | 56.7 | 0.03 | 0 | 56.7 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ13 | Any | Cap-Tons | 202 | 0 | None | 122 | 0.0687 | 0 | 122 | 0.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.074
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ13 | Any | Cap-Tons | 352 | 0 | None | 78.2 | 0.0488 | 0 | 78.2 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.304
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ13 | Any | Cap-Tons | 118 | 0 | None | 115 | 0.0731 | 0 | 115 | 0.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ13 | Any | Cap-Tons | 401 | 0 | None | 79.9 | 0.036 | 0 | 79.9 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.447
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ13 | Any | Cap-Tons | 25.3 | 0 | None | 84.7 | 0.0372 | 0 | 84.7 | 0.0372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.384
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ13 | Any | Cap-Tons | 283 | 0 | None | 95 | 0.0669 | 0 | 95 | 0.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.365
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ14 | Any | Cap-Tons | 732 | 0 | None | 82.3 | 0.0634 | 0 | 82.3 | 0.0634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ14 | Any | Cap-Tons | 396 | 0 | None | 54.8 | 0.0351 | 0 | 54.8 | 0.0351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.065
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ14 | Any | Cap-Tons | 2410 | 0 | None | 75.8 | 0.0587 | 0 | 75.8 | 0.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ14 | Any | Cap-Tons | 1040 | 0 | None | 52.2 | 0.0256 | 0 | 52.2 | 0.0256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ14 | Any | Cap-Tons | 207 | 0 | None | 117 | 0.0585 | 0 | 117 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.052
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ14 | Any | Cap-Tons | 366 | 0 | None | 75.5 | 0.0423 | 0 | 75.5 | 0.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.248
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ14 | Any | Cap-Tons | 121 | 0 | None | 110 | 0.0641 | 0 | 110 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ14 | Any | Cap-Tons | 419 | 0 | None | 78.5 | 0.0338 | 0 | 78.5 | 0.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.194
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ14 | Any | Cap-Tons | 26.7 | 0 | None | 83.1 | 0.0329 | 0 | 83.1 | 0.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ14 | Any | Cap-Tons | 285 | 0 | None | 91.5 | 0.0557 | 0 | 91.5 | 0.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.217
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ15 | Any | Cap-Tons | 960 | 0 | None | 126 | 0.0663 | 0 | 126 | 0.0663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ15 | Any | Cap-Tons | 512 | 0 | None | 90.9 | 0.0392 | 0 | 90.9 | 0.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.027
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ15 | Any | Cap-Tons | 3090 | 0 | None | 115 | 0.0621 | 0 | 115 | 0.0621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ15 | Any | Cap-Tons | 1230 | 0 | None | 88.8 | 0.0291 | 0 | 88.8 | 0.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ15 | Any | Cap-Tons | 270 | 0 | None | 170 | 0.0611 | 0 | 170 | 0.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.278
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ15 | Any | Cap-Tons | 452 | 0 | None | 118 | 0.0459 | 0 | 118 | 0.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.533
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ15 | Any | Cap-Tons | 156 | 0 | None | 177 | 0.0673 | 0 | 177 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ15 | Any | Cap-Tons | 518 | 0 | None | 116 | 0.0333 | 0 | 116 | 0.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.291
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ15 | Any | Cap-Tons | 31.9 | 0 | None | 131 | 0.0356 | 0 | 131 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.217
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ15 | Any | Cap-Tons | 359 | 0 | None | 141 | 0.062 | 0 | 141 | 0.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.195
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ16 | Any | Cap-Tons | 376 | 0 | None | 55.2 | 0.0464 | 0 | 55.2 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.139
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ16 | Any | Cap-Tons | 199 | 0 | None | 34.2 | 0.0217 | 0 | 34.2 | 0.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ16 | Any | Cap-Tons | 1330 | 0 | None | 48.7 | 0.0515 | 0 | 48.7 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.139
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ16 | Any | Cap-Tons | 656 | 0 | None | 30.8 | 0.0239 | 0 | 30.8 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ16 | Any | Cap-Tons | 116 | 0 | None | 91.1 | 0.0646 | 0 | 91.1 | 0.0646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.069
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ16 | Any | Cap-Tons | 223 | 0 | None | 46 | 0.0386 | 0 | 46 | 0.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.169
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ16 | Any | Cap-Tons | 78.6 | 0 | None | 55.3 | 0.0545 | 0 | 55.3 | 0.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ16 | Any | Cap-Tons | 292 | 0 | None | 47 | 0.0343 | 0 | 47 | 0.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.095
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ16 | Any | Cap-Tons | 16.8 | 0 | None | 52 | 0.0366 | 0 | 52 | 0.0366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.061
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ16 | Any | Cap-Tons | 176 | 0 | None | 54.6 | 0.0528 | 0 | 54.6 | 0.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.05
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ01 | Any | Cap-Tons | 298 | 0 | None | 27.6 | 0.0733 | 0 | 27.6 | 0.0733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ01 | Any | Cap-Tons | 145 | 0 | None | 18 | 0.0333 | 0 | 18 | 0.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ01 | Any | Cap-Tons | 1120 | 0 | None | 22.8 | 0.0547 | 0 | 22.8 | 0.0547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ01 | Any | Cap-Tons | 528 | 0 | None | 8.6 | 0.0188 | 0 | 8.6 | 0.0188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.006
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ01 | Any | Cap-Tons | 88.3 | 0 | None | 73.7 | 0.0463 | 0 | 73.7 | 0.0463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ01 | Any | Cap-Tons | 170 | 0 | None | 32.8 | 0.0369 | 0 | 32.8 | 0.0369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ01 | Any | Cap-Tons | 61.8 | 0 | None | 10.5 | 0.0296 | 0 | 10.5 | 0.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.006
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ01 | Any | Cap-Tons | 243 | 0 | None | 25.8 | 0.0246 | 0 | 25.8 | 0.0246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.012
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ01 | Any | Cap-Tons | 13.4 | 0 | None | 29.8 | 0.0252 | 0 | 29.8 | 0.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.018
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ01 | Any | Cap-Tons | 125 | 0 | None | 28.4 | 0.0529 | 0 | 28.4 | 0.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ02 | Any | Cap-Tons | 549 | 0 | None | 103 | 0.0948 | 0 | 103 | 0.0948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.038
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ02 | Any | Cap-Tons | 282 | 0 | None | 70 | 0.0389 | 0 | 70 | 0.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ02 | Any | Cap-Tons | 1920 | 0 | None | 91.5 | 0.104 | 0 | 91.5 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.038
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ02 | Any | Cap-Tons | 849 | 0 | None | 55.1 | 0.0532 | 0 | 55.1 | 0.0532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ02 | Any | Cap-Tons | 156 | 0 | None | 152 | 0.131 | 0 | 152 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.042
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ02 | Any | Cap-Tons | 285 | 0 | None | 98.1 | 0.0872 | 0 | 98.1 | 0.0872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ02 | Any | Cap-Tons | 100 | 0 | None | 100 | 0.121 | 0 | 100 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ02 | Any | Cap-Tons | 362 | 0 | None | 93.8 | 0.0675 | 0 | 93.8 | 0.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.178
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ02 | Any | Cap-Tons | 20.4 | 0 | None | 109 | 0.0775 | 0 | 109 | 0.0775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.05
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ02 | Any | Cap-Tons | 222 | 0 | None | 120 | 0.125 | 0 | 120 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ03 | Any | Cap-Tons | 421 | 0 | None | 78.3 | 0.056 | 0 | 78.3 | 0.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.143
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ03 | Any | Cap-Tons | 214 | 0 | None | 49.8 | 0.0112 | 0 | 49.8 | 0.0112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.078
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ03 | Any | Cap-Tons | 1490 | 0 | None | 64 | 0.0618 | 0 | 64 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.143
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ03 | Any | Cap-Tons | 582 | 0 | None | 42 | 0.0388 | 0 | 42 | 0.0388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.146
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ03 | Any | Cap-Tons | 121 | 0 | None | 124 | 0.0856 | 0 | 124 | 0.0856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.125
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ03 | Any | Cap-Tons | 221 | 0 | None | 82.6 | 0.0584 | 0 | 82.6 | 0.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.261
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ03 | Any | Cap-Tons | 77.9 | 0 | None | 57.3 | 0.0735 | 0 | 57.3 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.146
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ03 | Any | Cap-Tons | 285 | 0 | None | 74.6 | 0.0465 | 0 | 74.6 | 0.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.623
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ03 | Any | Cap-Tons | 17.3 | 0 | None | 80.1 | 0.049 | 0 | 80.1 | 0.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.301
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ03 | Any | Cap-Tons | 174 | 0 | None | 81.1 | 0.0876 | 0 | 81.1 | 0.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.305
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ04 | Any | Cap-Tons | 542 | 0 | None | 117 | 0.134 | 0 | 117 | 0.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ04 | Any | Cap-Tons | 281 | 0 | None | 78.5 | 0.0746 | 0 | 78.5 | 0.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ04 | Any | Cap-Tons | 1880 | 0 | None | 101 | 0.115 | 0 | 101 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ04 | Any | Cap-Tons | 816 | 0 | None | 66.3 | 0.0473 | 0 | 66.3 | 0.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ04 | Any | Cap-Tons | 163 | 0 | None | 161 | 0.106 | 0 | 161 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.093
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ04 | Any | Cap-Tons | 277 | 0 | None | 112 | 0.0782 | 0 | 112 | 0.0782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.199
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ04 | Any | Cap-Tons | 95.5 | 0 | None | 118 | 0.109 | 0 | 118 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ04 | Any | Cap-Tons | 351 | 0 | None | 107 | 0.0531 | 0 | 107 | 0.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.903
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ04 | Any | Cap-Tons | 20.9 | 0 | None | 119 | 0.0589 | 0 | 119 | 0.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.243
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ04 | Any | Cap-Tons | 222 | 0 | None | 131 | 0.113 | 0 | 131 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.15
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ05 | Any | Cap-Tons | 360 | 0 | None | 89.5 | 0.0768 | 0 | 89.5 | 0.0768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ05 | Any | Cap-Tons | 180 | 0 | None | 64.1 | 0.0437 | 0 | 64.1 | 0.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ05 | Any | Cap-Tons | 1300 | 0 | None | 71.9 | 0.0637 | 0 | 71.9 | 0.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ05 | Any | Cap-Tons | 644 | 0 | None | 37.5 | 0.0258 | 0 | 37.5 | 0.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ05 | Any | Cap-Tons | 102 | 0 | None | 140 | 0.063 | 0 | 140 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.041
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ05 | Any | Cap-Tons | 215 | 0 | None | 89.6 | 0.045 | 0 | 89.6 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ05 | Any | Cap-Tons | 77.4 | 0 | None | 55.7 | 0.0469 | 0 | 55.7 | 0.0469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ05 | Any | Cap-Tons | 278 | 0 | None | 83.2 | 0.0339 | 0 | 83.2 | 0.0339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.074
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ05 | Any | Cap-Tons | 15.2 | 0 | None | 93.9 | 0.0353 | 0 | 93.9 | 0.0353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ05 | Any | Cap-Tons | 164 | 0 | None | 84.8 | 0.0575 | 0 | 84.8 | 0.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ06 | Any | Cap-Tons | 585 | 0 | None | 136 | 0.113 | 0 | 136 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.228
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ06 | Any | Cap-Tons | 318 | 0 | None | 83.6 | 0.0569 | 0 | 83.6 | 0.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.111
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ06 | Any | Cap-Tons | 1960 | 0 | None | 109 | 0.0989 | 0 | 109 | 0.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.228
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ06 | Any | Cap-Tons | 842 | 0 | None | 79.3 | 0.0422 | 0 | 79.3 | 0.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.214
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ06 | Any | Cap-Tons | 154 | 0 | None | 183 | 0.0945 | 0 | 183 | 0.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.28
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ06 | Any | Cap-Tons | 298 | 0 | None | 136 | 0.0662 | 0 | 136 | 0.0662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.781
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ06 | Any | Cap-Tons | 102 | 0 | None | 124 | 0.0864 | 0 | 124 | 0.0864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.214
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ06 | Any | Cap-Tons | 369 | 0 | None | 130 | 0.0438 | 0 | 130 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.273
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ06 | Any | Cap-Tons | 21.8 | 0 | None | 139 | 0.0457 | 0 | 139 | 0.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.553
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ06 | Any | Cap-Tons | 233 | 0 | None | 149 | 0.102 | 0 | 149 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.861
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ07 | Any | Cap-Tons | 550 | 0 | None | 136 | 0.102 | 0 | 136 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.118
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ07 | Any | Cap-Tons | 303 | 0 | None | 81.3 | 0.0472 | 0 | 81.3 | 0.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ07 | Any | Cap-Tons | 1900 | 0 | None | 102 | 0.0839 | 0 | 102 | 0.0839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.118
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ07 | Any | Cap-Tons | 874 | 0 | None | 77.4 | 0.0328 | 0 | 77.4 | 0.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ07 | Any | Cap-Tons | 141 | 0 | None | 193 | 0.0772 | 0 | 193 | 0.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.323
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ07 | Any | Cap-Tons | 297 | 0 | None | 126 | 0.0541 | 0 | 126 | 0.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.286
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ07 | Any | Cap-Tons | 104 | 0 | None | 114 | 0.0622 | 0 | 114 | 0.0622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ07 | Any | Cap-Tons | 357 | 0 | None | 120 | 0.038 | 0 | 120 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.734
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ07 | Any | Cap-Tons | 20.8 | 0 | None | 132 | 0.0391 | 0 | 132 | 0.0391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.336
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ07 | Any | Cap-Tons | 228 | 0 | None | 142 | 0.0872 | 0 | 142 | 0.0872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.281
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ08 | Any | Cap-Tons | 641 | 0 | None | 148 | 0.0995 | 0 | 148 | 0.0995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ08 | Any | Cap-Tons | 344 | 0 | None | 97.2 | 0.0504 | 0 | 97.2 | 0.0504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.197
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ08 | Any | Cap-Tons | 2190 | 0 | None | 120 | 0.0859 | 0 | 120 | 0.0859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ08 | Any | Cap-Tons | 945 | 0 | None | 87.7 | 0.036 | 0 | 87.7 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ08 | Any | Cap-Tons | 164 | 0 | None | 206 | 0.0876 | 0 | 206 | 0.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.195
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ08 | Any | Cap-Tons | 332 | 0 | None | 141 | 0.0572 | 0 | 141 | 0.0572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.142
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ08 | Any | Cap-Tons | 113 | 0 | None | 150 | 0.0803 | 0 | 150 | 0.0803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ08 | Any | Cap-Tons | 391 | 0 | None | 139 | 0.0398 | 0 | 139 | 0.0398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.712
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ08 | Any | Cap-Tons | 22.6 | 0 | None | 155 | 0.0422 | 0 | 155 | 0.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.685
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ08 | Any | Cap-Tons | 254 | 0 | None | 167 | 0.092 | 0 | 167 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.032
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ09 | Any | Cap-Tons | 772 | 0 | None | 137 | 0.138 | 0 | 137 | 0.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.163
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ09 | Any | Cap-Tons | 409 | 0 | None | 92.6 | 0.0793 | 0 | 92.6 | 0.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.14
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ09 | Any | Cap-Tons | 2540 | 0 | None | 116 | 0.12 | 0 | 116 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.163
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ09 | Any | Cap-Tons | 1080 | 0 | None | 87.2 | 0.0515 | 0 | 87.2 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.255
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ09 | Any | Cap-Tons | 216 | 0 | None | 183 | 0.111 | 0 | 183 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.29
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ09 | Any | Cap-Tons | 364 | 0 | None | 137 | 0.0876 | 0 | 137 | 0.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.74
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ09 | Any | Cap-Tons | 129 | 0 | None | 151 | 0.106 | 0 | 151 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.255
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ09 | Any | Cap-Tons | 458 | 0 | None | 125 | 0.0542 | 0 | 125 | 0.0542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.078
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ09 | Any | Cap-Tons | 27.1 | 0 | None | 142 | 0.0594 | 0 | 142 | 0.0594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.526
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ09 | Any | Cap-Tons | 312 | 0 | None | 151 | 0.117 | 0 | 151 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.845
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ10 | Any | Cap-Tons | 687 | 0 | None | 156 | 0.143 | 0 | 156 | 0.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ10 | Any | Cap-Tons | 360 | 0 | None | 109 | 0.0836 | 0 | 109 | 0.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.312
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ10 | Any | Cap-Tons | 2310 | 0 | None | 134 | 0.125 | 0 | 134 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ10 | Any | Cap-Tons | 954 | 0 | None | 96.6 | 0.0543 | 0 | 96.6 | 0.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ10 | Any | Cap-Tons | 194 | 0 | None | 208 | 0.119 | 0 | 208 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.145
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ10 | Any | Cap-Tons | 338 | 0 | None | 149 | 0.0853 | 0 | 149 | 0.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.607
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ10 | Any | Cap-Tons | 115 | 0 | None | 180 | 0.123 | 0 | 180 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ10 | Any | Cap-Tons | 406 | 0 | None | 146 | 0.0584 | 0 | 146 | 0.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.227
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ10 | Any | Cap-Tons | 24.6 | 0 | None | 160 | 0.0624 | 0 | 160 | 0.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.865
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ10 | Any | Cap-Tons | 273 | 0 | None | 179 | 0.128 | 0 | 179 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.493
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ11 | Any | Cap-Tons | 635 | 0 | None | 166 | 0.114 | 0 | 166 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.058
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ11 | Any | Cap-Tons | 330 | 0 | None | 110 | 0.0458 | 0 | 110 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.044
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ11 | Any | Cap-Tons | 2120 | 0 | None | 151 | 0.13 | 0 | 151 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.058
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ11 | Any | Cap-Tons | 967 | 0 | None | 101 | 0.0627 | 0 | 101 | 0.0627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ11 | Any | Cap-Tons | 202 | 0 | None | 217 | 0.142 | 0 | 217 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.027
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ11 | Any | Cap-Tons | 346 | 0 | None | 141 | 0.101 | 0 | 141 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ11 | Any | Cap-Tons | 118 | 0 | None | 201 | 0.151 | 0 | 201 | 0.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ11 | Any | Cap-Tons | 409 | 0 | None | 140 | 0.082 | 0 | 140 | 0.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ11 | Any | Cap-Tons | 25 | 0 | None | 155 | 0.0898 | 0 | 155 | 0.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ11 | Any | Cap-Tons | 275 | 0 | None | 171 | 0.127 | 0 | 171 | 0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ12 | Any | Cap-Tons | 576 | 0 | None | 143 | 0.115 | 0 | 143 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.08
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ12 | Any | Cap-Tons | 301 | 0 | None | 94.5 | 0.0439 | 0 | 94.5 | 0.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.134
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ12 | Any | Cap-Tons | 1980 | 0 | None | 126 | 0.127 | 0 | 126 | 0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.08
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ12 | Any | Cap-Tons | 912 | 0 | None | 79.2 | 0.0602 | 0 | 79.2 | 0.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ12 | Any | Cap-Tons | 183 | 0 | None | 184 | 0.146 | 0 | 184 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.105
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ12 | Any | Cap-Tons | 323 | 0 | None | 119 | 0.0975 | 0 | 119 | 0.0975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.26
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ12 | Any | Cap-Tons | 110 | 0 | None | 151 | 0.146 | 0 | 151 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ12 | Any | Cap-Tons | 386 | 0 | None | 118 | 0.0774 | 0 | 118 | 0.0774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.847
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ12 | Any | Cap-Tons | 23.4 | 0 | None | 131 | 0.0859 | 0 | 131 | 0.0859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.312
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ12 | Any | Cap-Tons | 263 | 0 | None | 144 | 0.13 | 0 | 144 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.309
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ13 | Any | Cap-Tons | 678 | 0 | None | 165 | 0.0932 | 0 | 165 | 0.0932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.144
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ13 | Any | Cap-Tons | 362 | 0 | None | 111 | 0.0336 | 0 | 111 | 0.0336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ13 | Any | Cap-Tons | 2260 | 0 | None | 149 | 0.109 | 0 | 149 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.144
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ13 | Any | Cap-Tons | 978 | 0 | None | 104 | 0.055 | 0 | 104 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ13 | Any | Cap-Tons | 202 | 0 | None | 225 | 0.126 | 0 | 225 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.074
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ13 | Any | Cap-Tons | 352 | 0 | None | 143 | 0.0896 | 0 | 143 | 0.0896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.304
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ13 | Any | Cap-Tons | 118 | 0 | None | 211 | 0.134 | 0 | 211 | 0.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ13 | Any | Cap-Tons | 401 | 0 | None | 147 | 0.066 | 0 | 147 | 0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.447
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ13 | Any | Cap-Tons | 25.3 | 0 | None | 155 | 0.0682 | 0 | 155 | 0.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.384
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ13 | Any | Cap-Tons | 283 | 0 | None | 174 | 0.123 | 0 | 174 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.365
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ14 | Any | Cap-Tons | 732 | 0 | None | 151 | 0.116 | 0 | 151 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ14 | Any | Cap-Tons | 396 | 0 | None | 101 | 0.0645 | 0 | 101 | 0.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.065
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ14 | Any | Cap-Tons | 2410 | 0 | None | 139 | 0.108 | 0 | 139 | 0.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ14 | Any | Cap-Tons | 1040 | 0 | None | 95.8 | 0.047 | 0 | 95.8 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ14 | Any | Cap-Tons | 207 | 0 | None | 215 | 0.107 | 0 | 215 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.052
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ14 | Any | Cap-Tons | 366 | 0 | None | 139 | 0.0777 | 0 | 139 | 0.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.248
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ14 | Any | Cap-Tons | 121 | 0 | None | 201 | 0.118 | 0 | 201 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ14 | Any | Cap-Tons | 419 | 0 | None | 144 | 0.0621 | 0 | 144 | 0.0621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.194
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ14 | Any | Cap-Tons | 26.7 | 0 | None | 152 | 0.0604 | 0 | 152 | 0.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ14 | Any | Cap-Tons | 285 | 0 | None | 168 | 0.102 | 0 | 168 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.217
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ15 | Any | Cap-Tons | 960 | 0 | None | 232 | 0.122 | 0 | 232 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ15 | Any | Cap-Tons | 512 | 0 | None | 167 | 0.072 | 0 | 167 | 0.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.027
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ15 | Any | Cap-Tons | 3090 | 0 | None | 211 | 0.114 | 0 | 211 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ15 | Any | Cap-Tons | 1230 | 0 | None | 163 | 0.0535 | 0 | 163 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ15 | Any | Cap-Tons | 270 | 0 | None | 312 | 0.112 | 0 | 312 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.278
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ15 | Any | Cap-Tons | 452 | 0 | None | 216 | 0.0843 | 0 | 216 | 0.0843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.533
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ15 | Any | Cap-Tons | 156 | 0 | None | 325 | 0.124 | 0 | 325 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ15 | Any | Cap-Tons | 518 | 0 | None | 214 | 0.061 | 0 | 214 | 0.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.291
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ15 | Any | Cap-Tons | 31.9 | 0 | None | 240 | 0.0654 | 0 | 240 | 0.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.217
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ15 | Any | Cap-Tons | 359 | 0 | None | 258 | 0.114 | 0 | 258 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.195
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ16 | Any | Cap-Tons | 376 | 0 | None | 101 | 0.0851 | 0 | 101 | 0.0851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.139
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ16 | Any | Cap-Tons | 199 | 0 | None | 62.8 | 0.0399 | 0 | 62.8 | 0.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ16 | Any | Cap-Tons | 1330 | 0 | None | 89.3 | 0.0945 | 0 | 89.3 | 0.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.139
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ16 | Any | Cap-Tons | 656 | 0 | None | 56.5 | 0.0439 | 0 | 56.5 | 0.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ16 | Any | Cap-Tons | 116 | 0 | None | 167 | 0.118 | 0 | 167 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.069
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ16 | Any | Cap-Tons | 223 | 0 | None | 84.4 | 0.0708 | 0 | 84.4 | 0.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.169
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ16 | Any | Cap-Tons | 78.6 | 0 | None | 101 | 0.1 | 0 | 101 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ16 | Any | Cap-Tons | 292 | 0 | None | 86.3 | 0.063 | 0 | 86.3 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.095
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ16 | Any | Cap-Tons | 16.8 | 0 | None | 95.5 | 0.0671 | 0 | 95.5 | 0.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.061
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ16 | Any | Cap-Tons | 176 | 0 | None | 100 | 0.0969 | 0 | 100 | 0.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.05
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ01 | Any | Cap-Tons | 298 | 0 | None | 15 | 0.0399 | 0 | 15 | 0.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ01 | Any | Cap-Tons | 145 | 0 | None | 9.8 | 0.0181 | 0 | 9.8 | 0.0181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ01 | Any | Cap-Tons | 1120 | 0 | None | 12.4 | 0.0298 | 0 | 12.4 | 0.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ01 | Any | Cap-Tons | 528 | 0 | None | 4.7 | 0.0102 | 0 | 4.7 | 0.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.006
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ01 | Any | Cap-Tons | 88.3 | 0 | None | 40.2 | 0.0252 | 0 | 40.2 | 0.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ01 | Any | Cap-Tons | 170 | 0 | None | 17.9 | 0.0201 | 0 | 17.9 | 0.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ01 | Any | Cap-Tons | 61.8 | 0 | None | 5.7 | 0.0161 | 0 | 5.7 | 0.0161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.006
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ01 | Any | Cap-Tons | 243 | 0 | None | 14.1 | 0.0134 | 0 | 14.1 | 0.0134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.012
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ01 | Any | Cap-Tons | 13.4 | 0 | None | 16.2 | 0.0137 | 0 | 16.2 | 0.0137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.018
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ01 | Any | Cap-Tons | 125 | 0 | None | 15.5 | 0.0288 | 0 | 15.5 | 0.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ02 | Any | Cap-Tons | 549 | 0 | None | 56.3 | 0.0517 | 0 | 56.3 | 0.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.038
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ02 | Any | Cap-Tons | 282 | 0 | None | 38.2 | 0.0212 | 0 | 38.2 | 0.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ02 | Any | Cap-Tons | 1920 | 0 | None | 49.9 | 0.0569 | 0 | 49.9 | 0.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.038
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ02 | Any | Cap-Tons | 849 | 0 | None | 30 | 0.029 | 0 | 30 | 0.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ02 | Any | Cap-Tons | 156 | 0 | None | 83 | 0.0716 | 0 | 83 | 0.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.042
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ02 | Any | Cap-Tons | 285 | 0 | None | 53.5 | 0.0475 | 0 | 53.5 | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ02 | Any | Cap-Tons | 100 | 0 | None | 54.5 | 0.0659 | 0 | 54.5 | 0.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ02 | Any | Cap-Tons | 362 | 0 | None | 51.1 | 0.0368 | 0 | 51.1 | 0.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.178
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ02 | Any | Cap-Tons | 20.4 | 0 | None | 59.3 | 0.0422 | 0 | 59.3 | 0.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.05
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ02 | Any | Cap-Tons | 222 | 0 | None | 65.2 | 0.0682 | 0 | 65.2 | 0.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ03 | Any | Cap-Tons | 421 | 0 | None | 42.7 | 0.0305 | 0 | 42.7 | 0.0305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.143
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ03 | Any | Cap-Tons | 214 | 0 | None | 27.1 | 0.0061 | 0 | 27.1 | 0.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.078
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ03 | Any | Cap-Tons | 1490 | 0 | None | 34.9 | 0.0337 | 0 | 34.9 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.143
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ03 | Any | Cap-Tons | 582 | 0 | None | 22.9 | 0.0212 | 0 | 22.9 | 0.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.146
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ03 | Any | Cap-Tons | 121 | 0 | None | 67.8 | 0.0466 | 0 | 67.8 | 0.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.125
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ03 | Any | Cap-Tons | 221 | 0 | None | 45 | 0.0319 | 0 | 45 | 0.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.261
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ03 | Any | Cap-Tons | 77.9 | 0 | None | 31.3 | 0.04 | 0 | 31.3 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.146
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ03 | Any | Cap-Tons | 285 | 0 | None | 40.7 | 0.0254 | 0 | 40.7 | 0.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.623
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ03 | Any | Cap-Tons | 17.3 | 0 | None | 43.6 | 0.0267 | 0 | 43.6 | 0.0267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.301
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ03 | Any | Cap-Tons | 174 | 0 | None | 44.2 | 0.0477 | 0 | 44.2 | 0.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.305
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ04 | Any | Cap-Tons | 542 | 0 | None | 63.9 | 0.0732 | 0 | 63.9 | 0.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ04 | Any | Cap-Tons | 281 | 0 | None | 42.8 | 0.0407 | 0 | 42.8 | 0.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ04 | Any | Cap-Tons | 1880 | 0 | None | 55.3 | 0.063 | 0 | 55.3 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ04 | Any | Cap-Tons | 816 | 0 | None | 36.1 | 0.0258 | 0 | 36.1 | 0.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ04 | Any | Cap-Tons | 163 | 0 | None | 87.6 | 0.0578 | 0 | 87.6 | 0.0578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.093
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ04 | Any | Cap-Tons | 277 | 0 | None | 61.2 | 0.0426 | 0 | 61.2 | 0.0426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.199
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ04 | Any | Cap-Tons | 95.5 | 0 | None | 64.3 | 0.0592 | 0 | 64.3 | 0.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ04 | Any | Cap-Tons | 351 | 0 | None | 58.3 | 0.0289 | 0 | 58.3 | 0.0289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.903
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ04 | Any | Cap-Tons | 20.9 | 0 | None | 64.8 | 0.0321 | 0 | 64.8 | 0.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.243
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ04 | Any | Cap-Tons | 222 | 0 | None | 71.4 | 0.0618 | 0 | 71.4 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.15
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ05 | Any | Cap-Tons | 360 | 0 | None | 48.8 | 0.0419 | 0 | 48.8 | 0.0419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ05 | Any | Cap-Tons | 180 | 0 | None | 34.9 | 0.0238 | 0 | 34.9 | 0.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ05 | Any | Cap-Tons | 1300 | 0 | None | 39.2 | 0.0347 | 0 | 39.2 | 0.0347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ05 | Any | Cap-Tons | 644 | 0 | None | 20.4 | 0.0141 | 0 | 20.4 | 0.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ05 | Any | Cap-Tons | 102 | 0 | None | 76.5 | 0.0344 | 0 | 76.5 | 0.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.041
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ05 | Any | Cap-Tons | 215 | 0 | None | 48.8 | 0.0245 | 0 | 48.8 | 0.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ05 | Any | Cap-Tons | 77.4 | 0 | None | 30.4 | 0.0256 | 0 | 30.4 | 0.0256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ05 | Any | Cap-Tons | 278 | 0 | None | 45.3 | 0.0185 | 0 | 45.3 | 0.0185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.074
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ05 | Any | Cap-Tons | 15.2 | 0 | None | 51.2 | 0.0193 | 0 | 51.2 | 0.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ05 | Any | Cap-Tons | 164 | 0 | None | 46.2 | 0.0313 | 0 | 46.2 | 0.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ06 | Any | Cap-Tons | 585 | 0 | None | 74.1 | 0.0618 | 0 | 74.1 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.228
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ06 | Any | Cap-Tons | 318 | 0 | None | 45.6 | 0.031 | 0 | 45.6 | 0.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.111
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ06 | Any | Cap-Tons | 1960 | 0 | None | 59.6 | 0.0539 | 0 | 59.6 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.228
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ06 | Any | Cap-Tons | 842 | 0 | None | 43.2 | 0.023 | 0 | 43.2 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.214
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ06 | Any | Cap-Tons | 154 | 0 | None | 100 | 0.0515 | 0 | 100 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.28
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ06 | Any | Cap-Tons | 298 | 0 | None | 74.4 | 0.0361 | 0 | 74.4 | 0.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.781
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ06 | Any | Cap-Tons | 102 | 0 | None | 67.7 | 0.0471 | 0 | 67.7 | 0.0471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.214
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ06 | Any | Cap-Tons | 369 | 0 | None | 71.1 | 0.0239 | 0 | 71.1 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.273
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ06 | Any | Cap-Tons | 21.8 | 0 | None | 75.7 | 0.0249 | 0 | 75.7 | 0.0249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.553
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ06 | Any | Cap-Tons | 233 | 0 | None | 81.3 | 0.0556 | 0 | 81.3 | 0.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.861
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ07 | Any | Cap-Tons | 550 | 0 | None | 73.9 | 0.0554 | 0 | 73.9 | 0.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.118
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ07 | Any | Cap-Tons | 303 | 0 | None | 44.3 | 0.0257 | 0 | 44.3 | 0.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ07 | Any | Cap-Tons | 1900 | 0 | None | 55.6 | 0.0457 | 0 | 55.6 | 0.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.118
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ07 | Any | Cap-Tons | 874 | 0 | None | 42.2 | 0.0179 | 0 | 42.2 | 0.0179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ07 | Any | Cap-Tons | 141 | 0 | None | 105 | 0.0421 | 0 | 105 | 0.0421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.323
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ07 | Any | Cap-Tons | 297 | 0 | None | 68.6 | 0.0295 | 0 | 68.6 | 0.0295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.286
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ07 | Any | Cap-Tons | 104 | 0 | None | 62.3 | 0.0339 | 0 | 62.3 | 0.0339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ07 | Any | Cap-Tons | 357 | 0 | None | 65.5 | 0.0207 | 0 | 65.5 | 0.0207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.734
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ07 | Any | Cap-Tons | 20.8 | 0 | None | 71.9 | 0.0213 | 0 | 71.9 | 0.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.336
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ07 | Any | Cap-Tons | 228 | 0 | None | 77.3 | 0.0475 | 0 | 77.3 | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.281
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ08 | Any | Cap-Tons | 641 | 0 | None | 80.6 | 0.0542 | 0 | 80.6 | 0.0542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ08 | Any | Cap-Tons | 344 | 0 | None | 53 | 0.0275 | 0 | 53 | 0.0275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.197
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ08 | Any | Cap-Tons | 2190 | 0 | None | 65.3 | 0.0468 | 0 | 65.3 | 0.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ08 | Any | Cap-Tons | 945 | 0 | None | 47.8 | 0.0196 | 0 | 47.8 | 0.0196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ08 | Any | Cap-Tons | 164 | 0 | None | 112 | 0.0477 | 0 | 112 | 0.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.195
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ08 | Any | Cap-Tons | 332 | 0 | None | 76.6 | 0.0312 | 0 | 76.6 | 0.0312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.142
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ08 | Any | Cap-Tons | 113 | 0 | None | 81.7 | 0.0438 | 0 | 81.7 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ08 | Any | Cap-Tons | 391 | 0 | None | 75.8 | 0.0217 | 0 | 75.8 | 0.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.712
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ08 | Any | Cap-Tons | 22.6 | 0 | None | 84.4 | 0.023 | 0 | 84.4 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.685
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ08 | Any | Cap-Tons | 254 | 0 | None | 91.3 | 0.0502 | 0 | 91.3 | 0.0502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.032
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ09 | Any | Cap-Tons | 772 | 0 | None | 74.7 | 0.0751 | 0 | 74.7 | 0.0751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.163
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ09 | Any | Cap-Tons | 409 | 0 | None | 50.5 | 0.0432 | 0 | 50.5 | 0.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.14
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ09 | Any | Cap-Tons | 2540 | 0 | None | 63 | 0.0654 | 0 | 63 | 0.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.163
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ09 | Any | Cap-Tons | 1080 | 0 | None | 47.5 | 0.0281 | 0 | 47.5 | 0.0281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.255
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ09 | Any | Cap-Tons | 216 | 0 | None | 100 | 0.0603 | 0 | 100 | 0.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.29
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ09 | Any | Cap-Tons | 364 | 0 | None | 74.8 | 0.0477 | 0 | 74.8 | 0.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.74
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ09 | Any | Cap-Tons | 129 | 0 | None | 82.2 | 0.0575 | 0 | 82.2 | 0.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.255
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ09 | Any | Cap-Tons | 458 | 0 | None | 68.2 | 0.0296 | 0 | 68.2 | 0.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.078
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ09 | Any | Cap-Tons | 27.1 | 0 | None | 77.5 | 0.0324 | 0 | 77.5 | 0.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.526
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ09 | Any | Cap-Tons | 312 | 0 | None | 82.2 | 0.0638 | 0 | 82.2 | 0.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.845
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ10 | Any | Cap-Tons | 687 | 0 | None | 85.3 | 0.0782 | 0 | 85.3 | 0.0782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ10 | Any | Cap-Tons | 360 | 0 | None | 59.4 | 0.0456 | 0 | 59.4 | 0.0456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.312
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ10 | Any | Cap-Tons | 2310 | 0 | None | 73.2 | 0.0684 | 0 | 73.2 | 0.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ10 | Any | Cap-Tons | 954 | 0 | None | 52.6 | 0.0296 | 0 | 52.6 | 0.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ10 | Any | Cap-Tons | 194 | 0 | None | 113 | 0.0651 | 0 | 113 | 0.0651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.145
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ10 | Any | Cap-Tons | 338 | 0 | None | 81.2 | 0.0465 | 0 | 81.2 | 0.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.607
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ10 | Any | Cap-Tons | 115 | 0 | None | 97.9 | 0.0669 | 0 | 97.9 | 0.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ10 | Any | Cap-Tons | 406 | 0 | None | 79.3 | 0.0318 | 0 | 79.3 | 0.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.227
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ10 | Any | Cap-Tons | 24.6 | 0 | None | 87 | 0.034 | 0 | 87 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.865
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ10 | Any | Cap-Tons | 273 | 0 | None | 97.4 | 0.0696 | 0 | 97.4 | 0.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.493
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ11 | Any | Cap-Tons | 635 | 0 | None | 90.7 | 0.0619 | 0 | 90.7 | 0.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.058
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ11 | Any | Cap-Tons | 330 | 0 | None | 59.9 | 0.025 | 0 | 59.9 | 0.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.044
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ11 | Any | Cap-Tons | 2120 | 0 | None | 82.5 | 0.0709 | 0 | 82.5 | 0.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.058
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ11 | Any | Cap-Tons | 967 | 0 | None | 55.2 | 0.0342 | 0 | 55.2 | 0.0342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ11 | Any | Cap-Tons | 202 | 0 | None | 118 | 0.0775 | 0 | 118 | 0.0775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.027
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ11 | Any | Cap-Tons | 346 | 0 | None | 76.7 | 0.0549 | 0 | 76.7 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ11 | Any | Cap-Tons | 118 | 0 | None | 109 | 0.0823 | 0 | 109 | 0.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ11 | Any | Cap-Tons | 409 | 0 | None | 76.4 | 0.0447 | 0 | 76.4 | 0.0447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ11 | Any | Cap-Tons | 25 | 0 | None | 84.4 | 0.0489 | 0 | 84.4 | 0.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ11 | Any | Cap-Tons | 275 | 0 | None | 93.1 | 0.0694 | 0 | 93.1 | 0.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ12 | Any | Cap-Tons | 576 | 0 | None | 77.9 | 0.0626 | 0 | 77.9 | 0.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.08
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ12 | Any | Cap-Tons | 301 | 0 | None | 51.5 | 0.0239 | 0 | 51.5 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.134
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ12 | Any | Cap-Tons | 1980 | 0 | None | 68.8 | 0.0694 | 0 | 68.8 | 0.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.08
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ12 | Any | Cap-Tons | 912 | 0 | None | 43.2 | 0.0328 | 0 | 43.2 | 0.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ12 | Any | Cap-Tons | 183 | 0 | None | 101 | 0.0794 | 0 | 101 | 0.0794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.105
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ12 | Any | Cap-Tons | 323 | 0 | None | 64.7 | 0.0531 | 0 | 64.7 | 0.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.26
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ12 | Any | Cap-Tons | 110 | 0 | None | 82.4 | 0.0794 | 0 | 82.4 | 0.0794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ12 | Any | Cap-Tons | 386 | 0 | None | 64.4 | 0.0422 | 0 | 64.4 | 0.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.847
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ12 | Any | Cap-Tons | 23.4 | 0 | None | 71.1 | 0.0468 | 0 | 71.1 | 0.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.312
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ12 | Any | Cap-Tons | 263 | 0 | None | 78.7 | 0.0707 | 0 | 78.7 | 0.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.309
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ13 | Any | Cap-Tons | 678 | 0 | None | 90.1 | 0.0508 | 0 | 90.1 | 0.0508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.144
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ13 | Any | Cap-Tons | 362 | 0 | None | 60.4 | 0.0183 | 0 | 60.4 | 0.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ13 | Any | Cap-Tons | 2260 | 0 | None | 81.2 | 0.0597 | 0 | 81.2 | 0.0597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.144
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ13 | Any | Cap-Tons | 978 | 0 | None | 56.7 | 0.03 | 0 | 56.7 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ13 | Any | Cap-Tons | 202 | 0 | None | 122 | 0.0687 | 0 | 122 | 0.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.074
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ13 | Any | Cap-Tons | 352 | 0 | None | 78.2 | 0.0488 | 0 | 78.2 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.304
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ13 | Any | Cap-Tons | 118 | 0 | None | 115 | 0.0731 | 0 | 115 | 0.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ13 | Any | Cap-Tons | 401 | 0 | None | 79.9 | 0.036 | 0 | 79.9 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.447
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ13 | Any | Cap-Tons | 25.3 | 0 | None | 84.7 | 0.0372 | 0 | 84.7 | 0.0372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.384
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ13 | Any | Cap-Tons | 283 | 0 | None | 95 | 0.0669 | 0 | 95 | 0.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.365
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ14 | Any | Cap-Tons | 732 | 0 | None | 82.3 | 0.0634 | 0 | 82.3 | 0.0634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ14 | Any | Cap-Tons | 396 | 0 | None | 54.8 | 0.0351 | 0 | 54.8 | 0.0351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.065
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ14 | Any | Cap-Tons | 2410 | 0 | None | 75.8 | 0.0587 | 0 | 75.8 | 0.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ14 | Any | Cap-Tons | 1040 | 0 | None | 52.2 | 0.0256 | 0 | 52.2 | 0.0256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ14 | Any | Cap-Tons | 207 | 0 | None | 117 | 0.0585 | 0 | 117 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.052
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ14 | Any | Cap-Tons | 366 | 0 | None | 75.5 | 0.0423 | 0 | 75.5 | 0.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.248
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ14 | Any | Cap-Tons | 121 | 0 | None | 110 | 0.0641 | 0 | 110 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ14 | Any | Cap-Tons | 419 | 0 | None | 78.5 | 0.0338 | 0 | 78.5 | 0.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.194
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ14 | Any | Cap-Tons | 26.7 | 0 | None | 83.1 | 0.0329 | 0 | 83.1 | 0.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ14 | Any | Cap-Tons | 285 | 0 | None | 91.5 | 0.0557 | 0 | 91.5 | 0.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.217
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ15 | Any | Cap-Tons | 960 | 0 | None | 126 | 0.0663 | 0 | 126 | 0.0663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ15 | Any | Cap-Tons | 512 | 0 | None | 90.9 | 0.0392 | 0 | 90.9 | 0.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.027
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ15 | Any | Cap-Tons | 3090 | 0 | None | 115 | 0.0621 | 0 | 115 | 0.0621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ15 | Any | Cap-Tons | 1230 | 0 | None | 88.8 | 0.0291 | 0 | 88.8 | 0.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ15 | Any | Cap-Tons | 270 | 0 | None | 170 | 0.0611 | 0 | 170 | 0.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.278
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ15 | Any | Cap-Tons | 452 | 0 | None | 118 | 0.0459 | 0 | 118 | 0.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.533
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ15 | Any | Cap-Tons | 156 | 0 | None | 177 | 0.0673 | 0 | 177 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ15 | Any | Cap-Tons | 518 | 0 | None | 116 | 0.0333 | 0 | 116 | 0.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.291
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ15 | Any | Cap-Tons | 31.9 | 0 | None | 131 | 0.0356 | 0 | 131 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.217
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ15 | Any | Cap-Tons | 359 | 0 | None | 141 | 0.062 | 0 | 141 | 0.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.195
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ16 | Any | Cap-Tons | 376 | 0 | None | 55.2 | 0.0464 | 0 | 55.2 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.139
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ16 | Any | Cap-Tons | 199 | 0 | None | 34.2 | 0.0217 | 0 | 34.2 | 0.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ16 | Any | Cap-Tons | 1330 | 0 | None | 48.7 | 0.0515 | 0 | 48.7 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.139
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ16 | Any | Cap-Tons | 656 | 0 | None | 30.8 | 0.0239 | 0 | 30.8 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ16 | Any | Cap-Tons | 116 | 0 | None | 91.1 | 0.0646 | 0 | 91.1 | 0.0646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.069
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ16 | Any | Cap-Tons | 223 | 0 | None | 46 | 0.0386 | 0 | 46 | 0.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.169
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ16 | Any | Cap-Tons | 78.6 | 0 | None | 55.3 | 0.0545 | 0 | 55.3 | 0.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ16 | Any | Cap-Tons | 292 | 0 | None | 47 | 0.0343 | 0 | 47 | 0.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.095
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ16 | Any | Cap-Tons | 16.8 | 0 | None | 52 | 0.0366 | 0 | 52 | 0.0366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.061
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ16 | Any | Cap-Tons | 176 | 0 | None | 54.6 | 0.0528 | 0 | 54.6 | 0.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.05
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ01 | Any | Cap-Tons | 298 | 0 | None | 27.6 | 0.0733 | 0 | 27.6 | 0.0733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ01 | Any | Cap-Tons | 145 | 0 | None | 18 | 0.0333 | 0 | 18 | 0.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ01 | Any | Cap-Tons | 1120 | 0 | None | 22.8 | 0.0547 | 0 | 22.8 | 0.0547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ01 | Any | Cap-Tons | 528 | 0 | None | 8.6 | 0.0188 | 0 | 8.6 | 0.0188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.006
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ01 | Any | Cap-Tons | 88.3 | 0 | None | 73.7 | 0.0463 | 0 | 73.7 | 0.0463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ01 | Any | Cap-Tons | 170 | 0 | None | 32.8 | 0.0369 | 0 | 32.8 | 0.0369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ01 | Any | Cap-Tons | 61.8 | 0 | None | 10.5 | 0.0296 | 0 | 10.5 | 0.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.006
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ01 | Any | Cap-Tons | 243 | 0 | None | 25.8 | 0.0246 | 0 | 25.8 | 0.0246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.012
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ01 | Any | Cap-Tons | 13.4 | 0 | None | 29.8 | 0.0252 | 0 | 29.8 | 0.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.018
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ01 | Any | Cap-Tons | 125 | 0 | None | 28.4 | 0.0529 | 0 | 28.4 | 0.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.01
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ02 | Any | Cap-Tons | 549 | 0 | None | 103 | 0.0948 | 0 | 103 | 0.0948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.038
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ02 | Any | Cap-Tons | 282 | 0 | None | 70 | 0.0389 | 0 | 70 | 0.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.026
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ02 | Any | Cap-Tons | 1920 | 0 | None | 91.5 | 0.104 | 0 | 91.5 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.038
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ02 | Any | Cap-Tons | 849 | 0 | None | 55.1 | 0.0532 | 0 | 55.1 | 0.0532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ02 | Any | Cap-Tons | 156 | 0 | None | 152 | 0.131 | 0 | 152 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.042
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ02 | Any | Cap-Tons | 285 | 0 | None | 98.1 | 0.0872 | 0 | 98.1 | 0.0872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ02 | Any | Cap-Tons | 100 | 0 | None | 100 | 0.121 | 0 | 100 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ02 | Any | Cap-Tons | 362 | 0 | None | 93.8 | 0.0675 | 0 | 93.8 | 0.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.178
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ02 | Any | Cap-Tons | 20.4 | 0 | None | 109 | 0.0775 | 0 | 109 | 0.0775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.05
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ02 | Any | Cap-Tons | 222 | 0 | None | 120 | 0.125 | 0 | 120 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ03 | Any | Cap-Tons | 421 | 0 | None | 78.3 | 0.056 | 0 | 78.3 | 0.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.143
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ03 | Any | Cap-Tons | 214 | 0 | None | 49.8 | 0.0112 | 0 | 49.8 | 0.0112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.078
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ03 | Any | Cap-Tons | 1490 | 0 | None | 64 | 0.0618 | 0 | 64 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.143
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ03 | Any | Cap-Tons | 582 | 0 | None | 42 | 0.0388 | 0 | 42 | 0.0388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.146
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ03 | Any | Cap-Tons | 121 | 0 | None | 124 | 0.0856 | 0 | 124 | 0.0856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.125
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ03 | Any | Cap-Tons | 221 | 0 | None | 82.6 | 0.0584 | 0 | 82.6 | 0.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.261
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ03 | Any | Cap-Tons | 77.9 | 0 | None | 57.3 | 0.0735 | 0 | 57.3 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.146
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ03 | Any | Cap-Tons | 285 | 0 | None | 74.6 | 0.0465 | 0 | 74.6 | 0.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.623
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ03 | Any | Cap-Tons | 17.3 | 0 | None | 80.1 | 0.049 | 0 | 80.1 | 0.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.301
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ03 | Any | Cap-Tons | 174 | 0 | None | 81.1 | 0.0876 | 0 | 81.1 | 0.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.305
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ04 | Any | Cap-Tons | 542 | 0 | None | 117 | 0.134 | 0 | 117 | 0.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ04 | Any | Cap-Tons | 281 | 0 | None | 78.5 | 0.0746 | 0 | 78.5 | 0.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.053
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ04 | Any | Cap-Tons | 1880 | 0 | None | 101 | 0.115 | 0 | 101 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ04 | Any | Cap-Tons | 816 | 0 | None | 66.3 | 0.0473 | 0 | 66.3 | 0.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ04 | Any | Cap-Tons | 163 | 0 | None | 161 | 0.106 | 0 | 161 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.093
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ04 | Any | Cap-Tons | 277 | 0 | None | 112 | 0.0782 | 0 | 112 | 0.0782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.199
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ04 | Any | Cap-Tons | 95.5 | 0 | None | 118 | 0.109 | 0 | 118 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ04 | Any | Cap-Tons | 351 | 0 | None | 107 | 0.0531 | 0 | 107 | 0.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.903
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ04 | Any | Cap-Tons | 20.9 | 0 | None | 119 | 0.0589 | 0 | 119 | 0.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.243
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ04 | Any | Cap-Tons | 222 | 0 | None | 131 | 0.113 | 0 | 131 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.15
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ05 | Any | Cap-Tons | 360 | 0 | None | 89.5 | 0.0768 | 0 | 89.5 | 0.0768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ05 | Any | Cap-Tons | 180 | 0 | None | 64.1 | 0.0437 | 0 | 64.1 | 0.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ05 | Any | Cap-Tons | 1300 | 0 | None | 71.9 | 0.0637 | 0 | 71.9 | 0.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ05 | Any | Cap-Tons | 644 | 0 | None | 37.5 | 0.0258 | 0 | 37.5 | 0.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ05 | Any | Cap-Tons | 102 | 0 | None | 140 | 0.063 | 0 | 140 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.041
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ05 | Any | Cap-Tons | 215 | 0 | None | 89.6 | 0.045 | 0 | 89.6 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ05 | Any | Cap-Tons | 77.4 | 0 | None | 55.7 | 0.0469 | 0 | 55.7 | 0.0469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ05 | Any | Cap-Tons | 278 | 0 | None | 83.2 | 0.0339 | 0 | 83.2 | 0.0339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.074
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ05 | Any | Cap-Tons | 15.2 | 0 | None | 93.9 | 0.0353 | 0 | 93.9 | 0.0353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ05 | Any | Cap-Tons | 164 | 0 | None | 84.8 | 0.0575 | 0 | 84.8 | 0.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ06 | Any | Cap-Tons | 585 | 0 | None | 136 | 0.113 | 0 | 136 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.228
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ06 | Any | Cap-Tons | 318 | 0 | None | 83.6 | 0.0569 | 0 | 83.6 | 0.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.111
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ06 | Any | Cap-Tons | 1960 | 0 | None | 109 | 0.0989 | 0 | 109 | 0.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.228
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ06 | Any | Cap-Tons | 842 | 0 | None | 79.3 | 0.0422 | 0 | 79.3 | 0.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.214
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ06 | Any | Cap-Tons | 154 | 0 | None | 183 | 0.0945 | 0 | 183 | 0.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.28
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ06 | Any | Cap-Tons | 298 | 0 | None | 136 | 0.0662 | 0 | 136 | 0.0662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.781
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ06 | Any | Cap-Tons | 102 | 0 | None | 124 | 0.0864 | 0 | 124 | 0.0864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.214
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ06 | Any | Cap-Tons | 369 | 0 | None | 130 | 0.0438 | 0 | 130 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.273
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ06 | Any | Cap-Tons | 21.8 | 0 | None | 139 | 0.0457 | 0 | 139 | 0.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.553
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ06 | Any | Cap-Tons | 233 | 0 | None | 149 | 0.102 | 0 | 149 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.861
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ07 | Any | Cap-Tons | 550 | 0 | None | 136 | 0.102 | 0 | 136 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.118
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ07 | Any | Cap-Tons | 303 | 0 | None | 81.3 | 0.0472 | 0 | 81.3 | 0.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ07 | Any | Cap-Tons | 1900 | 0 | None | 102 | 0.0839 | 0 | 102 | 0.0839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.118
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ07 | Any | Cap-Tons | 874 | 0 | None | 77.4 | 0.0328 | 0 | 77.4 | 0.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ07 | Any | Cap-Tons | 141 | 0 | None | 193 | 0.0772 | 0 | 193 | 0.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.323
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ07 | Any | Cap-Tons | 297 | 0 | None | 126 | 0.0541 | 0 | 126 | 0.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.286
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ07 | Any | Cap-Tons | 104 | 0 | None | 114 | 0.0622 | 0 | 114 | 0.0622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.083
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ07 | Any | Cap-Tons | 357 | 0 | None | 120 | 0.038 | 0 | 120 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.734
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ07 | Any | Cap-Tons | 20.8 | 0 | None | 132 | 0.0391 | 0 | 132 | 0.0391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.336
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ07 | Any | Cap-Tons | 228 | 0 | None | 142 | 0.0872 | 0 | 142 | 0.0872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.281
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ08 | Any | Cap-Tons | 641 | 0 | None | 148 | 0.0995 | 0 | 148 | 0.0995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ08 | Any | Cap-Tons | 344 | 0 | None | 97.2 | 0.0504 | 0 | 97.2 | 0.0504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.197
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ08 | Any | Cap-Tons | 2190 | 0 | None | 120 | 0.0859 | 0 | 120 | 0.0859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ08 | Any | Cap-Tons | 945 | 0 | None | 87.7 | 0.036 | 0 | 87.7 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ08 | Any | Cap-Tons | 164 | 0 | None | 206 | 0.0876 | 0 | 206 | 0.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.195
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ08 | Any | Cap-Tons | 332 | 0 | None | 141 | 0.0572 | 0 | 141 | 0.0572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.142
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ08 | Any | Cap-Tons | 113 | 0 | None | 150 | 0.0803 | 0 | 150 | 0.0803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ08 | Any | Cap-Tons | 391 | 0 | None | 139 | 0.0398 | 0 | 139 | 0.0398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.712
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ08 | Any | Cap-Tons | 22.6 | 0 | None | 155 | 0.0422 | 0 | 155 | 0.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.685
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ08 | Any | Cap-Tons | 254 | 0 | None | 167 | 0.092 | 0 | 167 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.032
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ09 | Any | Cap-Tons | 772 | 0 | None | 137 | 0.138 | 0 | 137 | 0.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.163
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ09 | Any | Cap-Tons | 409 | 0 | None | 92.6 | 0.0793 | 0 | 92.6 | 0.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.14
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ09 | Any | Cap-Tons | 2540 | 0 | None | 116 | 0.12 | 0 | 116 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.163
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ09 | Any | Cap-Tons | 1080 | 0 | None | 87.2 | 0.0515 | 0 | 87.2 | 0.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.255
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ09 | Any | Cap-Tons | 216 | 0 | None | 183 | 0.111 | 0 | 183 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.29
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ09 | Any | Cap-Tons | 364 | 0 | None | 137 | 0.0876 | 0 | 137 | 0.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.74
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ09 | Any | Cap-Tons | 129 | 0 | None | 151 | 0.106 | 0 | 151 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.255
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ09 | Any | Cap-Tons | 458 | 0 | None | 125 | 0.0542 | 0 | 125 | 0.0542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.078
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ09 | Any | Cap-Tons | 27.1 | 0 | None | 142 | 0.0594 | 0 | 142 | 0.0594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.526
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ09 | Any | Cap-Tons | 312 | 0 | None | 151 | 0.117 | 0 | 151 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.845
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ10 | Any | Cap-Tons | 687 | 0 | None | 156 | 0.143 | 0 | 156 | 0.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ10 | Any | Cap-Tons | 360 | 0 | None | 109 | 0.0836 | 0 | 109 | 0.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.312
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ10 | Any | Cap-Tons | 2310 | 0 | None | 134 | 0.125 | 0 | 134 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ10 | Any | Cap-Tons | 954 | 0 | None | 96.6 | 0.0543 | 0 | 96.6 | 0.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ10 | Any | Cap-Tons | 194 | 0 | None | 208 | 0.119 | 0 | 208 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.145
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ10 | Any | Cap-Tons | 338 | 0 | None | 149 | 0.0853 | 0 | 149 | 0.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.607
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ10 | Any | Cap-Tons | 115 | 0 | None | 180 | 0.123 | 0 | 180 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.247
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ10 | Any | Cap-Tons | 406 | 0 | None | 146 | 0.0584 | 0 | 146 | 0.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.227
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ10 | Any | Cap-Tons | 24.6 | 0 | None | 160 | 0.0624 | 0 | 160 | 0.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.865
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ10 | Any | Cap-Tons | 273 | 0 | None | 179 | 0.128 | 0 | 179 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.493
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ11 | Any | Cap-Tons | 635 | 0 | None | 166 | 0.114 | 0 | 166 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.058
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ11 | Any | Cap-Tons | 330 | 0 | None | 110 | 0.0458 | 0 | 110 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.044
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ11 | Any | Cap-Tons | 2120 | 0 | None | 151 | 0.13 | 0 | 151 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.058
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ11 | Any | Cap-Tons | 967 | 0 | None | 101 | 0.0627 | 0 | 101 | 0.0627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ11 | Any | Cap-Tons | 202 | 0 | None | 217 | 0.142 | 0 | 217 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.027
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ11 | Any | Cap-Tons | 346 | 0 | None | 141 | 0.101 | 0 | 141 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ11 | Any | Cap-Tons | 118 | 0 | None | 201 | 0.151 | 0 | 201 | 0.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ11 | Any | Cap-Tons | 409 | 0 | None | 140 | 0.082 | 0 | 140 | 0.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ11 | Any | Cap-Tons | 25 | 0 | None | 155 | 0.0898 | 0 | 155 | 0.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ11 | Any | Cap-Tons | 275 | 0 | None | 171 | 0.127 | 0 | 171 | 0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ12 | Any | Cap-Tons | 576 | 0 | None | 143 | 0.115 | 0 | 143 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.08
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ12 | Any | Cap-Tons | 301 | 0 | None | 94.5 | 0.0439 | 0 | 94.5 | 0.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.134
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ12 | Any | Cap-Tons | 1980 | 0 | None | 126 | 0.127 | 0 | 126 | 0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.08
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ12 | Any | Cap-Tons | 912 | 0 | None | 79.2 | 0.0602 | 0 | 79.2 | 0.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ12 | Any | Cap-Tons | 183 | 0 | None | 184 | 0.146 | 0 | 184 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.105
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ12 | Any | Cap-Tons | 323 | 0 | None | 119 | 0.0975 | 0 | 119 | 0.0975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.26
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ12 | Any | Cap-Tons | 110 | 0 | None | 151 | 0.146 | 0 | 151 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.148
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ12 | Any | Cap-Tons | 386 | 0 | None | 118 | 0.0774 | 0 | 118 | 0.0774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.847
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ12 | Any | Cap-Tons | 23.4 | 0 | None | 131 | 0.0859 | 0 | 131 | 0.0859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.312
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ12 | Any | Cap-Tons | 263 | 0 | None | 144 | 0.13 | 0 | 144 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.309
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ13 | Any | Cap-Tons | 678 | 0 | None | 165 | 0.0932 | 0 | 165 | 0.0932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.144
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ13 | Any | Cap-Tons | 362 | 0 | None | 111 | 0.0336 | 0 | 111 | 0.0336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.167
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ13 | Any | Cap-Tons | 2260 | 0 | None | 149 | 0.109 | 0 | 149 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.144
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ13 | Any | Cap-Tons | 978 | 0 | None | 104 | 0.055 | 0 | 104 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ13 | Any | Cap-Tons | 202 | 0 | None | 225 | 0.126 | 0 | 225 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.074
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ13 | Any | Cap-Tons | 352 | 0 | None | 143 | 0.0896 | 0 | 143 | 0.0896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.304
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ13 | Any | Cap-Tons | 118 | 0 | None | 211 | 0.134 | 0 | 211 | 0.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ13 | Any | Cap-Tons | 401 | 0 | None | 147 | 0.066 | 0 | 147 | 0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.447
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ13 | Any | Cap-Tons | 25.3 | 0 | None | 155 | 0.0682 | 0 | 155 | 0.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.384
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ13 | Any | Cap-Tons | 283 | 0 | None | 174 | 0.123 | 0 | 174 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.365
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ14 | Any | Cap-Tons | 732 | 0 | None | 151 | 0.116 | 0 | 151 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ14 | Any | Cap-Tons | 396 | 0 | None | 101 | 0.0645 | 0 | 101 | 0.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.065
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ14 | Any | Cap-Tons | 2410 | 0 | None | 139 | 0.108 | 0 | 139 | 0.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ14 | Any | Cap-Tons | 1040 | 0 | None | 95.8 | 0.047 | 0 | 95.8 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ14 | Any | Cap-Tons | 207 | 0 | None | 215 | 0.107 | 0 | 215 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.052
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ14 | Any | Cap-Tons | 366 | 0 | None | 139 | 0.0777 | 0 | 139 | 0.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.248
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ14 | Any | Cap-Tons | 121 | 0 | None | 201 | 0.118 | 0 | 201 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ14 | Any | Cap-Tons | 419 | 0 | None | 144 | 0.0621 | 0 | 144 | 0.0621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.194
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ14 | Any | Cap-Tons | 26.7 | 0 | None | 152 | 0.0604 | 0 | 152 | 0.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ14 | Any | Cap-Tons | 285 | 0 | None | 168 | 0.102 | 0 | 168 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.217
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ15 | Any | Cap-Tons | 960 | 0 | None | 232 | 0.122 | 0 | 232 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ15 | Any | Cap-Tons | 512 | 0 | None | 167 | 0.072 | 0 | 167 | 0.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.027
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ15 | Any | Cap-Tons | 3090 | 0 | None | 211 | 0.114 | 0 | 211 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ15 | Any | Cap-Tons | 1230 | 0 | None | 163 | 0.0535 | 0 | 163 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ15 | Any | Cap-Tons | 270 | 0 | None | 312 | 0.112 | 0 | 312 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.278
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ15 | Any | Cap-Tons | 452 | 0 | None | 216 | 0.0843 | 0 | 216 | 0.0843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.533
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ15 | Any | Cap-Tons | 156 | 0 | None | 325 | 0.124 | 0 | 325 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ15 | Any | Cap-Tons | 518 | 0 | None | 214 | 0.061 | 0 | 214 | 0.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.291
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ15 | Any | Cap-Tons | 31.9 | 0 | None | 240 | 0.0654 | 0 | 240 | 0.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.217
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ15 | Any | Cap-Tons | 359 | 0 | None | 258 | 0.114 | 0 | 258 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.195
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ECC | New | New | CZ16 | Any | Cap-Tons | 376 | 0 | None | 101 | 0.0851 | 0 | 101 | 0.0851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.139
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | ESe | New | New | CZ16 | Any | Cap-Tons | 199 | 0 | None | 62.8 | 0.0399 | 0 | 62.8 | 0.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | EUn | New | New | CZ16 | Any | Cap-Tons | 1330 | 0 | None | 89.3 | 0.0945 | 0 | 89.3 | 0.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.139
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Hsp | New | New | CZ16 | Any | Cap-Tons | 656 | 0 | None | 56.5 | 0.0439 | 0 | 56.5 | 0.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Htl | New | New | CZ16 | Any | Cap-Tons | 116 | 0 | None | 167 | 0.118 | 0 | 167 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.069
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | MBT | New | New | CZ16 | Any | Cap-Tons | 223 | 0 | None | 84.4 | 0.0708 | 0 | 84.4 | 0.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.169
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Nrs | New | New | CZ16 | Any | Cap-Tons | 78.6 | 0 | None | 101 | 0.1 | 0 | 101 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfL | New | New | CZ16 | Any | Cap-Tons | 292 | 0 | None | 86.3 | 0.063 | 0 | 86.3 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.095
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | OfS | New | New | CZ16 | Any | Cap-Tons | 16.8 | 0 | None | 95.5 | 0.0671 | 0 | 95.5 | 0.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.061
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-03 09:32 | Any | Rt3 | New | New | CZ16 | Any | Cap-Tons | 176 | 0 | None | 100 | 0.0969 | 0 | 100 | 0.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.05
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ECC | Ex | Ex | CZ05 | Any | Cap-Tons | 421 | 0 | None | 80.9 | 0.0673 | 0 | 48.4 | 0.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-03 09:30 | SCE | ESe | Ex | Ex | CZ05 | Any | Cap-Tons | 224 | 0 | None | 69 | 0.0399 | 0 | 41.3 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.007
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ05 | Any | Cap-Tons | 517 | 0 | None | 94.4 | 0.0818 | 0 | 46.2 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.014
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ05 | Any | Cap-Tons | 247 | 0 | None | 81.9 | 0.0521 | 0 | 40 | 0.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ05 | Any | Cap-Tons | 1910 | 0 | None | 95.6 | 0.0741 | 0 | 46.8 | 0.0362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.014
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ05 | Any | Cap-Tons | 626 | 0 | None | 60.4 | 0.0402 | 0 | 29.5 | 0.0196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.846
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ05 | Any | Cap-Tons | 203 | 0 | None | 211 | 0.0801 | 0 | 103 | 0.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.137
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ05 | Any | Cap-Tons | 264 | 0 | None | 93.9 | 0.0597 | 0 | 45.9 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.387
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ05 | Any | Cap-Tons | 90.7 | 0 | None | 136 | 0.0856 | 0 | 66.3 | 0.0419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.846
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ05 | Any | Cap-Tons | 364 | 0 | None | 107 | 0.0536 | 0 | 52.4 | 0.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.225
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ05 | Any | Cap-Tons | 24.9 | 0 | None | 122 | 0.0623 | 0 | 59.5 | 0.0305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.285
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ05 | Any | Cap-Tons | 194 | 0 | None | 103 | 0.0728 | 0 | 50.5 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.557
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ06 | Any | Cap-Tons | 765 | 0 | None | 165 | 0.123 | 0 | 80.4 | 0.0601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.375
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ06 | Any | Cap-Tons | 394 | 0 | None | 122 | 0.0761 | 0 | 59.6 | 0.0372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.902
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ06 | Any | Cap-Tons | 2610 | 0 | None | 148 | 0.112 | 0 | 72.3 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.375
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ06 | Any | Cap-Tons | 809 | 0 | None | 131 | 0.0663 | 0 | 63.9 | 0.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.571
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ06 | Any | Cap-Tons | 268 | 0 | None | 249 | 0.109 | 0 | 122 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.006
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ06 | Any | Cap-Tons | 356 | 0 | None | 159 | 0.0834 | 0 | 77.5 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 32.51
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ06 | Any | Cap-Tons | 128 | 0 | None | 225 | 0.125 | 0 | 110 | 0.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.571
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ06 | Any | Cap-Tons | 466 | 0 | None | 170 | 0.0691 | 0 | 83 | 0.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 109.432
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ06 | Any | Cap-Tons | 31.9 | 0 | None | 191 | 0.0769 | 0 | 93.5 | 0.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.662
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ06 | Any | Cap-Tons | 266 | 0 | None | 180 | 0.113 | 0 | 88.1 | 0.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 31.015
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ08 | Any | Cap-Tons | 813 | 0 | None | 188 | 0.114 | 0 | 92 | 0.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.447
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ08 | Any | Cap-Tons | 422 | 0 | None | 148 | 0.0755 | 0 | 72.2 | 0.0369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.927
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ08 | Any | Cap-Tons | 2840 | 0 | None | 166 | 0.103 | 0 | 81.1 | 0.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.447
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ08 | Any | Cap-Tons | 883 | 0 | None | 143 | 0.0585 | 0 | 70.1 | 0.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.377
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ08 | Any | Cap-Tons | 284 | 0 | None | 271 | 0.102 | 0 | 132 | 0.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.317
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ08 | Any | Cap-Tons | 389 | 0 | None | 174 | 0.0752 | 0 | 85 | 0.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 47.444
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ08 | Any | Cap-Tons | 138 | 0 | None | 258 | 0.119 | 0 | 126 | 0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.377
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ08 | Any | Cap-Tons | 511 | 0 | None | 178 | 0.0598 | 0 | 87.2 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 132.939
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ08 | Any | Cap-Tons | 33.1 | 0 | None | 211 | 0.0747 | 0 | 103 | 0.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 29.77
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ08 | Any | Cap-Tons | 286 | 0 | None | 215 | 0.113 | 0 | 105 | 0.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 35.172
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ09 | Any | Cap-Tons | 985 | 0 | None | 174 | 0.151 | 0 | 85.3 | 0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.959
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ09 | Any | Cap-Tons | 508 | 0 | None | 132 | 0.0986 | 0 | 64.7 | 0.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.851
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ09 | Any | Cap-Tons | 3310 | 0 | None | 161 | 0.136 | 0 | 78.5 | 0.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.959
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ09 | Any | Cap-Tons | 1000 | 0 | None | 140 | 0.0798 | 0 | 68.6 | 0.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.611
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ09 | Any | Cap-Tons | 348 | 0 | None | 249 | 0.128 | 0 | 122 | 0.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.431
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ09 | Any | Cap-Tons | 449 | 0 | None | 176 | 0.115 | 0 | 86 | 0.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.149
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ09 | Any | Cap-Tons | 171 | 0 | None | 241 | 0.146 | 0 | 118 | 0.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.611
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ09 | Any | Cap-Tons | 556 | 0 | None | 175 | 0.0923 | 0 | 85.7 | 0.0451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 79.468
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ09 | Any | Cap-Tons | 39.3 | 0 | None | 196 | 0.1 | 0 | 95.7 | 0.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.6
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ09 | Any | Cap-Tons | 346 | 0 | None | 186 | 0.13 | 0 | 91 | 0.0635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.751
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ10 | Any | Cap-Tons | 877 | 0 | None | 200 | 0.163 | 0 | 98 | 0.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.501
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ10 | Any | Cap-Tons | 454 | 0 | None | 161 | 0.113 | 0 | 78.7 | 0.0552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.428
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ10 | Any | Cap-Tons | 3050 | 0 | None | 184 | 0.143 | 0 | 90 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.501
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ10 | Any | Cap-Tons | 896 | 0 | None | 154 | 0.0841 | 0 | 75.2 | 0.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.854
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ10 | Any | Cap-Tons | 322 | 0 | None | 277 | 0.138 | 0 | 136 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ10 | Any | Cap-Tons | 414 | 0 | None | 180 | 0.106 | 0 | 88.2 | 0.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.966
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ10 | Any | Cap-Tons | 156 | 0 | None | 273 | 0.163 | 0 | 134 | 0.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.854
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ10 | Any | Cap-Tons | 516 | 0 | None | 198 | 0.0937 | 0 | 96.6 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 25.533
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ10 | Any | Cap-Tons | 36.7 | 0 | None | 218 | 0.108 | 0 | 106 | 0.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.244
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ10 | Any | Cap-Tons | 307 | 0 | None | 215 | 0.139 | 0 | 105 | 0.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.941
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ13 | Any | Cap-Tons | 890 | 0 | None | 208 | 0.126 | 0 | 102 | 0.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.874
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ13 | Any | Cap-Tons | 450 | 0 | None | 166 | 0.0612 | 0 | 81 | 0.0299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.284
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ13 | Any | Cap-Tons | 2950 | 0 | None | 201 | 0.137 | 0 | 98.3 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.874
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ13 | Any | Cap-Tons | 903 | 0 | None | 166 | 0.0892 | 0 | 81.2 | 0.0436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.371
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ13 | Any | Cap-Tons | 317 | 0 | None | 298 | 0.151 | 0 | 145 | 0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.474
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ13 | Any | Cap-Tons | 428 | 0 | None | 178 | 0.111 | 0 | 87.2 | 0.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.887
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ13 | Any | Cap-Tons | 160 | 0 | None | 298 | 0.171 | 0 | 146 | 0.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.371
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ13 | Any | Cap-Tons | 517 | 0 | None | 196 | 0.106 | 0 | 96 | 0.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.293
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ13 | Any | Cap-Tons | 36.3 | 0 | None | 221 | 0.116 | 0 | 108 | 0.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ13 | Any | Cap-Tons | 330 | 0 | None | 206 | 0.138 | 0 | 101 | 0.0676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.222
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ14 | Any | Cap-Tons | 952 | 0 | None | 193 | 0.134 | 0 | 94.1 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.617
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ14 | Any | Cap-Tons | 490 | 0 | None | 149 | 0.0952 | 0 | 73 | 0.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.86
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ14 | Any | Cap-Tons | 3180 | 0 | None | 188 | 0.131 | 0 | 91.9 | 0.0639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.617
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ14 | Any | Cap-Tons | 941 | 0 | None | 153 | 0.0747 | 0 | 74.6 | 0.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ14 | Any | Cap-Tons | 321 | 0 | None | 291 | 0.131 | 0 | 142 | 0.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.137
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ14 | Any | Cap-Tons | 440 | 0 | None | 176 | 0.0951 | 0 | 86 | 0.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.946
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ14 | Any | Cap-Tons | 162 | 0 | None | 297 | 0.156 | 0 | 145 | 0.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ14 | Any | Cap-Tons | 539 | 0 | None | 195 | 0.099 | 0 | 95.4 | 0.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.448
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ14 | Any | Cap-Tons | 38.1 | 0 | None | 217 | 0.105 | 0 | 106 | 0.0512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.955
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ14 | Any | Cap-Tons | 336 | 0 | None | 198 | 0.117 | 0 | 96.7 | 0.0574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.584
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ15 | Any | Cap-Tons | 1200 | 0 | None | 304 | 0.14 | 0 | 149 | 0.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.31
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ15 | Any | Cap-Tons | 630 | 0 | None | 239 | 0.0982 | 0 | 117 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.93
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ15 | Any | Cap-Tons | 3930 | 0 | None | 285 | 0.137 | 0 | 139 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.31
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ15 | Any | Cap-Tons | 1120 | 0 | None | 257 | 0.084 | 0 | 125 | 0.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.419
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ15 | Any | Cap-Tons | 383 | 0 | None | 410 | 0.138 | 0 | 200 | 0.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.563
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ15 | Any | Cap-Tons | 533 | 0 | None | 280 | 0.108 | 0 | 137 | 0.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.866
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ15 | Any | Cap-Tons | 209 | 0 | None | 444 | 0.158 | 0 | 217 | 0.0773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.419
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ15 | Any | Cap-Tons | 636 | 0 | None | 293 | 0.0986 | 0 | 143 | 0.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.977
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ15 | Any | Cap-Tons | 43.8 | 0 | None | 344 | 0.112 | 0 | 168 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.532
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ15 | Any | Cap-Tons | 410 | 0 | None | 311 | 0.131 | 0 | 152 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.204
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ16 | Any | Cap-Tons | 543 | 0 | None | 124 | 0.11 | 0 | 60.8 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.926
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ16 | Any | Cap-Tons | 268 | 0 | None | 95.2 | 0.0608 | 0 | 46.6 | 0.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.313
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ16 | Any | Cap-Tons | 1920 | 0 | None | 123 | 0.117 | 0 | 60 | 0.0572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.926
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ16 | Any | Cap-Tons | 633 | 0 | None | 90 | 0.0696 | 0 | 44 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.914
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ16 | Any | Cap-Tons | 206 | 0 | None | 237 | 0.137 | 0 | 116 | 0.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ16 | Any | Cap-Tons | 280 | 0 | None | 102 | 0.088 | 0 | 49.8 | 0.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.849
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ16 | Any | Cap-Tons | 102 | 0 | None | 180 | 0.146 | 0 | 88 | 0.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.914
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ16 | Any | Cap-Tons | 401 | 0 | None | 112 | 0.0929 | 0 | 54.7 | 0.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.012
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ16 | Any | Cap-Tons | 25.7 | 0 | None | 132 | 0.104 | 0 | 64.6 | 0.0507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.728
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ16 | Any | Cap-Tons | 225 | 0 | None | 112 | 0.107 | 0 | 54.7 | 0.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.946
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ05 | Any | Cap-Tons | 517 | 0 | None | 133 | 0.115 | 0 | 84.7 | 0.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.014
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ05 | Any | Cap-Tons | 247 | 0 | None | 115 | 0.0734 | 0 | 73.5 | 0.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ05 | Any | Cap-Tons | 1910 | 0 | None | 135 | 0.104 | 0 | 85.8 | 0.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.014
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ05 | Any | Cap-Tons | 626 | 0 | None | 85 | 0.0566 | 0 | 54.1 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.846
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ05 | Any | Cap-Tons | 203 | 0 | None | 297 | 0.113 | 0 | 189 | 0.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.137
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ05 | Any | Cap-Tons | 264 | 0 | None | 132 | 0.084 | 0 | 84.3 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.387
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ05 | Any | Cap-Tons | 90.7 | 0 | None | 191 | 0.121 | 0 | 122 | 0.0768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.846
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ05 | Any | Cap-Tons | 364 | 0 | None | 151 | 0.0754 | 0 | 96.2 | 0.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.225
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ05 | Any | Cap-Tons | 24.9 | 0 | None | 171 | 0.0878 | 0 | 109 | 0.0559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.285
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ05 | Any | Cap-Tons | 194 | 0 | None | 146 | 0.102 | 0 | 92.7 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.557
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ06 | Any | Cap-Tons | 765 | 0 | None | 232 | 0.173 | 0 | 148 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.375
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ06 | Any | Cap-Tons | 394 | 0 | None | 172 | 0.107 | 0 | 109 | 0.0683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.902
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ06 | Any | Cap-Tons | 2610 | 0 | None | 208 | 0.158 | 0 | 133 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.375
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ06 | Any | Cap-Tons | 809 | 0 | None | 184 | 0.0933 | 0 | 117 | 0.0595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.571
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ06 | Any | Cap-Tons | 268 | 0 | None | 350 | 0.154 | 0 | 223 | 0.0981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.006
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ06 | Any | Cap-Tons | 356 | 0 | None | 223 | 0.117 | 0 | 142 | 0.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 32.51
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ06 | Any | Cap-Tons | 128 | 0 | None | 316 | 0.177 | 0 | 202 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.571
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ06 | Any | Cap-Tons | 466 | 0 | None | 239 | 0.0973 | 0 | 152 | 0.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 109.432
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ06 | Any | Cap-Tons | 31.9 | 0 | None | 269 | 0.108 | 0 | 172 | 0.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.662
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ06 | Any | Cap-Tons | 266 | 0 | None | 254 | 0.159 | 0 | 162 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 31.015
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ08 | Any | Cap-Tons | 813 | 0 | None | 265 | 0.16 | 0 | 169 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.447
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ08 | Any | Cap-Tons | 422 | 0 | None | 208 | 0.106 | 0 | 132 | 0.0677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.927
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ08 | Any | Cap-Tons | 2840 | 0 | None | 234 | 0.144 | 0 | 149 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.447
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ08 | Any | Cap-Tons | 883 | 0 | None | 202 | 0.0824 | 0 | 129 | 0.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.377
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ08 | Any | Cap-Tons | 284 | 0 | None | 381 | 0.143 | 0 | 243 | 0.0914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.317
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ08 | Any | Cap-Tons | 389 | 0 | None | 245 | 0.106 | 0 | 156 | 0.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 47.444
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ08 | Any | Cap-Tons | 138 | 0 | None | 363 | 0.167 | 0 | 232 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.377
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ08 | Any | Cap-Tons | 511 | 0 | None | 251 | 0.0842 | 0 | 160 | 0.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 132.939
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ08 | Any | Cap-Tons | 33.1 | 0 | None | 298 | 0.105 | 0 | 190 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 29.77
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ08 | Any | Cap-Tons | 286 | 0 | None | 302 | 0.159 | 0 | 192 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 35.172
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ09 | Any | Cap-Tons | 985 | 0 | None | 246 | 0.213 | 0 | 156 | 0.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.959
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ09 | Any | Cap-Tons | 508 | 0 | None | 186 | 0.139 | 0 | 119 | 0.0885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.851
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ09 | Any | Cap-Tons | 3310 | 0 | None | 226 | 0.191 | 0 | 144 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.959
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ09 | Any | Cap-Tons | 1000 | 0 | None | 198 | 0.112 | 0 | 126 | 0.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.611
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ09 | Any | Cap-Tons | 348 | 0 | None | 350 | 0.181 | 0 | 223 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.431
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ09 | Any | Cap-Tons | 449 | 0 | None | 248 | 0.161 | 0 | 158 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.149
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ09 | Any | Cap-Tons | 171 | 0 | None | 340 | 0.206 | 0 | 216 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.611
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ09 | Any | Cap-Tons | 556 | 0 | None | 247 | 0.13 | 0 | 157 | 0.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 79.468
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ09 | Any | Cap-Tons | 39.3 | 0 | None | 276 | 0.141 | 0 | 176 | 0.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.6
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ09 | Any | Cap-Tons | 346 | 0 | None | 262 | 0.183 | 0 | 167 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.751
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ10 | Any | Cap-Tons | 877 | 0 | None | 282 | 0.229 | 0 | 180 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.501
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ10 | Any | Cap-Tons | 454 | 0 | None | 227 | 0.159 | 0 | 144 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.428
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ10 | Any | Cap-Tons | 3050 | 0 | None | 259 | 0.202 | 0 | 165 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.501
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ10 | Any | Cap-Tons | 896 | 0 | None | 217 | 0.118 | 0 | 138 | 0.0754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.854
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ10 | Any | Cap-Tons | 322 | 0 | None | 390 | 0.194 | 0 | 249 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ10 | Any | Cap-Tons | 414 | 0 | None | 254 | 0.15 | 0 | 162 | 0.0955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.966
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ10 | Any | Cap-Tons | 156 | 0 | None | 385 | 0.23 | 0 | 245 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.854
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ10 | Any | Cap-Tons | 516 | 0 | None | 278 | 0.132 | 0 | 177 | 0.0841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 25.533
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ10 | Any | Cap-Tons | 36.7 | 0 | None | 307 | 0.152 | 0 | 195 | 0.0971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.244
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ10 | Any | Cap-Tons | 307 | 0 | None | 302 | 0.196 | 0 | 193 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.941
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ13 | Any | Cap-Tons | 890 | 0 | None | 293 | 0.177 | 0 | 187 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.874
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ13 | Any | Cap-Tons | 450 | 0 | None | 233 | 0.0862 | 0 | 149 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.284
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ13 | Any | Cap-Tons | 2950 | 0 | None | 283 | 0.193 | 0 | 180 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.874
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ13 | Any | Cap-Tons | 903 | 0 | None | 234 | 0.126 | 0 | 149 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.371
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ13 | Any | Cap-Tons | 317 | 0 | None | 419 | 0.213 | 0 | 267 | 0.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.474
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ13 | Any | Cap-Tons | 428 | 0 | None | 251 | 0.156 | 0 | 160 | 0.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.887
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ13 | Any | Cap-Tons | 160 | 0 | None | 420 | 0.24 | 0 | 267 | 0.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.371
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ13 | Any | Cap-Tons | 517 | 0 | None | 277 | 0.15 | 0 | 176 | 0.0955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.293
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ13 | Any | Cap-Tons | 36.3 | 0 | None | 311 | 0.163 | 0 | 198 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ13 | Any | Cap-Tons | 330 | 0 | None | 290 | 0.195 | 0 | 184 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.222
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ14 | Any | Cap-Tons | 952 | 0 | None | 271 | 0.188 | 0 | 173 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.617
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ14 | Any | Cap-Tons | 490 | 0 | None | 210 | 0.134 | 0 | 134 | 0.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.86
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ14 | Any | Cap-Tons | 3180 | 0 | None | 265 | 0.184 | 0 | 169 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.617
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ14 | Any | Cap-Tons | 941 | 0 | None | 215 | 0.105 | 0 | 137 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ14 | Any | Cap-Tons | 321 | 0 | None | 410 | 0.185 | 0 | 261 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.137
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ14 | Any | Cap-Tons | 440 | 0 | None | 248 | 0.134 | 0 | 158 | 0.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.946
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ14 | Any | Cap-Tons | 162 | 0 | None | 419 | 0.22 | 0 | 267 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ14 | Any | Cap-Tons | 539 | 0 | None | 275 | 0.139 | 0 | 175 | 0.0888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.448
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ14 | Any | Cap-Tons | 38.1 | 0 | None | 305 | 0.147 | 0 | 194 | 0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.955
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ14 | Any | Cap-Tons | 336 | 0 | None | 278 | 0.165 | 0 | 177 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.584
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ15 | Any | Cap-Tons | 1200 | 0 | None | 429 | 0.197 | 0 | 273 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.31
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ15 | Any | Cap-Tons | 630 | 0 | None | 337 | 0.138 | 0 | 214 | 0.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.93
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ15 | Any | Cap-Tons | 3930 | 0 | None | 401 | 0.193 | 0 | 256 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.31
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ15 | Any | Cap-Tons | 1120 | 0 | None | 361 | 0.118 | 0 | 230 | 0.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.419
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ15 | Any | Cap-Tons | 383 | 0 | None | 577 | 0.194 | 0 | 367 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.563
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ15 | Any | Cap-Tons | 533 | 0 | None | 394 | 0.153 | 0 | 251 | 0.0973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.866
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ15 | Any | Cap-Tons | 209 | 0 | None | 625 | 0.223 | 0 | 398 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.419
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ15 | Any | Cap-Tons | 636 | 0 | None | 412 | 0.139 | 0 | 262 | 0.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.977
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ15 | Any | Cap-Tons | 43.8 | 0 | None | 484 | 0.158 | 0 | 308 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.532
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ15 | Any | Cap-Tons | 410 | 0 | None | 439 | 0.184 | 0 | 279 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.204
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ16 | Any | Cap-Tons | 543 | 0 | None | 175 | 0.155 | 0 | 112 | 0.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.926
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ16 | Any | Cap-Tons | 268 | 0 | None | 134 | 0.0855 | 0 | 85.4 | 0.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.313
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ16 | Any | Cap-Tons | 1920 | 0 | None | 173 | 0.165 | 0 | 110 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.926
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ16 | Any | Cap-Tons | 633 | 0 | None | 127 | 0.098 | 0 | 80.8 | 0.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.914
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ16 | Any | Cap-Tons | 206 | 0 | None | 334 | 0.192 | 0 | 213 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ16 | Any | Cap-Tons | 280 | 0 | None | 143 | 0.124 | 0 | 91.4 | 0.0789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.849
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ16 | Any | Cap-Tons | 102 | 0 | None | 253 | 0.206 | 0 | 161 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.914
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ16 | Any | Cap-Tons | 401 | 0 | None | 157 | 0.131 | 0 | 100 | 0.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.012
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ16 | Any | Cap-Tons | 25.7 | 0 | None | 186 | 0.146 | 0 | 119 | 0.0929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.728
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ16 | Any | Cap-Tons | 225 | 0 | None | 158 | 0.15 | 0 | 100 | 0.0958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.946
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ05 | Any | Cap-Tons | 517 | 0 | None | 94.4 | 0.0818 | 0 | 46.2 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.014
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ05 | Any | Cap-Tons | 247 | 0 | None | 81.9 | 0.0521 | 0 | 40 | 0.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ05 | Any | Cap-Tons | 1910 | 0 | None | 95.6 | 0.0741 | 0 | 46.8 | 0.0362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.014
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ05 | Any | Cap-Tons | 626 | 0 | None | 60.4 | 0.0402 | 0 | 29.5 | 0.0196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.846
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ05 | Any | Cap-Tons | 203 | 0 | None | 211 | 0.0801 | 0 | 103 | 0.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.137
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ05 | Any | Cap-Tons | 264 | 0 | None | 93.9 | 0.0597 | 0 | 45.9 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.387
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ05 | Any | Cap-Tons | 90.7 | 0 | None | 136 | 0.0856 | 0 | 66.3 | 0.0419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.846
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ05 | Any | Cap-Tons | 364 | 0 | None | 107 | 0.0536 | 0 | 52.4 | 0.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.225
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ05 | Any | Cap-Tons | 24.9 | 0 | None | 122 | 0.0623 | 0 | 59.5 | 0.0305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.285
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ05 | Any | Cap-Tons | 194 | 0 | None | 103 | 0.0728 | 0 | 50.5 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.557
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ06 | Any | Cap-Tons | 765 | 0 | None | 165 | 0.123 | 0 | 80.4 | 0.0601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.375
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ06 | Any | Cap-Tons | 394 | 0 | None | 122 | 0.0761 | 0 | 59.6 | 0.0372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.902
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ06 | Any | Cap-Tons | 2610 | 0 | None | 148 | 0.112 | 0 | 72.3 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.375
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ06 | Any | Cap-Tons | 809 | 0 | None | 131 | 0.0663 | 0 | 63.9 | 0.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.571
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ06 | Any | Cap-Tons | 268 | 0 | None | 249 | 0.109 | 0 | 122 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.006
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ06 | Any | Cap-Tons | 356 | 0 | None | 159 | 0.0834 | 0 | 77.5 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 32.51
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ06 | Any | Cap-Tons | 128 | 0 | None | 225 | 0.125 | 0 | 110 | 0.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.571
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ06 | Any | Cap-Tons | 466 | 0 | None | 170 | 0.0691 | 0 | 83 | 0.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 109.432
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ06 | Any | Cap-Tons | 31.9 | 0 | None | 191 | 0.0769 | 0 | 93.5 | 0.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.662
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ06 | Any | Cap-Tons | 266 | 0 | None | 180 | 0.113 | 0 | 88.1 | 0.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 31.015
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ08 | Any | Cap-Tons | 422 | 0 | None | 148 | 0.0755 | 0 | 72.2 | 0.0369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.927
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ08 | Any | Cap-Tons | 2840 | 0 | None | 166 | 0.103 | 0 | 81.1 | 0.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.447
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ08 | Any | Cap-Tons | 883 | 0 | None | 143 | 0.0585 | 0 | 70.1 | 0.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.377
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ08 | Any | Cap-Tons | 284 | 0 | None | 271 | 0.102 | 0 | 132 | 0.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.317
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ08 | Any | Cap-Tons | 389 | 0 | None | 174 | 0.0752 | 0 | 85 | 0.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 47.444
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ08 | Any | Cap-Tons | 138 | 0 | None | 258 | 0.119 | 0 | 126 | 0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.377
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ08 | Any | Cap-Tons | 511 | 0 | None | 178 | 0.0598 | 0 | 87.2 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 132.939
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ08 | Any | Cap-Tons | 33.1 | 0 | None | 211 | 0.0747 | 0 | 103 | 0.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 29.77
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ08 | Any | Cap-Tons | 286 | 0 | None | 215 | 0.113 | 0 | 105 | 0.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 35.172
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ09 | Any | Cap-Tons | 985 | 0 | None | 174 | 0.151 | 0 | 85.3 | 0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.959
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ09 | Any | Cap-Tons | 508 | 0 | None | 132 | 0.0986 | 0 | 64.7 | 0.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.851
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ09 | Any | Cap-Tons | 3310 | 0 | None | 161 | 0.136 | 0 | 78.5 | 0.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.959
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ09 | Any | Cap-Tons | 1000 | 0 | None | 140 | 0.0798 | 0 | 68.6 | 0.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.611
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ09 | Any | Cap-Tons | 348 | 0 | None | 249 | 0.128 | 0 | 122 | 0.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.431
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ09 | Any | Cap-Tons | 449 | 0 | None | 176 | 0.115 | 0 | 86 | 0.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.149
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ09 | Any | Cap-Tons | 171 | 0 | None | 241 | 0.146 | 0 | 118 | 0.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.611
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ09 | Any | Cap-Tons | 556 | 0 | None | 175 | 0.0923 | 0 | 85.7 | 0.0451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 79.468
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ09 | Any | Cap-Tons | 39.3 | 0 | None | 196 | 0.1 | 0 | 95.7 | 0.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.6
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ09 | Any | Cap-Tons | 346 | 0 | None | 186 | 0.13 | 0 | 91 | 0.0635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.751
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ10 | Any | Cap-Tons | 877 | 0 | None | 200 | 0.163 | 0 | 98 | 0.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.501
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ10 | Any | Cap-Tons | 454 | 0 | None | 161 | 0.113 | 0 | 78.7 | 0.0552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.428
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ10 | Any | Cap-Tons | 3050 | 0 | None | 184 | 0.143 | 0 | 90 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.501
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ10 | Any | Cap-Tons | 896 | 0 | None | 154 | 0.0841 | 0 | 75.2 | 0.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.854
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ10 | Any | Cap-Tons | 322 | 0 | None | 277 | 0.138 | 0 | 136 | 0.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ10 | Any | Cap-Tons | 414 | 0 | None | 180 | 0.106 | 0 | 88.2 | 0.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.966
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ10 | Any | Cap-Tons | 156 | 0 | None | 273 | 0.163 | 0 | 134 | 0.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.854
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ10 | Any | Cap-Tons | 516 | 0 | None | 198 | 0.0937 | 0 | 96.6 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 25.533
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ10 | Any | Cap-Tons | 36.7 | 0 | None | 218 | 0.108 | 0 | 106 | 0.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.244
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ10 | Any | Cap-Tons | 307 | 0 | None | 215 | 0.139 | 0 | 105 | 0.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.941
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ13 | Any | Cap-Tons | 890 | 0 | None | 208 | 0.126 | 0 | 102 | 0.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.874
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ13 | Any | Cap-Tons | 450 | 0 | None | 166 | 0.0612 | 0 | 81 | 0.0299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.284
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ13 | Any | Cap-Tons | 2950 | 0 | None | 201 | 0.137 | 0 | 98.3 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.874
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ13 | Any | Cap-Tons | 903 | 0 | None | 166 | 0.0892 | 0 | 81.2 | 0.0436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.371
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ13 | Any | Cap-Tons | 428 | 0 | None | 178 | 0.111 | 0 | 87.2 | 0.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.887
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ13 | Any | Cap-Tons | 160 | 0 | None | 298 | 0.171 | 0 | 146 | 0.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.371
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ13 | Any | Cap-Tons | 517 | 0 | None | 196 | 0.106 | 0 | 96 | 0.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.293
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ13 | Any | Cap-Tons | 36.3 | 0 | None | 221 | 0.116 | 0 | 108 | 0.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ13 | Any | Cap-Tons | 330 | 0 | None | 206 | 0.138 | 0 | 101 | 0.0676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.222
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ14 | Any | Cap-Tons | 952 | 0 | None | 193 | 0.134 | 0 | 94.1 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.617
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ14 | Any | Cap-Tons | 490 | 0 | None | 149 | 0.0952 | 0 | 73 | 0.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.86
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ14 | Any | Cap-Tons | 3180 | 0 | None | 188 | 0.131 | 0 | 91.9 | 0.0639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.617
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ14 | Any | Cap-Tons | 941 | 0 | None | 153 | 0.0747 | 0 | 74.6 | 0.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.231
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ14 | Any | Cap-Tons | 321 | 0 | None | 291 | 0.131 | 0 | 142 | 0.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.137
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ14 | Any | Cap-Tons | 440 | 0 | None | 176 | 0.0951 | 0 | 86 | 0.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.946
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ14 | Any | Cap-Tons | 162 | 0 | None | 297 | 0.156 | 0 | 145 | 0.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.231
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ14 | Any | Cap-Tons | 539 | 0 | None | 195 | 0.099 | 0 | 95.4 | 0.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.448
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ14 | Any | Cap-Tons | 38.1 | 0 | None | 217 | 0.105 | 0 | 106 | 0.0512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.955
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ14 | Any | Cap-Tons | 336 | 0 | None | 198 | 0.117 | 0 | 96.7 | 0.0574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.584
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ15 | Any | Cap-Tons | 1200 | 0 | None | 304 | 0.14 | 0 | 149 | 0.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.31
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ15 | Any | Cap-Tons | 630 | 0 | None | 239 | 0.0982 | 0 | 117 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.93
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ15 | Any | Cap-Tons | 3930 | 0 | None | 285 | 0.137 | 0 | 139 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.31
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ15 | Any | Cap-Tons | 1120 | 0 | None | 257 | 0.084 | 0 | 125 | 0.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.419
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ15 | Any | Cap-Tons | 383 | 0 | None | 410 | 0.138 | 0 | 200 | 0.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.563
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ15 | Any | Cap-Tons | 533 | 0 | None | 280 | 0.108 | 0 | 137 | 0.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.866
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ15 | Any | Cap-Tons | 209 | 0 | None | 444 | 0.158 | 0 | 217 | 0.0773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.419
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ15 | Any | Cap-Tons | 636 | 0 | None | 293 | 0.0986 | 0 | 143 | 0.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.977
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ15 | Any | Cap-Tons | 43.8 | 0 | None | 344 | 0.112 | 0 | 168 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.532
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ15 | Any | Cap-Tons | 410 | 0 | None | 311 | 0.131 | 0 | 152 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.204
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ16 | Any | Cap-Tons | 543 | 0 | None | 124 | 0.11 | 0 | 60.8 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.926
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ16 | Any | Cap-Tons | 268 | 0 | None | 95.2 | 0.0608 | 0 | 46.6 | 0.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.313
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ16 | Any | Cap-Tons | 1920 | 0 | None | 123 | 0.117 | 0 | 60 | 0.0572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.926
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ16 | Any | Cap-Tons | 633 | 0 | None | 90 | 0.0696 | 0 | 44 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.914
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ16 | Any | Cap-Tons | 206 | 0 | None | 237 | 0.137 | 0 | 116 | 0.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ16 | Any | Cap-Tons | 280 | 0 | None | 102 | 0.088 | 0 | 49.8 | 0.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.849
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ16 | Any | Cap-Tons | 102 | 0 | None | 180 | 0.146 | 0 | 88 | 0.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.914
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ16 | Any | Cap-Tons | 401 | 0 | None | 112 | 0.0929 | 0 | 54.7 | 0.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.012
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ16 | Any | Cap-Tons | 225 | 0 | None | 112 | 0.107 | 0 | 54.7 | 0.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.946
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ05 | Any | Cap-Tons | 517 | 0 | None | 133 | 0.115 | 0 | 84.7 | 0.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.014
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ05 | Any | Cap-Tons | 247 | 0 | None | 115 | 0.0734 | 0 | 73.5 | 0.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.062
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ05 | Any | Cap-Tons | 1910 | 0 | None | 135 | 0.104 | 0 | 85.8 | 0.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.014
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ05 | Any | Cap-Tons | 626 | 0 | None | 85 | 0.0566 | 0 | 54.1 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.846
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ05 | Any | Cap-Tons | 203 | 0 | None | 297 | 0.113 | 0 | 189 | 0.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.137
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ05 | Any | Cap-Tons | 264 | 0 | None | 132 | 0.084 | 0 | 84.3 | 0.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.387
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ05 | Any | Cap-Tons | 90.7 | 0 | None | 191 | 0.121 | 0 | 122 | 0.0768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.846
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ05 | Any | Cap-Tons | 364 | 0 | None | 151 | 0.0754 | 0 | 96.2 | 0.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.225
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ05 | Any | Cap-Tons | 24.9 | 0 | None | 171 | 0.0878 | 0 | 109 | 0.0559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.285
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ05 | Any | Cap-Tons | 194 | 0 | None | 146 | 0.102 | 0 | 92.7 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.557
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ06 | Any | Cap-Tons | 765 | 0 | None | 232 | 0.173 | 0 | 148 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.375
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ06 | Any | Cap-Tons | 394 | 0 | None | 172 | 0.107 | 0 | 109 | 0.0683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.902
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ06 | Any | Cap-Tons | 2610 | 0 | None | 208 | 0.158 | 0 | 133 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 11.375
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ06 | Any | Cap-Tons | 809 | 0 | None | 184 | 0.0933 | 0 | 117 | 0.0595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.571
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ06 | Any | Cap-Tons | 268 | 0 | None | 350 | 0.154 | 0 | 223 | 0.0981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 16.006
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ06 | Any | Cap-Tons | 356 | 0 | None | 223 | 0.117 | 0 | 142 | 0.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 32.51
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ06 | Any | Cap-Tons | 128 | 0 | None | 316 | 0.177 | 0 | 202 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 12.571
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ06 | Any | Cap-Tons | 466 | 0 | None | 239 | 0.0973 | 0 | 152 | 0.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 109.432
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ06 | Any | Cap-Tons | 31.9 | 0 | None | 269 | 0.108 | 0 | 172 | 0.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 24.662
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ06 | Any | Cap-Tons | 266 | 0 | None | 254 | 0.159 | 0 | 162 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 31.015
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ08 | Any | Cap-Tons | 813 | 0 | None | 265 | 0.16 | 0 | 169 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.447
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ08 | Any | Cap-Tons | 422 | 0 | None | 208 | 0.106 | 0 | 132 | 0.0677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.927
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ08 | Any | Cap-Tons | 2840 | 0 | None | 234 | 0.144 | 0 | 149 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.447
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ08 | Any | Cap-Tons | 883 | 0 | None | 202 | 0.0824 | 0 | 129 | 0.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.377
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ08 | Any | Cap-Tons | 284 | 0 | None | 381 | 0.143 | 0 | 243 | 0.0914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.317
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ08 | Any | Cap-Tons | 389 | 0 | None | 245 | 0.106 | 0 | 156 | 0.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 47.444
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ08 | Any | Cap-Tons | 138 | 0 | None | 363 | 0.167 | 0 | 232 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 13.377
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ08 | Any | Cap-Tons | 511 | 0 | None | 251 | 0.0842 | 0 | 160 | 0.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 132.939
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ08 | Any | Cap-Tons | 33.1 | 0 | None | 298 | 0.105 | 0 | 190 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 29.77
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ08 | Any | Cap-Tons | 286 | 0 | None | 302 | 0.159 | 0 | 192 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 35.172
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ09 | Any | Cap-Tons | 985 | 0 | None | 246 | 0.213 | 0 | 156 | 0.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.959
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ09 | Any | Cap-Tons | 508 | 0 | None | 186 | 0.139 | 0 | 119 | 0.0885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 9.851
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ09 | Any | Cap-Tons | 1000 | 0 | None | 198 | 0.112 | 0 | 126 | 0.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.611
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ09 | Any | Cap-Tons | 348 | 0 | None | 350 | 0.181 | 0 | 223 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 7.431
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ09 | Any | Cap-Tons | 449 | 0 | None | 248 | 0.161 | 0 | 158 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.149
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ09 | Any | Cap-Tons | 171 | 0 | None | 340 | 0.206 | 0 | 216 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.611
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ09 | Any | Cap-Tons | 556 | 0 | None | 247 | 0.13 | 0 | 157 | 0.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 79.468
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ09 | Any | Cap-Tons | 39.3 | 0 | None | 276 | 0.141 | 0 | 176 | 0.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 15.6
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ09 | Any | Cap-Tons | 346 | 0 | None | 262 | 0.183 | 0 | 167 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.751
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ10 | Any | Cap-Tons | 877 | 0 | None | 282 | 0.229 | 0 | 180 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.501
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ10 | Any | Cap-Tons | 454 | 0 | None | 227 | 0.159 | 0 | 144 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 10.428
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ10 | Any | Cap-Tons | 3050 | 0 | None | 259 | 0.202 | 0 | 165 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.501
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ10 | Any | Cap-Tons | 896 | 0 | None | 217 | 0.118 | 0 | 138 | 0.0754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.854
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ10 | Any | Cap-Tons | 322 | 0 | None | 390 | 0.194 | 0 | 249 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.175
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ10 | Any | Cap-Tons | 414 | 0 | None | 254 | 0.15 | 0 | 162 | 0.0955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 18.966
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ10 | Any | Cap-Tons | 156 | 0 | None | 385 | 0.23 | 0 | 245 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.854
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ10 | Any | Cap-Tons | 516 | 0 | None | 278 | 0.132 | 0 | 177 | 0.0841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 25.533
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ10 | Any | Cap-Tons | 36.7 | 0 | None | 307 | 0.152 | 0 | 195 | 0.0971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 20.244
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ10 | Any | Cap-Tons | 307 | 0 | None | 302 | 0.196 | 0 | 193 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 22.941
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ13 | Any | Cap-Tons | 890 | 0 | None | 293 | 0.177 | 0 | 187 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.874
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ13 | Any | Cap-Tons | 450 | 0 | None | 233 | 0.0862 | 0 | 149 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.284
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ13 | Any | Cap-Tons | 2950 | 0 | None | 283 | 0.193 | 0 | 180 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.874
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ13 | Any | Cap-Tons | 903 | 0 | None | 234 | 0.126 | 0 | 149 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.371
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ13 | Any | Cap-Tons | 317 | 0 | None | 419 | 0.213 | 0 | 267 | 0.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.474
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ13 | Any | Cap-Tons | 428 | 0 | None | 251 | 0.156 | 0 | 160 | 0.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.887
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ13 | Any | Cap-Tons | 160 | 0 | None | 420 | 0.24 | 0 | 267 | 0.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.371
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ13 | Any | Cap-Tons | 517 | 0 | None | 277 | 0.15 | 0 | 176 | 0.0955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.293
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ13 | Any | Cap-Tons | 36.3 | 0 | None | 311 | 0.163 | 0 | 198 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ13 | Any | Cap-Tons | 330 | 0 | None | 290 | 0.195 | 0 | 184 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.222
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ14 | Any | Cap-Tons | 952 | 0 | None | 271 | 0.188 | 0 | 173 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.617
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ14 | Any | Cap-Tons | 490 | 0 | None | 210 | 0.134 | 0 | 134 | 0.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.86
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ14 | Any | Cap-Tons | 3180 | 0 | None | 265 | 0.184 | 0 | 169 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.617
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ14 | Any | Cap-Tons | 941 | 0 | None | 215 | 0.105 | 0 | 137 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.231
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ14 | Any | Cap-Tons | 321 | 0 | None | 410 | 0.185 | 0 | 261 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.137
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ14 | Any | Cap-Tons | 440 | 0 | None | 248 | 0.134 | 0 | 158 | 0.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.946
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ14 | Any | Cap-Tons | 539 | 0 | None | 275 | 0.139 | 0 | 175 | 0.0888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.448
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ14 | Any | Cap-Tons | 38.1 | 0 | None | 305 | 0.147 | 0 | 194 | 0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.955
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ14 | Any | Cap-Tons | 336 | 0 | None | 278 | 0.165 | 0 | 177 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 4.584
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ15 | Any | Cap-Tons | 1200 | 0 | None | 429 | 0.197 | 0 | 273 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.31
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ15 | Any | Cap-Tons | 630 | 0 | None | 337 | 0.138 | 0 | 214 | 0.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.93
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ15 | Any | Cap-Tons | 3930 | 0 | None | 401 | 0.193 | 0 | 256 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.31
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ15 | Any | Cap-Tons | 1120 | 0 | None | 361 | 0.118 | 0 | 230 | 0.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.419
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ15 | Any | Cap-Tons | 383 | 0 | None | 577 | 0.194 | 0 | 367 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.563
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ15 | Any | Cap-Tons | 533 | 0 | None | 394 | 0.153 | 0 | 251 | 0.0973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.866
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ15 | Any | Cap-Tons | 209 | 0 | None | 625 | 0.223 | 0 | 398 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.419
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ15 | Any | Cap-Tons | 636 | 0 | None | 412 | 0.139 | 0 | 262 | 0.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.977
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ15 | Any | Cap-Tons | 43.8 | 0 | None | 484 | 0.158 | 0 | 308 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 5.532
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ15 | Any | Cap-Tons | 410 | 0 | None | 439 | 0.184 | 0 | 279 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.204
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Old | Ex | CZ16 | Any | Cap-Tons | 543 | 0 | None | 175 | 0.155 | 0 | 112 | 0.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.926
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Old | Ex | CZ16 | Any | Cap-Tons | 268 | 0 | None | 134 | 0.0855 | 0 | 85.4 | 0.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.313
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Old | Ex | CZ16 | Any | Cap-Tons | 1920 | 0 | None | 173 | 0.165 | 0 | 110 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.926
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Old | Ex | CZ16 | Any | Cap-Tons | 633 | 0 | None | 127 | 0.098 | 0 | 80.8 | 0.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.914
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Old | Ex | CZ16 | Any | Cap-Tons | 206 | 0 | None | 334 | 0.192 | 0 | 213 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.653
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Old | Ex | CZ16 | Any | Cap-Tons | 280 | 0 | None | 143 | 0.124 | 0 | 91.4 | 0.0789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.849
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Old | Ex | CZ16 | Any | Cap-Tons | 102 | 0 | None | 253 | 0.206 | 0 | 161 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.914
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Old | Ex | CZ16 | Any | Cap-Tons | 401 | 0 | None | 157 | 0.131 | 0 | 100 | 0.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.012
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Old | Ex | CZ16 | Any | Cap-Tons | 25.7 | 0 | None | 186 | 0.146 | 0 | 119 | 0.0929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.728
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Old | Ex | CZ16 | Any | Cap-Tons | 225 | 0 | None | 158 | 0.15 | 0 | 100 | 0.0958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.946
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ06 | Any | Cap-Tons | 608 | 0 | None | 74.9 | 0.0603 | 0 | 74.9 | 0.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ06 | Any | Cap-Tons | 329 | 0 | None | 46.9 | 0.0304 | 0 | 46.9 | 0.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ06 | Any | Cap-Tons | 2020 | 0 | None | 60.6 | 0.0541 | 0 | 60.6 | 0.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ06 | Any | Cap-Tons | 835 | 0 | None | 45.2 | 0.0242 | 0 | 45.2 | 0.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.011
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ06 | Any | Cap-Tons | 155 | 0 | None | 101 | 0.0517 | 0 | 101 | 0.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ06 | Any | Cap-Tons | 308 | 0 | None | 75.7 | 0.036 | 0 | 75.7 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.059
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ06 | Any | Cap-Tons | 101 | 0 | None | 72.5 | 0.0491 | 0 | 72.5 | 0.0491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.011
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ06 | Any | Cap-Tons | 376 | 0 | None | 72.1 | 0.0235 | 0 | 72.1 | 0.0235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ06 | Any | Cap-Tons | 22.2 | 0 | None | 77.8 | 0.0249 | 0 | 77.8 | 0.0249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.037
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ06 | Any | Cap-Tons | 241 | 0 | None | 84.2 | 0.0554 | 0 | 84.2 | 0.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ07 | Any | Cap-Tons | 570 | 0 | None | 75.1 | 0.0551 | 0 | 75.1 | 0.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.473
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ07 | Any | Cap-Tons | 316 | 0 | None | 45.5 | 0.0253 | 0 | 45.5 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.193
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ07 | Any | Cap-Tons | 1960 | 0 | None | 56.8 | 0.0457 | 0 | 56.8 | 0.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.473
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ07 | Any | Cap-Tons | 860 | 0 | None | 44.5 | 0.019 | 0 | 44.5 | 0.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.333
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ07 | Any | Cap-Tons | 141 | 0 | None | 107 | 0.0426 | 0 | 107 | 0.0426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.292
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ07 | Any | Cap-Tons | 306 | 0 | None | 70.4 | 0.0297 | 0 | 70.4 | 0.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.142
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ07 | Any | Cap-Tons | 103 | 0 | None | 67.1 | 0.0356 | 0 | 67.1 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.333
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ07 | Any | Cap-Tons | 366 | 0 | None | 66.6 | 0.0205 | 0 | 66.6 | 0.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.935
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ07 | Any | Cap-Tons | 21.2 | 0 | None | 74 | 0.0213 | 0 | 74 | 0.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.345
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ07 | Any | Cap-Tons | 235 | 0 | None | 80.9 | 0.048 | 0 | 80.9 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.122
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ08 | Any | Cap-Tons | 665 | 0 | None | 81.3 | 0.054 | 0 | 81.3 | 0.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ08 | Any | Cap-Tons | 355 | 0 | None | 54.1 | 0.027 | 0 | 54.1 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ08 | Any | Cap-Tons | 2250 | 0 | None | 66.5 | 0.0474 | 0 | 66.5 | 0.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ08 | Any | Cap-Tons | 930 | 0 | None | 50 | 0.0209 | 0 | 50 | 0.0209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ08 | Any | Cap-Tons | 165 | 0 | None | 113 | 0.0479 | 0 | 113 | 0.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ08 | Any | Cap-Tons | 341 | 0 | None | 78.1 | 0.0313 | 0 | 78.1 | 0.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.036
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ08 | Any | Cap-Tons | 111 | 0 | None | 86.6 | 0.0455 | 0 | 86.6 | 0.0455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ08 | Any | Cap-Tons | 399 | 0 | None | 76 | 0.0214 | 0 | 76 | 0.0214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.076
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ08 | Any | Cap-Tons | 23 | 0 | None | 85.7 | 0.0231 | 0 | 85.7 | 0.0231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ08 | Any | Cap-Tons | 261 | 0 | None | 93.8 | 0.0505 | 0 | 93.8 | 0.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ10 | Any | Cap-Tons | 709 | 0 | None | 85.5 | 0.0776 | 0 | 85.5 | 0.0776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.149
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ10 | Any | Cap-Tons | 370 | 0 | None | 59.8 | 0.0447 | 0 | 59.8 | 0.0447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.113
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ10 | Any | Cap-Tons | 2370 | 0 | None | 73.6 | 0.0678 | 0 | 73.6 | 0.0678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.149
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ10 | Any | Cap-Tons | 940 | 0 | None | 54.8 | 0.0317 | 0 | 54.8 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ10 | Any | Cap-Tons | 195 | 0 | None | 113 | 0.065 | 0 | 113 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.147
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ10 | Any | Cap-Tons | 346 | 0 | None | 82.4 | 0.0464 | 0 | 82.4 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.549
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ10 | Any | Cap-Tons | 115 | 0 | None | 101 | 0.0684 | 0 | 101 | 0.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ10 | Any | Cap-Tons | 414 | 0 | None | 79.5 | 0.0319 | 0 | 79.5 | 0.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.653
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ10 | Any | Cap-Tons | 25 | 0 | None | 87.2 | 0.034 | 0 | 87.2 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.3
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ10 | Any | Cap-Tons | 280 | 0 | None | 99 | 0.0698 | 0 | 99 | 0.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.418
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ14 | Any | Cap-Tons | 755 | 0 | None | 82 | 0.0628 | 0 | 82 | 0.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ14 | Any | Cap-Tons | 405 | 0 | None | 55.3 | 0.0347 | 0 | 55.3 | 0.0347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.003
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ14 | Any | Cap-Tons | 2470 | 0 | None | 75.7 | 0.0585 | 0 | 75.7 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ14 | Any | Cap-Tons | 1030 | 0 | None | 53.5 | 0.0265 | 0 | 53.5 | 0.0265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ14 | Any | Cap-Tons | 208 | 0 | None | 117 | 0.0585 | 0 | 117 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.015
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ14 | Any | Cap-Tons | 374 | 0 | None | 76.3 | 0.0423 | 0 | 76.3 | 0.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ14 | Any | Cap-Tons | 121 | 0 | None | 112 | 0.0648 | 0 | 112 | 0.0648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ14 | Any | Cap-Tons | 427 | 0 | None | 78.6 | 0.0337 | 0 | 78.6 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.016
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ14 | Any | Cap-Tons | 27.1 | 0 | None | 83.3 | 0.0328 | 0 | 83.3 | 0.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ14 | Any | Cap-Tons | 290 | 0 | None | 92.2 | 0.0556 | 0 | 92.2 | 0.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ15 | Any | Cap-Tons | 520 | 0 | None | 90.2 | 0.0394 | 0 | 90.2 | 0.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ15 | Any | Cap-Tons | 271 | 0 | None | 169 | 0.0609 | 0 | 169 | 0.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ15 | Any | Cap-Tons | 462 | 0 | None | 118 | 0.0452 | 0 | 118 | 0.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ15 | Any | Cap-Tons | 525 | 0 | None | 116 | 0.0334 | 0 | 116 | 0.0334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ15 | Any | Cap-Tons | 32.3 | 0 | None | 129 | 0.0354 | 0 | 129 | 0.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.003
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ15 | Any | Cap-Tons | 364 | 0 | None | 141 | 0.0617 | 0 | 141 | 0.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ06 | Any | Cap-Tons | 608 | 0 | None | 137 | 0.111 | 0 | 137 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ06 | Any | Cap-Tons | 329 | 0 | None | 86.1 | 0.0557 | 0 | 86.1 | 0.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ06 | Any | Cap-Tons | 2020 | 0 | None | 111 | 0.0993 | 0 | 111 | 0.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ06 | Any | Cap-Tons | 835 | 0 | None | 82.9 | 0.0444 | 0 | 82.9 | 0.0444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.011
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ06 | Any | Cap-Tons | 155 | 0 | None | 186 | 0.0948 | 0 | 186 | 0.0948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ06 | Any | Cap-Tons | 308 | 0 | None | 139 | 0.0661 | 0 | 139 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.059
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ06 | Any | Cap-Tons | 101 | 0 | None | 133 | 0.0901 | 0 | 133 | 0.0901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.011
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ06 | Any | Cap-Tons | 376 | 0 | None | 132 | 0.043 | 0 | 132 | 0.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ06 | Any | Cap-Tons | 22.2 | 0 | None | 143 | 0.0458 | 0 | 143 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.037
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ06 | Any | Cap-Tons | 241 | 0 | None | 155 | 0.102 | 0 | 155 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ07 | Any | Cap-Tons | 570 | 0 | None | 138 | 0.101 | 0 | 138 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.473
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ07 | Any | Cap-Tons | 316 | 0 | None | 83.5 | 0.0464 | 0 | 83.5 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.193
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ07 | Any | Cap-Tons | 1960 | 0 | None | 104 | 0.0838 | 0 | 104 | 0.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.473
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ07 | Any | Cap-Tons | 860 | 0 | None | 81.7 | 0.0348 | 0 | 81.7 | 0.0348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.333
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ07 | Any | Cap-Tons | 141 | 0 | None | 197 | 0.0781 | 0 | 197 | 0.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.292
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ07 | Any | Cap-Tons | 306 | 0 | None | 129 | 0.0544 | 0 | 129 | 0.0544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.142
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ07 | Any | Cap-Tons | 103 | 0 | None | 123 | 0.0653 | 0 | 123 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.333
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ07 | Any | Cap-Tons | 366 | 0 | None | 122 | 0.0376 | 0 | 122 | 0.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.935
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ07 | Any | Cap-Tons | 21.2 | 0 | None | 136 | 0.0392 | 0 | 136 | 0.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.345
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ07 | Any | Cap-Tons | 235 | 0 | None | 148 | 0.0881 | 0 | 148 | 0.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.122
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ08 | Any | Cap-Tons | 665 | 0 | None | 149 | 0.0991 | 0 | 149 | 0.0991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ08 | Any | Cap-Tons | 355 | 0 | None | 99.2 | 0.0496 | 0 | 99.2 | 0.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ08 | Any | Cap-Tons | 2250 | 0 | None | 122 | 0.087 | 0 | 122 | 0.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ08 | Any | Cap-Tons | 930 | 0 | None | 91.8 | 0.0384 | 0 | 91.8 | 0.0384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ08 | Any | Cap-Tons | 165 | 0 | None | 208 | 0.0878 | 0 | 208 | 0.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ08 | Any | Cap-Tons | 341 | 0 | None | 143 | 0.0575 | 0 | 143 | 0.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.036
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ08 | Any | Cap-Tons | 111 | 0 | None | 159 | 0.0835 | 0 | 159 | 0.0835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ08 | Any | Cap-Tons | 399 | 0 | None | 139 | 0.0393 | 0 | 139 | 0.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.076
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ08 | Any | Cap-Tons | 23 | 0 | None | 157 | 0.0423 | 0 | 157 | 0.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ08 | Any | Cap-Tons | 261 | 0 | None | 172 | 0.0927 | 0 | 172 | 0.0927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ10 | Any | Cap-Tons | 709 | 0 | None | 157 | 0.142 | 0 | 157 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.149
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ10 | Any | Cap-Tons | 370 | 0 | None | 110 | 0.0819 | 0 | 110 | 0.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.113
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ10 | Any | Cap-Tons | 2370 | 0 | None | 135 | 0.124 | 0 | 135 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.149
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ10 | Any | Cap-Tons | 940 | 0 | None | 101 | 0.0581 | 0 | 101 | 0.0581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ10 | Any | Cap-Tons | 195 | 0 | None | 207 | 0.119 | 0 | 207 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.147
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ10 | Any | Cap-Tons | 346 | 0 | None | 151 | 0.0852 | 0 | 151 | 0.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.549
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ10 | Any | Cap-Tons | 115 | 0 | None | 186 | 0.125 | 0 | 186 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ10 | Any | Cap-Tons | 414 | 0 | None | 146 | 0.0585 | 0 | 146 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.653
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ10 | Any | Cap-Tons | 25 | 0 | None | 160 | 0.0623 | 0 | 160 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.3
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ10 | Any | Cap-Tons | 280 | 0 | None | 182 | 0.128 | 0 | 182 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.418
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ14 | Any | Cap-Tons | 755 | 0 | None | 151 | 0.115 | 0 | 151 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ14 | Any | Cap-Tons | 405 | 0 | None | 101 | 0.0637 | 0 | 101 | 0.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.003
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ14 | Any | Cap-Tons | 2470 | 0 | None | 139 | 0.107 | 0 | 139 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ14 | Any | Cap-Tons | 1030 | 0 | None | 98.2 | 0.0486 | 0 | 98.2 | 0.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ14 | Any | Cap-Tons | 208 | 0 | None | 215 | 0.107 | 0 | 215 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.015
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ14 | Any | Cap-Tons | 374 | 0 | None | 140 | 0.0777 | 0 | 140 | 0.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ14 | Any | Cap-Tons | 121 | 0 | None | 205 | 0.119 | 0 | 205 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ14 | Any | Cap-Tons | 427 | 0 | None | 144 | 0.0618 | 0 | 144 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.016
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ14 | Any | Cap-Tons | 27.1 | 0 | None | 153 | 0.0602 | 0 | 153 | 0.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ14 | Any | Cap-Tons | 290 | 0 | None | 169 | 0.102 | 0 | 169 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ15 | Any | Cap-Tons | 520 | 0 | None | 165 | 0.0723 | 0 | 165 | 0.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ15 | Any | Cap-Tons | 271 | 0 | None | 310 | 0.112 | 0 | 310 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ15 | Any | Cap-Tons | 462 | 0 | None | 216 | 0.0829 | 0 | 216 | 0.0829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ15 | Any | Cap-Tons | 525 | 0 | None | 214 | 0.0613 | 0 | 214 | 0.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ15 | Any | Cap-Tons | 32.3 | 0 | None | 237 | 0.0649 | 0 | 237 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.003
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ15 | Any | Cap-Tons | 364 | 0 | None | 259 | 0.113 | 0 | 259 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ06 | Any | Cap-Tons | 608 | 0 | None | 74.9 | 0.0603 | 0 | 74.9 | 0.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ06 | Any | Cap-Tons | 329 | 0 | None | 46.9 | 0.0304 | 0 | 46.9 | 0.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ06 | Any | Cap-Tons | 2020 | 0 | None | 60.6 | 0.0541 | 0 | 60.6 | 0.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ06 | Any | Cap-Tons | 835 | 0 | None | 45.2 | 0.0242 | 0 | 45.2 | 0.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.011
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ06 | Any | Cap-Tons | 155 | 0 | None | 101 | 0.0517 | 0 | 101 | 0.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ06 | Any | Cap-Tons | 308 | 0 | None | 75.7 | 0.036 | 0 | 75.7 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.059
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ06 | Any | Cap-Tons | 101 | 0 | None | 72.5 | 0.0491 | 0 | 72.5 | 0.0491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.011
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ06 | Any | Cap-Tons | 376 | 0 | None | 72.1 | 0.0235 | 0 | 72.1 | 0.0235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ06 | Any | Cap-Tons | 22.2 | 0 | None | 77.8 | 0.0249 | 0 | 77.8 | 0.0249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.037
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ06 | Any | Cap-Tons | 241 | 0 | None | 84.2 | 0.0554 | 0 | 84.2 | 0.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ07 | Any | Cap-Tons | 570 | 0 | None | 75.1 | 0.0551 | 0 | 75.1 | 0.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.473
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ07 | Any | Cap-Tons | 316 | 0 | None | 45.5 | 0.0253 | 0 | 45.5 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.193
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ07 | Any | Cap-Tons | 1960 | 0 | None | 56.8 | 0.0457 | 0 | 56.8 | 0.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.473
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ07 | Any | Cap-Tons | 860 | 0 | None | 44.5 | 0.019 | 0 | 44.5 | 0.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.333
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ07 | Any | Cap-Tons | 141 | 0 | None | 107 | 0.0426 | 0 | 107 | 0.0426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.292
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ07 | Any | Cap-Tons | 306 | 0 | None | 70.4 | 0.0297 | 0 | 70.4 | 0.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.142
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ07 | Any | Cap-Tons | 103 | 0 | None | 67.1 | 0.0356 | 0 | 67.1 | 0.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.333
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ07 | Any | Cap-Tons | 366 | 0 | None | 66.6 | 0.0205 | 0 | 66.6 | 0.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.935
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ07 | Any | Cap-Tons | 21.2 | 0 | None | 74 | 0.0213 | 0 | 74 | 0.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.345
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ07 | Any | Cap-Tons | 235 | 0 | None | 80.9 | 0.048 | 0 | 80.9 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.122
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ08 | Any | Cap-Tons | 665 | 0 | None | 81.3 | 0.054 | 0 | 81.3 | 0.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ08 | Any | Cap-Tons | 355 | 0 | None | 54.1 | 0.027 | 0 | 54.1 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ08 | Any | Cap-Tons | 2250 | 0 | None | 66.5 | 0.0474 | 0 | 66.5 | 0.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ08 | Any | Cap-Tons | 930 | 0 | None | 50 | 0.0209 | 0 | 50 | 0.0209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ08 | Any | Cap-Tons | 165 | 0 | None | 113 | 0.0479 | 0 | 113 | 0.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ08 | Any | Cap-Tons | 341 | 0 | None | 78.1 | 0.0313 | 0 | 78.1 | 0.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.036
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ08 | Any | Cap-Tons | 111 | 0 | None | 86.6 | 0.0455 | 0 | 86.6 | 0.0455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ08 | Any | Cap-Tons | 399 | 0 | None | 76 | 0.0214 | 0 | 76 | 0.0214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.076
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ08 | Any | Cap-Tons | 23 | 0 | None | 85.7 | 0.0231 | 0 | 85.7 | 0.0231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ08 | Any | Cap-Tons | 261 | 0 | None | 93.8 | 0.0505 | 0 | 93.8 | 0.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ10 | Any | Cap-Tons | 709 | 0 | None | 85.5 | 0.0776 | 0 | 85.5 | 0.0776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.149
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ10 | Any | Cap-Tons | 370 | 0 | None | 59.8 | 0.0447 | 0 | 59.8 | 0.0447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.113
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ10 | Any | Cap-Tons | 2370 | 0 | None | 73.6 | 0.0678 | 0 | 73.6 | 0.0678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.149
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ10 | Any | Cap-Tons | 940 | 0 | None | 54.8 | 0.0317 | 0 | 54.8 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ10 | Any | Cap-Tons | 195 | 0 | None | 113 | 0.065 | 0 | 113 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.147
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ10 | Any | Cap-Tons | 346 | 0 | None | 82.4 | 0.0464 | 0 | 82.4 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.549
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ10 | Any | Cap-Tons | 115 | 0 | None | 101 | 0.0684 | 0 | 101 | 0.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ10 | Any | Cap-Tons | 414 | 0 | None | 79.5 | 0.0319 | 0 | 79.5 | 0.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.653
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ10 | Any | Cap-Tons | 25 | 0 | None | 87.2 | 0.034 | 0 | 87.2 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.3
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ10 | Any | Cap-Tons | 280 | 0 | None | 99 | 0.0698 | 0 | 99 | 0.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.418
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ14 | Any | Cap-Tons | 755 | 0 | None | 82 | 0.0628 | 0 | 82 | 0.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ14 | Any | Cap-Tons | 405 | 0 | None | 55.3 | 0.0347 | 0 | 55.3 | 0.0347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.003
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ14 | Any | Cap-Tons | 2470 | 0 | None | 75.7 | 0.0585 | 0 | 75.7 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ14 | Any | Cap-Tons | 1030 | 0 | None | 53.5 | 0.0265 | 0 | 53.5 | 0.0265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ14 | Any | Cap-Tons | 208 | 0 | None | 117 | 0.0585 | 0 | 117 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.015
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ14 | Any | Cap-Tons | 374 | 0 | None | 76.3 | 0.0423 | 0 | 76.3 | 0.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ14 | Any | Cap-Tons | 121 | 0 | None | 112 | 0.0648 | 0 | 112 | 0.0648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ14 | Any | Cap-Tons | 427 | 0 | None | 78.6 | 0.0337 | 0 | 78.6 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.016
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ14 | Any | Cap-Tons | 27.1 | 0 | None | 83.3 | 0.0328 | 0 | 83.3 | 0.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ14 | Any | Cap-Tons | 290 | 0 | None | 92.2 | 0.0556 | 0 | 92.2 | 0.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ15 | Any | Cap-Tons | 520 | 0 | None | 90.2 | 0.0394 | 0 | 90.2 | 0.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ15 | Any | Cap-Tons | 271 | 0 | None | 169 | 0.0609 | 0 | 169 | 0.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ15 | Any | Cap-Tons | 462 | 0 | None | 118 | 0.0452 | 0 | 118 | 0.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ15 | Any | Cap-Tons | 525 | 0 | None | 116 | 0.0334 | 0 | 116 | 0.0334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ15 | Any | Cap-Tons | 32.3 | 0 | None | 129 | 0.0354 | 0 | 129 | 0.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.003
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ15 | Any | Cap-Tons | 364 | 0 | None | 141 | 0.0617 | 0 | 141 | 0.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ06 | Any | Cap-Tons | 608 | 0 | None | 137 | 0.111 | 0 | 137 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ06 | Any | Cap-Tons | 329 | 0 | None | 86.1 | 0.0557 | 0 | 86.1 | 0.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ06 | Any | Cap-Tons | 2020 | 0 | None | 111 | 0.0993 | 0 | 111 | 0.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ06 | Any | Cap-Tons | 835 | 0 | None | 82.9 | 0.0444 | 0 | 82.9 | 0.0444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.011
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ06 | Any | Cap-Tons | 155 | 0 | None | 186 | 0.0948 | 0 | 186 | 0.0948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ06 | Any | Cap-Tons | 308 | 0 | None | 139 | 0.0661 | 0 | 139 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.059
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ06 | Any | Cap-Tons | 101 | 0 | None | 133 | 0.0901 | 0 | 133 | 0.0901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.011
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ06 | Any | Cap-Tons | 376 | 0 | None | 132 | 0.043 | 0 | 132 | 0.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.081
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ06 | Any | Cap-Tons | 22.2 | 0 | None | 143 | 0.0458 | 0 | 143 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.037
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ06 | Any | Cap-Tons | 241 | 0 | None | 155 | 0.102 | 0 | 155 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ07 | Any | Cap-Tons | 570 | 0 | None | 138 | 0.101 | 0 | 138 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.473
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ07 | Any | Cap-Tons | 316 | 0 | None | 83.5 | 0.0464 | 0 | 83.5 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.193
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ07 | Any | Cap-Tons | 1960 | 0 | None | 104 | 0.0838 | 0 | 104 | 0.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.473
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ07 | Any | Cap-Tons | 860 | 0 | None | 81.7 | 0.0348 | 0 | 81.7 | 0.0348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.333
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ07 | Any | Cap-Tons | 141 | 0 | None | 197 | 0.0781 | 0 | 197 | 0.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.292
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ07 | Any | Cap-Tons | 306 | 0 | None | 129 | 0.0544 | 0 | 129 | 0.0544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.142
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ07 | Any | Cap-Tons | 103 | 0 | None | 123 | 0.0653 | 0 | 123 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.333
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ07 | Any | Cap-Tons | 366 | 0 | None | 122 | 0.0376 | 0 | 122 | 0.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.935
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ07 | Any | Cap-Tons | 21.2 | 0 | None | 136 | 0.0392 | 0 | 136 | 0.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.345
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ07 | Any | Cap-Tons | 235 | 0 | None | 148 | 0.0881 | 0 | 148 | 0.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.122
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ08 | Any | Cap-Tons | 665 | 0 | None | 149 | 0.0991 | 0 | 149 | 0.0991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ08 | Any | Cap-Tons | 355 | 0 | None | 99.2 | 0.0496 | 0 | 99.2 | 0.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ08 | Any | Cap-Tons | 2250 | 0 | None | 122 | 0.087 | 0 | 122 | 0.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ08 | Any | Cap-Tons | 930 | 0 | None | 91.8 | 0.0384 | 0 | 91.8 | 0.0384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ08 | Any | Cap-Tons | 165 | 0 | None | 208 | 0.0878 | 0 | 208 | 0.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ08 | Any | Cap-Tons | 341 | 0 | None | 143 | 0.0575 | 0 | 143 | 0.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.036
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ08 | Any | Cap-Tons | 111 | 0 | None | 159 | 0.0835 | 0 | 159 | 0.0835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.019
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ08 | Any | Cap-Tons | 399 | 0 | None | 139 | 0.0393 | 0 | 139 | 0.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.076
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ08 | Any | Cap-Tons | 23 | 0 | None | 157 | 0.0423 | 0 | 157 | 0.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ08 | Any | Cap-Tons | 261 | 0 | None | 172 | 0.0927 | 0 | 172 | 0.0927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ10 | Any | Cap-Tons | 709 | 0 | None | 157 | 0.142 | 0 | 157 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.149
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ10 | Any | Cap-Tons | 370 | 0 | None | 110 | 0.0819 | 0 | 110 | 0.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.113
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ10 | Any | Cap-Tons | 2370 | 0 | None | 135 | 0.124 | 0 | 135 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.149
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ10 | Any | Cap-Tons | 940 | 0 | None | 101 | 0.0581 | 0 | 101 | 0.0581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ10 | Any | Cap-Tons | 195 | 0 | None | 207 | 0.119 | 0 | 207 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.147
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ10 | Any | Cap-Tons | 346 | 0 | None | 151 | 0.0852 | 0 | 151 | 0.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.549
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ10 | Any | Cap-Tons | 115 | 0 | None | 186 | 0.125 | 0 | 186 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.06
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ10 | Any | Cap-Tons | 414 | 0 | None | 146 | 0.0585 | 0 | 146 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.653
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ10 | Any | Cap-Tons | 25 | 0 | None | 160 | 0.0623 | 0 | 160 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.3
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ10 | Any | Cap-Tons | 280 | 0 | None | 182 | 0.128 | 0 | 182 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.418
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ECC | Rec | Rec | CZ14 | Any | Cap-Tons | 755 | 0 | None | 151 | 0.115 | 0 | 151 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ14 | Any | Cap-Tons | 405 | 0 | None | 101 | 0.0637 | 0 | 101 | 0.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.003
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | EUn | Rec | Rec | CZ14 | Any | Cap-Tons | 2470 | 0 | None | 139 | 0.107 | 0 | 139 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Hsp | Rec | Rec | CZ14 | Any | Cap-Tons | 1030 | 0 | None | 98.2 | 0.0486 | 0 | 98.2 | 0.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ14 | Any | Cap-Tons | 208 | 0 | None | 215 | 0.107 | 0 | 215 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.015
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ14 | Any | Cap-Tons | 374 | 0 | None | 140 | 0.0777 | 0 | 140 | 0.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Nrs | Rec | Rec | CZ14 | Any | Cap-Tons | 121 | 0 | None | 205 | 0.119 | 0 | 205 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ14 | Any | Cap-Tons | 427 | 0 | None | 144 | 0.0618 | 0 | 144 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.016
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ14 | Any | Cap-Tons | 27.1 | 0 | None | 153 | 0.0602 | 0 | 153 | 0.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.008
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ14 | Any | Cap-Tons | 290 | 0 | None | 169 | 0.102 | 0 | 169 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | ESe | Rec | Rec | CZ15 | Any | Cap-Tons | 520 | 0 | None | 165 | 0.0723 | 0 | 165 | 0.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Htl | Rec | Rec | CZ15 | Any | Cap-Tons | 271 | 0 | None | 310 | 0.112 | 0 | 310 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | MBT | Rec | Rec | CZ15 | Any | Cap-Tons | 462 | 0 | None | 216 | 0.0829 | 0 | 216 | 0.0829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfL | Rec | Rec | CZ15 | Any | Cap-Tons | 525 | 0 | None | 214 | 0.0613 | 0 | 214 | 0.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | OfS | Rec | Rec | CZ15 | Any | Cap-Tons | 32.3 | 0 | None | 237 | 0.0649 | 0 | 237 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.003
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SDG | Rt3 | Rec | Rec | CZ15 | Any | Cap-Tons | 364 | 0 | None | 259 | 0.113 | 0 | 259 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ01 | Any | Cap-Tons | 318 | 0 | None | 15.3 | 0.0394 | 0 | 15.3 | 0.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ01 | Any | Cap-Tons | 155 | 0 | None | 10.2 | 0.0176 | 0 | 10.2 | 0.0176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ01 | Any | Cap-Tons | 1180 | 0 | None | 12.9 | 0.0298 | 0 | 12.9 | 0.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ01 | Any | Cap-Tons | 530 | 0 | None | 4.9 | 0.0108 | 0 | 4.9 | 0.0108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ01 | Any | Cap-Tons | 88.8 | 0 | None | 41.2 | 0.0255 | 0 | 41.2 | 0.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ01 | Any | Cap-Tons | 178 | 0 | None | 18.3 | 0.0201 | 0 | 18.3 | 0.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ01 | Any | Cap-Tons | 62.8 | 0 | None | 6.4 | 0.017 | 0 | 6.4 | 0.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ01 | Any | Cap-Tons | 244 | 0 | None | 15.2 | 0.0141 | 0 | 15.2 | 0.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ01 | Any | Cap-Tons | 13.8 | 0 | None | 17.4 | 0.0139 | 0 | 17.4 | 0.0139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ01 | Any | Cap-Tons | 133 | 0 | None | 17.1 | 0.0293 | 0 | 17.1 | 0.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ02 | Any | Cap-Tons | 570 | 0 | None | 56.5 | 0.0504 | 0 | 56.5 | 0.0504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.151
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ02 | Any | Cap-Tons | 293 | 0 | None | 38.3 | 0.0202 | 0 | 38.3 | 0.0202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.105
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ02 | Any | Cap-Tons | 1980 | 0 | None | 50.2 | 0.0555 | 0 | 50.2 | 0.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.151
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ02 | Any | Cap-Tons | 835 | 0 | None | 31.4 | 0.0307 | 0 | 31.4 | 0.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.213
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ02 | Any | Cap-Tons | 157 | 0 | None | 83.4 | 0.0716 | 0 | 83.4 | 0.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.168
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ02 | Any | Cap-Tons | 294 | 0 | None | 54.1 | 0.0474 | 0 | 54.1 | 0.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.269
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ02 | Any | Cap-Tons | 99.2 | 0 | None | 58.1 | 0.0683 | 0 | 58.1 | 0.0683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.213
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ02 | Any | Cap-Tons | 360 | 0 | None | 52.9 | 0.0375 | 0 | 52.9 | 0.0375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.711
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ02 | Any | Cap-Tons | 20.6 | 0 | None | 60.6 | 0.0424 | 0 | 60.6 | 0.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.199
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ02 | Any | Cap-Tons | 229 | 0 | None | 66.6 | 0.0675 | 0 | 66.6 | 0.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.285
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ03 | Any | Cap-Tons | 438 | 0 | None | 43.3 | 0.0299 | 0 | 43.3 | 0.0299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.573
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ03 | Any | Cap-Tons | 226 | 0 | None | 27.4 | 0.0072 | 0 | 27.4 | 0.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.313
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ03 | Any | Cap-Tons | 1550 | 0 | None | 35.5 | 0.0334 | 0 | 35.5 | 0.0334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.573
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ03 | Any | Cap-Tons | 581 | 0 | None | 24 | 0.0222 | 0 | 24 | 0.0222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.583
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ03 | Any | Cap-Tons | 122 | 0 | None | 69 | 0.0469 | 0 | 69 | 0.0469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.501
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ03 | Any | Cap-Tons | 230 | 0 | None | 45.5 | 0.0317 | 0 | 45.5 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.045
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ03 | Any | Cap-Tons | 79.1 | 0 | None | 33.4 | 0.042 | 0 | 33.4 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.583
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ03 | Any | Cap-Tons | 292 | 0 | None | 41.6 | 0.0253 | 0 | 41.6 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.492
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ03 | Any | Cap-Tons | 17.7 | 0 | None | 45.2 | 0.027 | 0 | 45.2 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.205
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ03 | Any | Cap-Tons | 182 | 0 | None | 46.4 | 0.0474 | 0 | 46.4 | 0.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.22
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ04 | Any | Cap-Tons | 565 | 0 | None | 63.8 | 0.072 | 0 | 63.8 | 0.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ04 | Any | Cap-Tons | 292 | 0 | None | 43.3 | 0.0393 | 0 | 43.3 | 0.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.212
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ04 | Any | Cap-Tons | 1930 | 0 | None | 55.7 | 0.0623 | 0 | 55.7 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ04 | Any | Cap-Tons | 804 | 0 | None | 37.8 | 0.0275 | 0 | 37.8 | 0.0275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.298
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ04 | Any | Cap-Tons | 164 | 0 | None | 87.9 | 0.0579 | 0 | 87.9 | 0.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.372
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ04 | Any | Cap-Tons | 286 | 0 | None | 62.1 | 0.0425 | 0 | 62.1 | 0.0425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.796
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ04 | Any | Cap-Tons | 96.1 | 0 | None | 67.6 | 0.0604 | 0 | 67.6 | 0.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.298
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ04 | Any | Cap-Tons | 358 | 0 | None | 59.2 | 0.0292 | 0 | 59.2 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.61
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ04 | Any | Cap-Tons | 21.3 | 0 | None | 65.7 | 0.0321 | 0 | 65.7 | 0.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.971
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ04 | Any | Cap-Tons | 230 | 0 | None | 73 | 0.0615 | 0 | 73 | 0.0615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.601
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ05 | Any | Cap-Tons | 380 | 0 | None | 48.9 | 0.0413 | 0 | 48.9 | 0.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ05 | Any | Cap-Tons | 192 | 0 | None | 35 | 0.0228 | 0 | 35 | 0.0228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ05 | Any | Cap-Tons | 1350 | 0 | None | 40.1 | 0.0349 | 0 | 40.1 | 0.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ05 | Any | Cap-Tons | 646 | 0 | None | 21.4 | 0.0148 | 0 | 21.4 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ05 | Any | Cap-Tons | 102 | 0 | None | 77.7 | 0.0345 | 0 | 77.7 | 0.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.156
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ05 | Any | Cap-Tons | 222 | 0 | None | 49.8 | 0.0248 | 0 | 49.8 | 0.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.095
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ05 | Any | Cap-Tons | 77.2 | 0 | None | 33.2 | 0.0271 | 0 | 33.2 | 0.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ05 | Any | Cap-Tons | 286 | 0 | None | 46.2 | 0.0183 | 0 | 46.2 | 0.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.254
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ05 | Any | Cap-Tons | 15.7 | 0 | None | 53.1 | 0.0193 | 0 | 53.1 | 0.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.068
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ05 | Any | Cap-Tons | 172 | 0 | None | 48.9 | 0.0315 | 0 | 48.9 | 0.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ11 | Any | Cap-Tons | 653 | 0 | None | 90.4 | 0.0616 | 0 | 90.4 | 0.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.233
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ11 | Any | Cap-Tons | 339 | 0 | None | 60.1 | 0.0245 | 0 | 60.1 | 0.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.175
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ11 | Any | Cap-Tons | 2180 | 0 | None | 82.3 | 0.0695 | 0 | 82.3 | 0.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.233
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ11 | Any | Cap-Tons | 951 | 0 | None | 57.3 | 0.0358 | 0 | 57.3 | 0.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ11 | Any | Cap-Tons | 203 | 0 | None | 117 | 0.0774 | 0 | 117 | 0.0774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.109
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ11 | Any | Cap-Tons | 355 | 0 | None | 76.8 | 0.0539 | 0 | 76.8 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.324
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ11 | Any | Cap-Tons | 119 | 0 | None | 112 | 0.0847 | 0 | 112 | 0.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ11 | Any | Cap-Tons | 416 | 0 | None | 76.4 | 0.0446 | 0 | 76.4 | 0.0446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.411
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ11 | Any | Cap-Tons | 25.4 | 0 | None | 84.2 | 0.0487 | 0 | 84.2 | 0.0487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.3
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ11 | Any | Cap-Tons | 282 | 0 | None | 93.8 | 0.0684 | 0 | 93.8 | 0.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.325
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ12 | Any | Cap-Tons | 599 | 0 | None | 77.2 | 0.0609 | 0 | 77.2 | 0.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.319
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ12 | Any | Cap-Tons | 313 | 0 | None | 51.4 | 0.0239 | 0 | 51.4 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.535
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ12 | Any | Cap-Tons | 2040 | 0 | None | 68.9 | 0.0675 | 0 | 68.9 | 0.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.319
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ12 | Any | Cap-Tons | 898 | 0 | None | 44.9 | 0.0349 | 0 | 44.9 | 0.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.593
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ12 | Any | Cap-Tons | 184 | 0 | None | 100 | 0.0805 | 0 | 100 | 0.0805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ12 | Any | Cap-Tons | 333 | 0 | None | 65.1 | 0.0526 | 0 | 65.1 | 0.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ12 | Any | Cap-Tons | 110 | 0 | None | 85.3 | 0.0811 | 0 | 85.3 | 0.0811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.593
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ12 | Any | Cap-Tons | 394 | 0 | None | 64.5 | 0.042 | 0 | 64.5 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.387
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ12 | Any | Cap-Tons | 23.8 | 0 | None | 71.4 | 0.0465 | 0 | 71.4 | 0.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.248
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ12 | Any | Cap-Tons | 271 | 0 | None | 79.7 | 0.0688 | 0 | 79.7 | 0.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.236
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ13 | Any | Cap-Tons | 701 | 0 | None | 89.6 | 0.0496 | 0 | 89.6 | 0.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.352
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ13 | Any | Cap-Tons | 372 | 0 | None | 60.7 | 0.0186 | 0 | 60.7 | 0.0186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ13 | Any | Cap-Tons | 2320 | 0 | None | 81.1 | 0.0583 | 0 | 81.1 | 0.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.352
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ13 | Any | Cap-Tons | 962 | 0 | None | 58.9 | 0.0317 | 0 | 58.9 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.467
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ13 | Any | Cap-Tons | 203 | 0 | None | 122 | 0.0688 | 0 | 122 | 0.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ13 | Any | Cap-Tons | 361 | 0 | None | 78.1 | 0.0488 | 0 | 78.1 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.767
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ13 | Any | Cap-Tons | 119 | 0 | None | 117 | 0.0734 | 0 | 117 | 0.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.467
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ13 | Any | Cap-Tons | 409 | 0 | None | 79.8 | 0.0357 | 0 | 79.8 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.397
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ13 | Any | Cap-Tons | 25.7 | 0 | None | 84.5 | 0.0371 | 0 | 84.5 | 0.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.065
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ13 | Any | Cap-Tons | 290 | 0 | None | 95.7 | 0.0658 | 0 | 95.7 | 0.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.852
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ16 | Any | Cap-Tons | 395 | 0 | None | 55.1 | 0.045 | 0 | 55.1 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ16 | Any | Cap-Tons | 209 | 0 | None | 34.4 | 0.021 | 0 | 34.4 | 0.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.024
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ16 | Any | Cap-Tons | 1390 | 0 | None | 48.9 | 0.0511 | 0 | 48.9 | 0.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ16 | Any | Cap-Tons | 651 | 0 | None | 32.5 | 0.0253 | 0 | 32.5 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ16 | Any | Cap-Tons | 116 | 0 | None | 92.1 | 0.064 | 0 | 92.1 | 0.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.044
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ16 | Any | Cap-Tons | 231 | 0 | None | 46.8 | 0.0386 | 0 | 46.8 | 0.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.061
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ16 | Any | Cap-Tons | 78.4 | 0 | None | 58.7 | 0.0564 | 0 | 58.7 | 0.0564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ16 | Any | Cap-Tons | 299 | 0 | None | 47.1 | 0.0337 | 0 | 47.1 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ16 | Any | Cap-Tons | 17.1 | 0 | None | 53 | 0.0368 | 0 | 53 | 0.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.037
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ16 | Any | Cap-Tons | 184 | 0 | None | 55.5 | 0.0523 | 0 | 55.5 | 0.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.016
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ01 | Any | Cap-Tons | 318 | 0 | None | 28.1 | 0.0722 | 0 | 28.1 | 0.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ01 | Any | Cap-Tons | 155 | 0 | None | 18.7 | 0.0322 | 0 | 18.7 | 0.0322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ01 | Any | Cap-Tons | 1180 | 0 | None | 23.6 | 0.0547 | 0 | 23.6 | 0.0547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ01 | Any | Cap-Tons | 530 | 0 | None | 8.9 | 0.0198 | 0 | 8.9 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ01 | Any | Cap-Tons | 88.8 | 0 | None | 75.6 | 0.0468 | 0 | 75.6 | 0.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ01 | Any | Cap-Tons | 178 | 0 | None | 33.6 | 0.037 | 0 | 33.6 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ01 | Any | Cap-Tons | 62.8 | 0 | None | 11.8 | 0.0311 | 0 | 11.8 | 0.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ01 | Any | Cap-Tons | 244 | 0 | None | 27.8 | 0.0259 | 0 | 27.8 | 0.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ01 | Any | Cap-Tons | 13.8 | 0 | None | 31.9 | 0.0255 | 0 | 31.9 | 0.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ01 | Any | Cap-Tons | 133 | 0 | None | 31.3 | 0.0538 | 0 | 31.3 | 0.0538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ02 | Any | Cap-Tons | 570 | 0 | None | 104 | 0.0925 | 0 | 104 | 0.0925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.151
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ02 | Any | Cap-Tons | 293 | 0 | None | 70.3 | 0.037 | 0 | 70.3 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.105
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ02 | Any | Cap-Tons | 1980 | 0 | None | 92.1 | 0.102 | 0 | 92.1 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.151
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ02 | Any | Cap-Tons | 835 | 0 | None | 57.6 | 0.0563 | 0 | 57.6 | 0.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.213
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ02 | Any | Cap-Tons | 157 | 0 | None | 153 | 0.131 | 0 | 153 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.168
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ02 | Any | Cap-Tons | 294 | 0 | None | 99.3 | 0.0869 | 0 | 99.3 | 0.0869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.269
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ02 | Any | Cap-Tons | 99.2 | 0 | None | 107 | 0.125 | 0 | 107 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.213
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ02 | Any | Cap-Tons | 360 | 0 | None | 97 | 0.0689 | 0 | 97 | 0.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.711
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ02 | Any | Cap-Tons | 20.6 | 0 | None | 111 | 0.0778 | 0 | 111 | 0.0778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.199
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ02 | Any | Cap-Tons | 229 | 0 | None | 122 | 0.124 | 0 | 122 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.285
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ03 | Any | Cap-Tons | 438 | 0 | None | 79.5 | 0.0549 | 0 | 79.5 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.573
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ03 | Any | Cap-Tons | 226 | 0 | None | 50.3 | 0.0131 | 0 | 50.3 | 0.0131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.313
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ03 | Any | Cap-Tons | 1550 | 0 | None | 65.2 | 0.0612 | 0 | 65.2 | 0.0612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.573
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ03 | Any | Cap-Tons | 581 | 0 | None | 44 | 0.0408 | 0 | 44 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.583
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ03 | Any | Cap-Tons | 122 | 0 | None | 127 | 0.0861 | 0 | 127 | 0.0861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.501
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ03 | Any | Cap-Tons | 230 | 0 | None | 83.6 | 0.0581 | 0 | 83.6 | 0.0581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.045
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ03 | Any | Cap-Tons | 79.1 | 0 | None | 61.4 | 0.077 | 0 | 61.4 | 0.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.583
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ03 | Any | Cap-Tons | 292 | 0 | None | 76.2 | 0.0464 | 0 | 76.2 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.492
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ03 | Any | Cap-Tons | 17.7 | 0 | None | 83 | 0.0496 | 0 | 83 | 0.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.205
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ03 | Any | Cap-Tons | 182 | 0 | None | 85.1 | 0.087 | 0 | 85.1 | 0.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.22
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ04 | Any | Cap-Tons | 565 | 0 | None | 117 | 0.132 | 0 | 117 | 0.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ04 | Any | Cap-Tons | 292 | 0 | None | 79.4 | 0.0722 | 0 | 79.4 | 0.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.212
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ04 | Any | Cap-Tons | 1930 | 0 | None | 102 | 0.114 | 0 | 102 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ04 | Any | Cap-Tons | 804 | 0 | None | 69.3 | 0.0505 | 0 | 69.3 | 0.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.298
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ04 | Any | Cap-Tons | 164 | 0 | None | 161 | 0.106 | 0 | 161 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.372
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ04 | Any | Cap-Tons | 286 | 0 | None | 114 | 0.0781 | 0 | 114 | 0.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.796
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ04 | Any | Cap-Tons | 96.1 | 0 | None | 124 | 0.111 | 0 | 124 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.298
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ04 | Any | Cap-Tons | 358 | 0 | None | 109 | 0.0536 | 0 | 109 | 0.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.61
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ04 | Any | Cap-Tons | 21.3 | 0 | None | 120 | 0.0588 | 0 | 120 | 0.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.971
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ04 | Any | Cap-Tons | 230 | 0 | None | 134 | 0.113 | 0 | 134 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.601
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ05 | Any | Cap-Tons | 380 | 0 | None | 89.8 | 0.0758 | 0 | 89.8 | 0.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ05 | Any | Cap-Tons | 192 | 0 | None | 64.2 | 0.0418 | 0 | 64.2 | 0.0418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ05 | Any | Cap-Tons | 1350 | 0 | None | 73.6 | 0.0641 | 0 | 73.6 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ05 | Any | Cap-Tons | 646 | 0 | None | 39.3 | 0.0271 | 0 | 39.3 | 0.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ05 | Any | Cap-Tons | 102 | 0 | None | 143 | 0.0634 | 0 | 143 | 0.0634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.156
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ05 | Any | Cap-Tons | 222 | 0 | None | 91.4 | 0.0454 | 0 | 91.4 | 0.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.095
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ05 | Any | Cap-Tons | 77.2 | 0 | None | 60.9 | 0.0497 | 0 | 60.9 | 0.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ05 | Any | Cap-Tons | 286 | 0 | None | 84.8 | 0.0335 | 0 | 84.8 | 0.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.254
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ05 | Any | Cap-Tons | 15.7 | 0 | None | 97.5 | 0.0355 | 0 | 97.5 | 0.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.068
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ05 | Any | Cap-Tons | 172 | 0 | None | 89.7 | 0.0578 | 0 | 89.7 | 0.0578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ11 | Any | Cap-Tons | 653 | 0 | None | 166 | 0.113 | 0 | 166 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.233
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ11 | Any | Cap-Tons | 339 | 0 | None | 110 | 0.0449 | 0 | 110 | 0.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.175
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ11 | Any | Cap-Tons | 2180 | 0 | None | 151 | 0.127 | 0 | 151 | 0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.233
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ11 | Any | Cap-Tons | 951 | 0 | None | 105 | 0.0658 | 0 | 105 | 0.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ11 | Any | Cap-Tons | 203 | 0 | None | 215 | 0.142 | 0 | 215 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.109
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ11 | Any | Cap-Tons | 355 | 0 | None | 141 | 0.0989 | 0 | 141 | 0.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.324
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ11 | Any | Cap-Tons | 119 | 0 | None | 206 | 0.155 | 0 | 206 | 0.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ11 | Any | Cap-Tons | 416 | 0 | None | 140 | 0.0817 | 0 | 140 | 0.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.411
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ11 | Any | Cap-Tons | 25.4 | 0 | None | 154 | 0.0893 | 0 | 154 | 0.0893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.3
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ11 | Any | Cap-Tons | 282 | 0 | None | 172 | 0.125 | 0 | 172 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.325
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ12 | Any | Cap-Tons | 599 | 0 | None | 142 | 0.112 | 0 | 142 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.319
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ12 | Any | Cap-Tons | 313 | 0 | None | 94.3 | 0.0439 | 0 | 94.3 | 0.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.535
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ12 | Any | Cap-Tons | 2040 | 0 | None | 126 | 0.124 | 0 | 126 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.319
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ12 | Any | Cap-Tons | 898 | 0 | None | 82.5 | 0.0641 | 0 | 82.5 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.593
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ12 | Any | Cap-Tons | 184 | 0 | None | 184 | 0.148 | 0 | 184 | 0.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ12 | Any | Cap-Tons | 333 | 0 | None | 119 | 0.0965 | 0 | 119 | 0.0965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.04
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ12 | Any | Cap-Tons | 110 | 0 | None | 156 | 0.149 | 0 | 156 | 0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.593
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ12 | Any | Cap-Tons | 394 | 0 | None | 118 | 0.077 | 0 | 118 | 0.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.387
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ12 | Any | Cap-Tons | 23.8 | 0 | None | 131 | 0.0853 | 0 | 131 | 0.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.248
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ12 | Any | Cap-Tons | 271 | 0 | None | 146 | 0.126 | 0 | 146 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.236
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ13 | Any | Cap-Tons | 701 | 0 | None | 164 | 0.0911 | 0 | 164 | 0.0911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.352
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ13 | Any | Cap-Tons | 372 | 0 | None | 111 | 0.0341 | 0 | 111 | 0.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ13 | Any | Cap-Tons | 2320 | 0 | None | 149 | 0.107 | 0 | 149 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.352
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ13 | Any | Cap-Tons | 962 | 0 | None | 108 | 0.0582 | 0 | 108 | 0.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.467
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ13 | Any | Cap-Tons | 203 | 0 | None | 224 | 0.126 | 0 | 224 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ13 | Any | Cap-Tons | 361 | 0 | None | 143 | 0.0895 | 0 | 143 | 0.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.767
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ13 | Any | Cap-Tons | 119 | 0 | None | 214 | 0.135 | 0 | 214 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.467
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ13 | Any | Cap-Tons | 409 | 0 | None | 146 | 0.0656 | 0 | 146 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.397
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ13 | Any | Cap-Tons | 25.7 | 0 | None | 155 | 0.0681 | 0 | 155 | 0.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.065
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ13 | Any | Cap-Tons | 290 | 0 | None | 176 | 0.121 | 0 | 176 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.852
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ16 | Any | Cap-Tons | 395 | 0 | None | 101 | 0.0826 | 0 | 101 | 0.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ16 | Any | Cap-Tons | 209 | 0 | None | 63.2 | 0.0385 | 0 | 63.2 | 0.0385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.024
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ16 | Any | Cap-Tons | 1390 | 0 | None | 89.8 | 0.0938 | 0 | 89.8 | 0.0938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ16 | Any | Cap-Tons | 651 | 0 | None | 59.6 | 0.0464 | 0 | 59.6 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ16 | Any | Cap-Tons | 116 | 0 | None | 169 | 0.117 | 0 | 169 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.044
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ16 | Any | Cap-Tons | 231 | 0 | None | 85.8 | 0.0708 | 0 | 85.8 | 0.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.061
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ16 | Any | Cap-Tons | 78.4 | 0 | None | 108 | 0.103 | 0 | 108 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ16 | Any | Cap-Tons | 299 | 0 | None | 86.5 | 0.0619 | 0 | 86.5 | 0.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ16 | Any | Cap-Tons | 17.1 | 0 | None | 97.2 | 0.0674 | 0 | 97.2 | 0.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.037
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ16 | Any | Cap-Tons | 184 | 0 | None | 102 | 0.0959 | 0 | 102 | 0.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.016
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ01 | Any | Cap-Tons | 318 | 0 | None | 15.3 | 0.0394 | 0 | 15.3 | 0.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ01 | Any | Cap-Tons | 155 | 0 | None | 10.2 | 0.0176 | 0 | 10.2 | 0.0176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ01 | Any | Cap-Tons | 1180 | 0 | None | 12.9 | 0.0298 | 0 | 12.9 | 0.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ01 | Any | Cap-Tons | 530 | 0 | None | 4.9 | 0.0108 | 0 | 4.9 | 0.0108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ01 | Any | Cap-Tons | 88.8 | 0 | None | 41.2 | 0.0255 | 0 | 41.2 | 0.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ01 | Any | Cap-Tons | 178 | 0 | None | 18.3 | 0.0201 | 0 | 18.3 | 0.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ01 | Any | Cap-Tons | 62.8 | 0 | None | 6.4 | 0.017 | 0 | 6.4 | 0.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ01 | Any | Cap-Tons | 244 | 0 | None | 15.2 | 0.0141 | 0 | 15.2 | 0.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ01 | Any | Cap-Tons | 13.8 | 0 | None | 17.4 | 0.0139 | 0 | 17.4 | 0.0139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ01 | Any | Cap-Tons | 133 | 0 | None | 17.1 | 0.0293 | 0 | 17.1 | 0.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ02 | Any | Cap-Tons | 570 | 0 | None | 56.5 | 0.0504 | 0 | 56.5 | 0.0504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.151
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ02 | Any | Cap-Tons | 293 | 0 | None | 38.3 | 0.0202 | 0 | 38.3 | 0.0202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.105
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ02 | Any | Cap-Tons | 1980 | 0 | None | 50.2 | 0.0555 | 0 | 50.2 | 0.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.151
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ02 | Any | Cap-Tons | 835 | 0 | None | 31.4 | 0.0307 | 0 | 31.4 | 0.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.213
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ02 | Any | Cap-Tons | 157 | 0 | None | 83.4 | 0.0716 | 0 | 83.4 | 0.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.168
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ02 | Any | Cap-Tons | 294 | 0 | None | 54.1 | 0.0474 | 0 | 54.1 | 0.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.269
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ02 | Any | Cap-Tons | 99.2 | 0 | None | 58.1 | 0.0683 | 0 | 58.1 | 0.0683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.213
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ02 | Any | Cap-Tons | 360 | 0 | None | 52.9 | 0.0375 | 0 | 52.9 | 0.0375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.711
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ02 | Any | Cap-Tons | 20.6 | 0 | None | 60.6 | 0.0424 | 0 | 60.6 | 0.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.199
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ02 | Any | Cap-Tons | 229 | 0 | None | 66.6 | 0.0675 | 0 | 66.6 | 0.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.285
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ03 | Any | Cap-Tons | 438 | 0 | None | 43.3 | 0.0299 | 0 | 43.3 | 0.0299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.573
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ03 | Any | Cap-Tons | 226 | 0 | None | 27.4 | 0.0072 | 0 | 27.4 | 0.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.313
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ03 | Any | Cap-Tons | 1550 | 0 | None | 35.5 | 0.0334 | 0 | 35.5 | 0.0334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.573
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ03 | Any | Cap-Tons | 581 | 0 | None | 24 | 0.0222 | 0 | 24 | 0.0222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.583
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ03 | Any | Cap-Tons | 122 | 0 | None | 69 | 0.0469 | 0 | 69 | 0.0469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.501
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ03 | Any | Cap-Tons | 230 | 0 | None | 45.5 | 0.0317 | 0 | 45.5 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.045
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ03 | Any | Cap-Tons | 79.1 | 0 | None | 33.4 | 0.042 | 0 | 33.4 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.583
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ03 | Any | Cap-Tons | 292 | 0 | None | 41.6 | 0.0253 | 0 | 41.6 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.492
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ03 | Any | Cap-Tons | 17.7 | 0 | None | 45.2 | 0.027 | 0 | 45.2 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.205
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ03 | Any | Cap-Tons | 182 | 0 | None | 46.4 | 0.0474 | 0 | 46.4 | 0.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.22
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ04 | Any | Cap-Tons | 565 | 0 | None | 63.8 | 0.072 | 0 | 63.8 | 0.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ04 | Any | Cap-Tons | 292 | 0 | None | 43.3 | 0.0393 | 0 | 43.3 | 0.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.212
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ04 | Any | Cap-Tons | 1930 | 0 | None | 55.7 | 0.0623 | 0 | 55.7 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ04 | Any | Cap-Tons | 804 | 0 | None | 37.8 | 0.0275 | 0 | 37.8 | 0.0275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.298
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ04 | Any | Cap-Tons | 164 | 0 | None | 87.9 | 0.0579 | 0 | 87.9 | 0.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.372
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ04 | Any | Cap-Tons | 286 | 0 | None | 62.1 | 0.0425 | 0 | 62.1 | 0.0425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.796
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ04 | Any | Cap-Tons | 96.1 | 0 | None | 67.6 | 0.0604 | 0 | 67.6 | 0.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.298
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ04 | Any | Cap-Tons | 358 | 0 | None | 59.2 | 0.0292 | 0 | 59.2 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.61
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ04 | Any | Cap-Tons | 21.3 | 0 | None | 65.7 | 0.0321 | 0 | 65.7 | 0.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.971
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ04 | Any | Cap-Tons | 230 | 0 | None | 73 | 0.0615 | 0 | 73 | 0.0615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.601
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ05 | Any | Cap-Tons | 380 | 0 | None | 48.9 | 0.0413 | 0 | 48.9 | 0.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ05 | Any | Cap-Tons | 192 | 0 | None | 35 | 0.0228 | 0 | 35 | 0.0228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ05 | Any | Cap-Tons | 1350 | 0 | None | 40.1 | 0.0349 | 0 | 40.1 | 0.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ05 | Any | Cap-Tons | 646 | 0 | None | 21.4 | 0.0148 | 0 | 21.4 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ05 | Any | Cap-Tons | 102 | 0 | None | 77.7 | 0.0345 | 0 | 77.7 | 0.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.156
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ05 | Any | Cap-Tons | 222 | 0 | None | 49.8 | 0.0248 | 0 | 49.8 | 0.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.095
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ05 | Any | Cap-Tons | 77.2 | 0 | None | 33.2 | 0.0271 | 0 | 33.2 | 0.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ05 | Any | Cap-Tons | 286 | 0 | None | 46.2 | 0.0183 | 0 | 46.2 | 0.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.254
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ05 | Any | Cap-Tons | 15.7 | 0 | None | 53.1 | 0.0193 | 0 | 53.1 | 0.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.068
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ05 | Any | Cap-Tons | 172 | 0 | None | 48.9 | 0.0315 | 0 | 48.9 | 0.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ11 | Any | Cap-Tons | 653 | 0 | None | 90.4 | 0.0616 | 0 | 90.4 | 0.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.233
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ11 | Any | Cap-Tons | 339 | 0 | None | 60.1 | 0.0245 | 0 | 60.1 | 0.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.175
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ11 | Any | Cap-Tons | 2180 | 0 | None | 82.3 | 0.0695 | 0 | 82.3 | 0.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.233
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ11 | Any | Cap-Tons | 951 | 0 | None | 57.3 | 0.0358 | 0 | 57.3 | 0.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ11 | Any | Cap-Tons | 203 | 0 | None | 117 | 0.0774 | 0 | 117 | 0.0774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.109
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ11 | Any | Cap-Tons | 355 | 0 | None | 76.8 | 0.0539 | 0 | 76.8 | 0.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.324
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ11 | Any | Cap-Tons | 119 | 0 | None | 112 | 0.0847 | 0 | 112 | 0.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ11 | Any | Cap-Tons | 416 | 0 | None | 76.4 | 0.0446 | 0 | 76.4 | 0.0446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.411
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ11 | Any | Cap-Tons | 25.4 | 0 | None | 84.2 | 0.0487 | 0 | 84.2 | 0.0487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.3
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ11 | Any | Cap-Tons | 282 | 0 | None | 93.8 | 0.0684 | 0 | 93.8 | 0.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.325
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ12 | Any | Cap-Tons | 599 | 0 | None | 77.2 | 0.0609 | 0 | 77.2 | 0.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.319
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ12 | Any | Cap-Tons | 313 | 0 | None | 51.4 | 0.0239 | 0 | 51.4 | 0.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.535
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ12 | Any | Cap-Tons | 2040 | 0 | None | 68.9 | 0.0675 | 0 | 68.9 | 0.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.319
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ12 | Any | Cap-Tons | 898 | 0 | None | 44.9 | 0.0349 | 0 | 44.9 | 0.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.593
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ12 | Any | Cap-Tons | 184 | 0 | None | 100 | 0.0805 | 0 | 100 | 0.0805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ12 | Any | Cap-Tons | 333 | 0 | None | 65.1 | 0.0526 | 0 | 65.1 | 0.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ12 | Any | Cap-Tons | 110 | 0 | None | 85.3 | 0.0811 | 0 | 85.3 | 0.0811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.593
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ12 | Any | Cap-Tons | 394 | 0 | None | 64.5 | 0.042 | 0 | 64.5 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.387
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ12 | Any | Cap-Tons | 23.8 | 0 | None | 71.4 | 0.0465 | 0 | 71.4 | 0.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.248
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ12 | Any | Cap-Tons | 271 | 0 | None | 79.7 | 0.0688 | 0 | 79.7 | 0.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.236
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ13 | Any | Cap-Tons | 701 | 0 | None | 89.6 | 0.0496 | 0 | 89.6 | 0.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.352
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ13 | Any | Cap-Tons | 372 | 0 | None | 60.7 | 0.0186 | 0 | 60.7 | 0.0186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ13 | Any | Cap-Tons | 2320 | 0 | None | 81.1 | 0.0583 | 0 | 81.1 | 0.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.352
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ13 | Any | Cap-Tons | 962 | 0 | None | 58.9 | 0.0317 | 0 | 58.9 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.467
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ13 | Any | Cap-Tons | 203 | 0 | None | 122 | 0.0688 | 0 | 122 | 0.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ13 | Any | Cap-Tons | 361 | 0 | None | 78.1 | 0.0488 | 0 | 78.1 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.767
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ13 | Any | Cap-Tons | 119 | 0 | None | 117 | 0.0734 | 0 | 117 | 0.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.467
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ13 | Any | Cap-Tons | 409 | 0 | None | 79.8 | 0.0357 | 0 | 79.8 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.397
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ13 | Any | Cap-Tons | 25.7 | 0 | None | 84.5 | 0.0371 | 0 | 84.5 | 0.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.065
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ13 | Any | Cap-Tons | 290 | 0 | None | 95.7 | 0.0658 | 0 | 95.7 | 0.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.852
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ16 | Any | Cap-Tons | 395 | 0 | None | 55.1 | 0.045 | 0 | 55.1 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ16 | Any | Cap-Tons | 209 | 0 | None | 34.4 | 0.021 | 0 | 34.4 | 0.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.024
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ16 | Any | Cap-Tons | 1390 | 0 | None | 48.9 | 0.0511 | 0 | 48.9 | 0.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ16 | Any | Cap-Tons | 651 | 0 | None | 32.5 | 0.0253 | 0 | 32.5 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ16 | Any | Cap-Tons | 116 | 0 | None | 92.1 | 0.064 | 0 | 92.1 | 0.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.044
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ16 | Any | Cap-Tons | 231 | 0 | None | 46.8 | 0.0386 | 0 | 46.8 | 0.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.061
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ16 | Any | Cap-Tons | 78.4 | 0 | None | 58.7 | 0.0564 | 0 | 58.7 | 0.0564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ16 | Any | Cap-Tons | 299 | 0 | None | 47.1 | 0.0337 | 0 | 47.1 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ16 | Any | Cap-Tons | 17.1 | 0 | None | 53 | 0.0368 | 0 | 53 | 0.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.037
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ16 | Any | Cap-Tons | 184 | 0 | None | 55.5 | 0.0523 | 0 | 55.5 | 0.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.016
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ01 | Any | Cap-Tons | 318 | 0 | None | 28.1 | 0.0722 | 0 | 28.1 | 0.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ01 | Any | Cap-Tons | 155 | 0 | None | 18.7 | 0.0322 | 0 | 18.7 | 0.0322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ01 | Any | Cap-Tons | 1180 | 0 | None | 23.6 | 0.0547 | 0 | 23.6 | 0.0547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.032
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ01 | Any | Cap-Tons | 530 | 0 | None | 8.9 | 0.0198 | 0 | 8.9 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ01 | Any | Cap-Tons | 88.8 | 0 | None | 75.6 | 0.0468 | 0 | 75.6 | 0.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.039
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ01 | Any | Cap-Tons | 178 | 0 | None | 33.6 | 0.037 | 0 | 33.6 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ01 | Any | Cap-Tons | 62.8 | 0 | None | 11.8 | 0.0311 | 0 | 11.8 | 0.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.023
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ01 | Any | Cap-Tons | 244 | 0 | None | 27.8 | 0.0259 | 0 | 27.8 | 0.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.048
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ01 | Any | Cap-Tons | 13.8 | 0 | None | 31.9 | 0.0255 | 0 | 31.9 | 0.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ01 | Any | Cap-Tons | 133 | 0 | None | 31.3 | 0.0538 | 0 | 31.3 | 0.0538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ02 | Any | Cap-Tons | 570 | 0 | None | 104 | 0.0925 | 0 | 104 | 0.0925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.151
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ02 | Any | Cap-Tons | 293 | 0 | None | 70.3 | 0.037 | 0 | 70.3 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.105
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ02 | Any | Cap-Tons | 1980 | 0 | None | 92.1 | 0.102 | 0 | 92.1 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.151
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ02 | Any | Cap-Tons | 835 | 0 | None | 57.6 | 0.0563 | 0 | 57.6 | 0.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.213
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ02 | Any | Cap-Tons | 157 | 0 | None | 153 | 0.131 | 0 | 153 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.168
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ02 | Any | Cap-Tons | 294 | 0 | None | 99.3 | 0.0869 | 0 | 99.3 | 0.0869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.269
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ02 | Any | Cap-Tons | 99.2 | 0 | None | 107 | 0.125 | 0 | 107 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.213
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ02 | Any | Cap-Tons | 360 | 0 | None | 97 | 0.0689 | 0 | 97 | 0.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.711
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ02 | Any | Cap-Tons | 20.6 | 0 | None | 111 | 0.0778 | 0 | 111 | 0.0778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.199
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ02 | Any | Cap-Tons | 229 | 0 | None | 122 | 0.124 | 0 | 122 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.285
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ03 | Any | Cap-Tons | 438 | 0 | None | 79.5 | 0.0549 | 0 | 79.5 | 0.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.573
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ03 | Any | Cap-Tons | 226 | 0 | None | 50.3 | 0.0131 | 0 | 50.3 | 0.0131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.313
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ03 | Any | Cap-Tons | 1550 | 0 | None | 65.2 | 0.0612 | 0 | 65.2 | 0.0612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.573
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ03 | Any | Cap-Tons | 581 | 0 | None | 44 | 0.0408 | 0 | 44 | 0.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.583
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ03 | Any | Cap-Tons | 122 | 0 | None | 127 | 0.0861 | 0 | 127 | 0.0861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.501
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ03 | Any | Cap-Tons | 230 | 0 | None | 83.6 | 0.0581 | 0 | 83.6 | 0.0581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.045
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ03 | Any | Cap-Tons | 79.1 | 0 | None | 61.4 | 0.077 | 0 | 61.4 | 0.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.583
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ03 | Any | Cap-Tons | 292 | 0 | None | 76.2 | 0.0464 | 0 | 76.2 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 6.492
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ03 | Any | Cap-Tons | 17.7 | 0 | None | 83 | 0.0496 | 0 | 83 | 0.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.205
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ03 | Any | Cap-Tons | 182 | 0 | None | 85.1 | 0.087 | 0 | 85.1 | 0.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.22
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ04 | Any | Cap-Tons | 565 | 0 | None | 117 | 0.132 | 0 | 117 | 0.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ04 | Any | Cap-Tons | 292 | 0 | None | 79.4 | 0.0722 | 0 | 79.4 | 0.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.212
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ04 | Any | Cap-Tons | 1930 | 0 | None | 102 | 0.114 | 0 | 102 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ04 | Any | Cap-Tons | 804 | 0 | None | 69.3 | 0.0505 | 0 | 69.3 | 0.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.298
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ04 | Any | Cap-Tons | 164 | 0 | None | 161 | 0.106 | 0 | 161 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.372
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ04 | Any | Cap-Tons | 286 | 0 | None | 114 | 0.0781 | 0 | 114 | 0.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.796
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ04 | Any | Cap-Tons | 96.1 | 0 | None | 124 | 0.111 | 0 | 124 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.298
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ04 | Any | Cap-Tons | 358 | 0 | None | 109 | 0.0536 | 0 | 109 | 0.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.61
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ04 | Any | Cap-Tons | 21.3 | 0 | None | 120 | 0.0588 | 0 | 120 | 0.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.971
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ04 | Any | Cap-Tons | 230 | 0 | None | 134 | 0.113 | 0 | 134 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.601
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ05 | Any | Cap-Tons | 380 | 0 | None | 89.8 | 0.0758 | 0 | 89.8 | 0.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ05 | Any | Cap-Tons | 192 | 0 | None | 64.2 | 0.0418 | 0 | 64.2 | 0.0418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ05 | Any | Cap-Tons | 1350 | 0 | None | 73.6 | 0.0641 | 0 | 73.6 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.153
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ05 | Any | Cap-Tons | 646 | 0 | None | 39.3 | 0.0271 | 0 | 39.3 | 0.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ05 | Any | Cap-Tons | 102 | 0 | None | 143 | 0.0634 | 0 | 143 | 0.0634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.156
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ05 | Any | Cap-Tons | 222 | 0 | None | 91.4 | 0.0454 | 0 | 91.4 | 0.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.095
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ05 | Any | Cap-Tons | 77.2 | 0 | None | 60.9 | 0.0497 | 0 | 60.9 | 0.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.045
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ05 | Any | Cap-Tons | 286 | 0 | None | 84.8 | 0.0335 | 0 | 84.8 | 0.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.254
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ05 | Any | Cap-Tons | 15.7 | 0 | None | 97.5 | 0.0355 | 0 | 97.5 | 0.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.068
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ05 | Any | Cap-Tons | 172 | 0 | None | 89.7 | 0.0578 | 0 | 89.7 | 0.0578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.104
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ11 | Any | Cap-Tons | 653 | 0 | None | 166 | 0.113 | 0 | 166 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.233
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ11 | Any | Cap-Tons | 339 | 0 | None | 110 | 0.0449 | 0 | 110 | 0.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.175
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ11 | Any | Cap-Tons | 2180 | 0 | None | 151 | 0.127 | 0 | 151 | 0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.233
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ11 | Any | Cap-Tons | 951 | 0 | None | 105 | 0.0658 | 0 | 105 | 0.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ11 | Any | Cap-Tons | 203 | 0 | None | 215 | 0.142 | 0 | 215 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.109
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ11 | Any | Cap-Tons | 355 | 0 | None | 141 | 0.0989 | 0 | 141 | 0.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.324
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ11 | Any | Cap-Tons | 119 | 0 | None | 206 | 0.155 | 0 | 206 | 0.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.18
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ11 | Any | Cap-Tons | 416 | 0 | None | 140 | 0.0817 | 0 | 140 | 0.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.411
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ11 | Any | Cap-Tons | 25.4 | 0 | None | 154 | 0.0893 | 0 | 154 | 0.0893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.3
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ11 | Any | Cap-Tons | 282 | 0 | None | 172 | 0.125 | 0 | 172 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.325
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ12 | Any | Cap-Tons | 599 | 0 | None | 142 | 0.112 | 0 | 142 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.319
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ12 | Any | Cap-Tons | 313 | 0 | None | 94.3 | 0.0439 | 0 | 94.3 | 0.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.535
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ12 | Any | Cap-Tons | 2040 | 0 | None | 126 | 0.124 | 0 | 126 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.319
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ12 | Any | Cap-Tons | 898 | 0 | None | 82.5 | 0.0641 | 0 | 82.5 | 0.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.593
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ12 | Any | Cap-Tons | 184 | 0 | None | 184 | 0.148 | 0 | 184 | 0.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ12 | Any | Cap-Tons | 333 | 0 | None | 119 | 0.0965 | 0 | 119 | 0.0965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.04
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ12 | Any | Cap-Tons | 110 | 0 | None | 156 | 0.149 | 0 | 156 | 0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.593
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ12 | Any | Cap-Tons | 394 | 0 | None | 118 | 0.077 | 0 | 118 | 0.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 3.387
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ12 | Any | Cap-Tons | 23.8 | 0 | None | 131 | 0.0853 | 0 | 131 | 0.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.248
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ12 | Any | Cap-Tons | 271 | 0 | None | 146 | 0.126 | 0 | 146 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.236
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ13 | Any | Cap-Tons | 701 | 0 | None | 164 | 0.0911 | 0 | 164 | 0.0911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.352
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ13 | Any | Cap-Tons | 372 | 0 | None | 111 | 0.0341 | 0 | 111 | 0.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ13 | Any | Cap-Tons | 2320 | 0 | None | 149 | 0.107 | 0 | 149 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.352
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ13 | Any | Cap-Tons | 962 | 0 | None | 108 | 0.0582 | 0 | 108 | 0.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.467
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ13 | Any | Cap-Tons | 203 | 0 | None | 224 | 0.126 | 0 | 224 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.231
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ13 | Any | Cap-Tons | 361 | 0 | None | 143 | 0.0895 | 0 | 143 | 0.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.767
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ13 | Any | Cap-Tons | 119 | 0 | None | 214 | 0.135 | 0 | 214 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.467
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ13 | Any | Cap-Tons | 409 | 0 | None | 146 | 0.0656 | 0 | 146 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.397
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ13 | Any | Cap-Tons | 25.7 | 0 | None | 155 | 0.0681 | 0 | 155 | 0.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.065
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ13 | Any | Cap-Tons | 290 | 0 | None | 176 | 0.121 | 0 | 176 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.852
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ECC | Rec | Rec | CZ16 | Any | Cap-Tons | 395 | 0 | None | 101 | 0.0826 | 0 | 101 | 0.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | ESe | Rec | Rec | CZ16 | Any | Cap-Tons | 209 | 0 | None | 63.2 | 0.0385 | 0 | 63.2 | 0.0385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.024
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | EUn | Rec | Rec | CZ16 | Any | Cap-Tons | 1390 | 0 | None | 89.8 | 0.0938 | 0 | 89.8 | 0.0938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.005
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Hsp | Rec | Rec | CZ16 | Any | Cap-Tons | 651 | 0 | None | 59.6 | 0.0464 | 0 | 59.6 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Htl | Rec | Rec | CZ16 | Any | Cap-Tons | 116 | 0 | None | 169 | 0.117 | 0 | 169 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.044
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | MBT | Rec | Rec | CZ16 | Any | Cap-Tons | 231 | 0 | None | 85.8 | 0.0708 | 0 | 85.8 | 0.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.061
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Nrs | Rec | Rec | CZ16 | Any | Cap-Tons | 78.4 | 0 | None | 108 | 0.103 | 0 | 108 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.009
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfL | Rec | Rec | CZ16 | Any | Cap-Tons | 299 | 0 | None | 86.5 | 0.0619 | 0 | 86.5 | 0.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.035
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | OfS | Rec | Rec | CZ16 | Any | Cap-Tons | 17.1 | 0 | None | 97.2 | 0.0674 | 0 | 97.2 | 0.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.037
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | PGE | Rt3 | Rec | Rec | CZ16 | Any | Cap-Tons | 184 | 0 | None | 102 | 0.0959 | 0 | 102 | 0.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.016
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ05 | Any | Cap-Tons | 374 | 0 | None | 49 | 0.0415 | 0 | 49 | 0.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ05 | Any | Cap-Tons | 188 | 0 | None | 35.1 | 0.0231 | 0 | 35.1 | 0.0231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ05 | Any | Cap-Tons | 1340 | 0 | None | 39.9 | 0.0349 | 0 | 39.9 | 0.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ05 | Any | Cap-Tons | 646 | 0 | None | 21.4 | 0.0148 | 0 | 21.4 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ05 | Any | Cap-Tons | 102 | 0 | None | 77.7 | 0.0345 | 0 | 77.7 | 0.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ05 | Any | Cap-Tons | 222 | 0 | None | 49.8 | 0.0248 | 0 | 49.8 | 0.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ05 | Any | Cap-Tons | 77.2 | 0 | None | 33.2 | 0.0271 | 0 | 33.2 | 0.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ05 | Any | Cap-Tons | 286 | 0 | None | 46.2 | 0.0183 | 0 | 46.2 | 0.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.021
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ05 | Any | Cap-Tons | 15.7 | 0 | None | 53.1 | 0.0193 | 0 | 53.1 | 0.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.012
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ05 | Any | Cap-Tons | 172 | 0 | None | 48.9 | 0.0315 | 0 | 48.9 | 0.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ06 | Any | Cap-Tons | 608 | 0 | None | 74.9 | 0.0603 | 0 | 74.9 | 0.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ06 | Any | Cap-Tons | 329 | 0 | None | 46.9 | 0.0304 | 0 | 46.9 | 0.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.204
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ06 | Any | Cap-Tons | 2020 | 0 | None | 60.6 | 0.0541 | 0 | 60.6 | 0.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ06 | Any | Cap-Tons | 835 | 0 | None | 45.2 | 0.0242 | 0 | 45.2 | 0.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.392
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ06 | Any | Cap-Tons | 155 | 0 | None | 101 | 0.0517 | 0 | 101 | 0.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.48
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ06 | Any | Cap-Tons | 308 | 0 | None | 75.7 | 0.036 | 0 | 75.7 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.467
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ06 | Any | Cap-Tons | 101 | 0 | None | 72.6 | 0.0492 | 0 | 72.6 | 0.0492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.392
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ06 | Any | Cap-Tons | 376 | 0 | None | 72.1 | 0.0235 | 0 | 72.1 | 0.0235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.16
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ06 | Any | Cap-Tons | 22.2 | 0 | None | 77.8 | 0.0249 | 0 | 77.8 | 0.0249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.039
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ06 | Any | Cap-Tons | 241 | 0 | None | 84.2 | 0.0554 | 0 | 84.2 | 0.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.611
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ08 | Any | Cap-Tons | 663 | 0 | None | 81.3 | 0.054 | 0 | 81.3 | 0.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.689
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ08 | Any | Cap-Tons | 355 | 0 | None | 54.1 | 0.027 | 0 | 54.1 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ08 | Any | Cap-Tons | 2240 | 0 | None | 66.4 | 0.0474 | 0 | 66.4 | 0.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.689
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ08 | Any | Cap-Tons | 930 | 0 | None | 50.1 | 0.0209 | 0 | 50.1 | 0.0209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.425
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ08 | Any | Cap-Tons | 165 | 0 | None | 113 | 0.0479 | 0 | 113 | 0.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.303
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ08 | Any | Cap-Tons | 341 | 0 | None | 78.1 | 0.0313 | 0 | 78.1 | 0.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.135
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ08 | Any | Cap-Tons | 111 | 0 | None | 86.7 | 0.0455 | 0 | 86.7 | 0.0455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.425
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ08 | Any | Cap-Tons | 399 | 0 | None | 76 | 0.0214 | 0 | 76 | 0.0214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.691
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ08 | Any | Cap-Tons | 23 | 0 | None | 85.7 | 0.0231 | 0 | 85.7 | 0.0231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.254
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ08 | Any | Cap-Tons | 261 | 0 | None | 93.8 | 0.0505 | 0 | 93.8 | 0.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.845
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ09 | Any | Cap-Tons | 794 | 0 | None | 75 | 0.0747 | 0 | 75 | 0.0747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ09 | Any | Cap-Tons | 418 | 0 | None | 51.1 | 0.0436 | 0 | 51.1 | 0.0436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.204
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ09 | Any | Cap-Tons | 2610 | 0 | None | 63.5 | 0.0653 | 0 | 63.5 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ09 | Any | Cap-Tons | 1060 | 0 | None | 49.3 | 0.0297 | 0 | 49.3 | 0.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.271
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ09 | Any | Cap-Tons | 216 | 0 | None | 99.9 | 0.0604 | 0 | 99.9 | 0.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.301
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ09 | Any | Cap-Tons | 372 | 0 | None | 75.7 | 0.0475 | 0 | 75.7 | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.967
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ09 | Any | Cap-Tons | 127 | 0 | None | 86.7 | 0.0598 | 0 | 86.7 | 0.0598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.271
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ09 | Any | Cap-Tons | 464 | 0 | None | 68.9 | 0.0298 | 0 | 68.9 | 0.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.389
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ09 | Any | Cap-Tons | 27.5 | 0 | None | 77.4 | 0.0318 | 0 | 77.4 | 0.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.656
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ09 | Any | Cap-Tons | 319 | 0 | None | 84.2 | 0.064 | 0 | 84.2 | 0.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.021
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ10 | Any | Cap-Tons | 709 | 0 | None | 85.5 | 0.0776 | 0 | 85.5 | 0.0776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ10 | Any | Cap-Tons | 370 | 0 | None | 59.8 | 0.0447 | 0 | 59.8 | 0.0447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.569
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ10 | Any | Cap-Tons | 2370 | 0 | None | 73.6 | 0.0678 | 0 | 73.6 | 0.0678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ10 | Any | Cap-Tons | 940 | 0 | None | 54.8 | 0.0317 | 0 | 54.8 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ10 | Any | Cap-Tons | 195 | 0 | None | 113 | 0.065 | 0 | 113 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.215
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ10 | Any | Cap-Tons | 346 | 0 | None | 82.4 | 0.0464 | 0 | 82.4 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.939
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ10 | Any | Cap-Tons | 115 | 0 | None | 101 | 0.0684 | 0 | 101 | 0.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ10 | Any | Cap-Tons | 414 | 0 | None | 79.5 | 0.0319 | 0 | 79.5 | 0.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.127
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ10 | Any | Cap-Tons | 25 | 0 | None | 87.2 | 0.034 | 0 | 87.2 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.581
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ10 | Any | Cap-Tons | 280 | 0 | None | 99 | 0.0698 | 0 | 99 | 0.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.777
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ13 | Any | Cap-Tons | 701 | 0 | None | 89.6 | 0.0496 | 0 | 89.6 | 0.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ13 | Any | Cap-Tons | 372 | 0 | None | 60.7 | 0.0186 | 0 | 60.7 | 0.0186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.125
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ13 | Any | Cap-Tons | 2320 | 0 | None | 81.1 | 0.0583 | 0 | 81.1 | 0.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ13 | Any | Cap-Tons | 962 | 0 | None | 58.9 | 0.0317 | 0 | 58.9 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ13 | Any | Cap-Tons | 203 | 0 | None | 122 | 0.0688 | 0 | 122 | 0.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ13 | Any | Cap-Tons | 361 | 0 | None | 78.2 | 0.0488 | 0 | 78.2 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.223
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ13 | Any | Cap-Tons | 119 | 0 | None | 117 | 0.0734 | 0 | 117 | 0.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ13 | Any | Cap-Tons | 409 | 0 | None | 79.8 | 0.0357 | 0 | 79.8 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.196
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ13 | Any | Cap-Tons | 25.7 | 0 | None | 84.5 | 0.0371 | 0 | 84.5 | 0.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.237
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ13 | Any | Cap-Tons | 290 | 0 | None | 95.7 | 0.0658 | 0 | 95.7 | 0.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.305
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ14 | Any | Cap-Tons | 755 | 0 | None | 82 | 0.0628 | 0 | 82 | 0.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ14 | Any | Cap-Tons | 406 | 0 | None | 55.3 | 0.0347 | 0 | 55.3 | 0.0347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.129
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ14 | Any | Cap-Tons | 2470 | 0 | None | 75.7 | 0.0585 | 0 | 75.7 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ14 | Any | Cap-Tons | 1020 | 0 | None | 54.3 | 0.0269 | 0 | 54.3 | 0.0269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ14 | Any | Cap-Tons | 208 | 0 | None | 117 | 0.0585 | 0 | 117 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.097
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ14 | Any | Cap-Tons | 373 | 0 | None | 76.3 | 0.0423 | 0 | 76.3 | 0.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.486
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ14 | Any | Cap-Tons | 122 | 0 | None | 113 | 0.0652 | 0 | 113 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ14 | Any | Cap-Tons | 427 | 0 | None | 78.6 | 0.0337 | 0 | 78.6 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.381
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ14 | Any | Cap-Tons | 27.1 | 0 | None | 83.3 | 0.0328 | 0 | 83.3 | 0.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ14 | Any | Cap-Tons | 292 | 0 | None | 92.7 | 0.0556 | 0 | 92.7 | 0.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.432
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ15 | Any | Cap-Tons | 981 | 0 | None | 126 | 0.0656 | 0 | 126 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ15 | Any | Cap-Tons | 523 | 0 | None | 90.4 | 0.0393 | 0 | 90.4 | 0.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ15 | Any | Cap-Tons | 3150 | 0 | None | 115 | 0.0618 | 0 | 115 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ15 | Any | Cap-Tons | 1200 | 0 | None | 91.8 | 0.0308 | 0 | 91.8 | 0.0308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ15 | Any | Cap-Tons | 271 | 0 | None | 169 | 0.0609 | 0 | 169 | 0.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.549
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ15 | Any | Cap-Tons | 461 | 0 | None | 118 | 0.0452 | 0 | 118 | 0.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.064
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ15 | Any | Cap-Tons | 157 | 0 | None | 180 | 0.0681 | 0 | 180 | 0.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ15 | Any | Cap-Tons | 524 | 0 | None | 116 | 0.0334 | 0 | 116 | 0.0334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.581
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ15 | Any | Cap-Tons | 32.3 | 0 | None | 129 | 0.0354 | 0 | 129 | 0.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.432
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ15 | Any | Cap-Tons | 366 | 0 | None | 142 | 0.0618 | 0 | 142 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.388
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ16 | Any | Cap-Tons | 394 | 0 | None | 55.1 | 0.0451 | 0 | 55.1 | 0.0451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.277
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ16 | Any | Cap-Tons | 209 | 0 | None | 34.4 | 0.021 | 0 | 34.4 | 0.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ16 | Any | Cap-Tons | 1380 | 0 | None | 48.9 | 0.0512 | 0 | 48.9 | 0.0512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.277
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ16 | Any | Cap-Tons | 651 | 0 | None | 32.4 | 0.0252 | 0 | 32.4 | 0.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ16 | Any | Cap-Tons | 116 | 0 | None | 92.1 | 0.064 | 0 | 92.1 | 0.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.116
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ16 | Any | Cap-Tons | 231 | 0 | None | 46.8 | 0.0386 | 0 | 46.8 | 0.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.307
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ16 | Any | Cap-Tons | 78.4 | 0 | None | 58.6 | 0.0563 | 0 | 58.6 | 0.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ16 | Any | Cap-Tons | 299 | 0 | None | 47.1 | 0.0337 | 0 | 47.1 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.172
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ16 | Any | Cap-Tons | 17.1 | 0 | None | 53 | 0.0368 | 0 | 53 | 0.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ16 | Any | Cap-Tons | 184 | 0 | None | 55.5 | 0.0523 | 0 | 55.5 | 0.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.093
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ05 | Any | Cap-Tons | 374 | 0 | None | 90 | 0.0761 | 0 | 90 | 0.0761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ05 | Any | Cap-Tons | 188 | 0 | None | 64.3 | 0.0424 | 0 | 64.3 | 0.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ05 | Any | Cap-Tons | 1340 | 0 | None | 73.2 | 0.064 | 0 | 73.2 | 0.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ05 | Any | Cap-Tons | 646 | 0 | None | 39.3 | 0.0271 | 0 | 39.3 | 0.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ05 | Any | Cap-Tons | 102 | 0 | None | 143 | 0.0634 | 0 | 143 | 0.0634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ05 | Any | Cap-Tons | 222 | 0 | None | 91.4 | 0.0454 | 0 | 91.4 | 0.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ05 | Any | Cap-Tons | 77.2 | 0 | None | 60.9 | 0.0497 | 0 | 60.9 | 0.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ05 | Any | Cap-Tons | 286 | 0 | None | 84.8 | 0.0335 | 0 | 84.8 | 0.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.021
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ05 | Any | Cap-Tons | 15.7 | 0 | None | 97.5 | 0.0355 | 0 | 97.5 | 0.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.012
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ05 | Any | Cap-Tons | 172 | 0 | None | 89.8 | 0.0578 | 0 | 89.8 | 0.0578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ06 | Any | Cap-Tons | 608 | 0 | None | 137 | 0.111 | 0 | 137 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ06 | Any | Cap-Tons | 329 | 0 | None | 86.1 | 0.0558 | 0 | 86.1 | 0.0558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.204
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ06 | Any | Cap-Tons | 2020 | 0 | None | 111 | 0.0993 | 0 | 111 | 0.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ06 | Any | Cap-Tons | 835 | 0 | None | 83 | 0.0445 | 0 | 83 | 0.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.392
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ06 | Any | Cap-Tons | 155 | 0 | None | 186 | 0.0948 | 0 | 186 | 0.0948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.48
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ06 | Any | Cap-Tons | 308 | 0 | None | 139 | 0.0661 | 0 | 139 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.467
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ06 | Any | Cap-Tons | 101 | 0 | None | 133 | 0.0902 | 0 | 133 | 0.0902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.392
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ06 | Any | Cap-Tons | 376 | 0 | None | 132 | 0.043 | 0 | 132 | 0.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.16
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ06 | Any | Cap-Tons | 22.2 | 0 | None | 143 | 0.0458 | 0 | 143 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.039
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ06 | Any | Cap-Tons | 241 | 0 | None | 155 | 0.102 | 0 | 155 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.611
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ08 | Any | Cap-Tons | 663 | 0 | None | 149 | 0.0991 | 0 | 149 | 0.0991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.689
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ08 | Any | Cap-Tons | 355 | 0 | None | 99.2 | 0.0495 | 0 | 99.2 | 0.0495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ08 | Any | Cap-Tons | 2240 | 0 | None | 122 | 0.087 | 0 | 122 | 0.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.689
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ08 | Any | Cap-Tons | 930 | 0 | None | 91.9 | 0.0384 | 0 | 91.9 | 0.0384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.425
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ08 | Any | Cap-Tons | 165 | 0 | None | 208 | 0.0878 | 0 | 208 | 0.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.303
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ08 | Any | Cap-Tons | 341 | 0 | None | 143 | 0.0575 | 0 | 143 | 0.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.135
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ08 | Any | Cap-Tons | 111 | 0 | None | 159 | 0.0836 | 0 | 159 | 0.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.425
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ08 | Any | Cap-Tons | 399 | 0 | None | 139 | 0.0393 | 0 | 139 | 0.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.691
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ08 | Any | Cap-Tons | 23 | 0 | None | 157 | 0.0423 | 0 | 157 | 0.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.254
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ08 | Any | Cap-Tons | 261 | 0 | None | 172 | 0.0927 | 0 | 172 | 0.0927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.845
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ09 | Any | Cap-Tons | 794 | 0 | None | 138 | 0.137 | 0 | 138 | 0.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ09 | Any | Cap-Tons | 418 | 0 | None | 93.8 | 0.08 | 0 | 93.8 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.204
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ09 | Any | Cap-Tons | 2610 | 0 | None | 116 | 0.12 | 0 | 116 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ09 | Any | Cap-Tons | 1060 | 0 | None | 90.5 | 0.0546 | 0 | 90.5 | 0.0546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.271
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ09 | Any | Cap-Tons | 216 | 0 | None | 183 | 0.111 | 0 | 183 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.301
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ09 | Any | Cap-Tons | 372 | 0 | None | 139 | 0.0871 | 0 | 139 | 0.0871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.967
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ09 | Any | Cap-Tons | 127 | 0 | None | 159 | 0.11 | 0 | 159 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.271
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ09 | Any | Cap-Tons | 464 | 0 | None | 126 | 0.0548 | 0 | 126 | 0.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.389
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ09 | Any | Cap-Tons | 27.5 | 0 | None | 142 | 0.0584 | 0 | 142 | 0.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.656
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ09 | Any | Cap-Tons | 319 | 0 | None | 155 | 0.117 | 0 | 155 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.021
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ10 | Any | Cap-Tons | 709 | 0 | None | 157 | 0.142 | 0 | 157 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ10 | Any | Cap-Tons | 370 | 0 | None | 110 | 0.0819 | 0 | 110 | 0.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.569
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ10 | Any | Cap-Tons | 2370 | 0 | None | 135 | 0.124 | 0 | 135 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ10 | Any | Cap-Tons | 940 | 0 | None | 101 | 0.0581 | 0 | 101 | 0.0581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ10 | Any | Cap-Tons | 195 | 0 | None | 207 | 0.119 | 0 | 207 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.215
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ10 | Any | Cap-Tons | 346 | 0 | None | 151 | 0.0852 | 0 | 151 | 0.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.939
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ10 | Any | Cap-Tons | 115 | 0 | None | 186 | 0.125 | 0 | 186 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ10 | Any | Cap-Tons | 414 | 0 | None | 146 | 0.0585 | 0 | 146 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.127
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ10 | Any | Cap-Tons | 25 | 0 | None | 160 | 0.0623 | 0 | 160 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.581
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ10 | Any | Cap-Tons | 280 | 0 | None | 182 | 0.128 | 0 | 182 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.777
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ13 | Any | Cap-Tons | 701 | 0 | None | 164 | 0.0911 | 0 | 164 | 0.0911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ13 | Any | Cap-Tons | 372 | 0 | None | 111 | 0.0341 | 0 | 111 | 0.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.125
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ13 | Any | Cap-Tons | 2320 | 0 | None | 149 | 0.107 | 0 | 149 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ13 | Any | Cap-Tons | 962 | 0 | None | 108 | 0.0582 | 0 | 108 | 0.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ13 | Any | Cap-Tons | 203 | 0 | None | 224 | 0.126 | 0 | 224 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ13 | Any | Cap-Tons | 361 | 0 | None | 143 | 0.0895 | 0 | 143 | 0.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.223
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ13 | Any | Cap-Tons | 119 | 0 | None | 214 | 0.135 | 0 | 214 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ13 | Any | Cap-Tons | 409 | 0 | None | 146 | 0.0656 | 0 | 146 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.196
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ13 | Any | Cap-Tons | 25.7 | 0 | None | 155 | 0.0681 | 0 | 155 | 0.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.237
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ13 | Any | Cap-Tons | 290 | 0 | None | 176 | 0.121 | 0 | 176 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.305
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ14 | Any | Cap-Tons | 755 | 0 | None | 151 | 0.115 | 0 | 151 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ14 | Any | Cap-Tons | 406 | 0 | None | 102 | 0.0636 | 0 | 102 | 0.0636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.129
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ14 | Any | Cap-Tons | 2470 | 0 | None | 139 | 0.107 | 0 | 139 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ14 | Any | Cap-Tons | 1020 | 0 | None | 99.7 | 0.0494 | 0 | 99.7 | 0.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ14 | Any | Cap-Tons | 208 | 0 | None | 215 | 0.107 | 0 | 215 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.097
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ14 | Any | Cap-Tons | 373 | 0 | None | 140 | 0.0777 | 0 | 140 | 0.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.486
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ14 | Any | Cap-Tons | 122 | 0 | None | 207 | 0.12 | 0 | 207 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ14 | Any | Cap-Tons | 427 | 0 | None | 144 | 0.0618 | 0 | 144 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.381
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ14 | Any | Cap-Tons | 27.1 | 0 | None | 153 | 0.0602 | 0 | 153 | 0.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ14 | Any | Cap-Tons | 292 | 0 | None | 170 | 0.102 | 0 | 170 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.432
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ15 | Any | Cap-Tons | 981 | 0 | None | 231 | 0.12 | 0 | 231 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ15 | Any | Cap-Tons | 523 | 0 | None | 166 | 0.0721 | 0 | 166 | 0.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ15 | Any | Cap-Tons | 3150 | 0 | None | 211 | 0.113 | 0 | 211 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ15 | Any | Cap-Tons | 1200 | 0 | None | 168 | 0.0565 | 0 | 168 | 0.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ15 | Any | Cap-Tons | 271 | 0 | None | 310 | 0.112 | 0 | 310 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.549
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ15 | Any | Cap-Tons | 461 | 0 | None | 216 | 0.083 | 0 | 216 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.064
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ15 | Any | Cap-Tons | 157 | 0 | None | 330 | 0.125 | 0 | 330 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ15 | Any | Cap-Tons | 524 | 0 | None | 213 | 0.0612 | 0 | 213 | 0.0612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.581
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ15 | Any | Cap-Tons | 32.3 | 0 | None | 237 | 0.0649 | 0 | 237 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.432
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ15 | Any | Cap-Tons | 366 | 0 | None | 260 | 0.113 | 0 | 260 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.388
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ16 | Any | Cap-Tons | 394 | 0 | None | 101 | 0.0828 | 0 | 101 | 0.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.277
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ16 | Any | Cap-Tons | 209 | 0 | None | 63.2 | 0.0385 | 0 | 63.2 | 0.0385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ16 | Any | Cap-Tons | 1380 | 0 | None | 89.7 | 0.0939 | 0 | 89.7 | 0.0939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.277
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ16 | Any | Cap-Tons | 651 | 0 | None | 59.5 | 0.0463 | 0 | 59.5 | 0.0463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ16 | Any | Cap-Tons | 116 | 0 | None | 169 | 0.117 | 0 | 169 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.116
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ16 | Any | Cap-Tons | 231 | 0 | None | 85.8 | 0.0708 | 0 | 85.8 | 0.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.307
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ16 | Any | Cap-Tons | 78.4 | 0 | None | 108 | 0.103 | 0 | 108 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ16 | Any | Cap-Tons | 299 | 0 | None | 86.5 | 0.0619 | 0 | 86.5 | 0.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.172
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ16 | Any | Cap-Tons | 17.1 | 0 | None | 97.2 | 0.0674 | 0 | 97.2 | 0.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ16 | Any | Cap-Tons | 184 | 0 | None | 102 | 0.0959 | 0 | 102 | 0.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.093
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ05 | Any | Cap-Tons | 374 | 0 | None | 49 | 0.0415 | 0 | 49 | 0.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ05 | Any | Cap-Tons | 188 | 0 | None | 35.1 | 0.0231 | 0 | 35.1 | 0.0231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ05 | Any | Cap-Tons | 1340 | 0 | None | 39.9 | 0.0349 | 0 | 39.9 | 0.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ05 | Any | Cap-Tons | 646 | 0 | None | 21.4 | 0.0148 | 0 | 21.4 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ05 | Any | Cap-Tons | 102 | 0 | None | 77.7 | 0.0345 | 0 | 77.7 | 0.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ05 | Any | Cap-Tons | 222 | 0 | None | 49.8 | 0.0248 | 0 | 49.8 | 0.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ05 | Any | Cap-Tons | 77.2 | 0 | None | 33.2 | 0.0271 | 0 | 33.2 | 0.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ05 | Any | Cap-Tons | 286 | 0 | None | 46.2 | 0.0183 | 0 | 46.2 | 0.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.021
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ05 | Any | Cap-Tons | 15.7 | 0 | None | 53.1 | 0.0193 | 0 | 53.1 | 0.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.012
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ05 | Any | Cap-Tons | 172 | 0 | None | 48.9 | 0.0315 | 0 | 48.9 | 0.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ06 | Any | Cap-Tons | 608 | 0 | None | 74.9 | 0.0603 | 0 | 74.9 | 0.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ06 | Any | Cap-Tons | 329 | 0 | None | 46.9 | 0.0304 | 0 | 46.9 | 0.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.204
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ06 | Any | Cap-Tons | 2020 | 0 | None | 60.6 | 0.0541 | 0 | 60.6 | 0.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ06 | Any | Cap-Tons | 835 | 0 | None | 45.2 | 0.0242 | 0 | 45.2 | 0.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.392
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ06 | Any | Cap-Tons | 155 | 0 | None | 101 | 0.0517 | 0 | 101 | 0.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.48
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ06 | Any | Cap-Tons | 308 | 0 | None | 75.7 | 0.036 | 0 | 75.7 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.467
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ06 | Any | Cap-Tons | 101 | 0 | None | 72.6 | 0.0492 | 0 | 72.6 | 0.0492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.392
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ06 | Any | Cap-Tons | 376 | 0 | None | 72.1 | 0.0235 | 0 | 72.1 | 0.0235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.16
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ06 | Any | Cap-Tons | 22.2 | 0 | None | 77.8 | 0.0249 | 0 | 77.8 | 0.0249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.039
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ06 | Any | Cap-Tons | 241 | 0 | None | 84.2 | 0.0554 | 0 | 84.2 | 0.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.611
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ08 | Any | Cap-Tons | 663 | 0 | None | 81.3 | 0.054 | 0 | 81.3 | 0.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.689
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ08 | Any | Cap-Tons | 355 | 0 | None | 54.1 | 0.027 | 0 | 54.1 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ08 | Any | Cap-Tons | 2240 | 0 | None | 66.4 | 0.0474 | 0 | 66.4 | 0.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.689
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ08 | Any | Cap-Tons | 930 | 0 | None | 50.1 | 0.0209 | 0 | 50.1 | 0.0209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.425
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ08 | Any | Cap-Tons | 165 | 0 | None | 113 | 0.0479 | 0 | 113 | 0.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.303
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ08 | Any | Cap-Tons | 341 | 0 | None | 78.1 | 0.0313 | 0 | 78.1 | 0.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.135
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ08 | Any | Cap-Tons | 111 | 0 | None | 86.7 | 0.0455 | 0 | 86.7 | 0.0455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.425
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ08 | Any | Cap-Tons | 399 | 0 | None | 76 | 0.0214 | 0 | 76 | 0.0214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.691
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ08 | Any | Cap-Tons | 23 | 0 | None | 85.7 | 0.0231 | 0 | 85.7 | 0.0231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.254
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ08 | Any | Cap-Tons | 261 | 0 | None | 93.8 | 0.0505 | 0 | 93.8 | 0.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.845
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ09 | Any | Cap-Tons | 794 | 0 | None | 75 | 0.0747 | 0 | 75 | 0.0747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ09 | Any | Cap-Tons | 418 | 0 | None | 51.1 | 0.0436 | 0 | 51.1 | 0.0436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.204
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ09 | Any | Cap-Tons | 2610 | 0 | None | 63.5 | 0.0653 | 0 | 63.5 | 0.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ09 | Any | Cap-Tons | 1060 | 0 | None | 49.3 | 0.0297 | 0 | 49.3 | 0.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.271
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ09 | Any | Cap-Tons | 216 | 0 | None | 99.9 | 0.0604 | 0 | 99.9 | 0.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.301
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ09 | Any | Cap-Tons | 372 | 0 | None | 75.7 | 0.0475 | 0 | 75.7 | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.967
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ09 | Any | Cap-Tons | 127 | 0 | None | 86.7 | 0.0598 | 0 | 86.7 | 0.0598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.271
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ09 | Any | Cap-Tons | 464 | 0 | None | 68.9 | 0.0298 | 0 | 68.9 | 0.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.389
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ09 | Any | Cap-Tons | 27.5 | 0 | None | 77.4 | 0.0318 | 0 | 77.4 | 0.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.656
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ09 | Any | Cap-Tons | 319 | 0 | None | 84.2 | 0.064 | 0 | 84.2 | 0.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.021
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ10 | Any | Cap-Tons | 709 | 0 | None | 85.5 | 0.0776 | 0 | 85.5 | 0.0776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ10 | Any | Cap-Tons | 370 | 0 | None | 59.8 | 0.0447 | 0 | 59.8 | 0.0447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.569
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ10 | Any | Cap-Tons | 2370 | 0 | None | 73.6 | 0.0678 | 0 | 73.6 | 0.0678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ10 | Any | Cap-Tons | 940 | 0 | None | 54.8 | 0.0317 | 0 | 54.8 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ10 | Any | Cap-Tons | 195 | 0 | None | 113 | 0.065 | 0 | 113 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.215
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ10 | Any | Cap-Tons | 346 | 0 | None | 82.4 | 0.0464 | 0 | 82.4 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.939
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ10 | Any | Cap-Tons | 115 | 0 | None | 101 | 0.0684 | 0 | 101 | 0.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ10 | Any | Cap-Tons | 414 | 0 | None | 79.5 | 0.0319 | 0 | 79.5 | 0.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.127
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ10 | Any | Cap-Tons | 25 | 0 | None | 87.2 | 0.034 | 0 | 87.2 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.581
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ10 | Any | Cap-Tons | 280 | 0 | None | 99 | 0.0698 | 0 | 99 | 0.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.777
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ13 | Any | Cap-Tons | 701 | 0 | None | 89.6 | 0.0496 | 0 | 89.6 | 0.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ13 | Any | Cap-Tons | 372 | 0 | None | 60.7 | 0.0186 | 0 | 60.7 | 0.0186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.125
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ13 | Any | Cap-Tons | 2320 | 0 | None | 81.1 | 0.0583 | 0 | 81.1 | 0.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ13 | Any | Cap-Tons | 962 | 0 | None | 58.9 | 0.0317 | 0 | 58.9 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ13 | Any | Cap-Tons | 203 | 0 | None | 122 | 0.0688 | 0 | 122 | 0.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ13 | Any | Cap-Tons | 361 | 0 | None | 78.2 | 0.0488 | 0 | 78.2 | 0.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.223
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ13 | Any | Cap-Tons | 119 | 0 | None | 117 | 0.0734 | 0 | 117 | 0.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ13 | Any | Cap-Tons | 409 | 0 | None | 79.8 | 0.0357 | 0 | 79.8 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.196
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ13 | Any | Cap-Tons | 25.7 | 0 | None | 84.5 | 0.0371 | 0 | 84.5 | 0.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.237
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ13 | Any | Cap-Tons | 290 | 0 | None | 95.7 | 0.0658 | 0 | 95.7 | 0.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.305
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ14 | Any | Cap-Tons | 755 | 0 | None | 82 | 0.0628 | 0 | 82 | 0.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ14 | Any | Cap-Tons | 406 | 0 | None | 55.3 | 0.0347 | 0 | 55.3 | 0.0347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.129
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ14 | Any | Cap-Tons | 2470 | 0 | None | 75.7 | 0.0585 | 0 | 75.7 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ14 | Any | Cap-Tons | 1020 | 0 | None | 54.3 | 0.0269 | 0 | 54.3 | 0.0269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ14 | Any | Cap-Tons | 208 | 0 | None | 117 | 0.0585 | 0 | 117 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.097
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ14 | Any | Cap-Tons | 373 | 0 | None | 76.3 | 0.0423 | 0 | 76.3 | 0.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.486
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ14 | Any | Cap-Tons | 122 | 0 | None | 113 | 0.0652 | 0 | 113 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ14 | Any | Cap-Tons | 427 | 0 | None | 78.6 | 0.0337 | 0 | 78.6 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.381
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ14 | Any | Cap-Tons | 27.1 | 0 | None | 83.3 | 0.0328 | 0 | 83.3 | 0.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ14 | Any | Cap-Tons | 292 | 0 | None | 92.7 | 0.0556 | 0 | 92.7 | 0.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.432
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ15 | Any | Cap-Tons | 981 | 0 | None | 126 | 0.0656 | 0 | 126 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ15 | Any | Cap-Tons | 523 | 0 | None | 90.4 | 0.0393 | 0 | 90.4 | 0.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ15 | Any | Cap-Tons | 3150 | 0 | None | 115 | 0.0618 | 0 | 115 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ15 | Any | Cap-Tons | 1200 | 0 | None | 91.8 | 0.0308 | 0 | 91.8 | 0.0308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ15 | Any | Cap-Tons | 271 | 0 | None | 169 | 0.0609 | 0 | 169 | 0.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.549
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ15 | Any | Cap-Tons | 461 | 0 | None | 118 | 0.0452 | 0 | 118 | 0.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.064
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ15 | Any | Cap-Tons | 157 | 0 | None | 180 | 0.0681 | 0 | 180 | 0.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ15 | Any | Cap-Tons | 524 | 0 | None | 116 | 0.0334 | 0 | 116 | 0.0334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.581
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ15 | Any | Cap-Tons | 32.3 | 0 | None | 129 | 0.0354 | 0 | 129 | 0.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.432
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ15 | Any | Cap-Tons | 366 | 0 | None | 142 | 0.0618 | 0 | 142 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.388
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ16 | Any | Cap-Tons | 394 | 0 | None | 55.1 | 0.0451 | 0 | 55.1 | 0.0451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.277
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ16 | Any | Cap-Tons | 209 | 0 | None | 34.4 | 0.021 | 0 | 34.4 | 0.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ16 | Any | Cap-Tons | 1380 | 0 | None | 48.9 | 0.0512 | 0 | 48.9 | 0.0512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.277
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ16 | Any | Cap-Tons | 651 | 0 | None | 32.4 | 0.0252 | 0 | 32.4 | 0.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ16 | Any | Cap-Tons | 116 | 0 | None | 92.1 | 0.064 | 0 | 92.1 | 0.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.116
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ16 | Any | Cap-Tons | 231 | 0 | None | 46.8 | 0.0386 | 0 | 46.8 | 0.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.307
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ16 | Any | Cap-Tons | 78.4 | 0 | None | 58.6 | 0.0563 | 0 | 58.6 | 0.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ16 | Any | Cap-Tons | 299 | 0 | None | 47.1 | 0.0337 | 0 | 47.1 | 0.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.172
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ16 | Any | Cap-Tons | 17.1 | 0 | None | 53 | 0.0368 | 0 | 53 | 0.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ16 | Any | Cap-Tons | 184 | 0 | None | 55.5 | 0.0523 | 0 | 55.5 | 0.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.093
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ05 | Any | Cap-Tons | 374 | 0 | None | 90 | 0.0761 | 0 | 90 | 0.0761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ05 | Any | Cap-Tons | 188 | 0 | None | 64.3 | 0.0424 | 0 | 64.3 | 0.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ05 | Any | Cap-Tons | 1340 | 0 | None | 73.2 | 0.064 | 0 | 73.2 | 0.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.002
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ05 | Any | Cap-Tons | 646 | 0 | None | 39.3 | 0.0271 | 0 | 39.3 | 0.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ05 | Any | Cap-Tons | 102 | 0 | None | 143 | 0.0634 | 0 | 143 | 0.0634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.004
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ05 | Any | Cap-Tons | 222 | 0 | None | 91.4 | 0.0454 | 0 | 91.4 | 0.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.017
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ05 | Any | Cap-Tons | 77.2 | 0 | None | 60.9 | 0.0497 | 0 | 60.9 | 0.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.025
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ05 | Any | Cap-Tons | 286 | 0 | None | 84.8 | 0.0335 | 0 | 84.8 | 0.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.021
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ05 | Any | Cap-Tons | 15.7 | 0 | None | 97.5 | 0.0355 | 0 | 97.5 | 0.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.012
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ05 | Any | Cap-Tons | 172 | 0 | None | 89.8 | 0.0578 | 0 | 89.8 | 0.0578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.029
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ06 | Any | Cap-Tons | 608 | 0 | None | 137 | 0.111 | 0 | 137 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ06 | Any | Cap-Tons | 329 | 0 | None | 86.1 | 0.0558 | 0 | 86.1 | 0.0558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.204
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ06 | Any | Cap-Tons | 2020 | 0 | None | 111 | 0.0993 | 0 | 111 | 0.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.435
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ06 | Any | Cap-Tons | 835 | 0 | None | 83 | 0.0445 | 0 | 83 | 0.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.392
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ06 | Any | Cap-Tons | 155 | 0 | None | 186 | 0.0948 | 0 | 186 | 0.0948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.48
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ06 | Any | Cap-Tons | 308 | 0 | None | 139 | 0.0661 | 0 | 139 | 0.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.467
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ06 | Any | Cap-Tons | 101 | 0 | None | 133 | 0.0902 | 0 | 133 | 0.0902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.392
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ06 | Any | Cap-Tons | 376 | 0 | None | 132 | 0.043 | 0 | 132 | 0.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.16
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ06 | Any | Cap-Tons | 22.2 | 0 | None | 143 | 0.0458 | 0 | 143 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.039
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ06 | Any | Cap-Tons | 241 | 0 | None | 155 | 0.102 | 0 | 155 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.611
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ08 | Any | Cap-Tons | 663 | 0 | None | 149 | 0.0991 | 0 | 149 | 0.0991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.689
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ08 | Any | Cap-Tons | 355 | 0 | None | 99.2 | 0.0495 | 0 | 99.2 | 0.0495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.363
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ08 | Any | Cap-Tons | 2240 | 0 | None | 122 | 0.087 | 0 | 122 | 0.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.689
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ08 | Any | Cap-Tons | 930 | 0 | None | 91.9 | 0.0384 | 0 | 91.9 | 0.0384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.425
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ08 | Any | Cap-Tons | 165 | 0 | None | 208 | 0.0878 | 0 | 208 | 0.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.303
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ08 | Any | Cap-Tons | 341 | 0 | None | 143 | 0.0575 | 0 | 143 | 0.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.135
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ08 | Any | Cap-Tons | 111 | 0 | None | 159 | 0.0836 | 0 | 159 | 0.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.425
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ08 | Any | Cap-Tons | 399 | 0 | None | 139 | 0.0393 | 0 | 139 | 0.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.691
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ08 | Any | Cap-Tons | 23 | 0 | None | 157 | 0.0423 | 0 | 157 | 0.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.254
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ08 | Any | Cap-Tons | 261 | 0 | None | 172 | 0.0927 | 0 | 172 | 0.0927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.845
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ09 | Any | Cap-Tons | 794 | 0 | None | 138 | 0.137 | 0 | 138 | 0.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ09 | Any | Cap-Tons | 418 | 0 | None | 93.8 | 0.08 | 0 | 93.8 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.204
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ09 | Any | Cap-Tons | 2610 | 0 | None | 116 | 0.12 | 0 | 116 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.176
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ09 | Any | Cap-Tons | 1060 | 0 | None | 90.5 | 0.0546 | 0 | 90.5 | 0.0546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.271
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ09 | Any | Cap-Tons | 216 | 0 | None | 183 | 0.111 | 0 | 183 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.301
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ09 | Any | Cap-Tons | 372 | 0 | None | 139 | 0.0871 | 0 | 139 | 0.0871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.967
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ09 | Any | Cap-Tons | 127 | 0 | None | 159 | 0.11 | 0 | 159 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.271
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ09 | Any | Cap-Tons | 464 | 0 | None | 126 | 0.0548 | 0 | 126 | 0.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.389
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ09 | Any | Cap-Tons | 27.5 | 0 | None | 142 | 0.0584 | 0 | 142 | 0.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.656
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ09 | Any | Cap-Tons | 319 | 0 | None | 155 | 0.117 | 0 | 155 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.021
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ10 | Any | Cap-Tons | 709 | 0 | None | 157 | 0.142 | 0 | 157 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ10 | Any | Cap-Tons | 370 | 0 | None | 110 | 0.0819 | 0 | 110 | 0.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.569
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ10 | Any | Cap-Tons | 2370 | 0 | None | 135 | 0.124 | 0 | 135 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.421
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ10 | Any | Cap-Tons | 940 | 0 | None | 101 | 0.0581 | 0 | 101 | 0.0581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ10 | Any | Cap-Tons | 195 | 0 | None | 207 | 0.119 | 0 | 207 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.215
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ10 | Any | Cap-Tons | 346 | 0 | None | 151 | 0.0852 | 0 | 151 | 0.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.939
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ10 | Any | Cap-Tons | 115 | 0 | None | 186 | 0.125 | 0 | 186 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.463
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ10 | Any | Cap-Tons | 414 | 0 | None | 146 | 0.0585 | 0 | 146 | 0.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.127
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ10 | Any | Cap-Tons | 25 | 0 | None | 160 | 0.0623 | 0 | 160 | 0.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.581
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ10 | Any | Cap-Tons | 280 | 0 | None | 182 | 0.128 | 0 | 182 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 2.777
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ13 | Any | Cap-Tons | 701 | 0 | None | 164 | 0.0911 | 0 | 164 | 0.0911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ13 | Any | Cap-Tons | 372 | 0 | None | 111 | 0.0341 | 0 | 111 | 0.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.125
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ13 | Any | Cap-Tons | 2320 | 0 | None | 149 | 0.107 | 0 | 149 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.112
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ13 | Any | Cap-Tons | 962 | 0 | None | 108 | 0.0582 | 0 | 108 | 0.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ13 | Any | Cap-Tons | 203 | 0 | None | 224 | 0.126 | 0 | 224 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.03
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ13 | Any | Cap-Tons | 361 | 0 | None | 143 | 0.0895 | 0 | 143 | 0.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.223
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ13 | Any | Cap-Tons | 119 | 0 | None | 214 | 0.135 | 0 | 214 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.071
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ13 | Any | Cap-Tons | 409 | 0 | None | 146 | 0.0656 | 0 | 146 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.196
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ13 | Any | Cap-Tons | 25.7 | 0 | None | 155 | 0.0681 | 0 | 155 | 0.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.237
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ13 | Any | Cap-Tons | 290 | 0 | None | 176 | 0.121 | 0 | 176 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.305
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ14 | Any | Cap-Tons | 755 | 0 | None | 151 | 0.115 | 0 | 151 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ14 | Any | Cap-Tons | 406 | 0 | None | 102 | 0.0636 | 0 | 102 | 0.0636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.129
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ14 | Any | Cap-Tons | 2470 | 0 | None | 139 | 0.107 | 0 | 139 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.141
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ14 | Any | Cap-Tons | 1020 | 0 | None | 99.7 | 0.0494 | 0 | 99.7 | 0.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ14 | Any | Cap-Tons | 208 | 0 | None | 215 | 0.107 | 0 | 215 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.097
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ14 | Any | Cap-Tons | 373 | 0 | None | 140 | 0.0777 | 0 | 140 | 0.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.486
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ14 | Any | Cap-Tons | 122 | 0 | None | 207 | 0.12 | 0 | 207 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.075
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ14 | Any | Cap-Tons | 427 | 0 | None | 144 | 0.0618 | 0 | 144 | 0.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.381
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ14 | Any | Cap-Tons | 27.1 | 0 | None | 153 | 0.0602 | 0 | 153 | 0.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.203
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ14 | Any | Cap-Tons | 292 | 0 | None | 170 | 0.102 | 0 | 170 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.432
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ15 | Any | Cap-Tons | 981 | 0 | None | 231 | 0.12 | 0 | 231 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ15 | Any | Cap-Tons | 523 | 0 | None | 166 | 0.0721 | 0 | 166 | 0.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.051
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ15 | Any | Cap-Tons | 3150 | 0 | None | 211 | 0.113 | 0 | 211 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.123
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ15 | Any | Cap-Tons | 1200 | 0 | None | 168 | 0.0565 | 0 | 168 | 0.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ15 | Any | Cap-Tons | 271 | 0 | None | 310 | 0.112 | 0 | 310 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.549
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ15 | Any | Cap-Tons | 461 | 0 | None | 216 | 0.083 | 0 | 216 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 1.064
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ15 | Any | Cap-Tons | 157 | 0 | None | 330 | 0.125 | 0 | 330 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.096
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ15 | Any | Cap-Tons | 524 | 0 | None | 213 | 0.0612 | 0 | 213 | 0.0612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.581
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ15 | Any | Cap-Tons | 32.3 | 0 | None | 237 | 0.0649 | 0 | 237 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.432
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ15 | Any | Cap-Tons | 366 | 0 | None | 260 | 0.113 | 0 | 260 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.388
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ECC | Rec | Rec | CZ16 | Any | Cap-Tons | 394 | 0 | None | 101 | 0.0828 | 0 | 101 | 0.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.277
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | ESe | Rec | Rec | CZ16 | Any | Cap-Tons | 209 | 0 | None | 63.2 | 0.0385 | 0 | 63.2 | 0.0385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.067
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | EUn | Rec | Rec | CZ16 | Any | Cap-Tons | 1380 | 0 | None | 89.7 | 0.0939 | 0 | 89.7 | 0.0939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.277
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Hsp | Rec | Rec | CZ16 | Any | Cap-Tons | 651 | 0 | None | 59.5 | 0.0463 | 0 | 59.5 | 0.0463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Htl | Rec | Rec | CZ16 | Any | Cap-Tons | 116 | 0 | None | 169 | 0.117 | 0 | 169 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.116
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | MBT | Rec | Rec | CZ16 | Any | Cap-Tons | 231 | 0 | None | 85.8 | 0.0708 | 0 | 85.8 | 0.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.307
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Nrs | Rec | Rec | CZ16 | Any | Cap-Tons | 78.4 | 0 | None | 108 | 0.103 | 0 | 108 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.057
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfL | Rec | Rec | CZ16 | Any | Cap-Tons | 299 | 0 | None | 86.5 | 0.0619 | 0 | 86.5 | 0.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.172
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | OfS | Rec | Rec | CZ16 | Any | Cap-Tons | 17.1 | 0 | None | 97.2 | 0.0674 | 0 | 97.2 | 0.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.103
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | DEER2020 | D20 v0 | 2019-01-09 08:57 | SCE | Rt3 | Rec | Rec | CZ16 | Any | Cap-Tons | 184 | 0 | None | 102 | 0.0959 | 0 | 102 | 0.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEER:HVAC_Chillers | Annual | 2020 | 0.093
Note on G7: Akhilesh Endurthy: In

## DEER2020wts
DEER2020 Commercial Weights (in millions of square feet)
minimum set to 1000 sqft
ver | pa | bldgtype | bldgloc | bldgvint | wt_vint | era
2020 | PGE | Asm | CZ01 | 1975 | 0.491 | old
2020 | PGE | Asm | CZ01 | 1985 | 0.233 | old
2020 | PGE | Asm | CZ01 | 1996 | 0.158 | old
2020 | PGE | Asm | CZ01 | 2003 | 0.071 | ex
2020 | PGE | Asm | CZ01 | 2007 | 0.035 | ex
2020 | PGE | Asm | CZ01 | 2011 | 0.035 | ex
2020 | PGE | Asm | CZ01 | 2015 | 0.026 | ex
2020 | PGE | Asm | CZ01 | 2017 | 0.026 | rec
2020 | PGE | Asm | CZ01 | 2020 | 0.009 | rec
2020 | PGE | Asm | CZ01 | New | 0.009 | new
2020 | PGE | Asm | CZ02 | 1975 | 5.202 | old
2020 | PGE | Asm | CZ02 | 1985 | 2.346 | old
2020 | PGE | Asm | CZ02 | 1996 | 1.186 | old
2020 | PGE | Asm | CZ02 | 2003 | 0.597 | ex
2020 | PGE | Asm | CZ02 | 2007 | 0.269 | ex
2020 | PGE | Asm | CZ02 | 2011 | 0.269 | ex
2020 | PGE | Asm | CZ02 | 2015 | 0.202 | ex
2020 | PGE | Asm | CZ02 | 2017 | 0.202 | rec
2020 | PGE | Asm | CZ02 | 2020 | 0.067 | rec
2020 | PGE | Asm | CZ02 | New | 0.067 | new
2020 | PGE | Asm | CZ03 | 1975 | 29.94 | old
2020 | PGE | Asm | CZ03 | 1985 | 8.93 | old
2020 | PGE | Asm | CZ03 | 1996 | 5.631 | old
2020 | PGE | Asm | CZ03 | 2003 | 3.032 | ex
2020 | PGE | Asm | CZ03 | 2007 | 1.046 | ex
2020 | PGE | Asm | CZ03 | 2011 | 1.046 | ex
2020 | PGE | Asm | CZ03 | 2015 | 0.784 | ex
2020 | PGE | Asm | CZ03 | 2017 | 0.784 | rec
2020 | PGE | Asm | CZ03 | 2020 | 0.261 | rec
2020 | PGE | Asm | CZ03 | New | 0.261 | new
2020 | PGE | Asm | CZ04 | 1975 | 13.005 | old
2020 | PGE | Asm | CZ04 | 1985 | 7.296 | old
2020 | PGE | Asm | CZ04 | 1996 | 3.172 | old
2020 | PGE | Asm | CZ04 | 2003 | 1.566 | ex
2020 | PGE | Asm | CZ04 | 2007 | 0.795 | ex
2020 | PGE | Asm | CZ04 | 2011 | 0.795 | ex
2020 | PGE | Asm | CZ04 | 2015 | 0.597 | ex
2020 | PGE | Asm | CZ04 | 2017 | 0.597 | rec
2020 | PGE | Asm | CZ04 | 2020 | 0.199 | rec
2020 | PGE | Asm | CZ04 | New | 0.199 | new
2020 | PGE | Asm | CZ05 | 1975 | 1.551 | old
2020 | PGE | Asm | CZ05 | 1985 | 0.872 | old
2020 | PGE | Asm | CZ05 | 1996 | 0.379 | old
2020 | PGE | Asm | CZ05 | 2003 | 0.187 | ex
2020 | PGE | Asm | CZ05 | 2007 | 0.095 | ex
2020 | PGE | Asm | CZ05 | 2011 | 0.095 | ex
2020 | PGE | Asm | CZ05 | 2015 | 0.071 | ex
2020 | PGE | Asm | CZ05 | 2017 | 0.071 | rec
2020 | PGE | Asm | CZ05 | 2020 | 0.024 | rec
2020 | PGE | Asm | CZ05 | New | 0.024 | new
2020 | PGE | Asm | CZ11 | 1975 | 2.968 | old
2020 | PGE | Asm | CZ11 | 1985 | 1.919 | old
2020 | PGE | Asm | CZ11 | 1996 | 1.142 | old
2020 | PGE | Asm | CZ11 | 2003 | 0.582 | ex
2020 | PGE | Asm | CZ11 | 2007 | 0.324 | ex
2020 | PGE | Asm | CZ11 | 2011 | 0.324 | ex
2020 | PGE | Asm | CZ11 | 2015 | 0.243 | ex
2020 | PGE | Asm | CZ11 | 2017 | 0.243 | rec
2020 | PGE | Asm | CZ11 | 2020 | 0.081 | rec
2020 | PGE | Asm | CZ11 | New | 0.081 | new
2020 | PGE | Asm | CZ12 | 1975 | 12.779 | old
2020 | PGE | Asm | CZ12 | 1985 | 7.629 | old
2020 | PGE | Asm | CZ12 | 1996 | 3.643 | old
2020 | PGE | Asm | CZ12 | 2003 | 2.069 | ex
2020 | PGE | Asm | CZ12 | 2007 | 1.04 | ex
2020 | PGE | Asm | CZ12 | 2011 | 1.04 | ex
2020 | PGE | Asm | CZ12 | 2015 | 0.78 | ex
2020 | PGE | Asm | CZ12 | 2017 | 0.78 | rec
2020 | PGE | Asm | CZ12 | 2020 | 0.26 | rec
2020 | PGE | Asm | CZ12 | New | 0.26 | new
2020 | PGE | Asm | CZ13 | 1975 | 7.423 | old
2020 | PGE | Asm | CZ13 | 1985 | 4.75 | old
2020 | PGE | Asm | CZ13 | 1996 | 3.023 | old
2020 | PGE | Asm | CZ13 | 2003 | 1.222 | ex
2020 | PGE | Asm | CZ13 | 2007 | 0.767 | ex
2020 | PGE | Asm | CZ13 | 2011 | 0.767 | ex
2020 | PGE | Asm | CZ13 | 2015 | 0.575 | ex
2020 | PGE | Asm | CZ13 | 2017 | 0.575 | rec
2020 | PGE | Asm | CZ13 | 2020 | 0.192 | rec
2020 | PGE | Asm | CZ13 | New | 0.192 | new
2020 | PGE | Asm | CZ16 | 1975 | 0.714 | old
2020 | PGE | Asm | CZ16 | 1985 | 0.382 | old
2020 | PGE | Asm | CZ16 | 1996 | 0.255 | old
2020 | PGE | Asm | CZ16 | 2003 | 0.116 | ex
2020 | PGE | Asm | CZ16 | 2007 | 0.062 | ex
2020 | PGE | Asm | CZ16 | 2011 | 0.062 | ex
2020 | PGE | Asm | CZ16 | 2015 | 0.046 | ex
2020 | PGE | Asm | CZ16 | 2017 | 0.046 | rec
2020 | PGE | Asm | CZ16 | 2020 | 0.015 | rec
2020 | PGE | Asm | CZ16 | New | 0.015 | new
2020 | PGE | ECC | CZ01 | 1975 | 1.298 | old
2020 | PGE | ECC | CZ01 | 1985 | 0.236 | old
2020 | PGE | ECC | CZ01 | 1996 | 0.119 | old
2020 | PGE | ECC | CZ01 | 2003 | 0.043 | ex
2020 | PGE | ECC | CZ01 | 2007 | 0.032 | ex
2020 | PGE | ECC | CZ01 | 2011 | 0.032 | ex
2020 | PGE | ECC | CZ01 | 2015 | 0.024 | ex
2020 | PGE | ECC | CZ01 | 2017 | 0.024 | rec
2020 | PGE | ECC | CZ01 | 2020 | 0.008 | rec
2020 | PGE | ECC | CZ01 | New | 0.008 | new
2020 | PGE | ECC | CZ02 | 1975 | 2.853 | old
2020 | PGE | ECC | CZ02 | 1985 | 0.685 | old
2020 | PGE | ECC | CZ02 | 1996 | 0.397 | old
2020 | PGE | ECC | CZ02 | 2003 | 0.387 | ex
2020 | PGE | ECC | CZ02 | 2007 | 0.151 | ex
2020 | PGE | ECC | CZ02 | 2011 | 0.151 | ex
2020 | PGE | ECC | CZ02 | 2015 | 0.113 | ex
2020 | PGE | ECC | CZ02 | 2017 | 0.113 | rec
2020 | PGE | ECC | CZ02 | 2020 | 0.038 | rec
2020 | PGE | ECC | CZ02 | New | 0.038 | new
2020 | PGE | ECC | CZ03 | 1975 | 15.601 | old
2020 | PGE | ECC | CZ03 | 1985 | 2.662 | old
2020 | PGE | ECC | CZ03 | 1996 | 2.083 | old
2020 | PGE | ECC | CZ03 | 2003 | 1.643 | ex
2020 | PGE | ECC | CZ03 | 2007 | 0.574 | ex
2020 | PGE | ECC | CZ03 | 2011 | 0.574 | ex
2020 | PGE | ECC | CZ03 | 2015 | 0.43 | ex
2020 | PGE | ECC | CZ03 | 2017 | 0.43 | rec
2020 | PGE | ECC | CZ03 | 2020 | 0.143 | rec
2020 | PGE | ECC | CZ03 | New | 0.143 | new
2020 | PGE | ECC | CZ04 | 1975 | 3.418 | old
2020 | PGE | ECC | CZ04 | 1985 | 0.886 | old
2020 | PGE | ECC | CZ04 | 1996 | 0.501 | old
2020 | PGE | ECC | CZ04 | 2003 | 0.53 | ex
2020 | PGE | ECC | CZ04 | 2007 | 0.203 | ex
2020 | PGE | ECC | CZ04 | 2011 | 0.203 | ex
2020 | PGE | ECC | CZ04 | 2015 | 0.152 | ex
2020 | PGE | ECC | CZ04 | 2017 | 0.152 | rec
2020 | PGE | ECC | CZ04 | 2020 | 0.051 | rec
2020 | PGE | ECC | CZ04 | New | 0.051 | new
2020 | PGE | ECC | CZ05 | 1975 | 2.584 | old
2020 | PGE | ECC | CZ05 | 1985 | 0.67 | old
2020 | PGE | ECC | CZ05 | 1996 | 0.379 | old
2020 | PGE | ECC | CZ05 | 2003 | 0.4 | ex
2020 | PGE | ECC | CZ05 | 2007 | 0.153 | ex
2020 | PGE | ECC | CZ05 | 2011 | 0.153 | ex
2020 | PGE | ECC | CZ05 | 2015 | 0.115 | ex
2020 | PGE | ECC | CZ05 | 2017 | 0.115 | rec
2020 | PGE | ECC | CZ05 | 2020 | 0.038 | rec
2020 | PGE | ECC | CZ05 | New | 0.038 | new
2020 | PGE | ECC | CZ11 | 1975 | 3.496 | old
2020 | PGE | ECC | CZ11 | 1985 | 0.564 | old
2020 | PGE | ECC | CZ11 | 1996 | 0.579 | old
2020 | PGE | ECC | CZ11 | 2003 | 0.556 | ex
2020 | PGE | ECC | CZ11 | 2007 | 0.233 | ex
2020 | PGE | ECC | CZ11 | 2011 | 0.233 | ex
2020 | PGE | ECC | CZ11 | 2015 | 0.175 | ex
2020 | PGE | ECC | CZ11 | 2017 | 0.175 | rec
2020 | PGE | ECC | CZ11 | 2020 | 0.058 | rec
2020 | PGE | ECC | CZ11 | New | 0.058 | new
2020 | PGE | ECC | CZ12 | 1975 | 4.858 | old
2020 | PGE | ECC | CZ12 | 1985 | 0.977 | old
2020 | PGE | ECC | CZ12 | 1996 | 0.778 | old
2020 | PGE | ECC | CZ12 | 2003 | 0.799 | ex
2020 | PGE | ECC | CZ12 | 2007 | 0.318 | ex
2020 | PGE | ECC | CZ12 | 2011 | 0.318 | ex
2020 | PGE | ECC | CZ12 | 2015 | 0.239 | ex
2020 | PGE | ECC | CZ12 | 2017 | 0.239 | rec
2020 | PGE | ECC | CZ12 | 2020 | 0.08 | rec
2020 | PGE | ECC | CZ12 | New | 0.08 | new
2020 | PGE | ECC | CZ13 | 1975 | 5.278 | old
2020 | PGE | ECC | CZ13 | 1985 | 0.894 | old
2020 | PGE | ECC | CZ13 | 1996 | 0.874 | old
2020 | PGE | ECC | CZ13 | 2003 | 0.843 | ex
2020 | PGE | ECC | CZ13 | 2007 | 0.351 | ex
2020 | PGE | ECC | CZ13 | 2011 | 0.351 | ex
2020 | PGE | ECC | CZ13 | 2015 | 0.264 | ex
2020 | PGE | ECC | CZ13 | 2017 | 0.264 | rec
2020 | PGE | ECC | CZ13 | 2020 | 0.088 | rec
2020 | PGE | ECC | CZ13 | New | 0.088 | new
2020 | PGE | ECC | CZ16 | 1975 | 0.12 | old
2020 | PGE | ECC | CZ16 | 1985 | 0.02 | old
2020 | PGE | ECC | CZ16 | 1996 | 0.015 | old
2020 | PGE | ECC | CZ16 | 2003 | 0.011 | ex
2020 | PGE | ECC | CZ16 | 2007 | 0.005 | ex
2020 | PGE | ECC | CZ16 | 2011 | 0.005 | ex
2020 | PGE | ECC | CZ16 | 2015 | 0.004 | ex
2020 | PGE | ECC | CZ16 | 2017 | 0.004 | rec
2020 | PGE | ECC | CZ16 | 2020 | 0.001 | rec
2020 | PGE | ECC | CZ16 | New | 0.001 | new
2020 | PGE | EPr | CZ01 | 1975 | 0.431 | old
2020 | PGE | EPr | CZ01 | 1985 | 0.113 | old
2020 | PGE | EPr | CZ01 | 1996 | 0.058 | old
2020 | PGE | EPr | CZ01 | 2003 | 0.047 | ex
2020 | PGE | EPr | CZ01 | 2007 | 0.018 | ex
2020 | PGE | EPr | CZ01 | 2011 | 0.018 | ex
2020 | PGE | EPr | CZ01 | 2015 | 0.013 | ex
2020 | PGE | EPr | CZ01 | 2017 | 0.013 | rec
2020 | PGE | EPr | CZ01 | 2020 | 0.004 | rec
2020 | PGE | EPr | CZ01 | New | 0.004 | new
2020 | PGE | EPr | CZ02 | 1975 | 3.55 | old
2020 | PGE | EPr | CZ02 | 1985 | 0.451 | old
2020 | PGE | EPr | CZ02 | 1996 | 0.514 | old
2020 | PGE | EPr | CZ02 | 2003 | 0.333 | ex
2020 | PGE | EPr | CZ02 | 2007 | 0.105 | ex
2020 | PGE | EPr | CZ02 | 2011 | 0.105 | ex
2020 | PGE | EPr | CZ02 | 2015 | 0.079 | ex
2020 | PGE | EPr | CZ02 | 2017 | 0.079 | rec
2020 | PGE | EPr | CZ02 | 2020 | 0.026 | rec
2020 | PGE | EPr | CZ02 | New | 0.026 | new
2020 | PGE | EPr | CZ03 | 1975 | 15.07 | old
2020 | PGE | EPr | CZ03 | 1985 | 1.104 | old
2020 | PGE | EPr | CZ03 | 1996 | 1.609 | old
2020 | PGE | EPr | CZ03 | 2003 | 0.958 | ex
2020 | PGE | EPr | CZ03 | 2007 | 0.313 | ex
2020 | PGE | EPr | CZ03 | 2011 | 0.313 | ex
2020 | PGE | EPr | CZ03 | 2015 | 0.235 | ex
2020 | PGE | EPr | CZ03 | 2017 | 0.235 | rec
2020 | PGE | EPr | CZ03 | 2020 | 0.078 | rec
2020 | PGE | EPr | CZ03 | New | 0.078 | new
2020 | PGE | EPr | CZ04 | 1975 | 6.786 | old
2020 | PGE | EPr | CZ04 | 1985 | 0.813 | old
2020 | PGE | EPr | CZ04 | 1996 | 1.141 | old
2020 | PGE | EPr | CZ04 | 2003 | 0.72 | ex
2020 | PGE | EPr | CZ04 | 2007 | 0.211 | ex
2020 | PGE | EPr | CZ04 | 2011 | 0.211 | ex
2020 | PGE | EPr | CZ04 | 2015 | 0.159 | ex
2020 | PGE | EPr | CZ04 | 2017 | 0.159 | rec
2020 | PGE | EPr | CZ04 | 2020 | 0.053 | rec
2020 | PGE | EPr | CZ04 | New | 0.053 | new
2020 | PGE | EPr | CZ05 | 1975 | 0.937 | old
2020 | PGE | EPr | CZ05 | 1985 | 0.113 | old
2020 | PGE | EPr | CZ05 | 1996 | 0.159 | old
2020 | PGE | EPr | CZ05 | 2003 | 0.1 | ex
2020 | PGE | EPr | CZ05 | 2007 | 0.029 | ex
2020 | PGE | EPr | CZ05 | 2011 | 0.029 | ex
2020 | PGE | EPr | CZ05 | 2015 | 0.022 | ex
2020 | PGE | EPr | CZ05 | 2017 | 0.022 | rec
2020 | PGE | EPr | CZ05 | 2020 | 0.007 | rec
2020 | PGE | EPr | CZ05 | New | 0.007 | new
2020 | PGE | EPr | CZ11 | 1975 | 2.407 | old
2020 | PGE | EPr | CZ11 | 1985 | 0.528 | old
2020 | PGE | EPr | CZ11 | 1996 | 0.592 | old
2020 | PGE | EPr | CZ11 | 2003 | 0.462 | ex
2020 | PGE | EPr | CZ11 | 2007 | 0.174 | ex
2020 | PGE | EPr | CZ11 | 2011 | 0.174 | ex
2020 | PGE | EPr | CZ11 | 2015 | 0.131 | ex
2020 | PGE | EPr | CZ11 | 2017 | 0.131 | rec
2020 | PGE | EPr | CZ11 | 2020 | 0.044 | rec
2020 | PGE | EPr | CZ11 | New | 0.044 | new
2020 | PGE | EPr | CZ12 | 1975 | 9.141 | old
2020 | PGE | EPr | CZ12 | 1985 | 1.544 | old
2020 | PGE | EPr | CZ12 | 1996 | 1.833 | old
2020 | PGE | EPr | CZ12 | 2003 | 1.632 | ex
2020 | PGE | EPr | CZ12 | 2007 | 0.535 | ex
2020 | PGE | EPr | CZ12 | 2011 | 0.535 | ex
2020 | PGE | EPr | CZ12 | 2015 | 0.401 | ex
2020 | PGE | EPr | CZ12 | 2017 | 0.401 | rec
2020 | PGE | EPr | CZ12 | 2020 | 0.134 | rec
2020 | PGE | EPr | CZ12 | New | 0.134 | new
2020 | PGE | EPr | CZ13 | 1975 | 6.621 | old
2020 | PGE | EPr | CZ13 | 1985 | 1.292 | old
2020 | PGE | EPr | CZ13 | 1996 | 1.83 | old
2020 | PGE | EPr | CZ13 | 2003 | 1.018 | ex
2020 | PGE | EPr | CZ13 | 2007 | 0.422 | ex
2020 | PGE | EPr | CZ13 | 2011 | 0.422 | ex
2020 | PGE | EPr | CZ13 | 2015 | 0.316 | ex
2020 | PGE | EPr | CZ13 | 2017 | 0.316 | rec
2020 | PGE | EPr | CZ13 | 2020 | 0.105 | rec
2020 | PGE | EPr | CZ13 | New | 0.105 | new
2020 | PGE | EPr | CZ16 | 1975 | 0.379 | old
2020 | PGE | EPr | CZ16 | 1985 | 0.089 | old
2020 | PGE | EPr | CZ16 | 1996 | 0.08 | old
2020 | PGE | EPr | CZ16 | 2003 | 0.065 | ex
2020 | PGE | EPr | CZ16 | 2007 | 0.024 | ex
2020 | PGE | EPr | CZ16 | 2011 | 0.024 | ex
2020 | PGE | EPr | CZ16 | 2015 | 0.018 | ex
2020 | PGE | EPr | CZ16 | 2017 | 0.018 | rec
2020 | PGE | EPr | CZ16 | 2020 | 0.006 | rec
2020 | PGE | EPr | CZ16 | New | 0.006 | new
2020 | PGE | ERC | CZ01 | 1975 | 0.431 | old
2020 | PGE | ERC | CZ01 | 1985 | 0.113 | old
2020 | PGE | ERC | CZ01 | 1996 | 0.058 | old
2020 | PGE | ERC | CZ01 | 2003 | 0.047 | ex
2020 | PGE | ERC | CZ01 | 2007 | 0.018 | ex
2020 | PGE | ERC | CZ01 | 2011 | 0.018 | ex
2020 | PGE | ERC | CZ01 | 2015 | 0.013 | ex
2020 | PGE | ERC | CZ01 | 2017 | 0.013 | rec
2020 | PGE | ERC | CZ01 | 2020 | 0.004 | rec
2020 | PGE | ERC | CZ01 | New | 0.004 | new
2020 | PGE | ERC | CZ02 | 1975 | 3.55 | old
2020 | PGE | ERC | CZ02 | 1985 | 0.451 | old
2020 | PGE | ERC | CZ02 | 1996 | 0.514 | old
2020 | PGE | ERC | CZ02 | 2003 | 0.333 | ex
2020 | PGE | ERC | CZ02 | 2007 | 0.105 | ex
2020 | PGE | ERC | CZ02 | 2011 | 0.105 | ex
2020 | PGE | ERC | CZ02 | 2015 | 0.079 | ex
2020 | PGE | ERC | CZ02 | 2017 | 0.079 | rec
2020 | PGE | ERC | CZ02 | 2020 | 0.026 | rec
2020 | PGE | ERC | CZ02 | New | 0.026 | new
2020 | PGE | ERC | CZ03 | 1975 | 15.07 | old
2020 | PGE | ERC | CZ03 | 1985 | 1.104 | old
2020 | PGE | ERC | CZ03 | 1996 | 1.609 | old
2020 | PGE | ERC | CZ03 | 2003 | 0.958 | ex
2020 | PGE | ERC | CZ03 | 2007 | 0.313 | ex
2020 | PGE | ERC | CZ03 | 2011 | 0.313 | ex
2020 | PGE | ERC | CZ03 | 2015 | 0.235 | ex
2020 | PGE | ERC | CZ03 | 2017 | 0.235 | rec
2020 | PGE | ERC | CZ03 | 2020 | 0.078 | rec
2020 | PGE | ERC | CZ03 | New | 0.078 | new
2020 | PGE | ERC | CZ04 | 1975 | 6.786 | old
2020 | PGE | ERC | CZ04 | 1985 | 0.813 | old
2020 | PGE | ERC | CZ04 | 1996 | 1.141 | old
2020 | PGE | ERC | CZ04 | 2003 | 0.72 | ex
2020 | PGE | ERC | CZ04 | 2007 | 0.211 | ex
2020 | PGE | ERC | CZ04 | 2011 | 0.211 | ex
2020 | PGE | ERC | CZ04 | 2015 | 0.159 | ex
2020 | PGE | ERC | CZ04 | 2017 | 0.159 | rec
2020 | PGE | ERC | CZ04 | 2020 | 0.053 | rec
2020 | PGE | ERC | CZ04 | New | 0.053 | new
2020 | PGE | ERC | CZ05 | 1975 | 0.937 | old
2020 | PGE | ERC | CZ05 | 1985 | 0.113 | old
2020 | PGE | ERC | CZ05 | 1996 | 0.159 | old
2020 | PGE | ERC | CZ05 | 2003 | 0.1 | ex
2020 | PGE | ERC | CZ05 | 2007 | 0.029 | ex
2020 | PGE | ERC | CZ05 | 2011 | 0.029 | ex
2020 | PGE | ERC | CZ05 | 2015 | 0.022 | ex
2020 | PGE | ERC | CZ05 | 2017 | 0.022 | rec
2020 | PGE | ERC | CZ05 | 2020 | 0.007 | rec
2020 | PGE | ERC | CZ05 | New | 0.007 | new
2020 | PGE | ERC | CZ11 | 1975 | 2.407 | old
2020 | PGE | ERC | CZ11 | 1985 | 0.528 | old
2020 | PGE | ERC | CZ11 | 1996 | 0.592 | old
2020 | PGE | ERC | CZ11 | 2003 | 0.462 | ex
2020 | PGE | ERC | CZ11 | 2007 | 0.174 | ex
2020 | PGE | ERC | CZ11 | 2011 | 0.174 | ex
2020 | PGE | ERC | CZ11 | 2015 | 0.131 | ex
2020 | PGE | ERC | CZ11 | 2017 | 0.131 | rec
2020 | PGE | ERC | CZ11 | 2020 | 0.044 | rec
2020 | PGE | ERC | CZ11 | New | 0.044 | new
2020 | PGE | ERC | CZ12 | 1975 | 9.141 | old
2020 | PGE | ERC | CZ12 | 1985 | 1.544 | old
2020 | PGE | ERC | CZ12 | 1996 | 1.833 | old
2020 | PGE | ERC | CZ12 | 2003 | 1.632 | ex
2020 | PGE | ERC | CZ12 | 2007 | 0.535 | ex
2020 | PGE | ERC | CZ12 | 2011 | 0.535 | ex
2020 | PGE | ERC | CZ12 | 2015 | 0.401 | ex
2020 | PGE | ERC | CZ12 | 2017 | 0.401 | rec
2020 | PGE | ERC | CZ12 | 2020 | 0.134 | rec
2020 | PGE | ERC | CZ12 | New | 0.134 | new
2020 | PGE | ERC | CZ13 | 1975 | 6.621 | old
2020 | PGE | ERC | CZ13 | 1985 | 1.292 | old
2020 | PGE | ERC | CZ13 | 1996 | 1.83 | old
2020 | PGE | ERC | CZ13 | 2003 | 1.018 | ex
2020 | PGE | ERC | CZ13 | 2007 | 0.422 | ex
2020 | PGE | ERC | CZ13 | 2011 | 0.422 | ex
2020 | PGE | ERC | CZ13 | 2015 | 0.316 | ex
2020 | PGE | ERC | CZ13 | 2017 | 0.316 | rec
2020 | PGE | ERC | CZ13 | 2020 | 0.105 | rec
2020 | PGE | ERC | CZ13 | New | 0.105 | new
2020 | PGE | ERC | CZ16 | 1975 | 0.379 | old
2020 | PGE | ERC | CZ16 | 1985 | 0.089 | old
2020 | PGE | ERC | CZ16 | 1996 | 0.08 | old
2020 | PGE | ERC | CZ16 | 2003 | 0.065 | ex
2020 | PGE | ERC | CZ16 | 2007 | 0.024 | ex
2020 | PGE | ERC | CZ16 | 2011 | 0.024 | ex
2020 | PGE | ERC | CZ16 | 2015 | 0.018 | ex
2020 | PGE | ERC | CZ16 | 2017 | 0.018 | rec
2020 | PGE | ERC | CZ16 | 2020 | 0.006 | rec
2020 | PGE | ERC | CZ16 | New | 0.006 | new
2020 | PGE | ESe | CZ01 | 1975 | 0.431 | old
2020 | PGE | ESe | CZ01 | 1985 | 0.113 | old
2020 | PGE | ESe | CZ01 | 1996 | 0.058 | old
2020 | PGE | ESe | CZ01 | 2003 | 0.047 | ex
2020 | PGE | ESe | CZ01 | 2007 | 0.018 | ex
2020 | PGE | ESe | CZ01 | 2011 | 0.018 | ex
2020 | PGE | ESe | CZ01 | 2015 | 0.013 | ex
2020 | PGE | ESe | CZ01 | 2017 | 0.013 | rec
2020 | PGE | ESe | CZ01 | 2020 | 0.004 | rec
2020 | PGE | ESe | CZ01 | New | 0.004 | new
2020 | PGE | ESe | CZ02 | 1975 | 3.55 | old
2020 | PGE | ESe | CZ02 | 1985 | 0.451 | old
2020 | PGE | ESe | CZ02 | 1996 | 0.514 | old
2020 | PGE | ESe | CZ02 | 2003 | 0.333 | ex
2020 | PGE | ESe | CZ02 | 2007 | 0.105 | ex
2020 | PGE | ESe | CZ02 | 2011 | 0.105 | ex
2020 | PGE | ESe | CZ02 | 2015 | 0.079 | ex
2020 | PGE | ESe | CZ02 | 2017 | 0.079 | rec
2020 | PGE | ESe | CZ02 | 2020 | 0.026 | rec
2020 | PGE | ESe | CZ02 | New | 0.026 | new
2020 | PGE | ESe | CZ03 | 1975 | 15.07 | old
2020 | PGE | ESe | CZ03 | 1985 | 1.104 | old
2020 | PGE | ESe | CZ03 | 1996 | 1.609 | old
2020 | PGE | ESe | CZ03 | 2003 | 0.958 | ex
2020 | PGE | ESe | CZ03 | 2007 | 0.313 | ex
2020 | PGE | ESe | CZ03 | 2011 | 0.313 | ex
2020 | PGE | ESe | CZ03 | 2015 | 0.235 | ex
2020 | PGE | ESe | CZ03 | 2017 | 0.235 | rec
2020 | PGE | ESe | CZ03 | 2020 | 0.078 | rec
2020 | PGE | ESe | CZ03 | New | 0.078 | new
2020 | PGE | ESe | CZ04 | 1975 | 6.786 | old
2020 | PGE | ESe | CZ04 | 1985 | 0.813 | old
2020 | PGE | ESe | CZ04 | 1996 | 1.141 | old
2020 | PGE | ESe | CZ04 | 2003 | 0.72 | ex
2020 | PGE | ESe | CZ04 | 2007 | 0.211 | ex
2020 | PGE | ESe | CZ04 | 2011 | 0.211 | ex
2020 | PGE | ESe | CZ04 | 2015 | 0.159 | ex
2020 | PGE | ESe | CZ04 | 2017 | 0.159 | rec
2020 | PGE | ESe | CZ04 | 2020 | 0.053 | rec
2020 | PGE | ESe | CZ04 | New | 0.053 | new
2020 | PGE | ESe | CZ05 | 1975 | 0.937 | old
2020 | PGE | ESe | CZ05 | 1985 | 0.113 | old
2020 | PGE | ESe | CZ05 | 1996 | 0.159 | old
2020 | PGE | ESe | CZ05 | 2003 | 0.1 | ex
2020 | PGE | ESe | CZ05 | 2007 | 0.029 | ex
2020 | PGE | ESe | CZ05 | 2011 | 0.029 | ex
2020 | PGE | ESe | CZ05 | 2015 | 0.022 | ex
2020 | PGE | ESe | CZ05 | 2017 | 0.022 | rec
2020 | PGE | ESe | CZ05 | 2020 | 0.007 | rec
2020 | PGE | ESe | CZ05 | New | 0.007 | new
2020 | PGE | ESe | CZ11 | 1975 | 2.407 | old
2020 | PGE | ESe | CZ11 | 1985 | 0.528 | old
2020 | PGE | ESe | CZ11 | 1996 | 0.592 | old
2020 | PGE | ESe | CZ11 | 2003 | 0.462 | ex
2020 | PGE | ESe | CZ11 | 2007 | 0.174 | ex
2020 | PGE | ESe | CZ11 | 2011 | 0.174 | ex
2020 | PGE | ESe | CZ11 | 2015 | 0.131 | ex
2020 | PGE | ESe | CZ11 | 2017 | 0.131 | rec
2020 | PGE | ESe | CZ11 | 2020 | 0.044 | rec
2020 | PGE | ESe | CZ11 | New | 0.044 | new
2020 | PGE | ESe | CZ12 | 1975 | 9.141 | old
2020 | PGE | ESe | CZ12 | 1985 | 1.544 | old
2020 | PGE | ESe | CZ12 | 1996 | 1.833 | old
2020 | PGE | ESe | CZ12 | 2003 | 1.632 | ex
2020 | PGE | ESe | CZ12 | 2007 | 0.535 | ex
2020 | PGE | ESe | CZ12 | 2011 | 0.535 | ex
2020 | PGE | ESe | CZ12 | 2015 | 0.401 | ex
2020 | PGE | ESe | CZ12 | 2017 | 0.401 | rec
2020 | PGE | ESe | CZ12 | 2020 | 0.134 | rec
2020 | PGE | ESe | CZ12 | New | 0.134 | new
2020 | PGE | ESe | CZ13 | 1975 | 6.621 | old
2020 | PGE | ESe | CZ13 | 1985 | 1.292 | old
2020 | PGE | ESe | CZ13 | 1996 | 1.83 | old
2020 | PGE | ESe | CZ13 | 2003 | 1.018 | ex
2020 | PGE | ESe | CZ13 | 2007 | 0.422 | ex
2020 | PGE | ESe | CZ13 | 2011 | 0.422 | ex
2020 | PGE | ESe | CZ13 | 2015 | 0.316 | ex
2020 | PGE | ESe | CZ13 | 2017 | 0.316 | rec
2020 | PGE | ESe | CZ13 | 2020 | 0.105 | rec
2020 | PGE | ESe | CZ13 | New | 0.105 | new
2020 | PGE | ESe | CZ16 | 1975 | 0.379 | old
2020 | PGE | ESe | CZ16 | 1985 | 0.089 | old
2020 | PGE | ESe | CZ16 | 1996 | 0.08 | old
2020 | PGE | ESe | CZ16 | 2003 | 0.065 | ex
2020 | PGE | ESe | CZ16 | 2007 | 0.024 | ex
2020 | PGE | ESe | CZ16 | 2011 | 0.024 | ex
2020 | PGE | ESe | CZ16 | 2015 | 0.018 | ex
2020 | PGE | ESe | CZ16 | 2017 | 0.018 | rec
2020 | PGE | ESe | CZ16 | 2020 | 0.006 | rec
2020 | PGE | ESe | CZ16 | New | 0.006 | new
2020 | PGE | EUD | CZ01 | 1975 | 1.298 | old
2020 | PGE | EUD | CZ01 | 1985 | 0.236 | old
2020 | PGE | EUD | CZ01 | 1996 | 0.119 | old
2020 | PGE | EUD | CZ01 | 2003 | 0.043 | ex
2020 | PGE | EUD | CZ01 | 2007 | 0.032 | ex
2020 | PGE | EUD | CZ01 | 2011 | 0.032 | ex
2020 | PGE | EUD | CZ01 | 2015 | 0.024 | ex
2020 | PGE | EUD | CZ01 | 2017 | 0.024 | rec
2020 | PGE | EUD | CZ01 | 2020 | 0.008 | rec
2020 | PGE | EUD | CZ01 | New | 0.008 | new
2020 | PGE | EUD | CZ02 | 1975 | 2.853 | old
2020 | PGE | EUD | CZ02 | 1985 | 0.685 | old
2020 | PGE | EUD | CZ02 | 1996 | 0.397 | old
2020 | PGE | EUD | CZ02 | 2003 | 0.387 | ex
2020 | PGE | EUD | CZ02 | 2007 | 0.151 | ex
2020 | PGE | EUD | CZ02 | 2011 | 0.151 | ex
2020 | PGE | EUD | CZ02 | 2015 | 0.113 | ex
2020 | PGE | EUD | CZ02 | 2017 | 0.113 | rec
2020 | PGE | EUD | CZ02 | 2020 | 0.038 | rec
2020 | PGE | EUD | CZ02 | New | 0.038 | new
2020 | PGE | EUD | CZ03 | 1975 | 15.601 | old
2020 | PGE | EUD | CZ03 | 1985 | 2.662 | old
2020 | PGE | EUD | CZ03 | 1996 | 2.083 | old
2020 | PGE | EUD | CZ03 | 2003 | 1.643 | ex
2020 | PGE | EUD | CZ03 | 2007 | 0.574 | ex
2020 | PGE | EUD | CZ03 | 2011 | 0.574 | ex
2020 | PGE | EUD | CZ03 | 2015 | 0.43 | ex
2020 | PGE | EUD | CZ03 | 2017 | 0.43 | rec
2020 | PGE | EUD | CZ03 | 2020 | 0.143 | rec
2020 | PGE | EUD | CZ03 | New | 0.143 | new
2020 | PGE | EUD | CZ04 | 1975 | 3.418 | old
2020 | PGE | EUD | CZ04 | 1985 | 0.886 | old
2020 | PGE | EUD | CZ04 | 1996 | 0.501 | old
2020 | PGE | EUD | CZ04 | 2003 | 0.53 | ex
2020 | PGE | EUD | CZ04 | 2007 | 0.203 | ex
2020 | PGE | EUD | CZ04 | 2011 | 0.203 | ex
2020 | PGE | EUD | CZ04 | 2015 | 0.152 | ex
2020 | PGE | EUD | CZ04 | 2017 | 0.152 | rec
2020 | PGE | EUD | CZ04 | 2020 | 0.051 | rec
2020 | PGE | EUD | CZ04 | New | 0.051 | new
2020 | PGE | EUD | CZ05 | 1975 | 2.584 | old
2020 | PGE | EUD | CZ05 | 1985 | 0.67 | old
2020 | PGE | EUD | CZ05 | 1996 | 0.379 | old
2020 | PGE | EUD | CZ05 | 2003 | 0.4 | ex
2020 | PGE | EUD | CZ05 | 2007 | 0.153 | ex
2020 | PGE | EUD | CZ05 | 2011 | 0.153 | ex
2020 | PGE | EUD | CZ05 | 2015 | 0.115 | ex
2020 | PGE | EUD | CZ05 | 2017 | 0.115 | rec
2020 | PGE | EUD | CZ05 | 2020 | 0.038 | rec
2020 | PGE | EUD | CZ05 | New | 0.038 | new
2020 | PGE | EUD | CZ11 | 1975 | 3.496 | old
2020 | PGE | EUD | CZ11 | 1985 | 0.564 | old
2020 | PGE | EUD | CZ11 | 1996 | 0.579 | old
2020 | PGE | EUD | CZ11 | 2003 | 0.556 | ex
2020 | PGE | EUD | CZ11 | 2007 | 0.233 | ex
2020 | PGE | EUD | CZ11 | 2011 | 0.233 | ex
2020 | PGE | EUD | CZ11 | 2015 | 0.175 | ex
2020 | PGE | EUD | CZ11 | 2017 | 0.175 | rec
2020 | PGE | EUD | CZ11 | 2020 | 0.058 | rec
2020 | PGE | EUD | CZ11 | New | 0.058 | new
2020 | PGE | EUD | CZ12 | 1975 | 4.858 | old
2020 | PGE | EUD | CZ12 | 1985 | 0.977 | old
2020 | PGE | EUD | CZ12 | 1996 | 0.778 | old
2020 | PGE | EUD | CZ12 | 2003 | 0.799 | ex
2020 | PGE | EUD | CZ12 | 2007 | 0.318 | ex
2020 | PGE | EUD | CZ12 | 2011 | 0.318 | ex
2020 | PGE | EUD | CZ12 | 2015 | 0.239 | ex
2020 | PGE | EUD | CZ12 | 2017 | 0.239 | rec
2020 | PGE | EUD | CZ12 | 2020 | 0.08 | rec
2020 | PGE | EUD | CZ12 | New | 0.08 | new
2020 | PGE | EUD | CZ13 | 1975 | 5.278 | old
2020 | PGE | EUD | CZ13 | 1985 | 0.894 | old
2020 | PGE | EUD | CZ13 | 1996 | 0.874 | old
2020 | PGE | EUD | CZ13 | 2003 | 0.843 | ex
2020 | PGE | EUD | CZ13 | 2007 | 0.351 | ex
2020 | PGE | EUD | CZ13 | 2011 | 0.351 | ex
2020 | PGE | EUD | CZ13 | 2015 | 0.264 | ex
2020 | PGE | EUD | CZ13 | 2017 | 0.264 | rec
2020 | PGE | EUD | CZ13 | 2020 | 0.088 | rec
2020 | PGE | EUD | CZ13 | New | 0.088 | new
2020 | PGE | EUD | CZ16 | 1975 | 0.12 | old
2020 | PGE | EUD | CZ16 | 1985 | 0.02 | old
2020 | PGE | EUD | CZ16 | 1996 | 0.015 | old
2020 | PGE | EUD | CZ16 | 2003 | 0.011 | ex
2020 | PGE | EUD | CZ16 | 2007 | 0.005 | ex
2020 | PGE | EUD | CZ16 | 2011 | 0.005 | ex
2020 | PGE | EUD | CZ16 | 2015 | 0.004 | ex
2020 | PGE | EUD | CZ16 | 2017 | 0.004 | rec
2020 | PGE | EUD | CZ16 | 2020 | 0.001 | rec
2020 | PGE | EUD | CZ16 | New | 0.001 | new
2020 | PGE | EUn | CZ01 | 1975 | 1.298 | old
2020 | PGE | EUn | CZ01 | 1985 | 0.236 | old
2020 | PGE | EUn | CZ01 | 1996 | 0.119 | old
2020 | PGE | EUn | CZ01 | 2003 | 0.043 | ex
2020 | PGE | EUn | CZ01 | 2007 | 0.032 | ex
2020 | PGE | EUn | CZ01 | 2011 | 0.032 | ex
2020 | PGE | EUn | CZ01 | 2015 | 0.024 | ex
2020 | PGE | EUn | CZ01 | 2017 | 0.024 | rec
2020 | PGE | EUn | CZ01 | 2020 | 0.008 | rec
2020 | PGE | EUn | CZ01 | New | 0.008 | new
2020 | PGE | EUn | CZ02 | 1975 | 2.853 | old
2020 | PGE | EUn | CZ02 | 1985 | 0.685 | old
2020 | PGE | EUn | CZ02 | 1996 | 0.397 | old
2020 | PGE | EUn | CZ02 | 2003 | 0.387 | ex
2020 | PGE | EUn | CZ02 | 2007 | 0.151 | ex
2020 | PGE | EUn | CZ02 | 2011 | 0.151 | ex
2020 | PGE | EUn | CZ02 | 2015 | 0.113 | ex
2020 | PGE | EUn | CZ02 | 2017 | 0.113 | rec
2020 | PGE | EUn | CZ02 | 2020 | 0.038 | rec
2020 | PGE | EUn | CZ02 | New | 0.038 | new
2020 | PGE | EUn | CZ03 | 1975 | 15.601 | old
2020 | PGE | EUn | CZ03 | 1985 | 2.662 | old
2020 | PGE | EUn | CZ03 | 1996 | 2.083 | old
2020 | PGE | EUn | CZ03 | 2003 | 1.643 | ex
2020 | PGE | EUn | CZ03 | 2007 | 0.574 | ex
2020 | PGE | EUn | CZ03 | 2011 | 0.574 | ex
2020 | PGE | EUn | CZ03 | 2015 | 0.43 | ex
2020 | PGE | EUn | CZ03 | 2017 | 0.43 | rec
2020 | PGE | EUn | CZ03 | 2020 | 0.143 | rec
2020 | PGE | EUn | CZ03 | New | 0.143 | new
2020 | PGE | EUn | CZ04 | 1975 | 3.418 | old
2020 | PGE | EUn | CZ04 | 1985 | 0.886 | old
2020 | PGE | EUn | CZ04 | 1996 | 0.501 | old
2020 | PGE | EUn | CZ04 | 2003 | 0.53 | ex
2020 | PGE | EUn | CZ04 | 2007 | 0.203 | ex
2020 | PGE | EUn | CZ04 | 2011 | 0.203 | ex
2020 | PGE | EUn | CZ04 | 2015 | 0.152 | ex
2020 | PGE | EUn | CZ04 | 2017 | 0.152 | rec
2020 | PGE | EUn | CZ04 | 2020 | 0.051 | rec
2020 | PGE | EUn | CZ04 | New | 0.051 | new
2020 | PGE | EUn | CZ05 | 1975 | 2.584 | old
2020 | PGE | EUn | CZ05 | 1985 | 0.67 | old
2020 | PGE | EUn | CZ05 | 1996 | 0.379 | old
2020 | PGE | EUn | CZ05 | 2003 | 0.4 | ex
2020 | PGE | EUn | CZ05 | 2007 | 0.153 | ex
2020 | PGE | EUn | CZ05 | 2011 | 0.153 | ex
2020 | PGE | EUn | CZ05 | 2015 | 0.115 | ex
2020 | PGE | EUn | CZ05 | 2017 | 0.115 | rec
2020 | PGE | EUn | CZ05 | 2020 | 0.038 | rec
2020 | PGE | EUn | CZ05 | New | 0.038 | new
2020 | PGE | EUn | CZ11 | 1975 | 3.496 | old
2020 | PGE | EUn | CZ11 | 1985 | 0.564 | old
2020 | PGE | EUn | CZ11 | 1996 | 0.579 | old
2020 | PGE | EUn | CZ11 | 2003 | 0.556 | ex
2020 | PGE | EUn | CZ11 | 2007 | 0.233 | ex
2020 | PGE | EUn | CZ11 | 2011 | 0.233 | ex
2020 | PGE | EUn | CZ11 | 2015 | 0.175 | ex
2020 | PGE | EUn | CZ11 | 2017 | 0.175 | rec
2020 | PGE | EUn | CZ11 | 2020 | 0.058 | rec
2020 | PGE | EUn | CZ11 | New | 0.058 | new
2020 | PGE | EUn | CZ12 | 1975 | 4.858 | old
2020 | PGE | EUn | CZ12 | 1985 | 0.977 | old
2020 | PGE | EUn | CZ12 | 1996 | 0.778 | old
2020 | PGE | EUn | CZ12 | 2003 | 0.799 | ex
2020 | PGE | EUn | CZ12 | 2007 | 0.318 | ex
2020 | PGE | EUn | CZ12 | 2011 | 0.318 | ex
2020 | PGE | EUn | CZ12 | 2015 | 0.239 | ex
2020 | PGE | EUn | CZ12 | 2017 | 0.239 | rec
2020 | PGE | EUn | CZ12 | 2020 | 0.08 | rec
2020 | PGE | EUn | CZ12 | New | 0.08 | new
2020 | PGE | EUn | CZ13 | 1975 | 5.278 | old
2020 | PGE | EUn | CZ13 | 1985 | 0.894 | old
2020 | PGE | EUn | CZ13 | 1996 | 0.874 | old
2020 | PGE | EUn | CZ13 | 2003 | 0.843 | ex
2020 | PGE | EUn | CZ13 | 2007 | 0.351 | ex
2020 | PGE | EUn | CZ13 | 2011 | 0.351 | ex
2020 | PGE | EUn | CZ13 | 2015 | 0.264 | ex
2020 | PGE | EUn | CZ13 | 2017 | 0.264 | rec
2020 | PGE | EUn | CZ13 | 2020 | 0.088 | rec
2020 | PGE | EUn | CZ13 | New | 0.088 | new
2020 | PGE | EUn | CZ16 | 1975 | 0.12 | old
2020 | PGE | EUn | CZ16 | 1985 | 0.02 | old
2020 | PGE | EUn | CZ16 | 1996 | 0.015 | old
2020 | PGE | EUn | CZ16 | 2003 | 0.011 | ex
2020 | PGE | EUn | CZ16 | 2007 | 0.005 | ex
2020 | PGE | EUn | CZ16 | 2011 | 0.005 | ex
2020 | PGE | EUn | CZ16 | 2015 | 0.004 | ex
2020 | PGE | EUn | CZ16 | 2017 | 0.004 | rec
2020 | PGE | EUn | CZ16 | 2020 | 0.001 | rec
2020 | PGE | EUn | CZ16 | New | 0.001 | new
2020 | PGE | Gro | CZ01 | 1975 | 0.518 | old
2020 | PGE | Gro | CZ01 | 1985 | 0.348 | old
2020 | PGE | Gro | CZ01 | 1996 | 0.13 | old
2020 | PGE | Gro | CZ01 | 2003 | 0.058 | ex
2020 | PGE | Gro | CZ01 | 2007 | 0.035 | ex
2020 | PGE | Gro | CZ01 | 2011 | 0.035 | ex
2020 | PGE | Gro | CZ01 | 2015 | 0.026 | ex
2020 | PGE | Gro | CZ01 | 2017 | 0.026 | rec
2020 | PGE | Gro | CZ01 | 2020 | 0.009 | rec
2020 | PGE | Gro | CZ01 | New | 0.009 | new
2020 | PGE | Gro | CZ02 | 1975 | 3.952 | old
2020 | PGE | Gro | CZ02 | 1985 | 2.033 | old
2020 | PGE | Gro | CZ02 | 1996 | 1.168 | old
2020 | PGE | Gro | CZ02 | 2003 | 0.48 | ex
2020 | PGE | Gro | CZ02 | 2007 | 0.272 | ex
2020 | PGE | Gro | CZ02 | 2011 | 0.272 | ex
2020 | PGE | Gro | CZ02 | 2015 | 0.204 | ex
2020 | PGE | Gro | CZ02 | 2017 | 0.204 | rec
2020 | PGE | Gro | CZ02 | 2020 | 0.068 | rec
2020 | PGE | Gro | CZ02 | New | 0.068 | new
2020 | PGE | Gro | CZ03 | 1975 | 16.08 | old
2020 | PGE | Gro | CZ03 | 1985 | 5.953 | old
2020 | PGE | Gro | CZ03 | 1996 | 3.421 | old
2020 | PGE | Gro | CZ03 | 2003 | 1.37 | ex
2020 | PGE | Gro | CZ03 | 2007 | 0.874 | ex
2020 | PGE | Gro | CZ03 | 2011 | 0.874 | ex
2020 | PGE | Gro | CZ03 | 2015 | 0.655 | ex
2020 | PGE | Gro | CZ03 | 2017 | 0.655 | rec
2020 | PGE | Gro | CZ03 | 2020 | 0.218 | rec
2020 | PGE | Gro | CZ03 | New | 0.218 | new
2020 | PGE | Gro | CZ04 | 1975 | 5.925 | old
2020 | PGE | Gro | CZ04 | 1985 | 3.178 | old
2020 | PGE | Gro | CZ04 | 1996 | 1.957 | old
2020 | PGE | Gro | CZ04 | 2003 | 0.8 | ex
2020 | PGE | Gro | CZ04 | 2007 | 0.438 | ex
2020 | PGE | Gro | CZ04 | 2011 | 0.438 | ex
2020 | PGE | Gro | CZ04 | 2015 | 0.329 | ex
2020 | PGE | Gro | CZ04 | 2017 | 0.329 | rec
2020 | PGE | Gro | CZ04 | 2020 | 0.11 | rec
2020 | PGE | Gro | CZ04 | New | 0.11 | new
2020 | PGE | Gro | CZ05 | 1975 | 1.34 | old
2020 | PGE | Gro | CZ05 | 1985 | 0.721 | old
2020 | PGE | Gro | CZ05 | 1996 | 0.444 | old
2020 | PGE | Gro | CZ05 | 2003 | 0.182 | ex
2020 | PGE | Gro | CZ05 | 2007 | 0.099 | ex
2020 | PGE | Gro | CZ05 | 2011 | 0.099 | ex
2020 | PGE | Gro | CZ05 | 2015 | 0.075 | ex
2020 | PGE | Gro | CZ05 | 2017 | 0.075 | rec
2020 | PGE | Gro | CZ05 | 2020 | 0.025 | rec
2020 | PGE | Gro | CZ05 | New | 0.025 | new
2020 | PGE | Gro | CZ11 | 1975 | 2.704 | old
2020 | PGE | Gro | CZ11 | 1985 | 2.188 | old
2020 | PGE | Gro | CZ11 | 1996 | 1.225 | old
2020 | PGE | Gro | CZ11 | 2003 | 0.671 | ex
2020 | PGE | Gro | CZ11 | 2007 | 0.381 | ex
2020 | PGE | Gro | CZ11 | 2011 | 0.381 | ex
2020 | PGE | Gro | CZ11 | 2015 | 0.286 | ex
2020 | PGE | Gro | CZ11 | 2017 | 0.286 | rec
2020 | PGE | Gro | CZ11 | 2020 | 0.095 | rec
2020 | PGE | Gro | CZ11 | New | 0.095 | new
2020 | PGE | Gro | CZ12 | 1975 | 9.44 | old
2020 | PGE | Gro | CZ12 | 1985 | 6.199 | old
2020 | PGE | Gro | CZ12 | 1996 | 4.228 | old
2020 | PGE | Gro | CZ12 | 2003 | 2.363 | ex
2020 | PGE | Gro | CZ12 | 2007 | 1.084 | ex
2020 | PGE | Gro | CZ12 | 2011 | 1.084 | ex
2020 | PGE | Gro | CZ12 | 2015 | 0.813 | ex
2020 | PGE | Gro | CZ12 | 2017 | 0.813 | rec
2020 | PGE | Gro | CZ12 | 2020 | 0.271 | rec
2020 | PGE | Gro | CZ12 | New | 0.271 | new
2020 | PGE | Gro | CZ13 | 1975 | 6.245 | old
2020 | PGE | Gro | CZ13 | 1985 | 5.153 | old
2020 | PGE | Gro | CZ13 | 1996 | 2.639 | old
2020 | PGE | Gro | CZ13 | 2003 | 1.29 | ex
2020 | PGE | Gro | CZ13 | 2007 | 0.876 | ex
2020 | PGE | Gro | CZ13 | 2011 | 0.876 | ex
2020 | PGE | Gro | CZ13 | 2015 | 0.657 | ex
2020 | PGE | Gro | CZ13 | 2017 | 0.657 | rec
2020 | PGE | Gro | CZ13 | 2020 | 0.219 | rec
2020 | PGE | Gro | CZ13 | New | 0.219 | new
2020 | PGE | Gro | CZ16 | 1975 | 0.488 | old
2020 | PGE | Gro | CZ16 | 1985 | 0.373 | old
2020 | PGE | Gro | CZ16 | 1996 | 0.193 | old
2020 | PGE | Gro | CZ16 | 2003 | 0.104 | ex
2020 | PGE | Gro | CZ16 | 2007 | 0.058 | ex
2020 | PGE | Gro | CZ16 | 2011 | 0.058 | ex
2020 | PGE | Gro | CZ16 | 2015 | 0.043 | ex
2020 | PGE | Gro | CZ16 | 2017 | 0.043 | rec
2020 | PGE | Gro | CZ16 | 2020 | 0.014 | rec
2020 | PGE | Gro | CZ16 | New | 0.014 | new
2020 | PGE | HGR | CZ01 | 1975 | 0.321 | old
2020 | PGE | HGR | CZ01 | 1985 | 0.298 | old
2020 | PGE | HGR | CZ01 | 1996 | 0.086 | old
2020 | PGE | HGR | CZ01 | 2003 | 0.119 | ex
2020 | PGE | HGR | CZ01 | 2007 | 0.038 | ex
2020 | PGE | HGR | CZ01 | 2011 | 0.038 | ex
2020 | PGE | HGR | CZ01 | 2015 | 0.029 | ex
2020 | PGE | HGR | CZ01 | 2017 | 0.029 | rec
2020 | PGE | HGR | CZ01 | 2020 | 0.01 | rec
2020 | PGE | HGR | CZ01 | New | 0.01 | new
2020 | PGE | HGR | CZ02 | 1975 | 1.545 | old
2020 | PGE | HGR | CZ02 | 1985 | 1.332 | old
2020 | PGE | HGR | CZ02 | 1996 | 0.612 | old
2020 | PGE | HGR | CZ02 | 2003 | 0.362 | ex
2020 | PGE | HGR | CZ02 | 2007 | 0.168 | ex
2020 | PGE | HGR | CZ02 | 2011 | 0.168 | ex
2020 | PGE | HGR | CZ02 | 2015 | 0.126 | ex
2020 | PGE | HGR | CZ02 | 2017 | 0.126 | rec
2020 | PGE | HGR | CZ02 | 2020 | 0.042 | rec
2020 | PGE | HGR | CZ02 | New | 0.042 | new
2020 | PGE | HGR | CZ03 | 1975 | 11.887 | old
2020 | PGE | HGR | CZ03 | 1985 | 7.67 | old
2020 | PGE | HGR | CZ03 | 1996 | 3.548 | old
2020 | PGE | HGR | CZ03 | 2003 | 1.994 | ex
2020 | PGE | HGR | CZ03 | 2007 | 0.502 | ex
2020 | PGE | HGR | CZ03 | 2011 | 0.502 | ex
2020 | PGE | HGR | CZ03 | 2015 | 0.376 | ex
2020 | PGE | HGR | CZ03 | 2017 | 0.376 | rec
2020 | PGE | HGR | CZ03 | 2020 | 0.125 | rec
2020 | PGE | HGR | CZ03 | New | 0.125 | new
2020 | PGE | HGR | CZ04 | 1975 | 3.175 | old
2020 | PGE | HGR | CZ04 | 1985 | 2.811 | old
2020 | PGE | HGR | CZ04 | 1996 | 1.38 | old
2020 | PGE | HGR | CZ04 | 2003 | 0.699 | ex
2020 | PGE | HGR | CZ04 | 2007 | 0.372 | ex
2020 | PGE | HGR | CZ04 | 2011 | 0.372 | ex
2020 | PGE | HGR | CZ04 | 2015 | 0.279 | ex
2020 | PGE | HGR | CZ04 | 2017 | 0.279 | rec
2020 | PGE | HGR | CZ04 | 2020 | 0.093 | rec
2020 | PGE | HGR | CZ04 | New | 0.093 | new
2020 | PGE | HGR | CZ05 | 1975 | 1.323 | old
2020 | PGE | HGR | CZ05 | 1985 | 1.174 | old
2020 | PGE | HGR | CZ05 | 1996 | 0.577 | old
2020 | PGE | HGR | CZ05 | 2003 | 0.292 | ex
2020 | PGE | HGR | CZ05 | 2007 | 0.156 | ex
2020 | PGE | HGR | CZ05 | 2011 | 0.156 | ex
2020 | PGE | HGR | CZ05 | 2015 | 0.117 | ex
2020 | PGE | HGR | CZ05 | 2017 | 0.117 | rec
2020 | PGE | HGR | CZ05 | 2020 | 0.039 | rec
2020 | PGE | HGR | CZ05 | New | 0.039 | new
2020 | PGE | HGR | CZ11 | 1975 | 1.044 | old
2020 | PGE | HGR | CZ11 | 1985 | 0.65 | old
2020 | PGE | HGR | CZ11 | 1996 | 0.23 | old
2020 | PGE | HGR | CZ11 | 2003 | 0.206 | ex
2020 | PGE | HGR | CZ11 | 2007 | 0.11 | ex
2020 | PGE | HGR | CZ11 | 2011 | 0.11 | ex
2020 | PGE | HGR | CZ11 | 2015 | 0.082 | ex
2020 | PGE | HGR | CZ11 | 2017 | 0.082 | rec
2020 | PGE | HGR | CZ11 | 2020 | 0.027 | rec
2020 | PGE | HGR | CZ11 | New | 0.027 | new
2020 | PGE | HGR | CZ12 | 1975 | 3.052 | old
2020 | PGE | HGR | CZ12 | 1985 | 2.133 | old
2020 | PGE | HGR | CZ12 | 1996 | 1.252 | old
2020 | PGE | HGR | CZ12 | 2003 | 0.754 | ex
2020 | PGE | HGR | CZ12 | 2007 | 0.422 | ex
2020 | PGE | HGR | CZ12 | 2011 | 0.422 | ex
2020 | PGE | HGR | CZ12 | 2015 | 0.316 | ex
2020 | PGE | HGR | CZ12 | 2017 | 0.316 | rec
2020 | PGE | HGR | CZ12 | 2020 | 0.105 | rec
2020 | PGE | HGR | CZ12 | New | 0.105 | new
2020 | PGE | HGR | CZ13 | 1975 | 2.341 | old
2020 | PGE | HGR | CZ13 | 1985 | 1.441 | old
2020 | PGE | HGR | CZ13 | 1996 | 0.471 | old
2020 | PGE | HGR | CZ13 | 2003 | 0.417 | ex
2020 | PGE | HGR | CZ13 | 2007 | 0.231 | ex
2020 | PGE | HGR | CZ13 | 2011 | 0.231 | ex
2020 | PGE | HGR | CZ13 | 2015 | 0.173 | ex
2020 | PGE | HGR | CZ13 | 2017 | 0.173 | rec
2020 | PGE | HGR | CZ13 | 2020 | 0.058 | rec
2020 | PGE | HGR | CZ13 | New | 0.058 | new
2020 | PGE | HGR | CZ16 | 1975 | 0.386 | old
2020 | PGE | HGR | CZ16 | 1985 | 0.305 | old
2020 | PGE | HGR | CZ16 | 1996 | 0.089 | old
2020 | PGE | HGR | CZ16 | 2003 | 0.117 | ex
2020 | PGE | HGR | CZ16 | 2007 | 0.043 | ex
2020 | PGE | HGR | CZ16 | 2011 | 0.043 | ex
2020 | PGE | HGR | CZ16 | 2015 | 0.033 | ex
2020 | PGE | HGR | CZ16 | 2017 | 0.033 | rec
2020 | PGE | HGR | CZ16 | 2020 | 0.011 | rec
2020 | PGE | HGR | CZ16 | New | 0.011 | new
2020 | PGE | Hsp | CZ01 | 1975 | 0.388 | old
2020 | PGE | Hsp | CZ01 | 1985 | 0.124 | old
2020 | PGE | Hsp | CZ01 | 1996 | 0.102 | old
2020 | PGE | Hsp | CZ01 | 2003 | 0.08 | ex
2020 | PGE | Hsp | CZ01 | 2007 | 0.022 | ex
2020 | PGE | Hsp | CZ01 | 2011 | 0.022 | ex
2020 | PGE | Hsp | CZ01 | 2015 | 0.017 | ex
2020 | PGE | Hsp | CZ01 | 2017 | 0.017 | rec
2020 | PGE | Hsp | CZ01 | 2020 | 0.006 | rec
2020 | PGE | Hsp | CZ01 | New | 0.006 | new
2020 | PGE | Hsp | CZ02 | 1975 | 2.857 | old
2020 | PGE | Hsp | CZ02 | 1985 | 1.531 | old
2020 | PGE | Hsp | CZ02 | 1996 | 0.901 | old
2020 | PGE | Hsp | CZ02 | 2003 | 0.433 | ex
2020 | PGE | Hsp | CZ02 | 2007 | 0.213 | ex
2020 | PGE | Hsp | CZ02 | 2011 | 0.213 | ex
2020 | PGE | Hsp | CZ02 | 2015 | 0.16 | ex
2020 | PGE | Hsp | CZ02 | 2017 | 0.16 | rec
2020 | PGE | Hsp | CZ02 | 2020 | 0.053 | rec
2020 | PGE | Hsp | CZ02 | New | 0.053 | new
2020 | PGE | Hsp | CZ03 | 1975 | 9.813 | old
2020 | PGE | Hsp | CZ03 | 1985 | 4.185 | old
2020 | PGE | Hsp | CZ03 | 1996 | 2.546 | old
2020 | PGE | Hsp | CZ03 | 2003 | 0.578 | ex
2020 | PGE | Hsp | CZ03 | 2007 | 0.582 | ex
2020 | PGE | Hsp | CZ03 | 2011 | 0.582 | ex
2020 | PGE | Hsp | CZ03 | 2015 | 0.437 | ex
2020 | PGE | Hsp | CZ03 | 2017 | 0.437 | rec
2020 | PGE | Hsp | CZ03 | 2020 | 0.146 | rec
2020 | PGE | Hsp | CZ03 | New | 0.146 | new
2020 | PGE | Hsp | CZ04 | 1975 | 3.687 | old
2020 | PGE | Hsp | CZ04 | 1985 | 2.173 | old
2020 | PGE | Hsp | CZ04 | 1996 | 1.239 | old
2020 | PGE | Hsp | CZ04 | 2003 | 0.629 | ex
2020 | PGE | Hsp | CZ04 | 2007 | 0.298 | ex
2020 | PGE | Hsp | CZ04 | 2011 | 0.298 | ex
2020 | PGE | Hsp | CZ04 | 2015 | 0.223 | ex
2020 | PGE | Hsp | CZ04 | 2017 | 0.223 | rec
2020 | PGE | Hsp | CZ04 | 2020 | 0.075 | rec
2020 | PGE | Hsp | CZ04 | New | 0.075 | new
2020 | PGE | Hsp | CZ05 | 1975 | 0.561 | old
2020 | PGE | Hsp | CZ05 | 1985 | 0.331 | old
2020 | PGE | Hsp | CZ05 | 1996 | 0.189 | old
2020 | PGE | Hsp | CZ05 | 2003 | 0.096 | ex
2020 | PGE | Hsp | CZ05 | 2007 | 0.045 | ex
2020 | PGE | Hsp | CZ05 | 2011 | 0.045 | ex
2020 | PGE | Hsp | CZ05 | 2015 | 0.034 | ex
2020 | PGE | Hsp | CZ05 | 2017 | 0.034 | rec
2020 | PGE | Hsp | CZ05 | 2020 | 0.011 | rec
2020 | PGE | Hsp | CZ05 | New | 0.011 | new
2020 | PGE | Hsp | CZ11 | 1975 | 1.73 | old
2020 | PGE | Hsp | CZ11 | 1985 | 1.066 | old
2020 | PGE | Hsp | CZ11 | 1996 | 0.653 | old
2020 | PGE | Hsp | CZ11 | 2003 | 0.423 | ex
2020 | PGE | Hsp | CZ11 | 2007 | 0.18 | ex
2020 | PGE | Hsp | CZ11 | 2011 | 0.18 | ex
2020 | PGE | Hsp | CZ11 | 2015 | 0.135 | ex
2020 | PGE | Hsp | CZ11 | 2017 | 0.135 | rec
2020 | PGE | Hsp | CZ11 | 2020 | 0.045 | rec
2020 | PGE | Hsp | CZ11 | New | 0.045 | new
2020 | PGE | Hsp | CZ12 | 1975 | 5.792 | old
2020 | PGE | Hsp | CZ12 | 1985 | 3.537 | old
2020 | PGE | Hsp | CZ12 | 1996 | 2.33 | old
2020 | PGE | Hsp | CZ12 | 2003 | 1.048 | ex
2020 | PGE | Hsp | CZ12 | 2007 | 0.594 | ex
2020 | PGE | Hsp | CZ12 | 2011 | 0.594 | ex
2020 | PGE | Hsp | CZ12 | 2015 | 0.445 | ex
2020 | PGE | Hsp | CZ12 | 2017 | 0.445 | rec
2020 | PGE | Hsp | CZ12 | 2020 | 0.148 | rec
2020 | PGE | Hsp | CZ12 | New | 0.148 | new
2020 | PGE | Hsp | CZ13 | 1975 | 4.262 | old
2020 | PGE | Hsp | CZ13 | 1985 | 2.882 | old
2020 | PGE | Hsp | CZ13 | 1996 | 1.629 | old
2020 | PGE | Hsp | CZ13 | 2003 | 1.12 | ex
2020 | PGE | Hsp | CZ13 | 2007 | 0.467 | ex
2020 | PGE | Hsp | CZ13 | 2011 | 0.467 | ex
2020 | PGE | Hsp | CZ13 | 2015 | 0.35 | ex
2020 | PGE | Hsp | CZ13 | 2017 | 0.35 | rec
2020 | PGE | Hsp | CZ13 | 2020 | 0.117 | rec
2020 | PGE | Hsp | CZ13 | New | 0.117 | new
2020 | PGE | Hsp | CZ16 | 1975 | 0.113 | old
2020 | PGE | Hsp | CZ16 | 1985 | 0.052 | old
2020 | PGE | Hsp | CZ16 | 1996 | 0.035 | old
2020 | PGE | Hsp | CZ16 | 2003 | 0.026 | ex
2020 | PGE | Hsp | CZ16 | 2007 | 0.009 | ex
2020 | PGE | Hsp | CZ16 | 2011 | 0.009 | ex
2020 | PGE | Hsp | CZ16 | 2015 | 0.007 | ex
2020 | PGE | Hsp | CZ16 | 2017 | 0.007 | rec
2020 | PGE | Hsp | CZ16 | 2020 | 0.002 | rec
2020 | PGE | Hsp | CZ16 | New | 0.002 | new
2020 | PGE | Htl | CZ01 | 1975 | 0.321 | old
2020 | PGE | Htl | CZ01 | 1985 | 0.298 | old
2020 | PGE | Htl | CZ01 | 1996 | 0.086 | old
2020 | PGE | Htl | CZ01 | 2003 | 0.119 | ex
2020 | PGE | Htl | CZ01 | 2007 | 0.038 | ex
2020 | PGE | Htl | CZ01 | 2011 | 0.038 | ex
2020 | PGE | Htl | CZ01 | 2015 | 0.029 | ex
2020 | PGE | Htl | CZ01 | 2017 | 0.029 | rec
2020 | PGE | Htl | CZ01 | 2020 | 0.01 | rec
2020 | PGE | Htl | CZ01 | New | 0.01 | new
2020 | PGE | Htl | CZ02 | 1975 | 1.545 | old
2020 | PGE | Htl | CZ02 | 1985 | 1.332 | old
2020 | PGE | Htl | CZ02 | 1996 | 0.612 | old
2020 | PGE | Htl | CZ02 | 2003 | 0.362 | ex
2020 | PGE | Htl | CZ02 | 2007 | 0.168 | ex
2020 | PGE | Htl | CZ02 | 2011 | 0.168 | ex
2020 | PGE | Htl | CZ02 | 2015 | 0.126 | ex
2020 | PGE | Htl | CZ02 | 2017 | 0.126 | rec
2020 | PGE | Htl | CZ02 | 2020 | 0.042 | rec
2020 | PGE | Htl | CZ02 | New | 0.042 | new
2020 | PGE | Htl | CZ03 | 1975 | 11.887 | old
2020 | PGE | Htl | CZ03 | 1985 | 7.67 | old
2020 | PGE | Htl | CZ03 | 1996 | 3.548 | old
2020 | PGE | Htl | CZ03 | 2003 | 1.994 | ex
2020 | PGE | Htl | CZ03 | 2007 | 0.502 | ex
2020 | PGE | Htl | CZ03 | 2011 | 0.502 | ex
2020 | PGE | Htl | CZ03 | 2015 | 0.376 | ex
2020 | PGE | Htl | CZ03 | 2017 | 0.376 | rec
2020 | PGE | Htl | CZ03 | 2020 | 0.125 | rec
2020 | PGE | Htl | CZ03 | New | 0.125 | new
2020 | PGE | Htl | CZ04 | 1975 | 3.175 | old
2020 | PGE | Htl | CZ04 | 1985 | 2.811 | old
2020 | PGE | Htl | CZ04 | 1996 | 1.38 | old
2020 | PGE | Htl | CZ04 | 2003 | 0.699 | ex
2020 | PGE | Htl | CZ04 | 2007 | 0.372 | ex
2020 | PGE | Htl | CZ04 | 2011 | 0.372 | ex
2020 | PGE | Htl | CZ04 | 2015 | 0.279 | ex
2020 | PGE | Htl | CZ04 | 2017 | 0.279 | rec
2020 | PGE | Htl | CZ04 | 2020 | 0.093 | rec
2020 | PGE | Htl | CZ04 | New | 0.093 | new
2020 | PGE | Htl | CZ05 | 1975 | 1.323 | old
2020 | PGE | Htl | CZ05 | 1985 | 1.174 | old
2020 | PGE | Htl | CZ05 | 1996 | 0.577 | old
2020 | PGE | Htl | CZ05 | 2003 | 0.292 | ex
2020 | PGE | Htl | CZ05 | 2007 | 0.156 | ex
2020 | PGE | Htl | CZ05 | 2011 | 0.156 | ex
2020 | PGE | Htl | CZ05 | 2015 | 0.117 | ex
2020 | PGE | Htl | CZ05 | 2017 | 0.117 | rec
2020 | PGE | Htl | CZ05 | 2020 | 0.039 | rec
2020 | PGE | Htl | CZ05 | New | 0.039 | new
2020 | PGE | Htl | CZ11 | 1975 | 1.044 | old
2020 | PGE | Htl | CZ11 | 1985 | 0.65 | old
2020 | PGE | Htl | CZ11 | 1996 | 0.23 | old
2020 | PGE | Htl | CZ11 | 2003 | 0.206 | ex
2020 | PGE | Htl | CZ11 | 2007 | 0.11 | ex
2020 | PGE | Htl | CZ11 | 2011 | 0.11 | ex
2020 | PGE | Htl | CZ11 | 2015 | 0.082 | ex
2020 | PGE | Htl | CZ11 | 2017 | 0.082 | rec
2020 | PGE | Htl | CZ11 | 2020 | 0.027 | rec
2020 | PGE | Htl | CZ11 | New | 0.027 | new
2020 | PGE | Htl | CZ12 | 1975 | 3.052 | old
2020 | PGE | Htl | CZ12 | 1985 | 2.133 | old
2020 | PGE | Htl | CZ12 | 1996 | 1.252 | old
2020 | PGE | Htl | CZ12 | 2003 | 0.754 | ex
2020 | PGE | Htl | CZ12 | 2007 | 0.422 | ex
2020 | PGE | Htl | CZ12 | 2011 | 0.422 | ex
2020 | PGE | Htl | CZ12 | 2015 | 0.316 | ex
2020 | PGE | Htl | CZ12 | 2017 | 0.316 | rec
2020 | PGE | Htl | CZ12 | 2020 | 0.105 | rec
2020 | PGE | Htl | CZ12 | New | 0.105 | new
2020 | PGE | Htl | CZ13 | 1975 | 2.341 | old
2020 | PGE | Htl | CZ13 | 1985 | 1.441 | old
2020 | PGE | Htl | CZ13 | 1996 | 0.471 | old
2020 | PGE | Htl | CZ13 | 2003 | 0.417 | ex
2020 | PGE | Htl | CZ13 | 2007 | 0.231 | ex
2020 | PGE | Htl | CZ13 | 2011 | 0.231 | ex
2020 | PGE | Htl | CZ13 | 2015 | 0.173 | ex
2020 | PGE | Htl | CZ13 | 2017 | 0.173 | rec
2020 | PGE | Htl | CZ13 | 2020 | 0.058 | rec
2020 | PGE | Htl | CZ13 | New | 0.058 | new
2020 | PGE | Htl | CZ16 | 1975 | 0.386 | old
2020 | PGE | Htl | CZ16 | 1985 | 0.305 | old
2020 | PGE | Htl | CZ16 | 1996 | 0.089 | old
2020 | PGE | Htl | CZ16 | 2003 | 0.117 | ex
2020 | PGE | Htl | CZ16 | 2007 | 0.043 | ex
2020 | PGE | Htl | CZ16 | 2011 | 0.043 | ex
2020 | PGE | Htl | CZ16 | 2015 | 0.033 | ex
2020 | PGE | Htl | CZ16 | 2017 | 0.033 | rec
2020 | PGE | Htl | CZ16 | 2020 | 0.011 | rec
2020 | PGE | Htl | CZ16 | New | 0.011 | new
2020 | PGE | MBT | CZ01 | 1975 | 0.491 | old
2020 | PGE | MBT | CZ01 | 1985 | 0.233 | old
2020 | PGE | MBT | CZ01 | 1996 | 0.158 | old
2020 | PGE | MBT | CZ01 | 2003 | 0.071 | ex
2020 | PGE | MBT | CZ01 | 2007 | 0.035 | ex
2020 | PGE | MBT | CZ01 | 2011 | 0.035 | ex
2020 | PGE | MBT | CZ01 | 2015 | 0.026 | ex
2020 | PGE | MBT | CZ01 | 2017 | 0.026 | rec
2020 | PGE | MBT | CZ01 | 2020 | 0.009 | rec
2020 | PGE | MBT | CZ01 | New | 0.009 | new
2020 | PGE | MBT | CZ02 | 1975 | 5.202 | old
2020 | PGE | MBT | CZ02 | 1985 | 2.346 | old
2020 | PGE | MBT | CZ02 | 1996 | 1.186 | old
2020 | PGE | MBT | CZ02 | 2003 | 0.597 | ex
2020 | PGE | MBT | CZ02 | 2007 | 0.269 | ex
2020 | PGE | MBT | CZ02 | 2011 | 0.269 | ex
2020 | PGE | MBT | CZ02 | 2015 | 0.202 | ex
2020 | PGE | MBT | CZ02 | 2017 | 0.202 | rec
2020 | PGE | MBT | CZ02 | 2020 | 0.067 | rec
2020 | PGE | MBT | CZ02 | New | 0.067 | new
2020 | PGE | MBT | CZ03 | 1975 | 29.94 | old
2020 | PGE | MBT | CZ03 | 1985 | 8.93 | old
2020 | PGE | MBT | CZ03 | 1996 | 5.631 | old
2020 | PGE | MBT | CZ03 | 2003 | 3.032 | ex
2020 | PGE | MBT | CZ03 | 2007 | 1.046 | ex
2020 | PGE | MBT | CZ03 | 2011 | 1.046 | ex
2020 | PGE | MBT | CZ03 | 2015 | 0.784 | ex
2020 | PGE | MBT | CZ03 | 2017 | 0.784 | rec
2020 | PGE | MBT | CZ03 | 2020 | 0.261 | rec
2020 | PGE | MBT | CZ03 | New | 0.261 | new
2020 | PGE | MBT | CZ04 | 1975 | 13.005 | old
2020 | PGE | MBT | CZ04 | 1985 | 7.296 | old
2020 | PGE | MBT | CZ04 | 1996 | 3.172 | old
2020 | PGE | MBT | CZ04 | 2003 | 1.566 | ex
2020 | PGE | MBT | CZ04 | 2007 | 0.795 | ex
2020 | PGE | MBT | CZ04 | 2011 | 0.795 | ex
2020 | PGE | MBT | CZ04 | 2015 | 0.597 | ex
2020 | PGE | MBT | CZ04 | 2017 | 0.597 | rec
2020 | PGE | MBT | CZ04 | 2020 | 0.199 | rec
2020 | PGE | MBT | CZ04 | New | 0.199 | new
2020 | PGE | MBT | CZ05 | 1975 | 1.551 | old
2020 | PGE | MBT | CZ05 | 1985 | 0.872 | old
2020 | PGE | MBT | CZ05 | 1996 | 0.379 | old
2020 | PGE | MBT | CZ05 | 2003 | 0.187 | ex
2020 | PGE | MBT | CZ05 | 2007 | 0.095 | ex
2020 | PGE | MBT | CZ05 | 2011 | 0.095 | ex
2020 | PGE | MBT | CZ05 | 2015 | 0.071 | ex
2020 | PGE | MBT | CZ05 | 2017 | 0.071 | rec
2020 | PGE | MBT | CZ05 | 2020 | 0.024 | rec
2020 | PGE | MBT | CZ05 | New | 0.024 | new
2020 | PGE | MBT | CZ11 | 1975 | 2.968 | old
2020 | PGE | MBT | CZ11 | 1985 | 1.919 | old
2020 | PGE | MBT | CZ11 | 1996 | 1.142 | old
2020 | PGE | MBT | CZ11 | 2003 | 0.582 | ex
2020 | PGE | MBT | CZ11 | 2007 | 0.324 | ex
2020 | PGE | MBT | CZ11 | 2011 | 0.324 | ex
2020 | PGE | MBT | CZ11 | 2015 | 0.243 | ex
2020 | PGE | MBT | CZ11 | 2017 | 0.243 | rec
2020 | PGE | MBT | CZ11 | 2020 | 0.081 | rec
2020 | PGE | MBT | CZ11 | New | 0.081 | new
2020 | PGE | MBT | CZ12 | 1975 | 12.779 | old
2020 | PGE | MBT | CZ12 | 1985 | 7.629 | old
2020 | PGE | MBT | CZ12 | 1996 | 3.643 | old
2020 | PGE | MBT | CZ12 | 2003 | 2.069 | ex
2020 | PGE | MBT | CZ12 | 2007 | 1.04 | ex
2020 | PGE | MBT | CZ12 | 2011 | 1.04 | ex
2020 | PGE | MBT | CZ12 | 2015 | 0.78 | ex
2020 | PGE | MBT | CZ12 | 2017 | 0.78 | rec
2020 | PGE | MBT | CZ12 | 2020 | 0.26 | rec
2020 | PGE | MBT | CZ12 | New | 0.26 | new
2020 | PGE | MBT | CZ13 | 1975 | 7.423 | old
2020 | PGE | MBT | CZ13 | 1985 | 4.75 | old
2020 | PGE | MBT | CZ13 | 1996 | 3.023 | old
2020 | PGE | MBT | CZ13 | 2003 | 1.222 | ex
2020 | PGE | MBT | CZ13 | 2007 | 0.767 | ex
2020 | PGE | MBT | CZ13 | 2011 | 0.767 | ex
2020 | PGE | MBT | CZ13 | 2015 | 0.575 | ex
2020 | PGE | MBT | CZ13 | 2017 | 0.575 | rec
2020 | PGE | MBT | CZ13 | 2020 | 0.192 | rec
2020 | PGE | MBT | CZ13 | New | 0.192 | new
2020 | PGE | MBT | CZ16 | 1975 | 0.714 | old
2020 | PGE | MBT | CZ16 | 1985 | 0.382 | old
2020 | PGE | MBT | CZ16 | 1996 | 0.255 | old
2020 | PGE | MBT | CZ16 | 2003 | 0.116 | ex
2020 | PGE | MBT | CZ16 | 2007 | 0.062 | ex
2020 | PGE | MBT | CZ16 | 2011 | 0.062 | ex
2020 | PGE | MBT | CZ16 | 2015 | 0.046 | ex
2020 | PGE | MBT | CZ16 | 2017 | 0.046 | rec
2020 | PGE | MBT | CZ16 | 2020 | 0.015 | rec
2020 | PGE | MBT | CZ16 | New | 0.015 | new
2020 | PGE | MLI | CZ01 | 1975 | 0.491 | old
2020 | PGE | MLI | CZ01 | 1985 | 0.233 | old
2020 | PGE | MLI | CZ01 | 1996 | 0.158 | old
2020 | PGE | MLI | CZ01 | 2003 | 0.071 | ex
2020 | PGE | MLI | CZ01 | 2007 | 0.035 | ex
2020 | PGE | MLI | CZ01 | 2011 | 0.035 | ex
2020 | PGE | MLI | CZ01 | 2015 | 0.026 | ex
2020 | PGE | MLI | CZ01 | 2017 | 0.026 | rec
2020 | PGE | MLI | CZ01 | 2020 | 0.009 | rec
2020 | PGE | MLI | CZ01 | New | 0.009 | new
2020 | PGE | MLI | CZ02 | 1975 | 5.202 | old
2020 | PGE | MLI | CZ02 | 1985 | 2.346 | old
2020 | PGE | MLI | CZ02 | 1996 | 1.186 | old
2020 | PGE | MLI | CZ02 | 2003 | 0.597 | ex
2020 | PGE | MLI | CZ02 | 2007 | 0.269 | ex
2020 | PGE | MLI | CZ02 | 2011 | 0.269 | ex
2020 | PGE | MLI | CZ02 | 2015 | 0.202 | ex
2020 | PGE | MLI | CZ02 | 2017 | 0.202 | rec
2020 | PGE | MLI | CZ02 | 2020 | 0.067 | rec
2020 | PGE | MLI | CZ02 | New | 0.067 | new
2020 | PGE | MLI | CZ03 | 1975 | 29.94 | old
2020 | PGE | MLI | CZ03 | 1985 | 8.93 | old
2020 | PGE | MLI | CZ03 | 1996 | 5.631 | old
2020 | PGE | MLI | CZ03 | 2003 | 3.032 | ex
2020 | PGE | MLI | CZ03 | 2007 | 1.046 | ex
2020 | PGE | MLI | CZ03 | 2011 | 1.046 | ex
2020 | PGE | MLI | CZ03 | 2015 | 0.784 | ex
2020 | PGE | MLI | CZ03 | 2017 | 0.784 | rec
2020 | PGE | MLI | CZ03 | 2020 | 0.261 | rec
2020 | PGE | MLI | CZ03 | New | 0.261 | new
2020 | PGE | MLI | CZ04 | 1975 | 13.005 | old
2020 | PGE | MLI | CZ04 | 1985 | 7.296 | old
2020 | PGE | MLI | CZ04 | 1996 | 3.172 | old
2020 | PGE | MLI | CZ04 | 2003 | 1.566 | ex
2020 | PGE | MLI | CZ04 | 2007 | 0.795 | ex
2020 | PGE | MLI | CZ04 | 2011 | 0.795 | ex
2020 | PGE | MLI | CZ04 | 2015 | 0.597 | ex
2020 | PGE | MLI | CZ04 | 2017 | 0.597 | rec
2020 | PGE | MLI | CZ04 | 2020 | 0.199 | rec
2020 | PGE | MLI | CZ04 | New | 0.199 | new
2020 | PGE | MLI | CZ05 | 1975 | 1.551 | old
2020 | PGE | MLI | CZ05 | 1985 | 0.872 | old
2020 | PGE | MLI | CZ05 | 1996 | 0.379 | old
2020 | PGE | MLI | CZ05 | 2003 | 0.187 | ex
2020 | PGE | MLI | CZ05 | 2007 | 0.095 | ex
2020 | PGE | MLI | CZ05 | 2011 | 0.095 | ex
2020 | PGE | MLI | CZ05 | 2015 | 0.071 | ex
2020 | PGE | MLI | CZ05 | 2017 | 0.071 | rec
2020 | PGE | MLI | CZ05 | 2020 | 0.024 | rec
2020 | PGE | MLI | CZ05 | New | 0.024 | new
2020 | PGE | MLI | CZ11 | 1975 | 2.968 | old
2020 | PGE | MLI | CZ11 | 1985 | 1.919 | old
2020 | PGE | MLI | CZ11 | 1996 | 1.142 | old
2020 | PGE | MLI | CZ11 | 2003 | 0.582 | ex
2020 | PGE | MLI | CZ11 | 2007 | 0.324 | ex
2020 | PGE | MLI | CZ11 | 2011 | 0.324 | ex
2020 | PGE | MLI | CZ11 | 2015 | 0.243 | ex
2020 | PGE | MLI | CZ11 | 2017 | 0.243 | rec
2020 | PGE | MLI | CZ11 | 2020 | 0.081 | rec
2020 | PGE | MLI | CZ11 | New | 0.081 | new
2020 | PGE | MLI | CZ12 | 1975 | 12.779 | old
2020 | PGE | MLI | CZ12 | 1985 | 7.629 | old
2020 | PGE | MLI | CZ12 | 1996 | 3.643 | old
2020 | PGE | MLI | CZ12 | 2003 | 2.069 | ex
2020 | PGE | MLI | CZ12 | 2007 | 1.04 | ex
2020 | PGE | MLI | CZ12 | 2011 | 1.04 | ex
2020 | PGE | MLI | CZ12 | 2015 | 0.78 | ex
2020 | PGE | MLI | CZ12 | 2017 | 0.78 | rec
2020 | PGE | MLI | CZ12 | 2020 | 0.26 | rec
2020 | PGE | MLI | CZ12 | New | 0.26 | new
2020 | PGE | MLI | CZ13 | 1975 | 7.423 | old
2020 | PGE | MLI | CZ13 | 1985 | 4.75 | old
2020 | PGE | MLI | CZ13 | 1996 | 3.023 | old
2020 | PGE | MLI | CZ13 | 2003 | 1.222 | ex
2020 | PGE | MLI | CZ13 | 2007 | 0.767 | ex
2020 | PGE | MLI | CZ13 | 2011 | 0.767 | ex
2020 | PGE | MLI | CZ13 | 2015 | 0.575 | ex
2020 | PGE | MLI | CZ13 | 2017 | 0.575 | rec
2020 | PGE | MLI | CZ13 | 2020 | 0.192 | rec
2020 | PGE | MLI | CZ13 | New | 0.192 | new
2020 | PGE | MLI | CZ16 | 1975 | 0.714 | old
2020 | PGE | MLI | CZ16 | 1985 | 0.382 | old
2020 | PGE | MLI | CZ16 | 1996 | 0.255 | old
2020 | PGE | MLI | CZ16 | 2003 | 0.116 | ex
2020 | PGE | MLI | CZ16 | 2007 | 0.062 | ex
2020 | PGE | MLI | CZ16 | 2011 | 0.062 | ex
2020 | PGE | MLI | CZ16 | 2015 | 0.046 | ex
2020 | PGE | MLI | CZ16 | 2017 | 0.046 | rec
2020 | PGE | MLI | CZ16 | 2020 | 0.015 | rec
2020 | PGE | MLI | CZ16 | New | 0.015 | new
2020 | PGE | Mtl | CZ01 | 1975 | 0.321 | old
2020 | PGE | Mtl | CZ01 | 1985 | 0.298 | old
2020 | PGE | Mtl | CZ01 | 1996 | 0.086 | old
2020 | PGE | Mtl | CZ01 | 2003 | 0.119 | ex
2020 | PGE | Mtl | CZ01 | 2007 | 0.038 | ex
2020 | PGE | Mtl | CZ01 | 2011 | 0.038 | ex
2020 | PGE | Mtl | CZ01 | 2015 | 0.029 | ex
2020 | PGE | Mtl | CZ01 | 2017 | 0.029 | rec
2020 | PGE | Mtl | CZ01 | 2020 | 0.01 | rec
2020 | PGE | Mtl | CZ01 | New | 0.01 | new
2020 | PGE | Mtl | CZ02 | 1975 | 1.545 | old
2020 | PGE | Mtl | CZ02 | 1985 | 1.332 | old
2020 | PGE | Mtl | CZ02 | 1996 | 0.612 | old
2020 | PGE | Mtl | CZ02 | 2003 | 0.362 | ex
2020 | PGE | Mtl | CZ02 | 2007 | 0.168 | ex
2020 | PGE | Mtl | CZ02 | 2011 | 0.168 | ex
2020 | PGE | Mtl | CZ02 | 2015 | 0.126 | ex
2020 | PGE | Mtl | CZ02 | 2017 | 0.126 | rec
2020 | PGE | Mtl | CZ02 | 2020 | 0.042 | rec
2020 | PGE | Mtl | CZ02 | New | 0.042 | new
2020 | PGE | Mtl | CZ03 | 1975 | 11.887 | old
2020 | PGE | Mtl | CZ03 | 1985 | 7.67 | old
2020 | PGE | Mtl | CZ03 | 1996 | 3.548 | old
2020 | PGE | Mtl | CZ03 | 2003 | 1.994 | ex
2020 | PGE | Mtl | CZ03 | 2007 | 0.502 | ex
2020 | PGE | Mtl | CZ03 | 2011 | 0.502 | ex
2020 | PGE | Mtl | CZ03 | 2015 | 0.376 | ex
2020 | PGE | Mtl | CZ03 | 2017 | 0.376 | rec
2020 | PGE | Mtl | CZ03 | 2020 | 0.125 | rec
2020 | PGE | Mtl | CZ03 | New | 0.125 | new
2020 | PGE | Mtl | CZ04 | 1975 | 3.175 | old
2020 | PGE | Mtl | CZ04 | 1985 | 2.811 | old
2020 | PGE | Mtl | CZ04 | 1996 | 1.38 | old
2020 | PGE | Mtl | CZ04 | 2003 | 0.699 | ex
2020 | PGE | Mtl | CZ04 | 2007 | 0.372 | ex
2020 | PGE | Mtl | CZ04 | 2011 | 0.372 | ex
2020 | PGE | Mtl | CZ04 | 2015 | 0.279 | ex
2020 | PGE | Mtl | CZ04 | 2017 | 0.279 | rec
2020 | PGE | Mtl | CZ04 | 2020 | 0.093 | rec
2020 | PGE | Mtl | CZ04 | New | 0.093 | new
2020 | PGE | Mtl | CZ05 | 1975 | 1.323 | old
2020 | PGE | Mtl | CZ05 | 1985 | 1.174 | old
2020 | PGE | Mtl | CZ05 | 1996 | 0.577 | old
2020 | PGE | Mtl | CZ05 | 2003 | 0.292 | ex
2020 | PGE | Mtl | CZ05 | 2007 | 0.156 | ex
2020 | PGE | Mtl | CZ05 | 2011 | 0.156 | ex
2020 | PGE | Mtl | CZ05 | 2015 | 0.117 | ex
2020 | PGE | Mtl | CZ05 | 2017 | 0.117 | rec
2020 | PGE | Mtl | CZ05 | 2020 | 0.039 | rec
2020 | PGE | Mtl | CZ05 | New | 0.039 | new
2020 | PGE | Mtl | CZ11 | 1975 | 1.044 | old
2020 | PGE | Mtl | CZ11 | 1985 | 0.65 | old
2020 | PGE | Mtl | CZ11 | 1996 | 0.23 | old
2020 | PGE | Mtl | CZ11 | 2003 | 0.206 | ex
2020 | PGE | Mtl | CZ11 | 2007 | 0.11 | ex
2020 | PGE | Mtl | CZ11 | 2011 | 0.11 | ex
2020 | PGE | Mtl | CZ11 | 2015 | 0.082 | ex
2020 | PGE | Mtl | CZ11 | 2017 | 0.082 | rec
2020 | PGE | Mtl | CZ11 | 2020 | 0.027 | rec
2020 | PGE | Mtl | CZ11 | New | 0.027 | new
2020 | PGE | Mtl | CZ12 | 1975 | 3.052 | old
2020 | PGE | Mtl | CZ12 | 1985 | 2.133 | old
2020 | PGE | Mtl | CZ12 | 1996 | 1.252 | old
2020 | PGE | Mtl | CZ12 | 2003 | 0.754 | ex
2020 | PGE | Mtl | CZ12 | 2007 | 0.422 | ex
2020 | PGE | Mtl | CZ12 | 2011 | 0.422 | ex
2020 | PGE | Mtl | CZ12 | 2015 | 0.316 | ex
2020 | PGE | Mtl | CZ12 | 2017 | 0.316 | rec
2020 | PGE | Mtl | CZ12 | 2020 | 0.105 | rec
2020 | PGE | Mtl | CZ12 | New | 0.105 | new
2020 | PGE | Mtl | CZ13 | 1975 | 2.341 | old
2020 | PGE | Mtl | CZ13 | 1985 | 1.441 | old
2020 | PGE | Mtl | CZ13 | 1996 | 0.471 | old
2020 | PGE | Mtl | CZ13 | 2003 | 0.417 | ex
2020 | PGE | Mtl | CZ13 | 2007 | 0.231 | ex
2020 | PGE | Mtl | CZ13 | 2011 | 0.231 | ex
2020 | PGE | Mtl | CZ13 | 2015 | 0.173 | ex
2020 | PGE | Mtl | CZ13 | 2017 | 0.173 | rec
2020 | PGE | Mtl | CZ13 | 2020 | 0.058 | rec
2020 | PGE | Mtl | CZ13 | New | 0.058 | new
2020 | PGE | Mtl | CZ16 | 1975 | 0.386 | old
2020 | PGE | Mtl | CZ16 | 1985 | 0.305 | old
2020 | PGE | Mtl | CZ16 | 1996 | 0.089 | old
2020 | PGE | Mtl | CZ16 | 2003 | 0.117 | ex
2020 | PGE | Mtl | CZ16 | 2007 | 0.043 | ex
2020 | PGE | Mtl | CZ16 | 2011 | 0.043 | ex
2020 | PGE | Mtl | CZ16 | 2015 | 0.033 | ex
2020 | PGE | Mtl | CZ16 | 2017 | 0.033 | rec
2020 | PGE | Mtl | CZ16 | 2020 | 0.011 | rec
2020 | PGE | Mtl | CZ16 | New | 0.011 | new
2020 | PGE | Nrs | CZ01 | 1975 | 0.388 | old
2020 | PGE | Nrs | CZ01 | 1985 | 0.124 | old
2020 | PGE | Nrs | CZ01 | 1996 | 0.102 | old
2020 | PGE | Nrs | CZ01 | 2003 | 0.08 | ex
2020 | PGE | Nrs | CZ01 | 2007 | 0.022 | ex
2020 | PGE | Nrs | CZ01 | 2011 | 0.022 | ex
2020 | PGE | Nrs | CZ01 | 2015 | 0.017 | ex
2020 | PGE | Nrs | CZ01 | 2017 | 0.017 | rec
2020 | PGE | Nrs | CZ01 | 2020 | 0.006 | rec
2020 | PGE | Nrs | CZ01 | New | 0.006 | new
2020 | PGE | Nrs | CZ02 | 1975 | 2.857 | old
2020 | PGE | Nrs | CZ02 | 1985 | 1.531 | old
2020 | PGE | Nrs | CZ02 | 1996 | 0.901 | old
2020 | PGE | Nrs | CZ02 | 2003 | 0.433 | ex
2020 | PGE | Nrs | CZ02 | 2007 | 0.213 | ex
2020 | PGE | Nrs | CZ02 | 2011 | 0.213 | ex
2020 | PGE | Nrs | CZ02 | 2015 | 0.16 | ex
2020 | PGE | Nrs | CZ02 | 2017 | 0.16 | rec
2020 | PGE | Nrs | CZ02 | 2020 | 0.053 | rec
2020 | PGE | Nrs | CZ02 | New | 0.053 | new
2020 | PGE | Nrs | CZ03 | 1975 | 9.813 | old
2020 | PGE | Nrs | CZ03 | 1985 | 4.185 | old
2020 | PGE | Nrs | CZ03 | 1996 | 2.546 | old
2020 | PGE | Nrs | CZ03 | 2003 | 0.578 | ex
2020 | PGE | Nrs | CZ03 | 2007 | 0.582 | ex
2020 | PGE | Nrs | CZ03 | 2011 | 0.582 | ex
2020 | PGE | Nrs | CZ03 | 2015 | 0.437 | ex
2020 | PGE | Nrs | CZ03 | 2017 | 0.437 | rec
2020 | PGE | Nrs | CZ03 | 2020 | 0.146 | rec
2020 | PGE | Nrs | CZ03 | New | 0.146 | new
2020 | PGE | Nrs | CZ04 | 1975 | 3.687 | old
2020 | PGE | Nrs | CZ04 | 1985 | 2.173 | old
2020 | PGE | Nrs | CZ04 | 1996 | 1.239 | old
2020 | PGE | Nrs | CZ04 | 2003 | 0.629 | ex
2020 | PGE | Nrs | CZ04 | 2007 | 0.298 | ex
2020 | PGE | Nrs | CZ04 | 2011 | 0.298 | ex
2020 | PGE | Nrs | CZ04 | 2015 | 0.223 | ex
2020 | PGE | Nrs | CZ04 | 2017 | 0.223 | rec
2020 | PGE | Nrs | CZ04 | 2020 | 0.075 | rec
2020 | PGE | Nrs | CZ04 | New | 0.075 | new
2020 | PGE | Nrs | CZ05 | 1975 | 0.561 | old
2020 | PGE | Nrs | CZ05 | 1985 | 0.331 | old
2020 | PGE | Nrs | CZ05 | 1996 | 0.189 | old
2020 | PGE | Nrs | CZ05 | 2003 | 0.096 | ex
2020 | PGE | Nrs | CZ05 | 2007 | 0.045 | ex
2020 | PGE | Nrs | CZ05 | 2011 | 0.045 | ex
2020 | PGE | Nrs | CZ05 | 2015 | 0.034 | ex
2020 | PGE | Nrs | CZ05 | 2017 | 0.034 | rec
2020 | PGE | Nrs | CZ05 | 2020 | 0.011 | rec
2020 | PGE | Nrs | CZ05 | New | 0.011 | new
2020 | PGE | Nrs | CZ11 | 1975 | 1.73 | old
2020 | PGE | Nrs | CZ11 | 1985 | 1.066 | old
2020 | PGE | Nrs | CZ11 | 1996 | 0.653 | old
2020 | PGE | Nrs | CZ11 | 2003 | 0.423 | ex
2020 | PGE | Nrs | CZ11 | 2007 | 0.18 | ex
2020 | PGE | Nrs | CZ11 | 2011 | 0.18 | ex
2020 | PGE | Nrs | CZ11 | 2015 | 0.135 | ex
2020 | PGE | Nrs | CZ11 | 2017 | 0.135 | rec
2020 | PGE | Nrs | CZ11 | 2020 | 0.045 | rec
2020 | PGE | Nrs | CZ11 | New | 0.045 | new
2020 | PGE | Nrs | CZ12 | 1975 | 5.792 | old
2020 | PGE | Nrs | CZ12 | 1985 | 3.537 | old
2020 | PGE | Nrs | CZ12 | 1996 | 2.33 | old
2020 | PGE | Nrs | CZ12 | 2003 | 1.048 | ex
2020 | PGE | Nrs | CZ12 | 2007 | 0.594 | ex
2020 | PGE | Nrs | CZ12 | 2011 | 0.594 | ex
2020 | PGE | Nrs | CZ12 | 2015 | 0.445 | ex
2020 | PGE | Nrs | CZ12 | 2017 | 0.445 | rec
2020 | PGE | Nrs | CZ12 | 2020 | 0.148 | rec
2020 | PGE | Nrs | CZ12 | New | 0.148 | new
2020 | PGE | Nrs | CZ13 | 1975 | 4.262 | old
2020 | PGE | Nrs | CZ13 | 1985 | 2.882 | old
2020 | PGE | Nrs | CZ13 | 1996 | 1.629 | old
2020 | PGE | Nrs | CZ13 | 2003 | 1.12 | ex
2020 | PGE | Nrs | CZ13 | 2007 | 0.467 | ex
2020 | PGE | Nrs | CZ13 | 2011 | 0.467 | ex
2020 | PGE | Nrs | CZ13 | 2015 | 0.35 | ex
2020 | PGE | Nrs | CZ13 | 2017 | 0.35 | rec
2020 | PGE | Nrs | CZ13 | 2020 | 0.117 | rec
2020 | PGE | Nrs | CZ13 | New | 0.117 | new
2020 | PGE | Nrs | CZ16 | 1975 | 0.113 | old
2020 | PGE | Nrs | CZ16 | 1985 | 0.052 | old
2020 | PGE | Nrs | CZ16 | 1996 | 0.035 | old
2020 | PGE | Nrs | CZ16 | 2003 | 0.026 | ex
2020 | PGE | Nrs | CZ16 | 2007 | 0.009 | ex
2020 | PGE | Nrs | CZ16 | 2011 | 0.009 | ex
2020 | PGE | Nrs | CZ16 | 2015 | 0.007 | ex
2020 | PGE | Nrs | CZ16 | 2017 | 0.007 | rec
2020 | PGE | Nrs | CZ16 | 2020 | 0.002 | rec
2020 | PGE | Nrs | CZ16 | New | 0.002 | new
2020 | PGE | OfL | CZ01 | 1975 | 0.882 | old
2020 | PGE | OfL | CZ01 | 1985 | 0.311 | old
2020 | PGE | OfL | CZ01 | 1996 | 0.129 | old
2020 | PGE | OfL | CZ01 | 2003 | 0.221 | ex
2020 | PGE | OfL | CZ01 | 2007 | 0.048 | ex
2020 | PGE | OfL | CZ01 | 2011 | 0.048 | ex
2020 | PGE | OfL | CZ01 | 2015 | 0.036 | ex
2020 | PGE | OfL | CZ01 | 2017 | 0.036 | rec
2020 | PGE | OfL | CZ01 | 2020 | 0.012 | rec
2020 | PGE | OfL | CZ01 | New | 0.012 | new
2020 | PGE | OfL | CZ02 | 1975 | 6.779 | old
2020 | PGE | OfL | CZ02 | 1985 | 6.175 | old
2020 | PGE | OfL | CZ02 | 1996 | 2.891 | old
2020 | PGE | OfL | CZ02 | 2003 | 1.88 | ex
2020 | PGE | OfL | CZ02 | 2007 | 0.71 | ex
2020 | PGE | OfL | CZ02 | 2011 | 0.71 | ex
2020 | PGE | OfL | CZ02 | 2015 | 0.533 | ex
2020 | PGE | OfL | CZ02 | 2017 | 0.533 | rec
2020 | PGE | OfL | CZ02 | 2020 | 0.178 | rec
2020 | PGE | OfL | CZ02 | New | 0.178 | new
2020 | PGE | OfL | CZ03 | 1975 | 77.24 | old
2020 | PGE | OfL | CZ03 | 1985 | 69.197 | old
2020 | PGE | OfL | CZ03 | 1996 | 28.211 | old
2020 | PGE | OfL | CZ03 | 2003 | 16.702 | ex
2020 | PGE | OfL | CZ03 | 2007 | 6.493 | ex
2020 | PGE | OfL | CZ03 | 2011 | 6.493 | ex
2020 | PGE | OfL | CZ03 | 2015 | 4.869 | ex
2020 | PGE | OfL | CZ03 | 2017 | 4.869 | rec
2020 | PGE | OfL | CZ03 | 2020 | 1.623 | rec
2020 | PGE | OfL | CZ03 | New | 1.623 | new
2020 | PGE | OfL | CZ04 | 1975 | 27.42 | old
2020 | PGE | OfL | CZ04 | 1985 | 27.53 | old
2020 | PGE | OfL | CZ04 | 1996 | 14.391 | old
2020 | PGE | OfL | CZ04 | 2003 | 9.312 | ex
2020 | PGE | OfL | CZ04 | 2007 | 3.61 | ex
2020 | PGE | OfL | CZ04 | 2011 | 3.61 | ex
2020 | PGE | OfL | CZ04 | 2015 | 2.707 | ex
2020 | PGE | OfL | CZ04 | 2017 | 2.707 | rec
2020 | PGE | OfL | CZ04 | 2020 | 0.903 | rec
2020 | PGE | OfL | CZ04 | New | 0.903 | new
2020 | PGE | OfL | CZ05 | 1975 | 1.922 | old
2020 | PGE | OfL | CZ05 | 1985 | 1.932 | old
2020 | PGE | OfL | CZ05 | 1996 | 1.011 | old
2020 | PGE | OfL | CZ05 | 2003 | 0.655 | ex
2020 | PGE | OfL | CZ05 | 2007 | 0.254 | ex
2020 | PGE | OfL | CZ05 | 2011 | 0.254 | ex
2020 | PGE | OfL | CZ05 | 2015 | 0.19 | ex
2020 | PGE | OfL | CZ05 | 2017 | 0.19 | rec
2020 | PGE | OfL | CZ05 | 2020 | 0.064 | rec
2020 | PGE | OfL | CZ05 | New | 0.064 | new
2020 | PGE | OfL | CZ11 | 1975 | 2.907 | old
2020 | PGE | OfL | CZ11 | 1985 | 2.003 | old
2020 | PGE | OfL | CZ11 | 1996 | 0.833 | old
2020 | PGE | OfL | CZ11 | 2003 | 0.815 | ex
2020 | PGE | OfL | CZ11 | 2007 | 0.41 | ex
2020 | PGE | OfL | CZ11 | 2011 | 0.41 | ex
2020 | PGE | OfL | CZ11 | 2015 | 0.308 | ex
2020 | PGE | OfL | CZ11 | 2017 | 0.308 | rec
2020 | PGE | OfL | CZ11 | 2020 | 0.103 | rec
2020 | PGE | OfL | CZ11 | New | 0.103 | new
2020 | PGE | OfL | CZ12 | 1975 | 19.449 | old
2020 | PGE | OfL | CZ12 | 1985 | 17.363 | old
2020 | PGE | OfL | CZ12 | 1996 | 11.029 | old
2020 | PGE | OfL | CZ12 | 2003 | 8.297 | ex
2020 | PGE | OfL | CZ12 | 2007 | 3.387 | ex
2020 | PGE | OfL | CZ12 | 2011 | 3.387 | ex
2020 | PGE | OfL | CZ12 | 2015 | 2.54 | ex
2020 | PGE | OfL | CZ12 | 2017 | 2.54 | rec
2020 | PGE | OfL | CZ12 | 2020 | 0.847 | rec
2020 | PGE | OfL | CZ12 | New | 0.847 | new
2020 | PGE | OfL | CZ13 | 1975 | 10.297 | old
2020 | PGE | OfL | CZ13 | 1985 | 8.246 | old
2020 | PGE | OfL | CZ13 | 1996 | 2.465 | old
2020 | PGE | OfL | CZ13 | 2003 | 2.136 | ex
2020 | PGE | OfL | CZ13 | 2007 | 1.397 | ex
2020 | PGE | OfL | CZ13 | 2011 | 1.397 | ex
2020 | PGE | OfL | CZ13 | 2015 | 1.048 | ex
2020 | PGE | OfL | CZ13 | 2017 | 1.048 | rec
2020 | PGE | OfL | CZ13 | 2020 | 0.349 | rec
2020 | PGE | OfL | CZ13 | New | 0.349 | new
2020 | PGE | OfL | CZ16 | 1975 | 0.416 | old
2020 | PGE | OfL | CZ16 | 1985 | 0.179 | old
2020 | PGE | OfL | CZ16 | 1996 | 0.078 | old
2020 | PGE | OfL | CZ16 | 2003 | 0.112 | ex
2020 | PGE | OfL | CZ16 | 2007 | 0.035 | ex
2020 | PGE | OfL | CZ16 | 2011 | 0.035 | ex
2020 | PGE | OfL | CZ16 | 2015 | 0.026 | ex
2020 | PGE | OfL | CZ16 | 2017 | 0.026 | rec
2020 | PGE | OfL | CZ16 | 2020 | 0.009 | rec
2020 | PGE | OfL | CZ16 | New | 0.009 | new
2020 | PGE | OfS | CZ01 | 1975 | 1.123 | old
2020 | PGE | OfS | CZ01 | 1985 | 0.446 | old
2020 | PGE | OfS | CZ01 | 1996 | 0.329 | old
2020 | PGE | OfS | CZ01 | 2003 | 0.132 | ex
2020 | PGE | OfS | CZ01 | 2007 | 0.07 | ex
2020 | PGE | OfS | CZ01 | 2011 | 0.07 | ex
2020 | PGE | OfS | CZ01 | 2015 | 0.053 | ex
2020 | PGE | OfS | CZ01 | 2017 | 0.053 | rec
2020 | PGE | OfS | CZ01 | 2020 | 0.018 | rec
2020 | PGE | OfS | CZ01 | New | 0.018 | new
2020 | PGE | OfS | CZ02 | 1975 | 2.173 | old
2020 | PGE | OfS | CZ02 | 1985 | 1.635 | old
2020 | PGE | OfS | CZ02 | 1996 | 0.764 | old
2020 | PGE | OfS | CZ02 | 2003 | 0.3 | ex
2020 | PGE | OfS | CZ02 | 2007 | 0.199 | ex
2020 | PGE | OfS | CZ02 | 2011 | 0.199 | ex
2020 | PGE | OfS | CZ02 | 2015 | 0.149 | ex
2020 | PGE | OfS | CZ02 | 2017 | 0.149 | rec
2020 | PGE | OfS | CZ02 | 2020 | 0.05 | rec
2020 | PGE | OfS | CZ02 | New | 0.05 | new
2020 | PGE | OfS | CZ03 | 1975 | 12.46 | old
2020 | PGE | OfS | CZ03 | 1985 | 10.827 | old
2020 | PGE | OfS | CZ03 | 1996 | 4.222 | old
2020 | PGE | OfS | CZ03 | 2003 | 1.483 | ex
2020 | PGE | OfS | CZ03 | 2007 | 1.205 | ex
2020 | PGE | OfS | CZ03 | 2011 | 1.205 | ex
2020 | PGE | OfS | CZ03 | 2015 | 0.904 | ex
2020 | PGE | OfS | CZ03 | 2017 | 0.904 | rec
2020 | PGE | OfS | CZ03 | 2020 | 0.301 | rec
2020 | PGE | OfS | CZ03 | New | 0.301 | new
2020 | PGE | OfS | CZ04 | 1975 | 9.283 | old
2020 | PGE | OfS | CZ04 | 1985 | 8.247 | old
2020 | PGE | OfS | CZ04 | 1996 | 3.606 | old
2020 | PGE | OfS | CZ04 | 2003 | 1.461 | ex
2020 | PGE | OfS | CZ04 | 2007 | 0.97 | ex
2020 | PGE | OfS | CZ04 | 2011 | 0.97 | ex
2020 | PGE | OfS | CZ04 | 2015 | 0.728 | ex
2020 | PGE | OfS | CZ04 | 2017 | 0.728 | rec
2020 | PGE | OfS | CZ04 | 2020 | 0.243 | rec
2020 | PGE | OfS | CZ04 | New | 0.243 | new
2020 | PGE | OfS | CZ05 | 1975 | 0.653 | old
2020 | PGE | OfS | CZ05 | 1985 | 0.581 | old
2020 | PGE | OfS | CZ05 | 1996 | 0.254 | old
2020 | PGE | OfS | CZ05 | 2003 | 0.103 | ex
2020 | PGE | OfS | CZ05 | 2007 | 0.068 | ex
2020 | PGE | OfS | CZ05 | 2011 | 0.068 | ex
2020 | PGE | OfS | CZ05 | 2015 | 0.051 | ex
2020 | PGE | OfS | CZ05 | 2017 | 0.051 | rec
2020 | PGE | OfS | CZ05 | 2020 | 0.017 | rec
2020 | PGE | OfS | CZ05 | New | 0.017 | new
2020 | PGE | OfS | CZ11 | 1975 | 3.394 | old
2020 | PGE | OfS | CZ11 | 1985 | 2.103 | old
2020 | PGE | OfS | CZ11 | 1996 | 1.09 | old
2020 | PGE | OfS | CZ11 | 2003 | 0.583 | ex
2020 | PGE | OfS | CZ11 | 2007 | 0.3 | ex
2020 | PGE | OfS | CZ11 | 2011 | 0.3 | ex
2020 | PGE | OfS | CZ11 | 2015 | 0.225 | ex
2020 | PGE | OfS | CZ11 | 2017 | 0.225 | rec
2020 | PGE | OfS | CZ11 | 2020 | 0.075 | rec
2020 | PGE | OfS | CZ11 | New | 0.075 | new
2020 | PGE | OfS | CZ12 | 1975 | 13.11 | old
2020 | PGE | OfS | CZ12 | 1985 | 8.258 | old
2020 | PGE | OfS | CZ12 | 1996 | 4.435 | old
2020 | PGE | OfS | CZ12 | 2003 | 2.216 | ex
2020 | PGE | OfS | CZ12 | 2007 | 1.249 | ex
2020 | PGE | OfS | CZ12 | 2011 | 1.249 | ex
2020 | PGE | OfS | CZ12 | 2015 | 0.936 | ex
2020 | PGE | OfS | CZ12 | 2017 | 0.936 | rec
2020 | PGE | OfS | CZ12 | 2020 | 0.312 | rec
2020 | PGE | OfS | CZ12 | New | 0.312 | new
2020 | PGE | OfS | CZ13 | 1975 | 11.019 | old
2020 | PGE | OfS | CZ13 | 1985 | 8.143 | old
2020 | PGE | OfS | CZ13 | 1996 | 3.682 | old
2020 | PGE | OfS | CZ13 | 2003 | 2.09 | ex
2020 | PGE | OfS | CZ13 | 2007 | 1.065 | ex
2020 | PGE | OfS | CZ13 | 2011 | 1.065 | ex
2020 | PGE | OfS | CZ13 | 2015 | 0.799 | ex
2020 | PGE | OfS | CZ13 | 2017 | 0.799 | rec
2020 | PGE | OfS | CZ13 | 2020 | 0.266 | rec
2020 | PGE | OfS | CZ13 | New | 0.266 | new
2020 | PGE | OfS | CZ16 | 1975 | 0.536 | old
2020 | PGE | OfS | CZ16 | 1985 | 0.242 | old
2020 | PGE | OfS | CZ16 | 1996 | 0.161 | old
2020 | PGE | OfS | CZ16 | 2003 | 0.071 | ex
2020 | PGE | OfS | CZ16 | 2007 | 0.037 | ex
2020 | PGE | OfS | CZ16 | 2011 | 0.037 | ex
2020 | PGE | OfS | CZ16 | 2015 | 0.028 | ex
2020 | PGE | OfS | CZ16 | 2017 | 0.028 | rec
2020 | PGE | OfS | CZ16 | 2020 | 0.009 | rec
2020 | PGE | OfS | CZ16 | New | 0.009 | new
2020 | PGE | RFF | CZ01 | 1975 | 0.29 | old
2020 | PGE | RFF | CZ01 | 1985 | 0.042 | old
2020 | PGE | RFF | CZ01 | 1996 | 0.023 | old
2020 | PGE | RFF | CZ01 | 2003 | 0.007 | ex
2020 | PGE | RFF | CZ01 | 2007 | 0.007 | ex
2020 | PGE | RFF | CZ01 | 2011 | 0.007 | ex
2020 | PGE | RFF | CZ01 | 2015 | 0.005 | ex
2020 | PGE | RFF | CZ01 | 2017 | 0.005 | rec
2020 | PGE | RFF | CZ01 | 2020 | 0.002 | rec
2020 | PGE | RFF | CZ01 | New | 0.002 | new
2020 | PGE | RFF | CZ02 | 1975 | 1.122 | old
2020 | PGE | RFF | CZ02 | 1985 | 0.277 | old
2020 | PGE | RFF | CZ02 | 1996 | 0.175 | old
2020 | PGE | RFF | CZ02 | 2003 | 0.058 | ex
2020 | PGE | RFF | CZ02 | 2007 | 0.038 | ex
2020 | PGE | RFF | CZ02 | 2011 | 0.038 | ex
2020 | PGE | RFF | CZ02 | 2015 | 0.029 | ex
2020 | PGE | RFF | CZ02 | 2017 | 0.029 | rec
2020 | PGE | RFF | CZ02 | 2020 | 0.01 | rec
2020 | PGE | RFF | CZ02 | New | 0.01 | new
2020 | PGE | RFF | CZ03 | 1975 | 5.141 | old
2020 | PGE | RFF | CZ03 | 1985 | 1.244 | old
2020 | PGE | RFF | CZ03 | 1996 | 0.803 | old
2020 | PGE | RFF | CZ03 | 2003 | 0.246 | ex
2020 | PGE | RFF | CZ03 | 2007 | 0.192 | ex
2020 | PGE | RFF | CZ03 | 2011 | 0.192 | ex
2020 | PGE | RFF | CZ03 | 2015 | 0.144 | ex
2020 | PGE | RFF | CZ03 | 2017 | 0.144 | rec
2020 | PGE | RFF | CZ03 | 2020 | 0.048 | rec
2020 | PGE | RFF | CZ03 | New | 0.048 | new
2020 | PGE | RFF | CZ04 | 1975 | 2.173 | old
2020 | PGE | RFF | CZ04 | 1985 | 0.596 | old
2020 | PGE | RFF | CZ04 | 1996 | 0.378 | old
2020 | PGE | RFF | CZ04 | 2003 | 0.131 | ex
2020 | PGE | RFF | CZ04 | 2007 | 0.077 | ex
2020 | PGE | RFF | CZ04 | 2011 | 0.077 | ex
2020 | PGE | RFF | CZ04 | 2015 | 0.058 | ex
2020 | PGE | RFF | CZ04 | 2017 | 0.058 | rec
2020 | PGE | RFF | CZ04 | 2020 | 0.019 | rec
2020 | PGE | RFF | CZ04 | New | 0.019 | new
2020 | PGE | RFF | CZ05 | 1975 | 0.427 | old
2020 | PGE | RFF | CZ05 | 1985 | 0.117 | old
2020 | PGE | RFF | CZ05 | 1996 | 0.074 | old
2020 | PGE | RFF | CZ05 | 2003 | 0.026 | ex
2020 | PGE | RFF | CZ05 | 2007 | 0.015 | ex
2020 | PGE | RFF | CZ05 | 2011 | 0.015 | ex
2020 | PGE | RFF | CZ05 | 2015 | 0.011 | ex
2020 | PGE | RFF | CZ05 | 2017 | 0.011 | rec
2020 | PGE | RFF | CZ05 | 2020 | 0.004 | rec
2020 | PGE | RFF | CZ05 | New | 0.004 | new
2020 | PGE | RFF | CZ11 | 1975 | 0.948 | old
2020 | PGE | RFF | CZ11 | 1985 | 0.254 | old
2020 | PGE | RFF | CZ11 | 1996 | 0.172 | old
2020 | PGE | RFF | CZ11 | 2003 | 0.072 | ex
2020 | PGE | RFF | CZ11 | 2007 | 0.039 | ex
2020 | PGE | RFF | CZ11 | 2011 | 0.039 | ex
2020 | PGE | RFF | CZ11 | 2015 | 0.03 | ex
2020 | PGE | RFF | CZ11 | 2017 | 0.03 | rec
2020 | PGE | RFF | CZ11 | 2020 | 0.01 | rec
2020 | PGE | RFF | CZ11 | New | 0.01 | new
2020 | PGE | RFF | CZ12 | 1975 | 3.261 | old
2020 | PGE | RFF | CZ12 | 1985 | 0.857 | old
2020 | PGE | RFF | CZ12 | 1996 | 0.599 | old
2020 | PGE | RFF | CZ12 | 2003 | 0.277 | ex
2020 | PGE | RFF | CZ12 | 2007 | 0.139 | ex
2020 | PGE | RFF | CZ12 | 2011 | 0.139 | ex
2020 | PGE | RFF | CZ12 | 2015 | 0.104 | ex
2020 | PGE | RFF | CZ12 | 2017 | 0.104 | rec
2020 | PGE | RFF | CZ12 | 2020 | 0.035 | rec
2020 | PGE | RFF | CZ12 | New | 0.035 | new
2020 | PGE | RFF | CZ13 | 1975 | 2.178 | old
2020 | PGE | RFF | CZ13 | 1985 | 0.692 | old
2020 | PGE | RFF | CZ13 | 1996 | 0.459 | old
2020 | PGE | RFF | CZ13 | 2003 | 0.171 | ex
2020 | PGE | RFF | CZ13 | 2007 | 0.096 | ex
2020 | PGE | RFF | CZ13 | 2011 | 0.096 | ex
2020 | PGE | RFF | CZ13 | 2015 | 0.072 | ex
2020 | PGE | RFF | CZ13 | 2017 | 0.072 | rec
2020 | PGE | RFF | CZ13 | 2020 | 0.024 | rec
2020 | PGE | RFF | CZ13 | New | 0.024 | new
2020 | PGE | RFF | CZ16 | 1975 | 0.208 | old
2020 | PGE | RFF | CZ16 | 1985 | 0.046 | old
2020 | PGE | RFF | CZ16 | 1996 | 0.03 | old
2020 | PGE | RFF | CZ16 | 2003 | 0.012 | ex
2020 | PGE | RFF | CZ16 | 2007 | 0.007 | ex
2020 | PGE | RFF | CZ16 | 2011 | 0.007 | ex
2020 | PGE | RFF | CZ16 | 2015 | 0.005 | ex
2020 | PGE | RFF | CZ16 | 2017 | 0.005 | rec
2020 | PGE | RFF | CZ16 | 2020 | 0.002 | rec
2020 | PGE | RFF | CZ16 | New | 0.002 | new
2020 | PGE | RSD | CZ01 | 1975 | 0.29 | old
2020 | PGE | RSD | CZ01 | 1985 | 0.042 | old
2020 | PGE | RSD | CZ01 | 1996 | 0.023 | old
2020 | PGE | RSD | CZ01 | 2003 | 0.007 | ex
2020 | PGE | RSD | CZ01 | 2007 | 0.007 | ex
2020 | PGE | RSD | CZ01 | 2011 | 0.007 | ex
2020 | PGE | RSD | CZ01 | 2015 | 0.005 | ex
2020 | PGE | RSD | CZ01 | 2017 | 0.005 | rec
2020 | PGE | RSD | CZ01 | 2020 | 0.002 | rec
2020 | PGE | RSD | CZ01 | New | 0.002 | new
2020 | PGE | RSD | CZ02 | 1975 | 1.122 | old
2020 | PGE | RSD | CZ02 | 1985 | 0.277 | old
2020 | PGE | RSD | CZ02 | 1996 | 0.175 | old
2020 | PGE | RSD | CZ02 | 2003 | 0.058 | ex
2020 | PGE | RSD | CZ02 | 2007 | 0.038 | ex
2020 | PGE | RSD | CZ02 | 2011 | 0.038 | ex
2020 | PGE | RSD | CZ02 | 2015 | 0.029 | ex
2020 | PGE | RSD | CZ02 | 2017 | 0.029 | rec
2020 | PGE | RSD | CZ02 | 2020 | 0.01 | rec
2020 | PGE | RSD | CZ02 | New | 0.01 | new
2020 | PGE | RSD | CZ03 | 1975 | 5.141 | old
2020 | PGE | RSD | CZ03 | 1985 | 1.244 | old
2020 | PGE | RSD | CZ03 | 1996 | 0.803 | old
2020 | PGE | RSD | CZ03 | 2003 | 0.246 | ex
2020 | PGE | RSD | CZ03 | 2007 | 0.192 | ex
2020 | PGE | RSD | CZ03 | 2011 | 0.192 | ex
2020 | PGE | RSD | CZ03 | 2015 | 0.144 | ex
2020 | PGE | RSD | CZ03 | 2017 | 0.144 | rec
2020 | PGE | RSD | CZ03 | 2020 | 0.048 | rec
2020 | PGE | RSD | CZ03 | New | 0.048 | new
2020 | PGE | RSD | CZ04 | 1975 | 2.173 | old
2020 | PGE | RSD | CZ04 | 1985 | 0.596 | old
2020 | PGE | RSD | CZ04 | 1996 | 0.378 | old
2020 | PGE | RSD | CZ04 | 2003 | 0.131 | ex
2020 | PGE | RSD | CZ04 | 2007 | 0.077 | ex
2020 | PGE | RSD | CZ04 | 2011 | 0.077 | ex
2020 | PGE | RSD | CZ04 | 2015 | 0.058 | ex
2020 | PGE | RSD | CZ04 | 2017 | 0.058 | rec
2020 | PGE | RSD | CZ04 | 2020 | 0.019 | rec
2020 | PGE | RSD | CZ04 | New | 0.019 | new
2020 | PGE | RSD | CZ05 | 1975 | 0.427 | old
2020 | PGE | RSD | CZ05 | 1985 | 0.117 | old
2020 | PGE | RSD | CZ05 | 1996 | 0.074 | old
2020 | PGE | RSD | CZ05 | 2003 | 0.026 | ex
2020 | PGE | RSD | CZ05 | 2007 | 0.015 | ex
2020 | PGE | RSD | CZ05 | 2011 | 0.015 | ex
2020 | PGE | RSD | CZ05 | 2015 | 0.011 | ex
2020 | PGE | RSD | CZ05 | 2017 | 0.011 | rec
2020 | PGE | RSD | CZ05 | 2020 | 0.004 | rec
2020 | PGE | RSD | CZ05 | New | 0.004 | new
2020 | PGE | RSD | CZ11 | 1975 | 0.948 | old
2020 | PGE | RSD | CZ11 | 1985 | 0.254 | old
2020 | PGE | RSD | CZ11 | 1996 | 0.172 | old
2020 | PGE | RSD | CZ11 | 2003 | 0.072 | ex
2020 | PGE | RSD | CZ11 | 2007 | 0.039 | ex
2020 | PGE | RSD | CZ11 | 2011 | 0.039 | ex
2020 | PGE | RSD | CZ11 | 2015 | 0.03 | ex
2020 | PGE | RSD | CZ11 | 2017 | 0.03 | rec
2020 | PGE | RSD | CZ11 | 2020 | 0.01 | rec
2020 | PGE | RSD | CZ11 | New | 0.01 | new
2020 | PGE | RSD | CZ12 | 1975 | 3.261 | old
2020 | PGE | RSD | CZ12 | 1985 | 0.857 | old
2020 | PGE | RSD | CZ12 | 1996 | 0.599 | old
2020 | PGE | RSD | CZ12 | 2003 | 0.277 | ex
2020 | PGE | RSD | CZ12 | 2007 | 0.139 | ex
2020 | PGE | RSD | CZ12 | 2011 | 0.139 | ex
2020 | PGE | RSD | CZ12 | 2015 | 0.104 | ex
2020 | PGE | RSD | CZ12 | 2017 | 0.104 | rec
2020 | PGE | RSD | CZ12 | 2020 | 0.035 | rec
2020 | PGE | RSD | CZ12 | New | 0.035 | new
2020 | PGE | RSD | CZ13 | 1975 | 2.178 | old
2020 | PGE | RSD | CZ13 | 1985 | 0.692 | old
2020 | PGE | RSD | CZ13 | 1996 | 0.459 | old
2020 | PGE | RSD | CZ13 | 2003 | 0.171 | ex
2020 | PGE | RSD | CZ13 | 2007 | 0.096 | ex
2020 | PGE | RSD | CZ13 | 2011 | 0.096 | ex
2020 | PGE | RSD | CZ13 | 2015 | 0.072 | ex
2020 | PGE | RSD | CZ13 | 2017 | 0.072 | rec
2020 | PGE | RSD | CZ13 | 2020 | 0.024 | rec
2020 | PGE | RSD | CZ13 | New | 0.024 | new
2020 | PGE | RSD | CZ16 | 1975 | 0.208 | old
2020 | PGE | RSD | CZ16 | 1985 | 0.046 | old
2020 | PGE | RSD | CZ16 | 1996 | 0.03 | old
2020 | PGE | RSD | CZ16 | 2003 | 0.012 | ex
2020 | PGE | RSD | CZ16 | 2007 | 0.007 | ex
2020 | PGE | RSD | CZ16 | 2011 | 0.007 | ex
2020 | PGE | RSD | CZ16 | 2015 | 0.005 | ex
2020 | PGE | RSD | CZ16 | 2017 | 0.005 | rec
2020 | PGE | RSD | CZ16 | 2020 | 0.002 | rec
2020 | PGE | RSD | CZ16 | New | 0.002 | new
2020 | PGE | Rt3 | CZ01 | 1975 | 0.591 | old
2020 | PGE | Rt3 | CZ01 | 1985 | 0.397 | old
2020 | PGE | Rt3 | CZ01 | 1996 | 0.148 | old
2020 | PGE | Rt3 | CZ01 | 2003 | 0.066 | ex
2020 | PGE | Rt3 | CZ01 | 2007 | 0.04 | ex
2020 | PGE | Rt3 | CZ01 | 2011 | 0.04 | ex
2020 | PGE | Rt3 | CZ01 | 2015 | 0.03 | ex
2020 | PGE | Rt3 | CZ01 | 2017 | 0.03 | rec
2020 | PGE | Rt3 | CZ01 | 2020 | 0.01 | rec
2020 | PGE | Rt3 | CZ01 | New | 0.01 | new
2020 | PGE | Rt3 | CZ02 | 1975 | 4.226 | old
2020 | PGE | Rt3 | CZ02 | 1985 | 2.089 | old
2020 | PGE | Rt3 | CZ02 | 1996 | 1.222 | old
2020 | PGE | Rt3 | CZ02 | 2003 | 0.5 | ex
2020 | PGE | Rt3 | CZ02 | 2007 | 0.285 | ex
2020 | PGE | Rt3 | CZ02 | 2011 | 0.285 | ex
2020 | PGE | Rt3 | CZ02 | 2015 | 0.214 | ex
2020 | PGE | Rt3 | CZ02 | 2017 | 0.214 | rec
2020 | PGE | Rt3 | CZ02 | 2020 | 0.071 | rec
2020 | PGE | Rt3 | CZ02 | New | 0.071 | new
2020 | PGE | Rt3 | CZ03 | 1975 | 22.644 | old
2020 | PGE | Rt3 | CZ03 | 1985 | 8.299 | old
2020 | PGE | Rt3 | CZ03 | 1996 | 4.758 | old
2020 | PGE | Rt3 | CZ03 | 2003 | 1.903 | ex
2020 | PGE | Rt3 | CZ03 | 2007 | 1.22 | ex
2020 | PGE | Rt3 | CZ03 | 2011 | 1.22 | ex
2020 | PGE | Rt3 | CZ03 | 2015 | 0.915 | ex
2020 | PGE | Rt3 | CZ03 | 2017 | 0.915 | rec
2020 | PGE | Rt3 | CZ03 | 2020 | 0.305 | rec
2020 | PGE | Rt3 | CZ03 | New | 0.305 | new
2020 | PGE | Rt3 | CZ04 | 1975 | 8.189 | old
2020 | PGE | Rt3 | CZ04 | 1985 | 4.354 | old
2020 | PGE | Rt3 | CZ04 | 1996 | 2.678 | old
2020 | PGE | Rt3 | CZ04 | 2003 | 1.094 | ex
2020 | PGE | Rt3 | CZ04 | 2007 | 0.601 | ex
2020 | PGE | Rt3 | CZ04 | 2011 | 0.601 | ex
2020 | PGE | Rt3 | CZ04 | 2015 | 0.451 | ex
2020 | PGE | Rt3 | CZ04 | 2017 | 0.451 | rec
2020 | PGE | Rt3 | CZ04 | 2020 | 0.15 | rec
2020 | PGE | Rt3 | CZ04 | New | 0.15 | new
2020 | PGE | Rt3 | CZ05 | 1975 | 1.4 | old
2020 | PGE | Rt3 | CZ05 | 1985 | 0.753 | old
2020 | PGE | Rt3 | CZ05 | 1996 | 0.464 | old
2020 | PGE | Rt3 | CZ05 | 2003 | 0.19 | ex
2020 | PGE | Rt3 | CZ05 | 2007 | 0.104 | ex
2020 | PGE | Rt3 | CZ05 | 2011 | 0.104 | ex
2020 | PGE | Rt3 | CZ05 | 2015 | 0.078 | ex
2020 | PGE | Rt3 | CZ05 | 2017 | 0.078 | rec
2020 | PGE | Rt3 | CZ05 | 2020 | 0.026 | rec
2020 | PGE | Rt3 | CZ05 | New | 0.026 | new
2020 | PGE | Rt3 | CZ11 | 1975 | 2.568 | old
2020 | PGE | Rt3 | CZ11 | 1985 | 2.058 | old
2020 | PGE | Rt3 | CZ11 | 1996 | 1.098 | old
2020 | PGE | Rt3 | CZ11 | 2003 | 0.58 | ex
2020 | PGE | Rt3 | CZ11 | 2007 | 0.325 | ex
2020 | PGE | Rt3 | CZ11 | 2011 | 0.325 | ex
2020 | PGE | Rt3 | CZ11 | 2015 | 0.244 | ex
2020 | PGE | Rt3 | CZ11 | 2017 | 0.244 | rec
2020 | PGE | Rt3 | CZ11 | 2020 | 0.081 | rec
2020 | PGE | Rt3 | CZ11 | New | 0.081 | new
2020 | PGE | Rt3 | CZ12 | 1975 | 11.684 | old
2020 | PGE | Rt3 | CZ12 | 1985 | 7.36 | old
2020 | PGE | Rt3 | CZ12 | 1996 | 5.008 | old
2020 | PGE | Rt3 | CZ12 | 2003 | 2.704 | ex
2020 | PGE | Rt3 | CZ12 | 2007 | 1.236 | ex
2020 | PGE | Rt3 | CZ12 | 2011 | 1.236 | ex
2020 | PGE | Rt3 | CZ12 | 2015 | 0.927 | ex
2020 | PGE | Rt3 | CZ12 | 2017 | 0.927 | rec
2020 | PGE | Rt3 | CZ12 | 2020 | 0.309 | rec
2020 | PGE | Rt3 | CZ12 | New | 0.309 | new
2020 | PGE | Rt3 | CZ13 | 1975 | 6.573 | old
2020 | PGE | Rt3 | CZ13 | 1985 | 5.425 | old
2020 | PGE | Rt3 | CZ13 | 1996 | 2.779 | old
2020 | PGE | Rt3 | CZ13 | 2003 | 1.358 | ex
2020 | PGE | Rt3 | CZ13 | 2007 | 0.852 | ex
2020 | PGE | Rt3 | CZ13 | 2011 | 0.852 | ex
2020 | PGE | Rt3 | CZ13 | 2015 | 0.639 | ex
2020 | PGE | Rt3 | CZ13 | 2017 | 0.639 | rec
2020 | PGE | Rt3 | CZ13 | 2020 | 0.213 | rec
2020 | PGE | Rt3 | CZ13 | New | 0.213 | new
2020 | PGE | Rt3 | CZ16 | 1975 | 0.164 | old
2020 | PGE | Rt3 | CZ16 | 1985 | 0.12 | old
2020 | PGE | Rt3 | CZ16 | 1996 | 0.054 | old
2020 | PGE | Rt3 | CZ16 | 2003 | 0.027 | ex
2020 | PGE | Rt3 | CZ16 | 2007 | 0.015 | ex
2020 | PGE | Rt3 | CZ16 | 2011 | 0.015 | ex
2020 | PGE | Rt3 | CZ16 | 2015 | 0.012 | ex
2020 | PGE | Rt3 | CZ16 | 2017 | 0.012 | rec
2020 | PGE | Rt3 | CZ16 | 2020 | 0.004 | rec
2020 | PGE | Rt3 | CZ16 | New | 0.004 | new
2020 | PGE | RtL | CZ01 | 1975 | 0.591 | old
2020 | PGE | RtL | CZ01 | 1985 | 0.397 | old
2020 | PGE | RtL | CZ01 | 1996 | 0.148 | old
2020 | PGE | RtL | CZ01 | 2003 | 0.066 | ex
2020 | PGE | RtL | CZ01 | 2007 | 0.04 | ex
2020 | PGE | RtL | CZ01 | 2011 | 0.04 | ex
2020 | PGE | RtL | CZ01 | 2015 | 0.03 | ex
2020 | PGE | RtL | CZ01 | 2017 | 0.03 | rec
2020 | PGE | RtL | CZ01 | 2020 | 0.01 | rec
2020 | PGE | RtL | CZ01 | New | 0.01 | new
2020 | PGE | RtL | CZ02 | 1975 | 4.226 | old
2020 | PGE | RtL | CZ02 | 1985 | 2.089 | old
2020 | PGE | RtL | CZ02 | 1996 | 1.222 | old
2020 | PGE | RtL | CZ02 | 2003 | 0.5 | ex
2020 | PGE | RtL | CZ02 | 2007 | 0.285 | ex
2020 | PGE | RtL | CZ02 | 2011 | 0.285 | ex
2020 | PGE | RtL | CZ02 | 2015 | 0.214 | ex
2020 | PGE | RtL | CZ02 | 2017 | 0.214 | rec
2020 | PGE | RtL | CZ02 | 2020 | 0.071 | rec
2020 | PGE | RtL | CZ02 | New | 0.071 | new
2020 | PGE | RtL | CZ03 | 1975 | 22.644 | old
2020 | PGE | RtL | CZ03 | 1985 | 8.299 | old
2020 | PGE | RtL | CZ03 | 1996 | 4.758 | old
2020 | PGE | RtL | CZ03 | 2003 | 1.903 | ex
2020 | PGE | RtL | CZ03 | 2007 | 1.22 | ex
2020 | PGE | RtL | CZ03 | 2011 | 1.22 | ex
2020 | PGE | RtL | CZ03 | 2015 | 0.915 | ex
2020 | PGE | RtL | CZ03 | 2017 | 0.915 | rec
2020 | PGE | RtL | CZ03 | 2020 | 0.305 | rec
2020 | PGE | RtL | CZ03 | New | 0.305 | new
2020 | PGE | RtL | CZ04 | 1975 | 8.189 | old
2020 | PGE | RtL | CZ04 | 1985 | 4.354 | old
2020 | PGE | RtL | CZ04 | 1996 | 2.678 | old
2020 | PGE | RtL | CZ04 | 2003 | 1.094 | ex
2020 | PGE | RtL | CZ04 | 2007 | 0.601 | ex
2020 | PGE | RtL | CZ04 | 2011 | 0.601 | ex
2020 | PGE | RtL | CZ04 | 2015 | 0.451 | ex
2020 | PGE | RtL | CZ04 | 2017 | 0.451 | rec
2020 | PGE | RtL | CZ04 | 2020 | 0.15 | rec
2020 | PGE | RtL | CZ04 | New | 0.15 | new
2020 | PGE | RtL | CZ05 | 1975 | 1.4 | old
2020 | PGE | RtL | CZ05 | 1985 | 0.753 | old
2020 | PGE | RtL | CZ05 | 1996 | 0.464 | old
2020 | PGE | RtL | CZ05 | 2003 | 0.19 | ex
2020 | PGE | RtL | CZ05 | 2007 | 0.104 | ex
2020 | PGE | RtL | CZ05 | 2011 | 0.104 | ex
2020 | PGE | RtL | CZ05 | 2015 | 0.078 | ex
2020 | PGE | RtL | CZ05 | 2017 | 0.078 | rec
2020 | PGE | RtL | CZ05 | 2020 | 0.026 | rec
2020 | PGE | RtL | CZ05 | New | 0.026 | new
2020 | PGE | RtL | CZ11 | 1975 | 2.568 | old
2020 | PGE | RtL | CZ11 | 1985 | 2.058 | old
2020 | PGE | RtL | CZ11 | 1996 | 1.098 | old
2020 | PGE | RtL | CZ11 | 2003 | 0.58 | ex
2020 | PGE | RtL | CZ11 | 2007 | 0.325 | ex
2020 | PGE | RtL | CZ11 | 2011 | 0.325 | ex
2020 | PGE | RtL | CZ11 | 2015 | 0.244 | ex
2020 | PGE | RtL | CZ11 | 2017 | 0.244 | rec
2020 | PGE | RtL | CZ11 | 2020 | 0.081 | rec
2020 | PGE | RtL | CZ11 | New | 0.081 | new
2020 | PGE | RtL | CZ12 | 1975 | 11.684 | old
2020 | PGE | RtL | CZ12 | 1985 | 7.36 | old
2020 | PGE | RtL | CZ12 | 1996 | 5.008 | old
2020 | PGE | RtL | CZ12 | 2003 | 2.704 | ex
2020 | PGE | RtL | CZ12 | 2007 | 1.236 | ex
2020 | PGE | RtL | CZ12 | 2011 | 1.236 | ex
2020 | PGE | RtL | CZ12 | 2015 | 0.927 | ex
2020 | PGE | RtL | CZ12 | 2017 | 0.927 | rec
2020 | PGE | RtL | CZ12 | 2020 | 0.309 | rec
2020 | PGE | RtL | CZ12 | New | 0.309 | new
2020 | PGE | RtL | CZ13 | 1975 | 6.573 | old
2020 | PGE | RtL | CZ13 | 1985 | 5.425 | old
2020 | PGE | RtL | CZ13 | 1996 | 2.779 | old
2020 | PGE | RtL | CZ13 | 2003 | 1.358 | ex
2020 | PGE | RtL | CZ13 | 2007 | 0.852 | ex
2020 | PGE | RtL | CZ13 | 2011 | 0.852 | ex
2020 | PGE | RtL | CZ13 | 2015 | 0.639 | ex
2020 | PGE | RtL | CZ13 | 2017 | 0.639 | rec
2020 | PGE | RtL | CZ13 | 2020 | 0.213 | rec
2020 | PGE | RtL | CZ13 | New | 0.213 | new
2020 | PGE | RtL | CZ16 | 1975 | 0.164 | old
2020 | PGE | RtL | CZ16 | 1985 | 0.12 | old
2020 | PGE | RtL | CZ16 | 1996 | 0.054 | old
2020 | PGE | RtL | CZ16 | 2003 | 0.027 | ex
2020 | PGE | RtL | CZ16 | 2007 | 0.015 | ex
2020 | PGE | RtL | CZ16 | 2011 | 0.015 | ex
2020 | PGE | RtL | CZ16 | 2015 | 0.012 | ex
2020 | PGE | RtL | CZ16 | 2017 | 0.012 | rec
2020 | PGE | RtL | CZ16 | 2020 | 0.004 | rec
2020 | PGE | RtL | CZ16 | New | 0.004 | new
2020 | PGE | RtS | CZ01 | 1975 | 0.591 | old
2020 | PGE | RtS | CZ01 | 1985 | 0.397 | old
2020 | PGE | RtS | CZ01 | 1996 | 0.148 | old
2020 | PGE | RtS | CZ01 | 2003 | 0.066 | ex
2020 | PGE | RtS | CZ01 | 2007 | 0.04 | ex
2020 | PGE | RtS | CZ01 | 2011 | 0.04 | ex
2020 | PGE | RtS | CZ01 | 2015 | 0.03 | ex
2020 | PGE | RtS | CZ01 | 2017 | 0.03 | rec
2020 | PGE | RtS | CZ01 | 2020 | 0.01 | rec
2020 | PGE | RtS | CZ01 | New | 0.01 | new
2020 | PGE | RtS | CZ02 | 1975 | 4.226 | old
2020 | PGE | RtS | CZ02 | 1985 | 2.089 | old
2020 | PGE | RtS | CZ02 | 1996 | 1.222 | old
2020 | PGE | RtS | CZ02 | 2003 | 0.5 | ex
2020 | PGE | RtS | CZ02 | 2007 | 0.285 | ex
2020 | PGE | RtS | CZ02 | 2011 | 0.285 | ex
2020 | PGE | RtS | CZ02 | 2015 | 0.214 | ex
2020 | PGE | RtS | CZ02 | 2017 | 0.214 | rec
2020 | PGE | RtS | CZ02 | 2020 | 0.071 | rec
2020 | PGE | RtS | CZ02 | New | 0.071 | new
2020 | PGE | RtS | CZ03 | 1975 | 22.644 | old
2020 | PGE | RtS | CZ03 | 1985 | 8.299 | old
2020 | PGE | RtS | CZ03 | 1996 | 4.758 | old
2020 | PGE | RtS | CZ03 | 2003 | 1.903 | ex
2020 | PGE | RtS | CZ03 | 2007 | 1.22 | ex
2020 | PGE | RtS | CZ03 | 2011 | 1.22 | ex
2020 | PGE | RtS | CZ03 | 2015 | 0.915 | ex
2020 | PGE | RtS | CZ03 | 2017 | 0.915 | rec
2020 | PGE | RtS | CZ03 | 2020 | 0.305 | rec
2020 | PGE | RtS | CZ03 | New | 0.305 | new
2020 | PGE | RtS | CZ04 | 1975 | 8.189 | old
2020 | PGE | RtS | CZ04 | 1985 | 4.354 | old
2020 | PGE | RtS | CZ04 | 1996 | 2.678 | old
2020 | PGE | RtS | CZ04 | 2003 | 1.094 | ex
2020 | PGE | RtS | CZ04 | 2007 | 0.601 | ex
2020 | PGE | RtS | CZ04 | 2011 | 0.601 | ex
2020 | PGE | RtS | CZ04 | 2015 | 0.451 | ex
2020 | PGE | RtS | CZ04 | 2017 | 0.451 | rec
2020 | PGE | RtS | CZ04 | 2020 | 0.15 | rec
2020 | PGE | RtS | CZ04 | New | 0.15 | new
2020 | PGE | RtS | CZ05 | 1975 | 1.4 | old
2020 | PGE | RtS | CZ05 | 1985 | 0.753 | old
2020 | PGE | RtS | CZ05 | 1996 | 0.464 | old
2020 | PGE | RtS | CZ05 | 2003 | 0.19 | ex
2020 | PGE | RtS | CZ05 | 2007 | 0.104 | ex
2020 | PGE | RtS | CZ05 | 2011 | 0.104 | ex
2020 | PGE | RtS | CZ05 | 2015 | 0.078 | ex
2020 | PGE | RtS | CZ05 | 2017 | 0.078 | rec
2020 | PGE | RtS | CZ05 | 2020 | 0.026 | rec
2020 | PGE | RtS | CZ05 | New | 0.026 | new
2020 | PGE | RtS | CZ11 | 1975 | 2.568 | old
2020 | PGE | RtS | CZ11 | 1985 | 2.058 | old
2020 | PGE | RtS | CZ11 | 1996 | 1.098 | old
2020 | PGE | RtS | CZ11 | 2003 | 0.58 | ex
2020 | PGE | RtS | CZ11 | 2007 | 0.325 | ex
2020 | PGE | RtS | CZ11 | 2011 | 0.325 | ex
2020 | PGE | RtS | CZ11 | 2015 | 0.244 | ex
2020 | PGE | RtS | CZ11 | 2017 | 0.244 | rec
2020 | PGE | RtS | CZ11 | 2020 | 0.081 | rec
2020 | PGE | RtS | CZ11 | New | 0.081 | new
2020 | PGE | RtS | CZ12 | 1975 | 11.684 | old
2020 | PGE | RtS | CZ12 | 1985 | 7.36 | old
2020 | PGE | RtS | CZ12 | 1996 | 5.008 | old
2020 | PGE | RtS | CZ12 | 2003 | 2.704 | ex
2020 | PGE | RtS | CZ12 | 2007 | 1.236 | ex
2020 | PGE | RtS | CZ12 | 2011 | 1.236 | ex
2020 | PGE | RtS | CZ12 | 2015 | 0.927 | ex
2020 | PGE | RtS | CZ12 | 2017 | 0.927 | rec
2020 | PGE | RtS | CZ12 | 2020 | 0.309 | rec
2020 | PGE | RtS | CZ12 | New | 0.309 | new
2020 | PGE | RtS | CZ13 | 1975 | 6.573 | old
2020 | PGE | RtS | CZ13 | 1985 | 5.425 | old
2020 | PGE | RtS | CZ13 | 1996 | 2.779 | old
2020 | PGE | RtS | CZ13 | 2003 | 1.358 | ex
2020 | PGE | RtS | CZ13 | 2007 | 0.852 | ex
2020 | PGE | RtS | CZ13 | 2011 | 0.852 | ex
2020 | PGE | RtS | CZ13 | 2015 | 0.639 | ex
2020 | PGE | RtS | CZ13 | 2017 | 0.639 | rec
2020 | PGE | RtS | CZ13 | 2020 | 0.213 | rec
2020 | PGE | RtS | CZ13 | New | 0.213 | new
2020 | PGE | RtS | CZ16 | 1975 | 0.164 | old
2020 | PGE | RtS | CZ16 | 1985 | 0.12 | old
2020 | PGE | RtS | CZ16 | 1996 | 0.054 | old
2020 | PGE | RtS | CZ16 | 2003 | 0.027 | ex
2020 | PGE | RtS | CZ16 | 2007 | 0.015 | ex
2020 | PGE | RtS | CZ16 | 2011 | 0.015 | ex
2020 | PGE | RtS | CZ16 | 2015 | 0.012 | ex
2020 | PGE | RtS | CZ16 | 2017 | 0.012 | rec
2020 | PGE | RtS | CZ16 | 2020 | 0.004 | rec
2020 | PGE | RtS | CZ16 | New | 0.004 | new
2020 | PGE | SCn | CZ01 | 1975 | 0.392 | old
2020 | PGE | SCn | CZ01 | 1985 | 0.363 | old
2020 | PGE | SCn | CZ01 | 1996 | 0.256 | old
2020 | PGE | SCn | CZ01 | 2003 | 0.211 | ex
2020 | PGE | SCn | CZ01 | 2007 | 0.06 | ex
2020 | PGE | SCn | CZ01 | 2011 | 0.06 | ex
2020 | PGE | SCn | CZ01 | 2015 | 0.045 | ex
2020 | PGE | SCn | CZ01 | 2017 | 0.045 | rec
2020 | PGE | SCn | CZ01 | 2020 | 0.015 | rec
2020 | PGE | SCn | CZ01 | New | 0.015 | new
2020 | PGE | SCn | CZ02 | 1975 | 2.685 | old
2020 | PGE | SCn | CZ02 | 1985 | 4.274 | old
2020 | PGE | SCn | CZ02 | 1996 | 1.793 | old
2020 | PGE | SCn | CZ02 | 2003 | 0.81 | ex
2020 | PGE | SCn | CZ02 | 2007 | 0.355 | ex
2020 | PGE | SCn | CZ02 | 2011 | 0.355 | ex
2020 | PGE | SCn | CZ02 | 2015 | 0.266 | ex
2020 | PGE | SCn | CZ02 | 2017 | 0.266 | rec
2020 | PGE | SCn | CZ02 | 2020 | 0.089 | rec
2020 | PGE | SCn | CZ02 | New | 0.089 | new
2020 | PGE | SCn | CZ03 | 1975 | 23.411 | old
2020 | PGE | SCn | CZ03 | 1985 | 19.498 | old
2020 | PGE | SCn | CZ03 | 1996 | 6.232 | old
2020 | PGE | SCn | CZ03 | 2003 | 1.803 | ex
2020 | PGE | SCn | CZ03 | 2007 | 1.868 | ex
2020 | PGE | SCn | CZ03 | 2011 | 1.868 | ex
2020 | PGE | SCn | CZ03 | 2015 | 1.401 | ex
2020 | PGE | SCn | CZ03 | 2017 | 1.401 | rec
2020 | PGE | SCn | CZ03 | 2020 | 0.467 | rec
2020 | PGE | SCn | CZ03 | New | 0.467 | new
2020 | PGE | SCn | CZ04 | 1975 | 4.828 | old
2020 | PGE | SCn | CZ04 | 1985 | 8.688 | old
2020 | PGE | SCn | CZ04 | 1996 | 3.619 | old
2020 | PGE | SCn | CZ04 | 2003 | 1.577 | ex
2020 | PGE | SCn | CZ04 | 2007 | 0.68 | ex
2020 | PGE | SCn | CZ04 | 2011 | 0.68 | ex
2020 | PGE | SCn | CZ04 | 2015 | 0.51 | ex
2020 | PGE | SCn | CZ04 | 2017 | 0.51 | rec
2020 | PGE | SCn | CZ04 | 2020 | 0.17 | rec
2020 | PGE | SCn | CZ04 | New | 0.17 | new
2020 | PGE | SCn | CZ05 | 1975 | 0.359 | old
2020 | PGE | SCn | CZ05 | 1985 | 0.663 | old
2020 | PGE | SCn | CZ05 | 1996 | 0.278 | old
2020 | PGE | SCn | CZ05 | 2003 | 0.122 | ex
2020 | PGE | SCn | CZ05 | 2007 | 0.052 | ex
2020 | PGE | SCn | CZ05 | 2011 | 0.052 | ex
2020 | PGE | SCn | CZ05 | 2015 | 0.039 | ex
2020 | PGE | SCn | CZ05 | 2017 | 0.039 | rec
2020 | PGE | SCn | CZ05 | 2020 | 0.013 | rec
2020 | PGE | SCn | CZ05 | New | 0.013 | new
2020 | PGE | SCn | CZ11 | 1975 | 1.678 | old
2020 | PGE | SCn | CZ11 | 1985 | 2.957 | old
2020 | PGE | SCn | CZ11 | 1996 | 2.16 | old
2020 | PGE | SCn | CZ11 | 2003 | 1.529 | ex
2020 | PGE | SCn | CZ11 | 2007 | 0.684 | ex
2020 | PGE | SCn | CZ11 | 2011 | 0.684 | ex
2020 | PGE | SCn | CZ11 | 2015 | 0.513 | ex
2020 | PGE | SCn | CZ11 | 2017 | 0.513 | rec
2020 | PGE | SCn | CZ11 | 2020 | 0.171 | rec
2020 | PGE | SCn | CZ11 | New | 0.171 | new
2020 | PGE | SCn | CZ12 | 1975 | 5.924 | old
2020 | PGE | SCn | CZ12 | 1985 | 13.121 | old
2020 | PGE | SCn | CZ12 | 1996 | 9.539 | old
2020 | PGE | SCn | CZ12 | 2003 | 5.1 | ex
2020 | PGE | SCn | CZ12 | 2007 | 2.587 | ex
2020 | PGE | SCn | CZ12 | 2011 | 2.587 | ex
2020 | PGE | SCn | CZ12 | 2015 | 1.941 | ex
2020 | PGE | SCn | CZ12 | 2017 | 1.941 | rec
2020 | PGE | SCn | CZ12 | 2020 | 0.647 | rec
2020 | PGE | SCn | CZ12 | New | 0.647 | new
2020 | PGE | SCn | CZ13 | 1975 | 4.749 | old
2020 | PGE | SCn | CZ13 | 1985 | 7.675 | old
2020 | PGE | SCn | CZ13 | 1996 | 4.851 | old
2020 | PGE | SCn | CZ13 | 2003 | 3.782 | ex
2020 | PGE | SCn | CZ13 | 2007 | 1.585 | ex
2020 | PGE | SCn | CZ13 | 2011 | 1.585 | ex
2020 | PGE | SCn | CZ13 | 2015 | 1.189 | ex
2020 | PGE | SCn | CZ13 | 2017 | 1.189 | rec
2020 | PGE | SCn | CZ13 | 2020 | 0.396 | rec
2020 | PGE | SCn | CZ13 | New | 0.396 | new
2020 | PGE | SCn | CZ16 | 1975 | 0.249 | old
2020 | PGE | SCn | CZ16 | 1985 | 0.382 | old
2020 | PGE | SCn | CZ16 | 1996 | 0.245 | old
2020 | PGE | SCn | CZ16 | 2003 | 0.191 | ex
2020 | PGE | SCn | CZ16 | 2007 | 0.078 | ex
2020 | PGE | SCn | CZ16 | 2011 | 0.078 | ex
2020 | PGE | SCn | CZ16 | 2015 | 0.059 | ex
2020 | PGE | SCn | CZ16 | 2017 | 0.059 | rec
2020 | PGE | SCn | CZ16 | 2020 | 0.02 | rec
2020 | PGE | SCn | CZ16 | New | 0.02 | new
2020 | PGE | SUn | CZ01 | 1975 | 0.392 | old
2020 | PGE | SUn | CZ01 | 1985 | 0.363 | old
2020 | PGE | SUn | CZ01 | 1996 | 0.256 | old
2020 | PGE | SUn | CZ01 | 2003 | 0.211 | ex
2020 | PGE | SUn | CZ01 | 2007 | 0.06 | ex
2020 | PGE | SUn | CZ01 | 2011 | 0.06 | ex
2020 | PGE | SUn | CZ01 | 2015 | 0.045 | ex
2020 | PGE | SUn | CZ01 | 2017 | 0.045 | rec
2020 | PGE | SUn | CZ01 | 2020 | 0.015 | rec
2020 | PGE | SUn | CZ01 | New | 0.015 | new
2020 | PGE | SUn | CZ02 | 1975 | 2.685 | old
2020 | PGE | SUn | CZ02 | 1985 | 4.274 | old
2020 | PGE | SUn | CZ02 | 1996 | 1.793 | old
2020 | PGE | SUn | CZ02 | 2003 | 0.81 | ex
2020 | PGE | SUn | CZ02 | 2007 | 0.355 | ex
2020 | PGE | SUn | CZ02 | 2011 | 0.355 | ex
2020 | PGE | SUn | CZ02 | 2015 | 0.266 | ex
2020 | PGE | SUn | CZ02 | 2017 | 0.266 | rec
2020 | PGE | SUn | CZ02 | 2020 | 0.089 | rec
2020 | PGE | SUn | CZ02 | New | 0.089 | new
2020 | PGE | SUn | CZ03 | 1975 | 23.411 | old
2020 | PGE | SUn | CZ03 | 1985 | 19.498 | old
2020 | PGE | SUn | CZ03 | 1996 | 6.232 | old
2020 | PGE | SUn | CZ03 | 2003 | 1.803 | ex
2020 | PGE | SUn | CZ03 | 2007 | 1.868 | ex
2020 | PGE | SUn | CZ03 | 2011 | 1.868 | ex
2020 | PGE | SUn | CZ03 | 2015 | 1.401 | ex
2020 | PGE | SUn | CZ03 | 2017 | 1.401 | rec
2020 | PGE | SUn | CZ03 | 2020 | 0.467 | rec
2020 | PGE | SUn | CZ03 | New | 0.467 | new
2020 | PGE | SUn | CZ04 | 1975 | 4.828 | old
2020 | PGE | SUn | CZ04 | 1985 | 8.688 | old
2020 | PGE | SUn | CZ04 | 1996 | 3.619 | old
2020 | PGE | SUn | CZ04 | 2003 | 1.577 | ex
2020 | PGE | SUn | CZ04 | 2007 | 0.68 | ex
2020 | PGE | SUn | CZ04 | 2011 | 0.68 | ex
2020 | PGE | SUn | CZ04 | 2015 | 0.51 | ex
2020 | PGE | SUn | CZ04 | 2017 | 0.51 | rec
2020 | PGE | SUn | CZ04 | 2020 | 0.17 | rec
2020 | PGE | SUn | CZ04 | New | 0.17 | new
2020 | PGE | SUn | CZ05 | 1975 | 0.359 | old
2020 | PGE | SUn | CZ05 | 1985 | 0.663 | old
2020 | PGE | SUn | CZ05 | 1996 | 0.278 | old
2020 | PGE | SUn | CZ05 | 2003 | 0.122 | ex
2020 | PGE | SUn | CZ05 | 2007 | 0.052 | ex
2020 | PGE | SUn | CZ05 | 2011 | 0.052 | ex
2020 | PGE | SUn | CZ05 | 2015 | 0.039 | ex
2020 | PGE | SUn | CZ05 | 2017 | 0.039 | rec
2020 | PGE | SUn | CZ05 | 2020 | 0.013 | rec
2020 | PGE | SUn | CZ05 | New | 0.013 | new
2020 | PGE | SUn | CZ11 | 1975 | 1.678 | old
2020 | PGE | SUn | CZ11 | 1985 | 2.957 | old
2020 | PGE | SUn | CZ11 | 1996 | 2.16 | old
2020 | PGE | SUn | CZ11 | 2003 | 1.529 | ex
2020 | PGE | SUn | CZ11 | 2007 | 0.684 | ex
2020 | PGE | SUn | CZ11 | 2011 | 0.684 | ex
2020 | PGE | SUn | CZ11 | 2015 | 0.513 | ex
2020 | PGE | SUn | CZ11 | 2017 | 0.513 | rec
2020 | PGE | SUn | CZ11 | 2020 | 0.171 | rec
2020 | PGE | SUn | CZ11 | New | 0.171 | new
2020 | PGE | SUn | CZ12 | 1975 | 5.924 | old
2020 | PGE | SUn | CZ12 | 1985 | 13.121 | old
2020 | PGE | SUn | CZ12 | 1996 | 9.539 | old
2020 | PGE | SUn | CZ12 | 2003 | 5.1 | ex
2020 | PGE | SUn | CZ12 | 2007 | 2.587 | ex
2020 | PGE | SUn | CZ12 | 2011 | 2.587 | ex
2020 | PGE | SUn | CZ12 | 2015 | 1.941 | ex
2020 | PGE | SUn | CZ12 | 2017 | 1.941 | rec
2020 | PGE | SUn | CZ12 | 2020 | 0.647 | rec
2020 | PGE | SUn | CZ12 | New | 0.647 | new
2020 | PGE | SUn | CZ13 | 1975 | 4.749 | old
2020 | PGE | SUn | CZ13 | 1985 | 7.675 | old
2020 | PGE | SUn | CZ13 | 1996 | 4.851 | old
2020 | PGE | SUn | CZ13 | 2003 | 3.782 | ex
2020 | PGE | SUn | CZ13 | 2007 | 1.585 | ex
2020 | PGE | SUn | CZ13 | 2011 | 1.585 | ex
2020 | PGE | SUn | CZ13 | 2015 | 1.189 | ex
2020 | PGE | SUn | CZ13 | 2017 | 1.189 | rec
2020 | PGE | SUn | CZ13 | 2020 | 0.396 | rec
2020 | PGE | SUn | CZ13 | New | 0.396 | new
2020 | PGE | SUn | CZ16 | 1975 | 0.249 | old
2020 | PGE | SUn | CZ16 | 1985 | 0.382 | old
2020 | PGE | SUn | CZ16 | 1996 | 0.245 | old
2020 | PGE | SUn | CZ16 | 2003 | 0.191 | ex
2020 | PGE | SUn | CZ16 | 2007 | 0.078 | ex
2020 | PGE | SUn | CZ16 | 2011 | 0.078 | ex
2020 | PGE | SUn | CZ16 | 2015 | 0.059 | ex
2020 | PGE | SUn | CZ16 | 2017 | 0.059 | rec
2020 | PGE | SUn | CZ16 | 2020 | 0.02 | rec
2020 | PGE | SUn | CZ16 | New | 0.02 | new
2020 | PGE | WRf | CZ01 | 1975 | 0.038 | old
2020 | PGE | WRf | CZ01 | 1985 | 0.04 | old
2020 | PGE | WRf | CZ01 | 1996 | 0.026 | old
2020 | PGE | WRf | CZ01 | 2003 | 0.027 | ex
2020 | PGE | WRf | CZ01 | 2007 | 0.006 | ex
2020 | PGE | WRf | CZ01 | 2011 | 0.006 | ex
2020 | PGE | WRf | CZ01 | 2015 | 0.005 | ex
2020 | PGE | WRf | CZ01 | 2017 | 0.005 | rec
2020 | PGE | WRf | CZ01 | 2020 | 0.002 | rec
2020 | PGE | WRf | CZ01 | New | 0.002 | new
2020 | PGE | WRf | CZ02 | 1975 | 0.248 | old
2020 | PGE | WRf | CZ02 | 1985 | 0.332 | old
2020 | PGE | WRf | CZ02 | 1996 | 0.181 | old
2020 | PGE | WRf | CZ02 | 2003 | 0.074 | ex
2020 | PGE | WRf | CZ02 | 2007 | 0.034 | ex
2020 | PGE | WRf | CZ02 | 2011 | 0.034 | ex
2020 | PGE | WRf | CZ02 | 2015 | 0.026 | ex
2020 | PGE | WRf | CZ02 | 2017 | 0.026 | rec
2020 | PGE | WRf | CZ02 | 2020 | 0.009 | rec
2020 | PGE | WRf | CZ02 | New | 0.009 | new
2020 | PGE | WRf | CZ03 | 1975 | 3.719 | old
2020 | PGE | WRf | CZ03 | 1985 | 3.504 | old
2020 | PGE | WRf | CZ03 | 1996 | 1.615 | old
2020 | PGE | WRf | CZ03 | 2003 | 0.388 | ex
2020 | PGE | WRf | CZ03 | 2007 | 0.368 | ex
2020 | PGE | WRf | CZ03 | 2011 | 0.368 | ex
2020 | PGE | WRf | CZ03 | 2015 | 0.276 | ex
2020 | PGE | WRf | CZ03 | 2017 | 0.276 | rec
2020 | PGE | WRf | CZ03 | 2020 | 0.092 | rec
2020 | PGE | WRf | CZ03 | New | 0.092 | new
2020 | PGE | WRf | CZ04 | 1975 | 0.482 | old
2020 | PGE | WRf | CZ04 | 1985 | 0.726 | old
2020 | PGE | WRf | CZ04 | 1996 | 0.395 | old
2020 | PGE | WRf | CZ04 | 2003 | 0.122 | ex
2020 | PGE | WRf | CZ04 | 2007 | 0.067 | ex
2020 | PGE | WRf | CZ04 | 2011 | 0.067 | ex
2020 | PGE | WRf | CZ04 | 2015 | 0.05 | ex
2020 | PGE | WRf | CZ04 | 2017 | 0.05 | rec
2020 | PGE | WRf | CZ04 | 2020 | 0.017 | rec
2020 | PGE | WRf | CZ04 | New | 0.017 | new
2020 | PGE | WRf | CZ05 | 1975 | 0.283 | old
2020 | PGE | WRf | CZ05 | 1985 | 0.427 | old
2020 | PGE | WRf | CZ05 | 1996 | 0.232 | old
2020 | PGE | WRf | CZ05 | 2003 | 0.072 | ex
2020 | PGE | WRf | CZ05 | 2007 | 0.039 | ex
2020 | PGE | WRf | CZ05 | 2011 | 0.039 | ex
2020 | PGE | WRf | CZ05 | 2015 | 0.03 | ex
2020 | PGE | WRf | CZ05 | 2017 | 0.03 | rec
2020 | PGE | WRf | CZ05 | 2020 | 0.01 | rec
2020 | PGE | WRf | CZ05 | New | 0.01 | new
2020 | PGE | WRf | CZ11 | 1975 | 0.242 | old
2020 | PGE | WRf | CZ11 | 1985 | 0.396 | old
2020 | PGE | WRf | CZ11 | 1996 | 0.362 | old
2020 | PGE | WRf | CZ11 | 2003 | 0.136 | ex
2020 | PGE | WRf | CZ11 | 2007 | 0.091 | ex
2020 | PGE | WRf | CZ11 | 2011 | 0.091 | ex
2020 | PGE | WRf | CZ11 | 2015 | 0.068 | ex
2020 | PGE | WRf | CZ11 | 2017 | 0.068 | rec
2020 | PGE | WRf | CZ11 | 2020 | 0.023 | rec
2020 | PGE | WRf | CZ11 | New | 0.023 | new
2020 | PGE | WRf | CZ12 | 1975 | 0.797 | old
2020 | PGE | WRf | CZ12 | 1985 | 1.66 | old
2020 | PGE | WRf | CZ12 | 1996 | 2.072 | old
2020 | PGE | WRf | CZ12 | 2003 | 0.513 | ex
2020 | PGE | WRf | CZ12 | 2007 | 0.528 | ex
2020 | PGE | WRf | CZ12 | 2011 | 0.528 | ex
2020 | PGE | WRf | CZ12 | 2015 | 0.396 | ex
2020 | PGE | WRf | CZ12 | 2017 | 0.396 | rec
2020 | PGE | WRf | CZ12 | 2020 | 0.132 | rec
2020 | PGE | WRf | CZ12 | New | 0.132 | new
2020 | PGE | WRf | CZ13 | 1975 | 1.756 | old
2020 | PGE | WRf | CZ13 | 1985 | 2.729 | old
2020 | PGE | WRf | CZ13 | 1996 | 2.232 | old
2020 | PGE | WRf | CZ13 | 2003 | 0.927 | ex
2020 | PGE | WRf | CZ13 | 2007 | 0.553 | ex
2020 | PGE | WRf | CZ13 | 2011 | 0.553 | ex
2020 | PGE | WRf | CZ13 | 2015 | 0.415 | ex
2020 | PGE | WRf | CZ13 | 2017 | 0.415 | rec
2020 | PGE | WRf | CZ13 | 2020 | 0.138 | rec
2020 | PGE | WRf | CZ13 | New | 0.138 | new
2020 | PGE | WRf | CZ16 | 1975 | 0.002 | old
2020 | PGE | WRf | CZ16 | 1985 | 0.004 | old
2020 | PGE | WRf | CZ16 | 1996 | 0.003 | old
2020 | PGE | WRf | CZ16 | 2003 | 0.001 | ex
2020 | PGE | WRf | CZ16 | 2007 | 0.001 | ex
2020 | PGE | WRf | CZ16 | 2011 | 0.001 | ex
2020 | PGE | WRf | CZ16 | 2015 | 0.001 | ex
2020 | PGE | WRf | CZ16 | 2017 | 0.001 | rec
2020 | PGE | WRf | CZ16 | 2020 | 0.001 | rec
2020 | PGE | WRf | CZ16 | New | 0.001 | new
2020 | SCE | Asm | CZ05 | 1975 | 0.216 | old
2020 | SCE | Asm | CZ05 | 1985 | 0.115 | old
2020 | SCE | Asm | CZ05 | 1996 | 0.056 | old
2020 | SCE | Asm | CZ05 | 2003 | 0.028 | ex
2020 | SCE | Asm | CZ05 | 2007 | 0.018 | ex
2020 | SCE | Asm | CZ05 | 2011 | 0.018 | ex
2020 | SCE | Asm | CZ05 | 2015 | 0.013 | ex
2020 | SCE | Asm | CZ05 | 2017 | 0.013 | rec
2020 | SCE | Asm | CZ05 | 2020 | 0.004 | rec
2020 | SCE | Asm | CZ05 | New | 0.004 | new
2020 | SCE | Asm | CZ06 | 1975 | 18.175 | old
2020 | SCE | Asm | CZ06 | 1985 | 9.64 | old
2020 | SCE | Asm | CZ06 | 1996 | 4.695 | old
2020 | SCE | Asm | CZ06 | 2003 | 2.331 | ex
2020 | SCE | Asm | CZ06 | 2007 | 1.467 | ex
2020 | SCE | Asm | CZ06 | 2011 | 1.467 | ex
2020 | SCE | Asm | CZ06 | 2015 | 1.1 | ex
2020 | SCE | Asm | CZ06 | 2017 | 1.1 | rec
2020 | SCE | Asm | CZ06 | 2020 | 0.367 | rec
2020 | SCE | Asm | CZ06 | New | 0.367 | new
2020 | SCE | Asm | CZ08 | 1975 | 26.542 | old
2020 | SCE | Asm | CZ08 | 1985 | 14.036 | old
2020 | SCE | Asm | CZ08 | 1996 | 6.866 | old
2020 | SCE | Asm | CZ08 | 2003 | 3.418 | ex
2020 | SCE | Asm | CZ08 | 2007 | 2.135 | ex
2020 | SCE | Asm | CZ08 | 2011 | 2.135 | ex
2020 | SCE | Asm | CZ08 | 2015 | 1.601 | ex
2020 | SCE | Asm | CZ08 | 2017 | 1.601 | rec
2020 | SCE | Asm | CZ08 | 2020 | 0.534 | rec
2020 | SCE | Asm | CZ08 | New | 0.534 | new
2020 | SCE | Asm | CZ09 | 1975 | 12.478 | old
2020 | SCE | Asm | CZ09 | 1985 | 6.397 | old
2020 | SCE | Asm | CZ09 | 1996 | 3.274 | old
2020 | SCE | Asm | CZ09 | 2003 | 1.677 | ex
2020 | SCE | Asm | CZ09 | 2007 | 0.966 | ex
2020 | SCE | Asm | CZ09 | 2011 | 0.966 | ex
2020 | SCE | Asm | CZ09 | 2015 | 0.725 | ex
2020 | SCE | Asm | CZ09 | 2017 | 0.725 | rec
2020 | SCE | Asm | CZ09 | 2020 | 0.242 | rec
2020 | SCE | Asm | CZ09 | New | 0.242 | new
2020 | SCE | Asm | CZ10 | 1975 | 3.994 | old
2020 | SCE | Asm | CZ10 | 1985 | 9.306 | old
2020 | SCE | Asm | CZ10 | 1996 | 5.666 | old
2020 | SCE | Asm | CZ10 | 2003 | 5.288 | ex
2020 | SCE | Asm | CZ10 | 2007 | 2.938 | ex
2020 | SCE | Asm | CZ10 | 2011 | 2.938 | ex
2020 | SCE | Asm | CZ10 | 2015 | 2.204 | ex
2020 | SCE | Asm | CZ10 | 2017 | 2.204 | rec
2020 | SCE | Asm | CZ10 | 2020 | 0.735 | rec
2020 | SCE | Asm | CZ10 | New | 0.735 | new
2020 | SCE | Asm | CZ13 | 1975 | 0.899 | old
2020 | SCE | Asm | CZ13 | 1985 | 1.085 | old
2020 | SCE | Asm | CZ13 | 1996 | 0.903 | old
2020 | SCE | Asm | CZ13 | 2003 | 0.349 | ex
2020 | SCE | Asm | CZ13 | 2007 | 0.223 | ex
2020 | SCE | Asm | CZ13 | 2011 | 0.223 | ex
2020 | SCE | Asm | CZ13 | 2015 | 0.167 | ex
2020 | SCE | Asm | CZ13 | 2017 | 0.167 | rec
2020 | SCE | Asm | CZ13 | 2020 | 0.056 | rec
2020 | SCE | Asm | CZ13 | New | 0.056 | new
2020 | SCE | Asm | CZ14 | 1975 | 1.878 | old
2020 | SCE | Asm | CZ14 | 1985 | 1.916 | old
2020 | SCE | Asm | CZ14 | 1996 | 1.152 | old
2020 | SCE | Asm | CZ14 | 2003 | 0.877 | ex
2020 | SCE | Asm | CZ14 | 2007 | 0.486 | ex
2020 | SCE | Asm | CZ14 | 2011 | 0.486 | ex
2020 | SCE | Asm | CZ14 | 2015 | 0.364 | ex
2020 | SCE | Asm | CZ14 | 2017 | 0.364 | rec
2020 | SCE | Asm | CZ14 | 2020 | 0.122 | rec
2020 | SCE | Asm | CZ14 | New | 0.122 | new
2020 | SCE | Asm | CZ15 | 1975 | 1.446 | old
2020 | SCE | Asm | CZ15 | 1985 | 3.369 | old
2020 | SCE | Asm | CZ15 | 1996 | 2.051 | old
2020 | SCE | Asm | CZ15 | 2003 | 1.914 | ex
2020 | SCE | Asm | CZ15 | 2007 | 1.064 | ex
2020 | SCE | Asm | CZ15 | 2011 | 1.064 | ex
2020 | SCE | Asm | CZ15 | 2015 | 0.798 | ex
2020 | SCE | Asm | CZ15 | 2017 | 0.798 | rec
2020 | SCE | Asm | CZ15 | 2020 | 0.266 | rec
2020 | SCE | Asm | CZ15 | New | 0.266 | new
2020 | SCE | Asm | CZ16 | 1975 | 0.888 | old
2020 | SCE | Asm | CZ16 | 1985 | 1.175 | old
2020 | SCE | Asm | CZ16 | 1996 | 0.786 | old
2020 | SCE | Asm | CZ16 | 2003 | 0.535 | ex
2020 | SCE | Asm | CZ16 | 2007 | 0.306 | ex
2020 | SCE | Asm | CZ16 | 2011 | 0.306 | ex
2020 | SCE | Asm | CZ16 | 2015 | 0.23 | ex
2020 | SCE | Asm | CZ16 | 2017 | 0.23 | rec
2020 | SCE | Asm | CZ16 | 2020 | 0.077 | rec
2020 | SCE | Asm | CZ16 | New | 0.077 | new
2020 | SCE | ECC | CZ05 | 1975 | 0.009 | old
2020 | SCE | ECC | CZ05 | 1985 | 0.003 | old
2020 | SCE | ECC | CZ05 | 1996 | 0.002 | old
2020 | SCE | ECC | CZ05 | 2003 | 0.001 | ex
2020 | SCE | ECC | CZ05 | 2007 | 0.001 | ex
2020 | SCE | ECC | CZ05 | 2011 | 0.001 | ex
2020 | SCE | ECC | CZ05 | 2015 | 0.001 | ex
2020 | SCE | ECC | CZ05 | 2017 | 0.001 | rec
2020 | SCE | ECC | CZ05 | 2020 | 0.001 | rec
2020 | SCE | ECC | CZ05 | New | 0.001 | new
2020 | SCE | ECC | CZ06 | 1975 | 7.226 | old
2020 | SCE | ECC | CZ06 | 1985 | 2.474 | old
2020 | SCE | ECC | CZ06 | 1996 | 1.675 | old
2020 | SCE | ECC | CZ06 | 2003 | 0.979 | ex
2020 | SCE | ECC | CZ06 | 2007 | 0.435 | ex
2020 | SCE | ECC | CZ06 | 2011 | 0.435 | ex
2020 | SCE | ECC | CZ06 | 2015 | 0.326 | ex
2020 | SCE | ECC | CZ06 | 2017 | 0.326 | rec
2020 | SCE | ECC | CZ06 | 2020 | 0.109 | rec
2020 | SCE | ECC | CZ06 | New | 0.109 | new
2020 | SCE | ECC | CZ08 | 1975 | 11.773 | old
2020 | SCE | ECC | CZ08 | 1985 | 4.021 | old
2020 | SCE | ECC | CZ08 | 1996 | 2.653 | old
2020 | SCE | ECC | CZ08 | 2003 | 1.543 | ex
2020 | SCE | ECC | CZ08 | 2007 | 0.689 | ex
2020 | SCE | ECC | CZ08 | 2011 | 0.689 | ex
2020 | SCE | ECC | CZ08 | 2015 | 0.517 | ex
2020 | SCE | ECC | CZ08 | 2017 | 0.517 | rec
2020 | SCE | ECC | CZ08 | 2020 | 0.172 | rec
2020 | SCE | ECC | CZ08 | New | 0.172 | new
2020 | SCE | ECC | CZ09 | 1975 | 2.427 | old
2020 | SCE | ECC | CZ09 | 1985 | 0.848 | old
2020 | SCE | ECC | CZ09 | 1996 | 0.684 | old
2020 | SCE | ECC | CZ09 | 2003 | 0.411 | ex
2020 | SCE | ECC | CZ09 | 2007 | 0.176 | ex
2020 | SCE | ECC | CZ09 | 2011 | 0.176 | ex
2020 | SCE | ECC | CZ09 | 2015 | 0.132 | ex
2020 | SCE | ECC | CZ09 | 2017 | 0.132 | rec
2020 | SCE | ECC | CZ09 | 2020 | 0.044 | rec
2020 | SCE | ECC | CZ09 | New | 0.044 | new
2020 | SCE | ECC | CZ10 | 1975 | 2.219 | old
2020 | SCE | ECC | CZ10 | 1985 | 1.348 | old
2020 | SCE | ECC | CZ10 | 1996 | 0.934 | old
2020 | SCE | ECC | CZ10 | 2003 | 1.009 | ex
2020 | SCE | ECC | CZ10 | 2007 | 0.422 | ex
2020 | SCE | ECC | CZ10 | 2011 | 0.422 | ex
2020 | SCE | ECC | CZ10 | 2015 | 0.316 | ex
2020 | SCE | ECC | CZ10 | 2017 | 0.316 | rec
2020 | SCE | ECC | CZ10 | 2020 | 0.105 | rec
2020 | SCE | ECC | CZ10 | New | 0.105 | new
2020 | SCE | ECC | CZ13 | 1975 | 0.432 | old
2020 | SCE | ECC | CZ13 | 1985 | 0.256 | old
2020 | SCE | ECC | CZ13 | 1996 | 0.186 | old
2020 | SCE | ECC | CZ13 | 2003 | 0.208 | ex
2020 | SCE | ECC | CZ13 | 2007 | 0.112 | ex
2020 | SCE | ECC | CZ13 | 2011 | 0.112 | ex
2020 | SCE | ECC | CZ13 | 2015 | 0.084 | ex
2020 | SCE | ECC | CZ13 | 2017 | 0.084 | rec
2020 | SCE | ECC | CZ13 | 2020 | 0.028 | rec
2020 | SCE | ECC | CZ13 | New | 0.028 | new
2020 | SCE | ECC | CZ14 | 1975 | 0.823 | old
2020 | SCE | ECC | CZ14 | 1985 | 0.465 | old
2020 | SCE | ECC | CZ14 | 1996 | 0.329 | old
2020 | SCE | ECC | CZ14 | 2003 | 0.336 | ex
2020 | SCE | ECC | CZ14 | 2007 | 0.141 | ex
2020 | SCE | ECC | CZ14 | 2011 | 0.141 | ex
2020 | SCE | ECC | CZ14 | 2015 | 0.106 | ex
2020 | SCE | ECC | CZ14 | 2017 | 0.106 | rec
2020 | SCE | ECC | CZ14 | 2020 | 0.035 | rec
2020 | SCE | ECC | CZ14 | New | 0.035 | new
2020 | SCE | ECC | CZ15 | 1975 | 0.646 | old
2020 | SCE | ECC | CZ15 | 1985 | 0.392 | old
2020 | SCE | ECC | CZ15 | 1996 | 0.272 | old
2020 | SCE | ECC | CZ15 | 2003 | 0.294 | ex
2020 | SCE | ECC | CZ15 | 2007 | 0.123 | ex
2020 | SCE | ECC | CZ15 | 2011 | 0.123 | ex
2020 | SCE | ECC | CZ15 | 2015 | 0.092 | ex
2020 | SCE | ECC | CZ15 | 2017 | 0.092 | rec
2020 | SCE | ECC | CZ15 | 2020 | 0.031 | rec
2020 | SCE | ECC | CZ15 | New | 0.031 | new
2020 | SCE | ECC | CZ16 | 1975 | 1.447 | old
2020 | SCE | ECC | CZ16 | 1985 | 0.872 | old
2020 | SCE | ECC | CZ16 | 1996 | 0.607 | old
2020 | SCE | ECC | CZ16 | 2003 | 0.653 | ex
2020 | SCE | ECC | CZ16 | 2007 | 0.277 | ex
2020 | SCE | ECC | CZ16 | 2011 | 0.277 | ex
2020 | SCE | ECC | CZ16 | 2015 | 0.208 | ex
2020 | SCE | ECC | CZ16 | 2017 | 0.208 | rec
2020 | SCE | ECC | CZ16 | 2020 | 0.069 | rec
2020 | SCE | ECC | CZ16 | New | 0.069 | new
2020 | SCE | EPr | CZ05 | 1975 | 0.051 | old
2020 | SCE | EPr | CZ05 | 1985 | 0.006 | old
2020 | SCE | EPr | CZ05 | 1996 | 0.005 | old
2020 | SCE | EPr | CZ05 | 2003 | 0.004 | ex
2020 | SCE | EPr | CZ05 | 2007 | 0.001 | ex
2020 | SCE | EPr | CZ05 | 2011 | 0.001 | ex
2020 | SCE | EPr | CZ05 | 2015 | 0.001 | ex
2020 | SCE | EPr | CZ05 | 2017 | 0.001 | rec
2020 | SCE | EPr | CZ05 | 2020 | 0.001 | rec
2020 | SCE | EPr | CZ05 | New | 0.001 | new
2020 | SCE | EPr | CZ06 | 1975 | 8.989 | old
2020 | SCE | EPr | CZ06 | 1985 | 1.023 | old
2020 | SCE | EPr | CZ06 | 1996 | 0.89 | old
2020 | SCE | EPr | CZ06 | 2003 | 0.68 | ex
2020 | SCE | EPr | CZ06 | 2007 | 0.204 | ex
2020 | SCE | EPr | CZ06 | 2011 | 0.204 | ex
2020 | SCE | EPr | CZ06 | 2015 | 0.153 | ex
2020 | SCE | EPr | CZ06 | 2017 | 0.153 | rec
2020 | SCE | EPr | CZ06 | 2020 | 0.051 | rec
2020 | SCE | EPr | CZ06 | New | 0.051 | new
2020 | SCE | EPr | CZ08 | 1975 | 15.589 | old
2020 | SCE | EPr | CZ08 | 1985 | 1.777 | old
2020 | SCE | EPr | CZ08 | 1996 | 1.561 | old
2020 | SCE | EPr | CZ08 | 2003 | 1.232 | ex
2020 | SCE | EPr | CZ08 | 2007 | 0.363 | ex
2020 | SCE | EPr | CZ08 | 2011 | 0.363 | ex
2020 | SCE | EPr | CZ08 | 2015 | 0.272 | ex
2020 | SCE | EPr | CZ08 | 2017 | 0.272 | rec
2020 | SCE | EPr | CZ08 | 2020 | 0.091 | rec
2020 | SCE | EPr | CZ08 | New | 0.091 | new
2020 | SCE | EPr | CZ09 | 1975 | 8.081 | old
2020 | SCE | EPr | CZ09 | 1985 | 0.928 | old
2020 | SCE | EPr | CZ09 | 1996 | 0.842 | old
2020 | SCE | EPr | CZ09 | 2003 | 0.744 | ex
2020 | SCE | EPr | CZ09 | 2007 | 0.204 | ex
2020 | SCE | EPr | CZ09 | 2011 | 0.204 | ex
2020 | SCE | EPr | CZ09 | 2015 | 0.153 | ex
2020 | SCE | EPr | CZ09 | 2017 | 0.153 | rec
2020 | SCE | EPr | CZ09 | 2020 | 0.051 | rec
2020 | SCE | EPr | CZ09 | New | 0.051 | new
2020 | SCE | EPr | CZ10 | 1975 | 5.598 | old
2020 | SCE | EPr | CZ10 | 1985 | 2.398 | old
2020 | SCE | EPr | CZ10 | 1996 | 2.432 | old
2020 | SCE | EPr | CZ10 | 2003 | 2.248 | ex
2020 | SCE | EPr | CZ10 | 2007 | 0.57 | ex
2020 | SCE | EPr | CZ10 | 2011 | 0.57 | ex
2020 | SCE | EPr | CZ10 | 2015 | 0.427 | ex
2020 | SCE | EPr | CZ10 | 2017 | 0.427 | rec
2020 | SCE | EPr | CZ10 | 2020 | 0.142 | rec
2020 | SCE | EPr | CZ10 | New | 0.142 | new
2020 | SCE | EPr | CZ13 | 1975 | 1.468 | old
2020 | SCE | EPr | CZ13 | 1985 | 0.358 | old
2020 | SCE | EPr | CZ13 | 1996 | 0.458 | old
2020 | SCE | EPr | CZ13 | 2003 | 0.28 | ex
2020 | SCE | EPr | CZ13 | 2007 | 0.125 | ex
2020 | SCE | EPr | CZ13 | 2011 | 0.125 | ex
2020 | SCE | EPr | CZ13 | 2015 | 0.094 | ex
2020 | SCE | EPr | CZ13 | 2017 | 0.094 | rec
2020 | SCE | EPr | CZ13 | 2020 | 0.031 | rec
2020 | SCE | EPr | CZ13 | New | 0.031 | new
2020 | SCE | EPr | CZ14 | 1975 | 1.795 | old
2020 | SCE | EPr | CZ14 | 1985 | 0.528 | old
2020 | SCE | EPr | CZ14 | 1996 | 0.537 | old
2020 | SCE | EPr | CZ14 | 2003 | 0.495 | ex
2020 | SCE | EPr | CZ14 | 2007 | 0.129 | ex
2020 | SCE | EPr | CZ14 | 2011 | 0.129 | ex
2020 | SCE | EPr | CZ14 | 2015 | 0.097 | ex
2020 | SCE | EPr | CZ14 | 2017 | 0.097 | rec
2020 | SCE | EPr | CZ14 | 2020 | 0.032 | rec
2020 | SCE | EPr | CZ14 | New | 0.032 | new
2020 | SCE | EPr | CZ15 | 1975 | 0.499 | old
2020 | SCE | EPr | CZ15 | 1985 | 0.214 | old
2020 | SCE | EPr | CZ15 | 1996 | 0.217 | old
2020 | SCE | EPr | CZ15 | 2003 | 0.2 | ex
2020 | SCE | EPr | CZ15 | 2007 | 0.051 | ex
2020 | SCE | EPr | CZ15 | 2011 | 0.051 | ex
2020 | SCE | EPr | CZ15 | 2015 | 0.038 | ex
2020 | SCE | EPr | CZ15 | 2017 | 0.038 | rec
2020 | SCE | EPr | CZ15 | 2020 | 0.013 | rec
2020 | SCE | EPr | CZ15 | New | 0.013 | new
2020 | SCE | EPr | CZ16 | 1975 | 0.776 | old
2020 | SCE | EPr | CZ16 | 1985 | 0.261 | old
2020 | SCE | EPr | CZ16 | 1996 | 0.276 | old
2020 | SCE | EPr | CZ16 | 2003 | 0.238 | ex
2020 | SCE | EPr | CZ16 | 2007 | 0.067 | ex
2020 | SCE | EPr | CZ16 | 2011 | 0.067 | ex
2020 | SCE | EPr | CZ16 | 2015 | 0.05 | ex
2020 | SCE | EPr | CZ16 | 2017 | 0.05 | rec
2020 | SCE | EPr | CZ16 | 2020 | 0.017 | rec
2020 | SCE | EPr | CZ16 | New | 0.017 | new
2020 | SCE | ERC | CZ05 | 1975 | 0.051 | old
2020 | SCE | ERC | CZ05 | 1985 | 0.006 | old
2020 | SCE | ERC | CZ05 | 1996 | 0.005 | old
2020 | SCE | ERC | CZ05 | 2003 | 0.004 | ex
2020 | SCE | ERC | CZ05 | 2007 | 0.001 | ex
2020 | SCE | ERC | CZ05 | 2011 | 0.001 | ex
2020 | SCE | ERC | CZ05 | 2015 | 0.001 | ex
2020 | SCE | ERC | CZ05 | 2017 | 0.001 | rec
2020 | SCE | ERC | CZ05 | 2020 | 0.001 | rec
2020 | SCE | ERC | CZ05 | New | 0.001 | new
2020 | SCE | ERC | CZ06 | 1975 | 8.989 | old
2020 | SCE | ERC | CZ06 | 1985 | 1.023 | old
2020 | SCE | ERC | CZ06 | 1996 | 0.89 | old
2020 | SCE | ERC | CZ06 | 2003 | 0.68 | ex
2020 | SCE | ERC | CZ06 | 2007 | 0.204 | ex
2020 | SCE | ERC | CZ06 | 2011 | 0.204 | ex
2020 | SCE | ERC | CZ06 | 2015 | 0.153 | ex
2020 | SCE | ERC | CZ06 | 2017 | 0.153 | rec
2020 | SCE | ERC | CZ06 | 2020 | 0.051 | rec
2020 | SCE | ERC | CZ06 | New | 0.051 | new
2020 | SCE | ERC | CZ08 | 1975 | 15.589 | old
2020 | SCE | ERC | CZ08 | 1985 | 1.777 | old
2020 | SCE | ERC | CZ08 | 1996 | 1.561 | old
2020 | SCE | ERC | CZ08 | 2003 | 1.232 | ex
2020 | SCE | ERC | CZ08 | 2007 | 0.363 | ex
2020 | SCE | ERC | CZ08 | 2011 | 0.363 | ex
2020 | SCE | ERC | CZ08 | 2015 | 0.272 | ex
2020 | SCE | ERC | CZ08 | 2017 | 0.272 | rec
2020 | SCE | ERC | CZ08 | 2020 | 0.091 | rec
2020 | SCE | ERC | CZ08 | New | 0.091 | new
2020 | SCE | ERC | CZ09 | 1975 | 8.081 | old
2020 | SCE | ERC | CZ09 | 1985 | 0.928 | old
2020 | SCE | ERC | CZ09 | 1996 | 0.842 | old
2020 | SCE | ERC | CZ09 | 2003 | 0.744 | ex
2020 | SCE | ERC | CZ09 | 2007 | 0.204 | ex
2020 | SCE | ERC | CZ09 | 2011 | 0.204 | ex
2020 | SCE | ERC | CZ09 | 2015 | 0.153 | ex
2020 | SCE | ERC | CZ09 | 2017 | 0.153 | rec
2020 | SCE | ERC | CZ09 | 2020 | 0.051 | rec
2020 | SCE | ERC | CZ09 | New | 0.051 | new
2020 | SCE | ERC | CZ10 | 1975 | 5.598 | old
2020 | SCE | ERC | CZ10 | 1985 | 2.398 | old
2020 | SCE | ERC | CZ10 | 1996 | 2.432 | old
2020 | SCE | ERC | CZ10 | 2003 | 2.248 | ex
2020 | SCE | ERC | CZ10 | 2007 | 0.57 | ex
2020 | SCE | ERC | CZ10 | 2011 | 0.57 | ex
2020 | SCE | ERC | CZ10 | 2015 | 0.427 | ex
2020 | SCE | ERC | CZ10 | 2017 | 0.427 | rec
2020 | SCE | ERC | CZ10 | 2020 | 0.142 | rec
2020 | SCE | ERC | CZ10 | New | 0.142 | new
2020 | SCE | ERC | CZ13 | 1975 | 1.468 | old
2020 | SCE | ERC | CZ13 | 1985 | 0.358 | old
2020 | SCE | ERC | CZ13 | 1996 | 0.458 | old
2020 | SCE | ERC | CZ13 | 2003 | 0.28 | ex
2020 | SCE | ERC | CZ13 | 2007 | 0.125 | ex
2020 | SCE | ERC | CZ13 | 2011 | 0.125 | ex
2020 | SCE | ERC | CZ13 | 2015 | 0.094 | ex
2020 | SCE | ERC | CZ13 | 2017 | 0.094 | rec
2020 | SCE | ERC | CZ13 | 2020 | 0.031 | rec
2020 | SCE | ERC | CZ13 | New | 0.031 | new
2020 | SCE | ERC | CZ14 | 1975 | 1.795 | old
2020 | SCE | ERC | CZ14 | 1985 | 0.528 | old
2020 | SCE | ERC | CZ14 | 1996 | 0.537 | old
2020 | SCE | ERC | CZ14 | 2003 | 0.495 | ex
2020 | SCE | ERC | CZ14 | 2007 | 0.129 | ex
2020 | SCE | ERC | CZ14 | 2011 | 0.129 | ex
2020 | SCE | ERC | CZ14 | 2015 | 0.097 | ex
2020 | SCE | ERC | CZ14 | 2017 | 0.097 | rec
2020 | SCE | ERC | CZ14 | 2020 | 0.032 | rec
2020 | SCE | ERC | CZ14 | New | 0.032 | new
2020 | SCE | ERC | CZ15 | 1975 | 0.499 | old
2020 | SCE | ERC | CZ15 | 1985 | 0.214 | old
2020 | SCE | ERC | CZ15 | 1996 | 0.217 | old
2020 | SCE | ERC | CZ15 | 2003 | 0.2 | ex
2020 | SCE | ERC | CZ15 | 2007 | 0.051 | ex
2020 | SCE | ERC | CZ15 | 2011 | 0.051 | ex
2020 | SCE | ERC | CZ15 | 2015 | 0.038 | ex
2020 | SCE | ERC | CZ15 | 2017 | 0.038 | rec
2020 | SCE | ERC | CZ15 | 2020 | 0.013 | rec
2020 | SCE | ERC | CZ15 | New | 0.013 | new
2020 | SCE | ERC | CZ16 | 1975 | 0.776 | old
2020 | SCE | ERC | CZ16 | 1985 | 0.261 | old
2020 | SCE | ERC | CZ16 | 1996 | 0.276 | old
2020 | SCE | ERC | CZ16 | 2003 | 0.238 | ex
2020 | SCE | ERC | CZ16 | 2007 | 0.067 | ex
2020 | SCE | ERC | CZ16 | 2011 | 0.067 | ex
2020 | SCE | ERC | CZ16 | 2015 | 0.05 | ex
2020 | SCE | ERC | CZ16 | 2017 | 0.05 | rec
2020 | SCE | ERC | CZ16 | 2020 | 0.017 | rec
2020 | SCE | ERC | CZ16 | New | 0.017 | new
2020 | SCE | ESe | CZ05 | 1975 | 0.051 | old
2020 | SCE | ESe | CZ05 | 1985 | 0.006 | old
2020 | SCE | ESe | CZ05 | 1996 | 0.005 | old
2020 | SCE | ESe | CZ05 | 2003 | 0.004 | ex
2020 | SCE | ESe | CZ05 | 2007 | 0.001 | ex
2020 | SCE | ESe | CZ05 | 2011 | 0.001 | ex
2020 | SCE | ESe | CZ05 | 2015 | 0.001 | ex
2020 | SCE | ESe | CZ05 | 2017 | 0.001 | rec
2020 | SCE | ESe | CZ05 | 2020 | 0.001 | rec
2020 | SCE | ESe | CZ05 | New | 0.001 | new
2020 | SCE | ESe | CZ06 | 1975 | 8.989 | old
2020 | SCE | ESe | CZ06 | 1985 | 1.023 | old
2020 | SCE | ESe | CZ06 | 1996 | 0.89 | old
2020 | SCE | ESe | CZ06 | 2003 | 0.68 | ex
2020 | SCE | ESe | CZ06 | 2007 | 0.204 | ex
2020 | SCE | ESe | CZ06 | 2011 | 0.204 | ex
2020 | SCE | ESe | CZ06 | 2015 | 0.153 | ex
2020 | SCE | ESe | CZ06 | 2017 | 0.153 | rec
2020 | SCE | ESe | CZ06 | 2020 | 0.051 | rec
2020 | SCE | ESe | CZ06 | New | 0.051 | new
2020 | SCE | ESe | CZ08 | 1975 | 15.589 | old
2020 | SCE | ESe | CZ08 | 1985 | 1.777 | old
2020 | SCE | ESe | CZ08 | 1996 | 1.561 | old
2020 | SCE | ESe | CZ08 | 2003 | 1.232 | ex
2020 | SCE | ESe | CZ08 | 2007 | 0.363 | ex
2020 | SCE | ESe | CZ08 | 2011 | 0.363 | ex
2020 | SCE | ESe | CZ08 | 2015 | 0.272 | ex
2020 | SCE | ESe | CZ08 | 2017 | 0.272 | rec
2020 | SCE | ESe | CZ08 | 2020 | 0.091 | rec
2020 | SCE | ESe | CZ08 | New | 0.091 | new
2020 | SCE | ESe | CZ09 | 1975 | 8.081 | old
2020 | SCE | ESe | CZ09 | 1985 | 0.928 | old
2020 | SCE | ESe | CZ09 | 1996 | 0.842 | old
2020 | SCE | ESe | CZ09 | 2003 | 0.744 | ex
2020 | SCE | ESe | CZ09 | 2007 | 0.204 | ex
2020 | SCE | ESe | CZ09 | 2011 | 0.204 | ex
2020 | SCE | ESe | CZ09 | 2015 | 0.153 | ex
2020 | SCE | ESe | CZ09 | 2017 | 0.153 | rec
2020 | SCE | ESe | CZ09 | 2020 | 0.051 | rec
2020 | SCE | ESe | CZ09 | New | 0.051 | new
2020 | SCE | ESe | CZ10 | 1975 | 5.598 | old
2020 | SCE | ESe | CZ10 | 1985 | 2.398 | old
2020 | SCE | ESe | CZ10 | 1996 | 2.432 | old
2020 | SCE | ESe | CZ10 | 2003 | 2.248 | ex
2020 | SCE | ESe | CZ10 | 2007 | 0.57 | ex
2020 | SCE | ESe | CZ10 | 2011 | 0.57 | ex
2020 | SCE | ESe | CZ10 | 2015 | 0.427 | ex
2020 | SCE | ESe | CZ10 | 2017 | 0.427 | rec
2020 | SCE | ESe | CZ10 | 2020 | 0.142 | rec
2020 | SCE | ESe | CZ10 | New | 0.142 | new
2020 | SCE | ESe | CZ13 | 1975 | 1.468 | old
2020 | SCE | ESe | CZ13 | 1985 | 0.358 | old
2020 | SCE | ESe | CZ13 | 1996 | 0.458 | old
2020 | SCE | ESe | CZ13 | 2003 | 0.28 | ex
2020 | SCE | ESe | CZ13 | 2007 | 0.125 | ex
2020 | SCE | ESe | CZ13 | 2011 | 0.125 | ex
2020 | SCE | ESe | CZ13 | 2015 | 0.094 | ex
2020 | SCE | ESe | CZ13 | 2017 | 0.094 | rec
2020 | SCE | ESe | CZ13 | 2020 | 0.031 | rec
2020 | SCE | ESe | CZ13 | New | 0.031 | new
2020 | SCE | ESe | CZ14 | 1975 | 1.795 | old
2020 | SCE | ESe | CZ14 | 1985 | 0.528 | old
2020 | SCE | ESe | CZ14 | 1996 | 0.537 | old
2020 | SCE | ESe | CZ14 | 2003 | 0.495 | ex
2020 | SCE | ESe | CZ14 | 2007 | 0.129 | ex
2020 | SCE | ESe | CZ14 | 2011 | 0.129 | ex
2020 | SCE | ESe | CZ14 | 2015 | 0.097 | ex
2020 | SCE | ESe | CZ14 | 2017 | 0.097 | rec
2020 | SCE | ESe | CZ14 | 2020 | 0.032 | rec
2020 | SCE | ESe | CZ14 | New | 0.032 | new
2020 | SCE | ESe | CZ15 | 1975 | 0.499 | old
2020 | SCE | ESe | CZ15 | 1985 | 0.214 | old
2020 | SCE | ESe | CZ15 | 1996 | 0.217 | old
2020 | SCE | ESe | CZ15 | 2003 | 0.2 | ex
2020 | SCE | ESe | CZ15 | 2007 | 0.051 | ex
2020 | SCE | ESe | CZ15 | 2011 | 0.051 | ex
2020 | SCE | ESe | CZ15 | 2015 | 0.038 | ex
2020 | SCE | ESe | CZ15 | 2017 | 0.038 | rec
2020 | SCE | ESe | CZ15 | 2020 | 0.013 | rec
2020 | SCE | ESe | CZ15 | New | 0.013 | new
2020 | SCE | ESe | CZ16 | 1975 | 0.776 | old
2020 | SCE | ESe | CZ16 | 1985 | 0.261 | old
2020 | SCE | ESe | CZ16 | 1996 | 0.276 | old
2020 | SCE | ESe | CZ16 | 2003 | 0.238 | ex
2020 | SCE | ESe | CZ16 | 2007 | 0.067 | ex
2020 | SCE | ESe | CZ16 | 2011 | 0.067 | ex
2020 | SCE | ESe | CZ16 | 2015 | 0.05 | ex
2020 | SCE | ESe | CZ16 | 2017 | 0.05 | rec
2020 | SCE | ESe | CZ16 | 2020 | 0.017 | rec
2020 | SCE | ESe | CZ16 | New | 0.017 | new
2020 | SCE | EUD | CZ05 | 1975 | 0.009 | old
2020 | SCE | EUD | CZ05 | 1985 | 0.003 | old
2020 | SCE | EUD | CZ05 | 1996 | 0.002 | old
2020 | SCE | EUD | CZ05 | 2003 | 0.001 | ex
2020 | SCE | EUD | CZ05 | 2007 | 0.001 | ex
2020 | SCE | EUD | CZ05 | 2011 | 0.001 | ex
2020 | SCE | EUD | CZ05 | 2015 | 0.001 | ex
2020 | SCE | EUD | CZ05 | 2017 | 0.001 | rec
2020 | SCE | EUD | CZ05 | 2020 | 0.001 | rec
2020 | SCE | EUD | CZ05 | New | 0.001 | new
2020 | SCE | EUD | CZ06 | 1975 | 7.226 | old
2020 | SCE | EUD | CZ06 | 1985 | 2.474 | old
2020 | SCE | EUD | CZ06 | 1996 | 1.675 | old
2020 | SCE | EUD | CZ06 | 2003 | 0.979 | ex
2020 | SCE | EUD | CZ06 | 2007 | 0.435 | ex
2020 | SCE | EUD | CZ06 | 2011 | 0.435 | ex
2020 | SCE | EUD | CZ06 | 2015 | 0.326 | ex
2020 | SCE | EUD | CZ06 | 2017 | 0.326 | rec
2020 | SCE | EUD | CZ06 | 2020 | 0.109 | rec
2020 | SCE | EUD | CZ06 | New | 0.109 | new
2020 | SCE | EUD | CZ08 | 1975 | 11.773 | old
2020 | SCE | EUD | CZ08 | 1985 | 4.021 | old
2020 | SCE | EUD | CZ08 | 1996 | 2.653 | old
2020 | SCE | EUD | CZ08 | 2003 | 1.543 | ex
2020 | SCE | EUD | CZ08 | 2007 | 0.689 | ex
2020 | SCE | EUD | CZ08 | 2011 | 0.689 | ex
2020 | SCE | EUD | CZ08 | 2015 | 0.517 | ex
2020 | SCE | EUD | CZ08 | 2017 | 0.517 | rec
2020 | SCE | EUD | CZ08 | 2020 | 0.172 | rec
2020 | SCE | EUD | CZ08 | New | 0.172 | new
2020 | SCE | EUD | CZ09 | 1975 | 2.427 | old
2020 | SCE | EUD | CZ09 | 1985 | 0.848 | old
2020 | SCE | EUD | CZ09 | 1996 | 0.684 | old
2020 | SCE | EUD | CZ09 | 2003 | 0.411 | ex
2020 | SCE | EUD | CZ09 | 2007 | 0.176 | ex
2020 | SCE | EUD | CZ09 | 2011 | 0.176 | ex
2020 | SCE | EUD | CZ09 | 2015 | 0.132 | ex
2020 | SCE | EUD | CZ09 | 2017 | 0.132 | rec
2020 | SCE | EUD | CZ09 | 2020 | 0.044 | rec
2020 | SCE | EUD | CZ09 | New | 0.044 | new
2020 | SCE | EUD | CZ10 | 1975 | 2.219 | old
2020 | SCE | EUD | CZ10 | 1985 | 1.348 | old
2020 | SCE | EUD | CZ10 | 1996 | 0.934 | old
2020 | SCE | EUD | CZ10 | 2003 | 1.009 | ex
2020 | SCE | EUD | CZ10 | 2007 | 0.422 | ex
2020 | SCE | EUD | CZ10 | 2011 | 0.422 | ex
2020 | SCE | EUD | CZ10 | 2015 | 0.316 | ex
2020 | SCE | EUD | CZ10 | 2017 | 0.316 | rec
2020 | SCE | EUD | CZ10 | 2020 | 0.105 | rec
2020 | SCE | EUD | CZ10 | New | 0.105 | new
2020 | SCE | EUD | CZ13 | 1975 | 0.432 | old
2020 | SCE | EUD | CZ13 | 1985 | 0.256 | old
2020 | SCE | EUD | CZ13 | 1996 | 0.186 | old
2020 | SCE | EUD | CZ13 | 2003 | 0.208 | ex
2020 | SCE | EUD | CZ13 | 2007 | 0.112 | ex
2020 | SCE | EUD | CZ13 | 2011 | 0.112 | ex
2020 | SCE | EUD | CZ13 | 2015 | 0.084 | ex
2020 | SCE | EUD | CZ13 | 2017 | 0.084 | rec
2020 | SCE | EUD | CZ13 | 2020 | 0.028 | rec
2020 | SCE | EUD | CZ13 | New | 0.028 | new
2020 | SCE | EUD | CZ14 | 1975 | 0.823 | old
2020 | SCE | EUD | CZ14 | 1985 | 0.465 | old
2020 | SCE | EUD | CZ14 | 1996 | 0.329 | old
2020 | SCE | EUD | CZ14 | 2003 | 0.336 | ex
2020 | SCE | EUD | CZ14 | 2007 | 0.141 | ex
2020 | SCE | EUD | CZ14 | 2011 | 0.141 | ex
2020 | SCE | EUD | CZ14 | 2015 | 0.106 | ex
2020 | SCE | EUD | CZ14 | 2017 | 0.106 | rec
2020 | SCE | EUD | CZ14 | 2020 | 0.035 | rec
2020 | SCE | EUD | CZ14 | New | 0.035 | new
2020 | SCE | EUD | CZ15 | 1975 | 0.646 | old
2020 | SCE | EUD | CZ15 | 1985 | 0.392 | old
2020 | SCE | EUD | CZ15 | 1996 | 0.272 | old
2020 | SCE | EUD | CZ15 | 2003 | 0.294 | ex
2020 | SCE | EUD | CZ15 | 2007 | 0.123 | ex
2020 | SCE | EUD | CZ15 | 2011 | 0.123 | ex
2020 | SCE | EUD | CZ15 | 2015 | 0.092 | ex
2020 | SCE | EUD | CZ15 | 2017 | 0.092 | rec
2020 | SCE | EUD | CZ15 | 2020 | 0.031 | rec
2020 | SCE | EUD | CZ15 | New | 0.031 | new
2020 | SCE | EUD | CZ16 | 1975 | 1.447 | old
2020 | SCE | EUD | CZ16 | 1985 | 0.872 | old
2020 | SCE | EUD | CZ16 | 1996 | 0.607 | old
2020 | SCE | EUD | CZ16 | 2003 | 0.653 | ex
2020 | SCE | EUD | CZ16 | 2007 | 0.277 | ex
2020 | SCE | EUD | CZ16 | 2011 | 0.277 | ex
2020 | SCE | EUD | CZ16 | 2015 | 0.208 | ex
2020 | SCE | EUD | CZ16 | 2017 | 0.208 | rec
2020 | SCE | EUD | CZ16 | 2020 | 0.069 | rec
2020 | SCE | EUD | CZ16 | New | 0.069 | new
2020 | SCE | EUn | CZ05 | 1975 | 0.009 | old
2020 | SCE | EUn | CZ05 | 1985 | 0.003 | old
2020 | SCE | EUn | CZ05 | 1996 | 0.002 | old
2020 | SCE | EUn | CZ05 | 2003 | 0.001 | ex
2020 | SCE | EUn | CZ05 | 2007 | 0.001 | ex
2020 | SCE | EUn | CZ05 | 2011 | 0.001 | ex
2020 | SCE | EUn | CZ05 | 2015 | 0.001 | ex
2020 | SCE | EUn | CZ05 | 2017 | 0.001 | rec
2020 | SCE | EUn | CZ05 | 2020 | 0.001 | rec
2020 | SCE | EUn | CZ05 | New | 0.001 | new
2020 | SCE | EUn | CZ06 | 1975 | 7.226 | old
2020 | SCE | EUn | CZ06 | 1985 | 2.474 | old
2020 | SCE | EUn | CZ06 | 1996 | 1.675 | old
2020 | SCE | EUn | CZ06 | 2003 | 0.979 | ex
2020 | SCE | EUn | CZ06 | 2007 | 0.435 | ex
2020 | SCE | EUn | CZ06 | 2011 | 0.435 | ex
2020 | SCE | EUn | CZ06 | 2015 | 0.326 | ex
2020 | SCE | EUn | CZ06 | 2017 | 0.326 | rec
2020 | SCE | EUn | CZ06 | 2020 | 0.109 | rec
2020 | SCE | EUn | CZ06 | New | 0.109 | new
2020 | SCE | EUn | CZ08 | 1975 | 11.773 | old
2020 | SCE | EUn | CZ08 | 1985 | 4.021 | old
2020 | SCE | EUn | CZ08 | 1996 | 2.653 | old
2020 | SCE | EUn | CZ08 | 2003 | 1.543 | ex
2020 | SCE | EUn | CZ08 | 2007 | 0.689 | ex
2020 | SCE | EUn | CZ08 | 2011 | 0.689 | ex
2020 | SCE | EUn | CZ08 | 2015 | 0.517 | ex
2020 | SCE | EUn | CZ08 | 2017 | 0.517 | rec
2020 | SCE | EUn | CZ08 | 2020 | 0.172 | rec
2020 | SCE | EUn | CZ08 | New | 0.172 | new
2020 | SCE | EUn | CZ09 | 1975 | 2.427 | old
2020 | SCE | EUn | CZ09 | 1985 | 0.848 | old
2020 | SCE | EUn | CZ09 | 1996 | 0.684 | old
2020 | SCE | EUn | CZ09 | 2003 | 0.411 | ex
2020 | SCE | EUn | CZ09 | 2007 | 0.176 | ex
2020 | SCE | EUn | CZ09 | 2011 | 0.176 | ex
2020 | SCE | EUn | CZ09 | 2015 | 0.132 | ex
2020 | SCE | EUn | CZ09 | 2017 | 0.132 | rec
2020 | SCE | EUn | CZ09 | 2020 | 0.044 | rec
2020 | SCE | EUn | CZ09 | New | 0.044 | new
2020 | SCE | EUn | CZ10 | 1975 | 2.219 | old
2020 | SCE | EUn | CZ10 | 1985 | 1.348 | old
2020 | SCE | EUn | CZ10 | 1996 | 0.934 | old
2020 | SCE | EUn | CZ10 | 2003 | 1.009 | ex
2020 | SCE | EUn | CZ10 | 2007 | 0.422 | ex
2020 | SCE | EUn | CZ10 | 2011 | 0.422 | ex
2020 | SCE | EUn | CZ10 | 2015 | 0.316 | ex
2020 | SCE | EUn | CZ10 | 2017 | 0.316 | rec
2020 | SCE | EUn | CZ10 | 2020 | 0.105 | rec
2020 | SCE | EUn | CZ10 | New | 0.105 | new
2020 | SCE | EUn | CZ13 | 1975 | 0.432 | old
2020 | SCE | EUn | CZ13 | 1985 | 0.256 | old
2020 | SCE | EUn | CZ13 | 1996 | 0.186 | old
2020 | SCE | EUn | CZ13 | 2003 | 0.208 | ex
2020 | SCE | EUn | CZ13 | 2007 | 0.112 | ex
2020 | SCE | EUn | CZ13 | 2011 | 0.112 | ex
2020 | SCE | EUn | CZ13 | 2015 | 0.084 | ex
2020 | SCE | EUn | CZ13 | 2017 | 0.084 | rec
2020 | SCE | EUn | CZ13 | 2020 | 0.028 | rec
2020 | SCE | EUn | CZ13 | New | 0.028 | new
2020 | SCE | EUn | CZ14 | 1975 | 0.823 | old
2020 | SCE | EUn | CZ14 | 1985 | 0.465 | old
2020 | SCE | EUn | CZ14 | 1996 | 0.329 | old
2020 | SCE | EUn | CZ14 | 2003 | 0.336 | ex
2020 | SCE | EUn | CZ14 | 2007 | 0.141 | ex
2020 | SCE | EUn | CZ14 | 2011 | 0.141 | ex
2020 | SCE | EUn | CZ14 | 2015 | 0.106 | ex
2020 | SCE | EUn | CZ14 | 2017 | 0.106 | rec
2020 | SCE | EUn | CZ14 | 2020 | 0.035 | rec
2020 | SCE | EUn | CZ14 | New | 0.035 | new
2020 | SCE | EUn | CZ15 | 1975 | 0.646 | old
2020 | SCE | EUn | CZ15 | 1985 | 0.392 | old
2020 | SCE | EUn | CZ15 | 1996 | 0.272 | old
2020 | SCE | EUn | CZ15 | 2003 | 0.294 | ex
2020 | SCE | EUn | CZ15 | 2007 | 0.123 | ex
2020 | SCE | EUn | CZ15 | 2011 | 0.123 | ex
2020 | SCE | EUn | CZ15 | 2015 | 0.092 | ex
2020 | SCE | EUn | CZ15 | 2017 | 0.092 | rec
2020 | SCE | EUn | CZ15 | 2020 | 0.031 | rec
2020 | SCE | EUn | CZ15 | New | 0.031 | new
2020 | SCE | EUn | CZ16 | 1975 | 1.447 | old
2020 | SCE | EUn | CZ16 | 1985 | 0.872 | old
2020 | SCE | EUn | CZ16 | 1996 | 0.607 | old
2020 | SCE | EUn | CZ16 | 2003 | 0.653 | ex
2020 | SCE | EUn | CZ16 | 2007 | 0.277 | ex
2020 | SCE | EUn | CZ16 | 2011 | 0.277 | ex
2020 | SCE | EUn | CZ16 | 2015 | 0.208 | ex
2020 | SCE | EUn | CZ16 | 2017 | 0.208 | rec
2020 | SCE | EUn | CZ16 | 2020 | 0.069 | rec
2020 | SCE | EUn | CZ16 | New | 0.069 | new
2020 | SCE | Gro | CZ05 | 1975 | 0.206 | old
2020 | SCE | Gro | CZ05 | 1985 | 0.127 | old
2020 | SCE | Gro | CZ05 | 1996 | 0.072 | old
2020 | SCE | Gro | CZ05 | 2003 | 0.031 | ex
2020 | SCE | Gro | CZ05 | 2007 | 0.02 | ex
2020 | SCE | Gro | CZ05 | 2011 | 0.02 | ex
2020 | SCE | Gro | CZ05 | 2015 | 0.015 | ex
2020 | SCE | Gro | CZ05 | 2017 | 0.015 | rec
2020 | SCE | Gro | CZ05 | 2020 | 0.005 | rec
2020 | SCE | Gro | CZ05 | New | 0.005 | new
2020 | SCE | Gro | CZ06 | 1975 | 10.258 | old
2020 | SCE | Gro | CZ06 | 1985 | 6.358 | old
2020 | SCE | Gro | CZ06 | 1996 | 3.606 | old
2020 | SCE | Gro | CZ06 | 2003 | 1.568 | ex
2020 | SCE | Gro | CZ06 | 2007 | 1.004 | ex
2020 | SCE | Gro | CZ06 | 2011 | 1.004 | ex
2020 | SCE | Gro | CZ06 | 2015 | 0.753 | ex
2020 | SCE | Gro | CZ06 | 2017 | 0.753 | rec
2020 | SCE | Gro | CZ06 | 2020 | 0.251 | rec
2020 | SCE | Gro | CZ06 | New | 0.251 | new
2020 | SCE | Gro | CZ08 | 1975 | 14.995 | old
2020 | SCE | Gro | CZ08 | 1985 | 9.369 | old
2020 | SCE | Gro | CZ08 | 1996 | 5.289 | old
2020 | SCE | Gro | CZ08 | 2003 | 2.325 | ex
2020 | SCE | Gro | CZ08 | 2007 | 1.481 | ex
2020 | SCE | Gro | CZ08 | 2011 | 1.481 | ex
2020 | SCE | Gro | CZ08 | 2015 | 1.111 | ex
2020 | SCE | Gro | CZ08 | 2017 | 1.111 | rec
2020 | SCE | Gro | CZ08 | 2020 | 0.37 | rec
2020 | SCE | Gro | CZ08 | New | 0.37 | new
2020 | SCE | Gro | CZ09 | 1975 | 6.751 | old | 13.584 | 77.58%
2020 | SCE | Gro | CZ09 | 1985 | 4.408 | old
2020 | SCE | Gro | CZ09 | 1996 | 2.425 | old
2020 | SCE | Gro | CZ09 | 2003 | 1.129 | ex | 3.051 | 17.43%
2020 | SCE | Gro | CZ09 | 2007 | 0.699 | ex
2020 | SCE | Gro | CZ09 | 2011 | 0.699 | ex
2020 | SCE | Gro | CZ09 | 2015 | 0.524 | ex
2020 | SCE | Gro | CZ09 | 2017 | 0.524 | rec | 0.699 | 3.992%
2020 | SCE | Gro | CZ09 | 2020 | 0.175 | rec
2020 | SCE | Gro | CZ09 | New | 0.175 | new | 0.175 | 0.9995%
2020 | SCE | Gro | CZ10 | 1975 | 5.339 | old
2020 | SCE | Gro | CZ10 | 1985 | 8.676 | old
2020 | SCE | Gro | CZ10 | 1996 | 4.536 | old
2020 | SCE | Gro | CZ10 | 2003 | 3.226 | ex
2020 | SCE | Gro | CZ10 | 2007 | 2.001 | ex
2020 | SCE | Gro | CZ10 | 2011 | 2.001 | ex
2020 | SCE | Gro | CZ10 | 2015 | 1.501 | ex
2020 | SCE | Gro | CZ10 | 2017 | 1.501 | rec
2020 | SCE | Gro | CZ10 | 2020 | 0.5 | rec
2020 | SCE | Gro | CZ10 | New | 0.5 | new
2020 | SCE | Gro | CZ13 | 1975 | 1.32 | old
2020 | SCE | Gro | CZ13 | 1985 | 0.834 | old
2020 | SCE | Gro | CZ13 | 1996 | 0.679 | old
2020 | SCE | Gro | CZ13 | 2003 | 0.382 | ex
2020 | SCE | Gro | CZ13 | 2007 | 0.25 | ex
2020 | SCE | Gro | CZ13 | 2011 | 0.25 | ex
2020 | SCE | Gro | CZ13 | 2015 | 0.187 | ex
2020 | SCE | Gro | CZ13 | 2017 | 0.187 | rec
2020 | SCE | Gro | CZ13 | 2020 | 0.063 | rec
2020 | SCE | Gro | CZ13 | New | 0.063 | new
2020 | SCE | Gro | CZ14 | 1975 | 1.531 | old
2020 | SCE | Gro | CZ14 | 1985 | 1.981 | old
2020 | SCE | Gro | CZ14 | 1996 | 1.06 | old
2020 | SCE | Gro | CZ14 | 2003 | 0.712 | ex
2020 | SCE | Gro | CZ14 | 2007 | 0.441 | ex
2020 | SCE | Gro | CZ14 | 2011 | 0.441 | ex
2020 | SCE | Gro | CZ14 | 2015 | 0.331 | ex
2020 | SCE | Gro | CZ14 | 2017 | 0.331 | rec
2020 | SCE | Gro | CZ14 | 2020 | 0.11 | rec
2020 | SCE | Gro | CZ14 | New | 0.11 | new
2020 | SCE | Gro | CZ15 | 1975 | 0.751 | old
2020 | SCE | Gro | CZ15 | 1985 | 1.22 | old
2020 | SCE | Gro | CZ15 | 1996 | 0.638 | old
2020 | SCE | Gro | CZ15 | 2003 | 0.454 | ex
2020 | SCE | Gro | CZ15 | 2007 | 0.281 | ex
2020 | SCE | Gro | CZ15 | 2011 | 0.281 | ex
2020 | SCE | Gro | CZ15 | 2015 | 0.211 | ex
2020 | SCE | Gro | CZ15 | 2017 | 0.211 | rec
2020 | SCE | Gro | CZ15 | 2020 | 0.07 | rec
2020 | SCE | Gro | CZ15 | New | 0.07 | new
2020 | SCE | Gro | CZ16 | 1975 | 0.677 | old
2020 | SCE | Gro | CZ16 | 1985 | 0.727 | old
2020 | SCE | Gro | CZ16 | 1996 | 0.433 | old
2020 | SCE | Gro | CZ16 | 2003 | 0.278 | ex
2020 | SCE | Gro | CZ16 | 2007 | 0.175 | ex
2020 | SCE | Gro | CZ16 | 2011 | 0.175 | ex
2020 | SCE | Gro | CZ16 | 2015 | 0.131 | ex
2020 | SCE | Gro | CZ16 | 2017 | 0.131 | rec
2020 | SCE | Gro | CZ16 | 2020 | 0.044 | rec
2020 | SCE | Gro | CZ16 | New | 0.044 | new
2020 | SCE | HGR | CZ05 | 1975 | 0.052 | old
2020 | SCE | HGR | CZ05 | 1985 | 0.067 | old
2020 | SCE | HGR | CZ05 | 1996 | 0.018 | old
2020 | SCE | HGR | CZ05 | 2003 | 0.01 | ex
2020 | SCE | HGR | CZ05 | 2007 | 0.004 | ex
2020 | SCE | HGR | CZ05 | 2011 | 0.004 | ex
2020 | SCE | HGR | CZ05 | 2015 | 0.003 | ex
2020 | SCE | HGR | CZ05 | 2017 | 0.003 | rec
2020 | SCE | HGR | CZ05 | 2020 | 0.001 | rec
2020 | SCE | HGR | CZ05 | New | 0.001 | new
2020 | SCE | HGR | CZ06 | 1975 | 6.021 | old
2020 | SCE | HGR | CZ06 | 1985 | 7.873 | old
2020 | SCE | HGR | CZ06 | 1996 | 2.112 | old
2020 | SCE | HGR | CZ06 | 2003 | 1.144 | ex
2020 | SCE | HGR | CZ06 | 2007 | 0.48 | ex
2020 | SCE | HGR | CZ06 | 2011 | 0.48 | ex
2020 | SCE | HGR | CZ06 | 2015 | 0.36 | ex
2020 | SCE | HGR | CZ06 | 2017 | 0.36 | rec
2020 | SCE | HGR | CZ06 | 2020 | 0.12 | rec
2020 | SCE | HGR | CZ06 | New | 0.12 | new
2020 | SCE | HGR | CZ08 | 1975 | 3.884 | old
2020 | SCE | HGR | CZ08 | 1985 | 5.073 | old
2020 | SCE | HGR | CZ08 | 1996 | 1.36 | old
2020 | SCE | HGR | CZ08 | 2003 | 0.743 | ex
2020 | SCE | HGR | CZ08 | 2007 | 0.303 | ex
2020 | SCE | HGR | CZ08 | 2011 | 0.303 | ex
2020 | SCE | HGR | CZ08 | 2015 | 0.227 | ex
2020 | SCE | HGR | CZ08 | 2017 | 0.227 | rec
2020 | SCE | HGR | CZ08 | 2020 | 0.076 | rec
2020 | SCE | HGR | CZ08 | New | 0.076 | new
2020 | SCE | HGR | CZ09 | 1975 | 2.76 | old
2020 | SCE | HGR | CZ09 | 1985 | 3.681 | old
2020 | SCE | HGR | CZ09 | 1996 | 0.99 | old
2020 | SCE | HGR | CZ09 | 2003 | 0.471 | ex
2020 | SCE | HGR | CZ09 | 2007 | 0.301 | ex
2020 | SCE | HGR | CZ09 | 2011 | 0.301 | ex
2020 | SCE | HGR | CZ09 | 2015 | 0.226 | ex
2020 | SCE | HGR | CZ09 | 2017 | 0.226 | rec
2020 | SCE | HGR | CZ09 | 2020 | 0.075 | rec
2020 | SCE | HGR | CZ09 | New | 0.075 | new
2020 | SCE | HGR | CZ10 | 1975 | 0.484 | old
2020 | SCE | HGR | CZ10 | 1985 | 1.441 | old
2020 | SCE | HGR | CZ10 | 1996 | 0.25 | old
2020 | SCE | HGR | CZ10 | 2003 | 0.395 | ex
2020 | SCE | HGR | CZ10 | 2007 | 0.215 | ex
2020 | SCE | HGR | CZ10 | 2011 | 0.215 | ex
2020 | SCE | HGR | CZ10 | 2015 | 0.161 | ex
2020 | SCE | HGR | CZ10 | 2017 | 0.161 | rec
2020 | SCE | HGR | CZ10 | 2020 | 0.054 | rec
2020 | SCE | HGR | CZ10 | New | 0.054 | new
2020 | SCE | HGR | CZ13 | 1975 | 0.163 | old
2020 | SCE | HGR | CZ13 | 1985 | 0.21 | old
2020 | SCE | HGR | CZ13 | 1996 | 0.101 | old
2020 | SCE | HGR | CZ13 | 2003 | 0.031 | ex
2020 | SCE | HGR | CZ13 | 2007 | 0.03 | ex
2020 | SCE | HGR | CZ13 | 2011 | 0.03 | ex
2020 | SCE | HGR | CZ13 | 2015 | 0.022 | ex
2020 | SCE | HGR | CZ13 | 2017 | 0.022 | rec
2020 | SCE | HGR | CZ13 | 2020 | 0.008 | rec
2020 | SCE | HGR | CZ13 | New | 0.008 | new
2020 | SCE | HGR | CZ14 | 1975 | 0.32 | old
2020 | SCE | HGR | CZ14 | 1985 | 0.671 | old
2020 | SCE | HGR | CZ14 | 1996 | 0.146 | old
2020 | SCE | HGR | CZ14 | 2003 | 0.138 | ex
2020 | SCE | HGR | CZ14 | 2007 | 0.097 | ex
2020 | SCE | HGR | CZ14 | 2011 | 0.097 | ex
2020 | SCE | HGR | CZ14 | 2015 | 0.073 | ex
2020 | SCE | HGR | CZ14 | 2017 | 0.073 | rec
2020 | SCE | HGR | CZ14 | 2020 | 0.024 | rec
2020 | SCE | HGR | CZ14 | New | 0.024 | new
2020 | SCE | HGR | CZ15 | 1975 | 1.238 | old
2020 | SCE | HGR | CZ15 | 1985 | 3.686 | old
2020 | SCE | HGR | CZ15 | 1996 | 0.639 | old
2020 | SCE | HGR | CZ15 | 2003 | 1.009 | ex
2020 | SCE | HGR | CZ15 | 2007 | 0.549 | ex
2020 | SCE | HGR | CZ15 | 2011 | 0.549 | ex
2020 | SCE | HGR | CZ15 | 2015 | 0.412 | ex
2020 | SCE | HGR | CZ15 | 2017 | 0.412 | rec
2020 | SCE | HGR | CZ15 | 2020 | 0.137 | rec
2020 | SCE | HGR | CZ15 | New | 0.137 | new
2020 | SCE | HGR | CZ16 | 1975 | 0.564 | old
2020 | SCE | HGR | CZ16 | 1985 | 0.83 | old
2020 | SCE | HGR | CZ16 | 1996 | 0.259 | old
2020 | SCE | HGR | CZ16 | 2003 | 0.103 | ex
2020 | SCE | HGR | CZ16 | 2007 | 0.116 | ex
2020 | SCE | HGR | CZ16 | 2011 | 0.116 | ex
2020 | SCE | HGR | CZ16 | 2015 | 0.087 | ex
2020 | SCE | HGR | CZ16 | 2017 | 0.087 | rec
2020 | SCE | HGR | CZ16 | 2020 | 0.029 | rec
2020 | SCE | HGR | CZ16 | New | 0.029 | new
2020 | SCE | Hsp | CZ05 | 1975 | 0.449 | old
2020 | SCE | Hsp | CZ05 | 1985 | 0.306 | old
2020 | SCE | Hsp | CZ05 | 1996 | 0.091 | old
2020 | SCE | Hsp | CZ05 | 2003 | 0.083 | ex
2020 | SCE | Hsp | CZ05 | 2007 | 0.025 | ex
2020 | SCE | Hsp | CZ05 | 2011 | 0.025 | ex
2020 | SCE | Hsp | CZ05 | 2015 | 0.019 | ex
2020 | SCE | Hsp | CZ05 | 2017 | 0.019 | rec
2020 | SCE | Hsp | CZ05 | 2020 | 0.006 | rec
2020 | SCE | Hsp | CZ05 | New | 0.006 | new
2020 | SCE | Hsp | CZ06 | 1975 | 6.752 | old
2020 | SCE | Hsp | CZ06 | 1985 | 4.462 | old
2020 | SCE | Hsp | CZ06 | 1996 | 1.357 | old
2020 | SCE | Hsp | CZ06 | 2003 | 1.244 | ex
2020 | SCE | Hsp | CZ06 | 2007 | 0.392 | ex
2020 | SCE | Hsp | CZ06 | 2011 | 0.392 | ex
2020 | SCE | Hsp | CZ06 | 2015 | 0.294 | ex
2020 | SCE | Hsp | CZ06 | 2017 | 0.294 | rec
2020 | SCE | Hsp | CZ06 | 2020 | 0.098 | rec
2020 | SCE | Hsp | CZ06 | New | 0.098 | new
2020 | SCE | Hsp | CZ08 | 1975 | 7.214 | old
2020 | SCE | Hsp | CZ08 | 1985 | 4.719 | old
2020 | SCE | Hsp | CZ08 | 1996 | 1.444 | old
2020 | SCE | Hsp | CZ08 | 2003 | 1.327 | ex
2020 | SCE | Hsp | CZ08 | 2007 | 0.425 | ex
2020 | SCE | Hsp | CZ08 | 2011 | 0.425 | ex
2020 | SCE | Hsp | CZ08 | 2015 | 0.319 | ex
2020 | SCE | Hsp | CZ08 | 2017 | 0.319 | rec
2020 | SCE | Hsp | CZ08 | 2020 | 0.106 | rec
2020 | SCE | Hsp | CZ08 | New | 0.106 | new
2020 | SCE | Hsp | CZ09 | 1975 | 3.813 | old
2020 | SCE | Hsp | CZ09 | 1985 | 2.085 | old
2020 | SCE | Hsp | CZ09 | 1996 | 0.713 | old
2020 | SCE | Hsp | CZ09 | 2003 | 0.687 | ex
2020 | SCE | Hsp | CZ09 | 2007 | 0.27 | ex
2020 | SCE | Hsp | CZ09 | 2011 | 0.27 | ex
2020 | SCE | Hsp | CZ09 | 2015 | 0.203 | ex
2020 | SCE | Hsp | CZ09 | 2017 | 0.203 | rec
2020 | SCE | Hsp | CZ09 | 2020 | 0.068 | rec
2020 | SCE | Hsp | CZ09 | New | 0.068 | new
2020 | SCE | Hsp | CZ10 | 1975 | 2.381 | old
2020 | SCE | Hsp | CZ10 | 1985 | 2.816 | old
2020 | SCE | Hsp | CZ10 | 1996 | 1.657 | old
2020 | SCE | Hsp | CZ10 | 2003 | 0.589 | ex
2020 | SCE | Hsp | CZ10 | 2007 | 0.463 | ex
2020 | SCE | Hsp | CZ10 | 2011 | 0.463 | ex
2020 | SCE | Hsp | CZ10 | 2015 | 0.347 | ex
2020 | SCE | Hsp | CZ10 | 2017 | 0.347 | rec
2020 | SCE | Hsp | CZ10 | 2020 | 0.116 | rec
2020 | SCE | Hsp | CZ10 | New | 0.116 | new
2020 | SCE | Hsp | CZ13 | 1975 | 0.438 | old
2020 | SCE | Hsp | CZ13 | 1985 | 0.51 | old
2020 | SCE | Hsp | CZ13 | 1996 | 0.423 | old
2020 | SCE | Hsp | CZ13 | 2003 | 0.077 | ex
2020 | SCE | Hsp | CZ13 | 2007 | 0.071 | ex
2020 | SCE | Hsp | CZ13 | 2011 | 0.071 | ex
2020 | SCE | Hsp | CZ13 | 2015 | 0.053 | ex
2020 | SCE | Hsp | CZ13 | 2017 | 0.053 | rec
2020 | SCE | Hsp | CZ13 | 2020 | 0.018 | rec
2020 | SCE | Hsp | CZ13 | New | 0.018 | new
2020 | SCE | Hsp | CZ14 | 1975 | 0.522 | old
2020 | SCE | Hsp | CZ14 | 1985 | 0.463 | old
2020 | SCE | Hsp | CZ14 | 1996 | 0.246 | old
2020 | SCE | Hsp | CZ14 | 2003 | 0.113 | ex
2020 | SCE | Hsp | CZ14 | 2007 | 0.074 | ex
2020 | SCE | Hsp | CZ14 | 2011 | 0.074 | ex
2020 | SCE | Hsp | CZ14 | 2015 | 0.056 | ex
2020 | SCE | Hsp | CZ14 | 2017 | 0.056 | rec
2020 | SCE | Hsp | CZ14 | 2020 | 0.019 | rec
2020 | SCE | Hsp | CZ14 | New | 0.019 | new
2020 | SCE | Hsp | CZ15 | 1975 | 0.493 | old
2020 | SCE | Hsp | CZ15 | 1985 | 0.583 | old
2020 | SCE | Hsp | CZ15 | 1996 | 0.343 | old
2020 | SCE | Hsp | CZ15 | 2003 | 0.122 | ex
2020 | SCE | Hsp | CZ15 | 2007 | 0.096 | ex
2020 | SCE | Hsp | CZ15 | 2011 | 0.096 | ex
2020 | SCE | Hsp | CZ15 | 2015 | 0.072 | ex
2020 | SCE | Hsp | CZ15 | 2017 | 0.072 | rec
2020 | SCE | Hsp | CZ15 | 2020 | 0.024 | rec
2020 | SCE | Hsp | CZ15 | New | 0.024 | new
2020 | SCE | Hsp | CZ16 | 1975 | 0.329 | old
2020 | SCE | Hsp | CZ16 | 1985 | 0.361 | old
2020 | SCE | Hsp | CZ16 | 1996 | 0.224 | old
2020 | SCE | Hsp | CZ16 | 2003 | 0.074 | ex
2020 | SCE | Hsp | CZ16 | 2007 | 0.057 | ex
2020 | SCE | Hsp | CZ16 | 2011 | 0.057 | ex
2020 | SCE | Hsp | CZ16 | 2015 | 0.043 | ex
2020 | SCE | Hsp | CZ16 | 2017 | 0.043 | rec
2020 | SCE | Hsp | CZ16 | 2020 | 0.014 | rec
2020 | SCE | Hsp | CZ16 | New | 0.014 | new
2020 | SCE | Htl | CZ05 | 1975 | 0.052 | old
2020 | SCE | Htl | CZ05 | 1985 | 0.067 | old
2020 | SCE | Htl | CZ05 | 1996 | 0.018 | old
2020 | SCE | Htl | CZ05 | 2003 | 0.01 | ex
2020 | SCE | Htl | CZ05 | 2007 | 0.004 | ex
2020 | SCE | Htl | CZ05 | 2011 | 0.004 | ex
2020 | SCE | Htl | CZ05 | 2015 | 0.003 | ex
2020 | SCE | Htl | CZ05 | 2017 | 0.003 | rec
2020 | SCE | Htl | CZ05 | 2020 | 0.001 | rec
2020 | SCE | Htl | CZ05 | New | 0.001 | new
2020 | SCE | Htl | CZ06 | 1975 | 6.021 | old
2020 | SCE | Htl | CZ06 | 1985 | 7.873 | old
2020 | SCE | Htl | CZ06 | 1996 | 2.112 | old
2020 | SCE | Htl | CZ06 | 2003 | 1.144 | ex
2020 | SCE | Htl | CZ06 | 2007 | 0.48 | ex
2020 | SCE | Htl | CZ06 | 2011 | 0.48 | ex
2020 | SCE | Htl | CZ06 | 2015 | 0.36 | ex
2020 | SCE | Htl | CZ06 | 2017 | 0.36 | rec
2020 | SCE | Htl | CZ06 | 2020 | 0.12 | rec
2020 | SCE | Htl | CZ06 | New | 0.12 | new
2020 | SCE | Htl | CZ08 | 1975 | 3.884 | old
2020 | SCE | Htl | CZ08 | 1985 | 5.073 | old
2020 | SCE | Htl | CZ08 | 1996 | 1.36 | old
2020 | SCE | Htl | CZ08 | 2003 | 0.743 | ex
2020 | SCE | Htl | CZ08 | 2007 | 0.303 | ex
2020 | SCE | Htl | CZ08 | 2011 | 0.303 | ex
2020 | SCE | Htl | CZ08 | 2015 | 0.227 | ex
2020 | SCE | Htl | CZ08 | 2017 | 0.227 | rec
2020 | SCE | Htl | CZ08 | 2020 | 0.076 | rec
2020 | SCE | Htl | CZ08 | New | 0.076 | new
2020 | SCE | Htl | CZ09 | 1975 | 2.76 | old
2020 | SCE | Htl | CZ09 | 1985 | 3.681 | old
2020 | SCE | Htl | CZ09 | 1996 | 0.99 | old
2020 | SCE | Htl | CZ09 | 2003 | 0.471 | ex
2020 | SCE | Htl | CZ09 | 2007 | 0.301 | ex
2020 | SCE | Htl | CZ09 | 2011 | 0.301 | ex
2020 | SCE | Htl | CZ09 | 2015 | 0.226 | ex
2020 | SCE | Htl | CZ09 | 2017 | 0.226 | rec
2020 | SCE | Htl | CZ09 | 2020 | 0.075 | rec
2020 | SCE | Htl | CZ09 | New | 0.075 | new
2020 | SCE | Htl | CZ10 | 1975 | 0.484 | old
2020 | SCE | Htl | CZ10 | 1985 | 1.441 | old
2020 | SCE | Htl | CZ10 | 1996 | 0.25 | old
2020 | SCE | Htl | CZ10 | 2003 | 0.395 | ex
2020 | SCE | Htl | CZ10 | 2007 | 0.215 | ex
2020 | SCE | Htl | CZ10 | 2011 | 0.215 | ex
2020 | SCE | Htl | CZ10 | 2015 | 0.161 | ex
2020 | SCE | Htl | CZ10 | 2017 | 0.161 | rec
2020 | SCE | Htl | CZ10 | 2020 | 0.054 | rec
2020 | SCE | Htl | CZ10 | New | 0.054 | new
2020 | SCE | Htl | CZ13 | 1975 | 0.163 | old
2020 | SCE | Htl | CZ13 | 1985 | 0.21 | old
2020 | SCE | Htl | CZ13 | 1996 | 0.101 | old
2020 | SCE | Htl | CZ13 | 2003 | 0.031 | ex
2020 | SCE | Htl | CZ13 | 2007 | 0.03 | ex
2020 | SCE | Htl | CZ13 | 2011 | 0.03 | ex
2020 | SCE | Htl | CZ13 | 2015 | 0.022 | ex
2020 | SCE | Htl | CZ13 | 2017 | 0.022 | rec
2020 | SCE | Htl | CZ13 | 2020 | 0.008 | rec
2020 | SCE | Htl | CZ13 | New | 0.008 | new
2020 | SCE | Htl | CZ14 | 1975 | 0.32 | old
2020 | SCE | Htl | CZ14 | 1985 | 0.671 | old
2020 | SCE | Htl | CZ14 | 1996 | 0.146 | old
2020 | SCE | Htl | CZ14 | 2003 | 0.138 | ex
2020 | SCE | Htl | CZ14 | 2007 | 0.097 | ex
2020 | SCE | Htl | CZ14 | 2011 | 0.097 | ex
2020 | SCE | Htl | CZ14 | 2015 | 0.073 | ex
2020 | SCE | Htl | CZ14 | 2017 | 0.073 | rec
2020 | SCE | Htl | CZ14 | 2020 | 0.024 | rec
2020 | SCE | Htl | CZ14 | New | 0.024 | new
2020 | SCE | Htl | CZ15 | 1975 | 1.238 | old
2020 | SCE | Htl | CZ15 | 1985 | 3.686 | old
2020 | SCE | Htl | CZ15 | 1996 | 0.639 | old
2020 | SCE | Htl | CZ15 | 2003 | 1.009 | ex
2020 | SCE | Htl | CZ15 | 2007 | 0.549 | ex
2020 | SCE | Htl | CZ15 | 2011 | 0.549 | ex
2020 | SCE | Htl | CZ15 | 2015 | 0.412 | ex
2020 | SCE | Htl | CZ15 | 2017 | 0.412 | rec
2020 | SCE | Htl | CZ15 | 2020 | 0.137 | rec
2020 | SCE | Htl | CZ15 | New | 0.137 | new
2020 | SCE | Htl | CZ16 | 1975 | 0.564 | old
2020 | SCE | Htl | CZ16 | 1985 | 0.83 | old
2020 | SCE | Htl | CZ16 | 1996 | 0.259 | old
2020 | SCE | Htl | CZ16 | 2003 | 0.103 | ex
2020 | SCE | Htl | CZ16 | 2007 | 0.116 | ex
2020 | SCE | Htl | CZ16 | 2011 | 0.116 | ex
2020 | SCE | Htl | CZ16 | 2015 | 0.087 | ex
2020 | SCE | Htl | CZ16 | 2017 | 0.087 | rec
2020 | SCE | Htl | CZ16 | 2020 | 0.029 | rec
2020 | SCE | Htl | CZ16 | New | 0.029 | new
2020 | SCE | MBT | CZ05 | 1975 | 0.216 | old
2020 | SCE | MBT | CZ05 | 1985 | 0.115 | old
2020 | SCE | MBT | CZ05 | 1996 | 0.056 | old
2020 | SCE | MBT | CZ05 | 2003 | 0.028 | ex
2020 | SCE | MBT | CZ05 | 2007 | 0.018 | ex
2020 | SCE | MBT | CZ05 | 2011 | 0.018 | ex
2020 | SCE | MBT | CZ05 | 2015 | 0.013 | ex
2020 | SCE | MBT | CZ05 | 2017 | 0.013 | rec
2020 | SCE | MBT | CZ05 | 2020 | 0.004 | rec
2020 | SCE | MBT | CZ05 | New | 0.004 | new
2020 | SCE | MBT | CZ06 | 1975 | 18.175 | old
2020 | SCE | MBT | CZ06 | 1985 | 9.64 | old
2020 | SCE | MBT | CZ06 | 1996 | 4.695 | old
2020 | SCE | MBT | CZ06 | 2003 | 2.331 | ex
2020 | SCE | MBT | CZ06 | 2007 | 1.467 | ex
2020 | SCE | MBT | CZ06 | 2011 | 1.467 | ex
2020 | SCE | MBT | CZ06 | 2015 | 1.1 | ex
2020 | SCE | MBT | CZ06 | 2017 | 1.1 | rec
2020 | SCE | MBT | CZ06 | 2020 | 0.367 | rec
2020 | SCE | MBT | CZ06 | New | 0.367 | new
2020 | SCE | MBT | CZ08 | 1975 | 26.542 | old
2020 | SCE | MBT | CZ08 | 1985 | 14.036 | old
2020 | SCE | MBT | CZ08 | 1996 | 6.866 | old
2020 | SCE | MBT | CZ08 | 2003 | 3.418 | ex
2020 | SCE | MBT | CZ08 | 2007 | 2.135 | ex
2020 | SCE | MBT | CZ08 | 2011 | 2.135 | ex
2020 | SCE | MBT | CZ08 | 2015 | 1.601 | ex
2020 | SCE | MBT | CZ08 | 2017 | 1.601 | rec
2020 | SCE | MBT | CZ08 | 2020 | 0.534 | rec
2020 | SCE | MBT | CZ08 | New | 0.534 | new
2020 | SCE | MBT | CZ09 | 1975 | 12.478 | old
2020 | SCE | MBT | CZ09 | 1985 | 6.397 | old
2020 | SCE | MBT | CZ09 | 1996 | 3.274 | old
2020 | SCE | MBT | CZ09 | 2003 | 1.677 | ex
2020 | SCE | MBT | CZ09 | 2007 | 0.966 | ex
2020 | SCE | MBT | CZ09 | 2011 | 0.966 | ex
2020 | SCE | MBT | CZ09 | 2015 | 0.725 | ex
2020 | SCE | MBT | CZ09 | 2017 | 0.725 | rec
2020 | SCE | MBT | CZ09 | 2020 | 0.242 | rec
2020 | SCE | MBT | CZ09 | New | 0.242 | new
2020 | SCE | MBT | CZ10 | 1975 | 3.994 | old
2020 | SCE | MBT | CZ10 | 1985 | 9.306 | old
2020 | SCE | MBT | CZ10 | 1996 | 5.666 | old
2020 | SCE | MBT | CZ10 | 2003 | 5.288 | ex
2020 | SCE | MBT | CZ10 | 2007 | 2.938 | ex
2020 | SCE | MBT | CZ10 | 2011 | 2.938 | ex
2020 | SCE | MBT | CZ10 | 2015 | 2.204 | ex
2020 | SCE | MBT | CZ10 | 2017 | 2.204 | rec
2020 | SCE | MBT | CZ10 | 2020 | 0.735 | rec
2020 | SCE | MBT | CZ10 | New | 0.735 | new
2020 | SCE | MBT | CZ13 | 1975 | 0.899 | old
2020 | SCE | MBT | CZ13 | 1985 | 1.085 | old
2020 | SCE | MBT | CZ13 | 1996 | 0.903 | old
2020 | SCE | MBT | CZ13 | 2003 | 0.349 | ex
2020 | SCE | MBT | CZ13 | 2007 | 0.223 | ex
2020 | SCE | MBT | CZ13 | 2011 | 0.223 | ex
2020 | SCE | MBT | CZ13 | 2015 | 0.167 | ex
2020 | SCE | MBT | CZ13 | 2017 | 0.167 | rec
2020 | SCE | MBT | CZ13 | 2020 | 0.056 | rec
2020 | SCE | MBT | CZ13 | New | 0.056 | new
2020 | SCE | MBT | CZ14 | 1975 | 1.878 | old
2020 | SCE | MBT | CZ14 | 1985 | 1.916 | old
2020 | SCE | MBT | CZ14 | 1996 | 1.152 | old
2020 | SCE | MBT | CZ14 | 2003 | 0.877 | ex
2020 | SCE | MBT | CZ14 | 2007 | 0.486 | ex
2020 | SCE | MBT | CZ14 | 2011 | 0.486 | ex
2020 | SCE | MBT | CZ14 | 2015 | 0.364 | ex
2020 | SCE | MBT | CZ14 | 2017 | 0.364 | rec
2020 | SCE | MBT | CZ14 | 2020 | 0.122 | rec
2020 | SCE | MBT | CZ14 | New | 0.122 | new
2020 | SCE | MBT | CZ15 | 1975 | 1.446 | old
2020 | SCE | MBT | CZ15 | 1985 | 3.369 | old
2020 | SCE | MBT | CZ15 | 1996 | 2.051 | old
2020 | SCE | MBT | CZ15 | 2003 | 1.914 | ex
2020 | SCE | MBT | CZ15 | 2007 | 1.064 | ex
2020 | SCE | MBT | CZ15 | 2011 | 1.064 | ex
2020 | SCE | MBT | CZ15 | 2015 | 0.798 | ex
2020 | SCE | MBT | CZ15 | 2017 | 0.798 | rec
2020 | SCE | MBT | CZ15 | 2020 | 0.266 | rec
2020 | SCE | MBT | CZ15 | New | 0.266 | new
2020 | SCE | MBT | CZ16 | 1975 | 0.888 | old
2020 | SCE | MBT | CZ16 | 1985 | 1.175 | old
2020 | SCE | MBT | CZ16 | 1996 | 0.786 | old
2020 | SCE | MBT | CZ16 | 2003 | 0.535 | ex
2020 | SCE | MBT | CZ16 | 2007 | 0.306 | ex
2020 | SCE | MBT | CZ16 | 2011 | 0.306 | ex
2020 | SCE | MBT | CZ16 | 2015 | 0.23 | ex
2020 | SCE | MBT | CZ16 | 2017 | 0.23 | rec
2020 | SCE | MBT | CZ16 | 2020 | 0.077 | rec
2020 | SCE | MBT | CZ16 | New | 0.077 | new
2020 | SCE | MLI | CZ05 | 1975 | 0.216 | old
2020 | SCE | MLI | CZ05 | 1985 | 0.115 | old
2020 | SCE | MLI | CZ05 | 1996 | 0.056 | old
2020 | SCE | MLI | CZ05 | 2003 | 0.028 | ex
2020 | SCE | MLI | CZ05 | 2007 | 0.018 | ex
2020 | SCE | MLI | CZ05 | 2011 | 0.018 | ex
2020 | SCE | MLI | CZ05 | 2015 | 0.013 | ex
2020 | SCE | MLI | CZ05 | 2017 | 0.013 | rec
2020 | SCE | MLI | CZ05 | 2020 | 0.004 | rec
2020 | SCE | MLI | CZ05 | New | 0.004 | new
2020 | SCE | MLI | CZ06 | 1975 | 18.175 | old
2020 | SCE | MLI | CZ06 | 1985 | 9.64 | old
2020 | SCE | MLI | CZ06 | 1996 | 4.695 | old
2020 | SCE | MLI | CZ06 | 2003 | 2.331 | ex
2020 | SCE | MLI | CZ06 | 2007 | 1.467 | ex
2020 | SCE | MLI | CZ06 | 2011 | 1.467 | ex
2020 | SCE | MLI | CZ06 | 2015 | 1.1 | ex
2020 | SCE | MLI | CZ06 | 2017 | 1.1 | rec
2020 | SCE | MLI | CZ06 | 2020 | 0.367 | rec
2020 | SCE | MLI | CZ06 | New | 0.367 | new
2020 | SCE | MLI | CZ08 | 1975 | 26.542 | old
2020 | SCE | MLI | CZ08 | 1985 | 14.036 | old
2020 | SCE | MLI | CZ08 | 1996 | 6.866 | old
2020 | SCE | MLI | CZ08 | 2003 | 3.418 | ex
2020 | SCE | MLI | CZ08 | 2007 | 2.135 | ex
2020 | SCE | MLI | CZ08 | 2011 | 2.135 | ex
2020 | SCE | MLI | CZ08 | 2015 | 1.601 | ex
2020 | SCE | MLI | CZ08 | 2017 | 1.601 | rec
2020 | SCE | MLI | CZ08 | 2020 | 0.534 | rec
2020 | SCE | MLI | CZ08 | New | 0.534 | new
2020 | SCE | MLI | CZ09 | 1975 | 12.478 | old
2020 | SCE | MLI | CZ09 | 1985 | 6.397 | old
2020 | SCE | MLI | CZ09 | 1996 | 3.274 | old
2020 | SCE | MLI | CZ09 | 2003 | 1.677 | ex
2020 | SCE | MLI | CZ09 | 2007 | 0.966 | ex
2020 | SCE | MLI | CZ09 | 2011 | 0.966 | ex
2020 | SCE | MLI | CZ09 | 2015 | 0.725 | ex
2020 | SCE | MLI | CZ09 | 2017 | 0.725 | rec
2020 | SCE | MLI | CZ09 | 2020 | 0.242 | rec
2020 | SCE | MLI | CZ09 | New | 0.242 | new
2020 | SCE | MLI | CZ10 | 1975 | 3.994 | old
2020 | SCE | MLI | CZ10 | 1985 | 9.306 | old
2020 | SCE | MLI | CZ10 | 1996 | 5.666 | old
2020 | SCE | MLI | CZ10 | 2003 | 5.288 | ex
2020 | SCE | MLI | CZ10 | 2007 | 2.938 | ex
2020 | SCE | MLI | CZ10 | 2011 | 2.938 | ex
2020 | SCE | MLI | CZ10 | 2015 | 2.204 | ex
2020 | SCE | MLI | CZ10 | 2017 | 2.204 | rec
2020 | SCE | MLI | CZ10 | 2020 | 0.735 | rec
2020 | SCE | MLI | CZ10 | New | 0.735 | new
2020 | SCE | MLI | CZ13 | 1975 | 0.899 | old
2020 | SCE | MLI | CZ13 | 1985 | 1.085 | old
2020 | SCE | MLI | CZ13 | 1996 | 0.903 | old
2020 | SCE | MLI | CZ13 | 2003 | 0.349 | ex
2020 | SCE | MLI | CZ13 | 2007 | 0.223 | ex
2020 | SCE | MLI | CZ13 | 2011 | 0.223 | ex
2020 | SCE | MLI | CZ13 | 2015 | 0.167 | ex
2020 | SCE | MLI | CZ13 | 2017 | 0.167 | rec
2020 | SCE | MLI | CZ13 | 2020 | 0.056 | rec
2020 | SCE | MLI | CZ13 | New | 0.056 | new
2020 | SCE | MLI | CZ14 | 1975 | 1.878 | old
2020 | SCE | MLI | CZ14 | 1985 | 1.916 | old
2020 | SCE | MLI | CZ14 | 1996 | 1.152 | old
2020 | SCE | MLI | CZ14 | 2003 | 0.877 | ex
2020 | SCE | MLI | CZ14 | 2007 | 0.486 | ex
2020 | SCE | MLI | CZ14 | 2011 | 0.486 | ex
2020 | SCE | MLI | CZ14 | 2015 | 0.364 | ex
2020 | SCE | MLI | CZ14 | 2017 | 0.364 | rec
2020 | SCE | MLI | CZ14 | 2020 | 0.122 | rec
2020 | SCE | MLI | CZ14 | New | 0.122 | new
2020 | SCE | MLI | CZ15 | 1975 | 1.446 | old
2020 | SCE | MLI | CZ15 | 1985 | 3.369 | old
2020 | SCE | MLI | CZ15 | 1996 | 2.051 | old
2020 | SCE | MLI | CZ15 | 2003 | 1.914 | ex
2020 | SCE | MLI | CZ15 | 2007 | 1.064 | ex
2020 | SCE | MLI | CZ15 | 2011 | 1.064 | ex
2020 | SCE | MLI | CZ15 | 2015 | 0.798 | ex
2020 | SCE | MLI | CZ15 | 2017 | 0.798 | rec
2020 | SCE | MLI | CZ15 | 2020 | 0.266 | rec
2020 | SCE | MLI | CZ15 | New | 0.266 | new
2020 | SCE | MLI | CZ16 | 1975 | 0.888 | old
2020 | SCE | MLI | CZ16 | 1985 | 1.175 | old
2020 | SCE | MLI | CZ16 | 1996 | 0.786 | old
2020 | SCE | MLI | CZ16 | 2003 | 0.535 | ex
2020 | SCE | MLI | CZ16 | 2007 | 0.306 | ex
2020 | SCE | MLI | CZ16 | 2011 | 0.306 | ex
2020 | SCE | MLI | CZ16 | 2015 | 0.23 | ex
2020 | SCE | MLI | CZ16 | 2017 | 0.23 | rec
2020 | SCE | MLI | CZ16 | 2020 | 0.077 | rec
2020 | SCE | MLI | CZ16 | New | 0.077 | new
2020 | SCE | Mtl | CZ05 | 1975 | 0.052 | old
2020 | SCE | Mtl | CZ05 | 1985 | 0.067 | old
2020 | SCE | Mtl | CZ05 | 1996 | 0.018 | old
2020 | SCE | Mtl | CZ05 | 2003 | 0.01 | ex
2020 | SCE | Mtl | CZ05 | 2007 | 0.004 | ex
2020 | SCE | Mtl | CZ05 | 2011 | 0.004 | ex
2020 | SCE | Mtl | CZ05 | 2015 | 0.003 | ex
2020 | SCE | Mtl | CZ05 | 2017 | 0.003 | rec
2020 | SCE | Mtl | CZ05 | 2020 | 0.001 | rec
2020 | SCE | Mtl | CZ05 | New | 0.001 | new
2020 | SCE | Mtl | CZ06 | 1975 | 6.021 | old
2020 | SCE | Mtl | CZ06 | 1985 | 7.873 | old
2020 | SCE | Mtl | CZ06 | 1996 | 2.112 | old
2020 | SCE | Mtl | CZ06 | 2003 | 1.144 | ex
2020 | SCE | Mtl | CZ06 | 2007 | 0.48 | ex
2020 | SCE | Mtl | CZ06 | 2011 | 0.48 | ex
2020 | SCE | Mtl | CZ06 | 2015 | 0.36 | ex
2020 | SCE | Mtl | CZ06 | 2017 | 0.36 | rec
2020 | SCE | Mtl | CZ06 | 2020 | 0.12 | rec
2020 | SCE | Mtl | CZ06 | New | 0.12 | new
2020 | SCE | Mtl | CZ08 | 1975 | 3.884 | old
2020 | SCE | Mtl | CZ08 | 1985 | 5.073 | old
2020 | SCE | Mtl | CZ08 | 1996 | 1.36 | old
2020 | SCE | Mtl | CZ08 | 2003 | 0.743 | ex
2020 | SCE | Mtl | CZ08 | 2007 | 0.303 | ex
2020 | SCE | Mtl | CZ08 | 2011 | 0.303 | ex
2020 | SCE | Mtl | CZ08 | 2015 | 0.227 | ex
2020 | SCE | Mtl | CZ08 | 2017 | 0.227 | rec
2020 | SCE | Mtl | CZ08 | 2020 | 0.076 | rec
2020 | SCE | Mtl | CZ08 | New | 0.076 | new
2020 | SCE | Mtl | CZ09 | 1975 | 2.76 | old
2020 | SCE | Mtl | CZ09 | 1985 | 3.681 | old
2020 | SCE | Mtl | CZ09 | 1996 | 0.99 | old
2020 | SCE | Mtl | CZ09 | 2003 | 0.471 | ex
2020 | SCE | Mtl | CZ09 | 2007 | 0.301 | ex
2020 | SCE | Mtl | CZ09 | 2011 | 0.301 | ex
2020 | SCE | Mtl | CZ09 | 2015 | 0.226 | ex
2020 | SCE | Mtl | CZ09 | 2017 | 0.226 | rec
2020 | SCE | Mtl | CZ09 | 2020 | 0.075 | rec
2020 | SCE | Mtl | CZ09 | New | 0.075 | new
2020 | SCE | Mtl | CZ10 | 1975 | 0.484 | old
2020 | SCE | Mtl | CZ10 | 1985 | 1.441 | old
2020 | SCE | Mtl | CZ10 | 1996 | 0.25 | old
2020 | SCE | Mtl | CZ10 | 2003 | 0.395 | ex
2020 | SCE | Mtl | CZ10 | 2007 | 0.215 | ex
2020 | SCE | Mtl | CZ10 | 2011 | 0.215 | ex
2020 | SCE | Mtl | CZ10 | 2015 | 0.161 | ex
2020 | SCE | Mtl | CZ10 | 2017 | 0.161 | rec
2020 | SCE | Mtl | CZ10 | 2020 | 0.054 | rec
2020 | SCE | Mtl | CZ10 | New | 0.054 | new
2020 | SCE | Mtl | CZ13 | 1975 | 0.163 | old
2020 | SCE | Mtl | CZ13 | 1985 | 0.21 | old
2020 | SCE | Mtl | CZ13 | 1996 | 0.101 | old
2020 | SCE | Mtl | CZ13 | 2003 | 0.031 | ex
2020 | SCE | Mtl | CZ13 | 2007 | 0.03 | ex
2020 | SCE | Mtl | CZ13 | 2011 | 0.03 | ex
2020 | SCE | Mtl | CZ13 | 2015 | 0.022 | ex
2020 | SCE | Mtl | CZ13 | 2017 | 0.022 | rec
2020 | SCE | Mtl | CZ13 | 2020 | 0.008 | rec
2020 | SCE | Mtl | CZ13 | New | 0.008 | new
2020 | SCE | Mtl | CZ14 | 1975 | 0.32 | old
2020 | SCE | Mtl | CZ14 | 1985 | 0.671 | old
2020 | SCE | Mtl | CZ14 | 1996 | 0.146 | old
2020 | SCE | Mtl | CZ14 | 2003 | 0.138 | ex
2020 | SCE | Mtl | CZ14 | 2007 | 0.097 | ex
2020 | SCE | Mtl | CZ14 | 2011 | 0.097 | ex
2020 | SCE | Mtl | CZ14 | 2015 | 0.073 | ex
2020 | SCE | Mtl | CZ14 | 2017 | 0.073 | rec
2020 | SCE | Mtl | CZ14 | 2020 | 0.024 | rec
2020 | SCE | Mtl | CZ14 | New | 0.024 | new
2020 | SCE | Mtl | CZ15 | 1975 | 1.238 | old
2020 | SCE | Mtl | CZ15 | 1985 | 3.686 | old
2020 | SCE | Mtl | CZ15 | 1996 | 0.639 | old
2020 | SCE | Mtl | CZ15 | 2003 | 1.009 | ex
2020 | SCE | Mtl | CZ15 | 2007 | 0.549 | ex
2020 | SCE | Mtl | CZ15 | 2011 | 0.549 | ex
2020 | SCE | Mtl | CZ15 | 2015 | 0.412 | ex
2020 | SCE | Mtl | CZ15 | 2017 | 0.412 | rec
2020 | SCE | Mtl | CZ15 | 2020 | 0.137 | rec
2020 | SCE | Mtl | CZ15 | New | 0.137 | new
2020 | SCE | Mtl | CZ16 | 1975 | 0.564 | old
2020 | SCE | Mtl | CZ16 | 1985 | 0.83 | old
2020 | SCE | Mtl | CZ16 | 1996 | 0.259 | old
2020 | SCE | Mtl | CZ16 | 2003 | 0.103 | ex
2020 | SCE | Mtl | CZ16 | 2007 | 0.116 | ex
2020 | SCE | Mtl | CZ16 | 2011 | 0.116 | ex
2020 | SCE | Mtl | CZ16 | 2015 | 0.087 | ex
2020 | SCE | Mtl | CZ16 | 2017 | 0.087 | rec
2020 | SCE | Mtl | CZ16 | 2020 | 0.029 | rec
2020 | SCE | Mtl | CZ16 | New | 0.029 | new
2020 | SCE | Nrs | CZ05 | 1975 | 0.449 | old
2020 | SCE | Nrs | CZ05 | 1985 | 0.306 | old
2020 | SCE | Nrs | CZ05 | 1996 | 0.091 | old
2020 | SCE | Nrs | CZ05 | 2003 | 0.083 | ex
2020 | SCE | Nrs | CZ05 | 2007 | 0.025 | ex
2020 | SCE | Nrs | CZ05 | 2011 | 0.025 | ex
2020 | SCE | Nrs | CZ05 | 2015 | 0.019 | ex
2020 | SCE | Nrs | CZ05 | 2017 | 0.019 | rec
2020 | SCE | Nrs | CZ05 | 2020 | 0.006 | rec
2020 | SCE | Nrs | CZ05 | New | 0.006 | new
2020 | SCE | Nrs | CZ06 | 1975 | 6.752 | old
2020 | SCE | Nrs | CZ06 | 1985 | 4.462 | old
2020 | SCE | Nrs | CZ06 | 1996 | 1.357 | old
2020 | SCE | Nrs | CZ06 | 2003 | 1.244 | ex
2020 | SCE | Nrs | CZ06 | 2007 | 0.392 | ex
2020 | SCE | Nrs | CZ06 | 2011 | 0.392 | ex
2020 | SCE | Nrs | CZ06 | 2015 | 0.294 | ex
2020 | SCE | Nrs | CZ06 | 2017 | 0.294 | rec
2020 | SCE | Nrs | CZ06 | 2020 | 0.098 | rec
2020 | SCE | Nrs | CZ06 | New | 0.098 | new
2020 | SCE | Nrs | CZ08 | 1975 | 7.214 | old
2020 | SCE | Nrs | CZ08 | 1985 | 4.719 | old
2020 | SCE | Nrs | CZ08 | 1996 | 1.444 | old
2020 | SCE | Nrs | CZ08 | 2003 | 1.327 | ex
2020 | SCE | Nrs | CZ08 | 2007 | 0.425 | ex
2020 | SCE | Nrs | CZ08 | 2011 | 0.425 | ex
2020 | SCE | Nrs | CZ08 | 2015 | 0.319 | ex
2020 | SCE | Nrs | CZ08 | 2017 | 0.319 | rec
2020 | SCE | Nrs | CZ08 | 2020 | 0.106 | rec
2020 | SCE | Nrs | CZ08 | New | 0.106 | new
2020 | SCE | Nrs | CZ09 | 1975 | 3.813 | old
2020 | SCE | Nrs | CZ09 | 1985 | 2.085 | old
2020 | SCE | Nrs | CZ09 | 1996 | 0.713 | old
2020 | SCE | Nrs | CZ09 | 2003 | 0.687 | ex
2020 | SCE | Nrs | CZ09 | 2007 | 0.27 | ex
2020 | SCE | Nrs | CZ09 | 2011 | 0.27 | ex
2020 | SCE | Nrs | CZ09 | 2015 | 0.203 | ex
2020 | SCE | Nrs | CZ09 | 2017 | 0.203 | rec
2020 | SCE | Nrs | CZ09 | 2020 | 0.068 | rec
2020 | SCE | Nrs | CZ09 | New | 0.068 | new
2020 | SCE | Nrs | CZ10 | 1975 | 2.381 | old
2020 | SCE | Nrs | CZ10 | 1985 | 2.816 | old
2020 | SCE | Nrs | CZ10 | 1996 | 1.657 | old
2020 | SCE | Nrs | CZ10 | 2003 | 0.589 | ex
2020 | SCE | Nrs | CZ10 | 2007 | 0.463 | ex
2020 | SCE | Nrs | CZ10 | 2011 | 0.463 | ex
2020 | SCE | Nrs | CZ10 | 2015 | 0.347 | ex
2020 | SCE | Nrs | CZ10 | 2017 | 0.347 | rec
2020 | SCE | Nrs | CZ10 | 2020 | 0.116 | rec
2020 | SCE | Nrs | CZ10 | New | 0.116 | new
2020 | SCE | Nrs | CZ13 | 1975 | 0.438 | old
2020 | SCE | Nrs | CZ13 | 1985 | 0.51 | old
2020 | SCE | Nrs | CZ13 | 1996 | 0.423 | old
2020 | SCE | Nrs | CZ13 | 2003 | 0.077 | ex
2020 | SCE | Nrs | CZ13 | 2007 | 0.071 | ex
2020 | SCE | Nrs | CZ13 | 2011 | 0.071 | ex
2020 | SCE | Nrs | CZ13 | 2015 | 0.053 | ex
2020 | SCE | Nrs | CZ13 | 2017 | 0.053 | rec
2020 | SCE | Nrs | CZ13 | 2020 | 0.018 | rec
2020 | SCE | Nrs | CZ13 | New | 0.018 | new
2020 | SCE | Nrs | CZ14 | 1975 | 0.522 | old
2020 | SCE | Nrs | CZ14 | 1985 | 0.463 | old
2020 | SCE | Nrs | CZ14 | 1996 | 0.246 | old
2020 | SCE | Nrs | CZ14 | 2003 | 0.113 | ex
2020 | SCE | Nrs | CZ14 | 2007 | 0.074 | ex
2020 | SCE | Nrs | CZ14 | 2011 | 0.074 | ex
2020 | SCE | Nrs | CZ14 | 2015 | 0.056 | ex
2020 | SCE | Nrs | CZ14 | 2017 | 0.056 | rec
2020 | SCE | Nrs | CZ14 | 2020 | 0.019 | rec
2020 | SCE | Nrs | CZ14 | New | 0.019 | new
2020 | SCE | Nrs | CZ15 | 1975 | 0.493 | old
2020 | SCE | Nrs | CZ15 | 1985 | 0.583 | old
2020 | SCE | Nrs | CZ15 | 1996 | 0.343 | old
2020 | SCE | Nrs | CZ15 | 2003 | 0.122 | ex
2020 | SCE | Nrs | CZ15 | 2007 | 0.096 | ex
2020 | SCE | Nrs | CZ15 | 2011 | 0.096 | ex
2020 | SCE | Nrs | CZ15 | 2015 | 0.072 | ex
2020 | SCE | Nrs | CZ15 | 2017 | 0.072 | rec
2020 | SCE | Nrs | CZ15 | 2020 | 0.024 | rec
2020 | SCE | Nrs | CZ15 | New | 0.024 | new
2020 | SCE | Nrs | CZ16 | 1975 | 0.329 | old
2020 | SCE | Nrs | CZ16 | 1985 | 0.361 | old
2020 | SCE | Nrs | CZ16 | 1996 | 0.224 | old
2020 | SCE | Nrs | CZ16 | 2003 | 0.074 | ex
2020 | SCE | Nrs | CZ16 | 2007 | 0.057 | ex
2020 | SCE | Nrs | CZ16 | 2011 | 0.057 | ex
2020 | SCE | Nrs | CZ16 | 2015 | 0.043 | ex
2020 | SCE | Nrs | CZ16 | 2017 | 0.043 | rec
2020 | SCE | Nrs | CZ16 | 2020 | 0.014 | rec
2020 | SCE | Nrs | CZ16 | New | 0.014 | new
2020 | SCE | OfL | CZ05 | 1975 | 0.491 | old
2020 | SCE | OfL | CZ05 | 1985 | 0.617 | old
2020 | SCE | OfL | CZ05 | 1996 | 0.117 | old
2020 | SCE | OfL | CZ05 | 2003 | 0.062 | ex
2020 | SCE | OfL | CZ05 | 2007 | 0.021 | ex
2020 | SCE | OfL | CZ05 | 2011 | 0.021 | ex
2020 | SCE | OfL | CZ05 | 2015 | 0.016 | ex
2020 | SCE | OfL | CZ05 | 2017 | 0.016 | rec
2020 | SCE | OfL | CZ05 | 2020 | 0.005 | rec
2020 | SCE | OfL | CZ05 | New | 0.005 | new
2020 | SCE | OfL | CZ06 | 1975 | 44.014 | old
2020 | SCE | OfL | CZ06 | 1985 | 55.204 | old
2020 | SCE | OfL | CZ06 | 1996 | 10.214 | old
2020 | SCE | OfL | CZ06 | 2003 | 5.519 | ex
2020 | SCE | OfL | CZ06 | 2007 | 2.16 | ex
2020 | SCE | OfL | CZ06 | 2011 | 2.16 | ex
2020 | SCE | OfL | CZ06 | 2015 | 1.62 | ex
2020 | SCE | OfL | CZ06 | 2017 | 1.62 | rec
2020 | SCE | OfL | CZ06 | 2020 | 0.54 | rec
2020 | SCE | OfL | CZ06 | New | 0.54 | new
2020 | SCE | OfL | CZ08 | 1975 | 53.51 | old
2020 | SCE | OfL | CZ08 | 1985 | 67.081 | old
2020 | SCE | OfL | CZ08 | 1996 | 12.348 | old
2020 | SCE | OfL | CZ08 | 2003 | 6.69 | ex
2020 | SCE | OfL | CZ08 | 2007 | 2.691 | ex
2020 | SCE | OfL | CZ08 | 2011 | 2.691 | ex
2020 | SCE | OfL | CZ08 | 2015 | 2.018 | ex
2020 | SCE | OfL | CZ08 | 2017 | 2.018 | rec
2020 | SCE | OfL | CZ08 | 2020 | 0.673 | rec
2020 | SCE | OfL | CZ08 | New | 0.673 | new
2020 | SCE | OfL | CZ09 | 1975 | 32.47 | old
2020 | SCE | OfL | CZ09 | 1985 | 40.31 | old
2020 | SCE | OfL | CZ09 | 1996 | 6.688 | old
2020 | SCE | OfL | CZ09 | 2003 | 3.84 | ex
2020 | SCE | OfL | CZ09 | 2007 | 2.39 | ex
2020 | SCE | OfL | CZ09 | 2011 | 2.39 | ex
2020 | SCE | OfL | CZ09 | 2015 | 1.792 | ex
2020 | SCE | OfL | CZ09 | 2017 | 1.792 | rec
2020 | SCE | OfL | CZ09 | 2020 | 0.597 | rec
2020 | SCE | OfL | CZ09 | New | 0.597 | new
2020 | SCE | OfL | CZ10 | 1975 | 8.506 | old
2020 | SCE | OfL | CZ10 | 1985 | 13.454 | old
2020 | SCE | OfL | CZ10 | 1996 | 3.573 | old
2020 | SCE | OfL | CZ10 | 2003 | 4.559 | ex
2020 | SCE | OfL | CZ10 | 2007 | 2.127 | ex
2020 | SCE | OfL | CZ10 | 2011 | 2.127 | ex
2020 | SCE | OfL | CZ10 | 2015 | 1.595 | ex
2020 | SCE | OfL | CZ10 | 2017 | 1.595 | rec
2020 | SCE | OfL | CZ10 | 2020 | 0.532 | rec
2020 | SCE | OfL | CZ10 | New | 0.532 | new
2020 | SCE | OfL | CZ13 | 1975 | 1.388 | old
2020 | SCE | OfL | CZ13 | 1985 | 1.545 | old
2020 | SCE | OfL | CZ13 | 1996 | 0.36 | old
2020 | SCE | OfL | CZ13 | 2003 | 0.167 | ex
2020 | SCE | OfL | CZ13 | 2007 | 0.196 | ex
2020 | SCE | OfL | CZ13 | 2011 | 0.196 | ex
2020 | SCE | OfL | CZ13 | 2015 | 0.147 | ex
2020 | SCE | OfL | CZ13 | 2017 | 0.147 | rec
2020 | SCE | OfL | CZ13 | 2020 | 0.049 | rec
2020 | SCE | OfL | CZ13 | New | 0.049 | new
2020 | SCE | OfL | CZ14 | 1975 | 2.454 | old
2020 | SCE | OfL | CZ14 | 1985 | 3.33 | old
2020 | SCE | OfL | CZ14 | 1996 | 0.664 | old
2020 | SCE | OfL | CZ14 | 2003 | 0.659 | ex
2020 | SCE | OfL | CZ14 | 2007 | 0.381 | ex
2020 | SCE | OfL | CZ14 | 2011 | 0.381 | ex
2020 | SCE | OfL | CZ14 | 2015 | 0.286 | ex
2020 | SCE | OfL | CZ14 | 2017 | 0.286 | rec
2020 | SCE | OfL | CZ14 | 2020 | 0.095 | rec
2020 | SCE | OfL | CZ14 | New | 0.095 | new
2020 | SCE | OfL | CZ15 | 1975 | 2.324 | old
2020 | SCE | OfL | CZ15 | 1985 | 3.677 | old
2020 | SCE | OfL | CZ15 | 1996 | 0.976 | old
2020 | SCE | OfL | CZ15 | 2003 | 1.246 | ex
2020 | SCE | OfL | CZ15 | 2007 | 0.581 | ex
2020 | SCE | OfL | CZ15 | 2011 | 0.581 | ex
2020 | SCE | OfL | CZ15 | 2015 | 0.436 | ex
2020 | SCE | OfL | CZ15 | 2017 | 0.436 | rec
2020 | SCE | OfL | CZ15 | 2020 | 0.145 | rec
2020 | SCE | OfL | CZ15 | New | 0.145 | new
2020 | SCE | OfL | CZ16 | 1975 | 1.177 | old
2020 | SCE | OfL | CZ16 | 1985 | 1.533 | old
2020 | SCE | OfL | CZ16 | 1996 | 0.302 | old
2020 | SCE | OfL | CZ16 | 2003 | 0.265 | ex
2020 | SCE | OfL | CZ16 | 2007 | 0.171 | ex
2020 | SCE | OfL | CZ16 | 2011 | 0.171 | ex
2020 | SCE | OfL | CZ16 | 2015 | 0.129 | ex
2020 | SCE | OfL | CZ16 | 2017 | 0.129 | rec
2020 | SCE | OfL | CZ16 | 2020 | 0.043 | rec
2020 | SCE | OfL | CZ16 | New | 0.043 | new
2020 | SCE | OfS | CZ05 | 1975 | 0.161 | old
2020 | SCE | OfS | CZ05 | 1985 | 0.09 | old
2020 | SCE | OfS | CZ05 | 1996 | 0.034 | old
2020 | SCE | OfS | CZ05 | 2003 | 0.013 | ex
2020 | SCE | OfS | CZ05 | 2007 | 0.012 | ex
2020 | SCE | OfS | CZ05 | 2011 | 0.012 | ex
2020 | SCE | OfS | CZ05 | 2015 | 0.009 | ex
2020 | SCE | OfS | CZ05 | 2017 | 0.009 | rec
2020 | SCE | OfS | CZ05 | 2020 | 0.003 | rec
2020 | SCE | OfS | CZ05 | New | 0.003 | new
2020 | SCE | OfS | CZ06 | 1975 | 13.919 | old
2020 | SCE | OfS | CZ06 | 1985 | 7.758 | old
2020 | SCE | OfS | CZ06 | 1996 | 2.985 | old
2020 | SCE | OfS | CZ06 | 2003 | 1.21 | ex
2020 | SCE | OfS | CZ06 | 2007 | 1.039 | ex
2020 | SCE | OfS | CZ06 | 2011 | 1.039 | ex
2020 | SCE | OfS | CZ06 | 2015 | 0.779 | ex
2020 | SCE | OfS | CZ06 | 2017 | 0.779 | rec
2020 | SCE | OfS | CZ06 | 2020 | 0.26 | rec
2020 | SCE | OfS | CZ06 | New | 0.26 | new
2020 | SCE | OfS | CZ08 | 1975 | 16.797 | old
2020 | SCE | OfS | CZ08 | 1985 | 9.355 | old
2020 | SCE | OfS | CZ08 | 1996 | 3.618 | old
2020 | SCE | OfS | CZ08 | 2003 | 1.473 | ex
2020 | SCE | OfS | CZ08 | 2007 | 1.254 | ex
2020 | SCE | OfS | CZ08 | 2011 | 1.254 | ex
2020 | SCE | OfS | CZ08 | 2015 | 0.94 | ex
2020 | SCE | OfS | CZ08 | 2017 | 0.94 | rec
2020 | SCE | OfS | CZ08 | 2020 | 0.314 | rec
2020 | SCE | OfS | CZ08 | New | 0.314 | new
2020 | SCE | OfS | CZ09 | 1975 | 8.748 | old
2020 | SCE | OfS | CZ09 | 1985 | 4.784 | old
2020 | SCE | OfS | CZ09 | 1996 | 2.068 | old
2020 | SCE | OfS | CZ09 | 2003 | 0.917 | ex
2020 | SCE | OfS | CZ09 | 2007 | 0.656 | ex
2020 | SCE | OfS | CZ09 | 2011 | 0.656 | ex
2020 | SCE | OfS | CZ09 | 2015 | 0.492 | ex
2020 | SCE | OfS | CZ09 | 2017 | 0.492 | rec
2020 | SCE | OfS | CZ09 | 2020 | 0.164 | rec
2020 | SCE | OfS | CZ09 | New | 0.164 | new
2020 | SCE | OfS | CZ10 | 1975 | 8.314 | old
2020 | SCE | OfS | CZ10 | 1985 | 7.781 | old
2020 | SCE | OfS | CZ10 | 1996 | 4.149 | old
2020 | SCE | OfS | CZ10 | 2003 | 3.04 | ex
2020 | SCE | OfS | CZ10 | 2007 | 1.581 | ex
2020 | SCE | OfS | CZ10 | 2011 | 1.581 | ex
2020 | SCE | OfS | CZ10 | 2015 | 1.186 | ex
2020 | SCE | OfS | CZ10 | 2017 | 1.186 | rec
2020 | SCE | OfS | CZ10 | 2020 | 0.395 | rec
2020 | SCE | OfS | CZ10 | New | 0.395 | new
2020 | SCE | OfS | CZ13 | 1975 | 2.712 | old
2020 | SCE | OfS | CZ13 | 1985 | 1.513 | old
2020 | SCE | OfS | CZ13 | 1996 | 0.856 | old
2020 | SCE | OfS | CZ13 | 2003 | 0.403 | ex
2020 | SCE | OfS | CZ13 | 2007 | 0.237 | ex
2020 | SCE | OfS | CZ13 | 2011 | 0.237 | ex
2020 | SCE | OfS | CZ13 | 2015 | 0.178 | ex
2020 | SCE | OfS | CZ13 | 2017 | 0.178 | rec
2020 | SCE | OfS | CZ13 | 2020 | 0.059 | rec
2020 | SCE | OfS | CZ13 | New | 0.059 | new
2020 | SCE | OfS | CZ14 | 1975 | 1.324 | old
2020 | SCE | OfS | CZ14 | 1985 | 1.066 | old
2020 | SCE | OfS | CZ14 | 1996 | 0.565 | old
2020 | SCE | OfS | CZ14 | 2003 | 0.383 | ex
2020 | SCE | OfS | CZ14 | 2007 | 0.203 | ex
2020 | SCE | OfS | CZ14 | 2011 | 0.203 | ex
2020 | SCE | OfS | CZ14 | 2015 | 0.152 | ex
2020 | SCE | OfS | CZ14 | 2017 | 0.152 | rec
2020 | SCE | OfS | CZ14 | 2020 | 0.051 | rec
2020 | SCE | OfS | CZ14 | New | 0.051 | new
2020 | SCE | OfS | CZ15 | 1975 | 2.272 | old
2020 | SCE | OfS | CZ15 | 1985 | 2.126 | old
2020 | SCE | OfS | CZ15 | 1996 | 1.134 | old
2020 | SCE | OfS | CZ15 | 2003 | 0.831 | ex
2020 | SCE | OfS | CZ15 | 2007 | 0.432 | ex
2020 | SCE | OfS | CZ15 | 2011 | 0.432 | ex
2020 | SCE | OfS | CZ15 | 2015 | 0.324 | ex
2020 | SCE | OfS | CZ15 | 2017 | 0.324 | rec
2020 | SCE | OfS | CZ15 | 2020 | 0.108 | rec
2020 | SCE | OfS | CZ15 | New | 0.108 | new
2020 | SCE | OfS | CZ16 | 1975 | 0.837 | old
2020 | SCE | OfS | CZ16 | 1985 | 0.578 | old
2020 | SCE | OfS | CZ16 | 1996 | 0.313 | old
2020 | SCE | OfS | CZ16 | 2003 | 0.188 | ex
2020 | SCE | OfS | CZ16 | 2007 | 0.103 | ex
2020 | SCE | OfS | CZ16 | 2011 | 0.103 | ex
2020 | SCE | OfS | CZ16 | 2015 | 0.077 | ex
2020 | SCE | OfS | CZ16 | 2017 | 0.077 | rec
2020 | SCE | OfS | CZ16 | 2020 | 0.026 | rec
2020 | SCE | OfS | CZ16 | New | 0.026 | new
2020 | SCE | RFF | CZ05 | 1975 | 0.051 | old
2020 | SCE | RFF | CZ05 | 1985 | 0.048 | old
2020 | SCE | RFF | CZ05 | 1996 | 0.019 | old
2020 | SCE | RFF | CZ05 | 2003 | 0.008 | ex
2020 | SCE | RFF | CZ05 | 2007 | 0.007 | ex
2020 | SCE | RFF | CZ05 | 2011 | 0.007 | ex
2020 | SCE | RFF | CZ05 | 2015 | 0.005 | ex
2020 | SCE | RFF | CZ05 | 2017 | 0.005 | rec
2020 | SCE | RFF | CZ05 | 2020 | 0.002 | rec
2020 | SCE | RFF | CZ05 | New | 0.002 | new
2020 | SCE | RFF | CZ06 | 1975 | 3.533 | old
2020 | SCE | RFF | CZ06 | 1985 | 3.29 | old
2020 | SCE | RFF | CZ06 | 1996 | 1.299 | old
2020 | SCE | RFF | CZ06 | 2003 | 0.557 | ex
2020 | SCE | RFF | CZ06 | 2007 | 0.489 | ex
2020 | SCE | RFF | CZ06 | 2011 | 0.489 | ex
2020 | SCE | RFF | CZ06 | 2015 | 0.367 | ex
2020 | SCE | RFF | CZ06 | 2017 | 0.367 | rec
2020 | SCE | RFF | CZ06 | 2020 | 0.122 | rec
2020 | SCE | RFF | CZ06 | New | 0.122 | new
2020 | SCE | RFF | CZ08 | 1975 | 4.068 | old
2020 | SCE | RFF | CZ08 | 1985 | 3.777 | old
2020 | SCE | RFF | CZ08 | 1996 | 1.488 | old
2020 | SCE | RFF | CZ08 | 2003 | 0.664 | ex
2020 | SCE | RFF | CZ08 | 2007 | 0.552 | ex
2020 | SCE | RFF | CZ08 | 2011 | 0.552 | ex
2020 | SCE | RFF | CZ08 | 2015 | 0.414 | ex
2020 | SCE | RFF | CZ08 | 2017 | 0.414 | rec
2020 | SCE | RFF | CZ08 | 2020 | 0.138 | rec
2020 | SCE | RFF | CZ08 | New | 0.138 | new
2020 | SCE | RFF | CZ09 | 1975 | 2.281 | old
2020 | SCE | RFF | CZ09 | 1985 | 2.088 | old
2020 | SCE | RFF | CZ09 | 1996 | 0.812 | old
2020 | SCE | RFF | CZ09 | 2003 | 0.438 | ex
2020 | SCE | RFF | CZ09 | 2007 | 0.277 | ex
2020 | SCE | RFF | CZ09 | 2011 | 0.277 | ex
2020 | SCE | RFF | CZ09 | 2015 | 0.207 | ex
2020 | SCE | RFF | CZ09 | 2017 | 0.207 | rec
2020 | SCE | RFF | CZ09 | 2020 | 0.069 | rec
2020 | SCE | RFF | CZ09 | New | 0.069 | new
2020 | SCE | RFF | CZ10 | 1975 | 1.682 | old
2020 | SCE | RFF | CZ10 | 1985 | 3.155 | old
2020 | SCE | RFF | CZ10 | 1996 | 1.726 | old
2020 | SCE | RFF | CZ10 | 2003 | 1.892 | ex
2020 | SCE | RFF | CZ10 | 2007 | 0.643 | ex
2020 | SCE | RFF | CZ10 | 2011 | 0.643 | ex
2020 | SCE | RFF | CZ10 | 2015 | 0.482 | ex
2020 | SCE | RFF | CZ10 | 2017 | 0.482 | rec
2020 | SCE | RFF | CZ10 | 2020 | 0.161 | rec
2020 | SCE | RFF | CZ10 | New | 0.161 | new
2020 | SCE | RFF | CZ13 | 1975 | 0.209 | old
2020 | SCE | RFF | CZ13 | 1985 | 0.22 | old
2020 | SCE | RFF | CZ13 | 1996 | 0.17 | old
2020 | SCE | RFF | CZ13 | 2003 | 0.088 | ex
2020 | SCE | RFF | CZ13 | 2007 | 0.044 | ex
2020 | SCE | RFF | CZ13 | 2011 | 0.044 | ex
2020 | SCE | RFF | CZ13 | 2015 | 0.033 | ex
2020 | SCE | RFF | CZ13 | 2017 | 0.033 | rec
2020 | SCE | RFF | CZ13 | 2020 | 0.011 | rec
2020 | SCE | RFF | CZ13 | New | 0.011 | new
2020 | SCE | RFF | CZ14 | 1975 | 0.433 | old
2020 | SCE | RFF | CZ14 | 1985 | 0.659 | old
2020 | SCE | RFF | CZ14 | 1996 | 0.345 | old
2020 | SCE | RFF | CZ14 | 2003 | 0.348 | ex
2020 | SCE | RFF | CZ14 | 2007 | 0.123 | ex
2020 | SCE | RFF | CZ14 | 2011 | 0.123 | ex
2020 | SCE | RFF | CZ14 | 2015 | 0.092 | ex
2020 | SCE | RFF | CZ14 | 2017 | 0.092 | rec
2020 | SCE | RFF | CZ14 | 2020 | 0.031 | rec
2020 | SCE | RFF | CZ14 | New | 0.031 | new
2020 | SCE | RFF | CZ15 | 1975 | 0.329 | old
2020 | SCE | RFF | CZ15 | 1985 | 0.617 | old
2020 | SCE | RFF | CZ15 | 1996 | 0.338 | old
2020 | SCE | RFF | CZ15 | 2003 | 0.37 | ex
2020 | SCE | RFF | CZ15 | 2007 | 0.126 | ex
2020 | SCE | RFF | CZ15 | 2011 | 0.126 | ex
2020 | SCE | RFF | CZ15 | 2015 | 0.094 | ex
2020 | SCE | RFF | CZ15 | 2017 | 0.094 | rec
2020 | SCE | RFF | CZ15 | 2020 | 0.031 | rec
2020 | SCE | RFF | CZ15 | New | 0.031 | new
2020 | SCE | RFF | CZ16 | 1975 | 0.173 | old
2020 | SCE | RFF | CZ16 | 1985 | 0.248 | old
2020 | SCE | RFF | CZ16 | 1996 | 0.142 | old
2020 | SCE | RFF | CZ16 | 2003 | 0.127 | ex
2020 | SCE | RFF | CZ16 | 2007 | 0.047 | ex
2020 | SCE | RFF | CZ16 | 2011 | 0.047 | ex
2020 | SCE | RFF | CZ16 | 2015 | 0.035 | ex
2020 | SCE | RFF | CZ16 | 2017 | 0.035 | rec
2020 | SCE | RFF | CZ16 | 2020 | 0.012 | rec
2020 | SCE | RFF | CZ16 | New | 0.012 | new
2020 | SCE | RSD | CZ05 | 1975 | 0.051 | old
2020 | SCE | RSD | CZ05 | 1985 | 0.048 | old
2020 | SCE | RSD | CZ05 | 1996 | 0.019 | old
2020 | SCE | RSD | CZ05 | 2003 | 0.008 | ex
2020 | SCE | RSD | CZ05 | 2007 | 0.007 | ex
2020 | SCE | RSD | CZ05 | 2011 | 0.007 | ex
2020 | SCE | RSD | CZ05 | 2015 | 0.005 | ex
2020 | SCE | RSD | CZ05 | 2017 | 0.005 | rec
2020 | SCE | RSD | CZ05 | 2020 | 0.002 | rec
2020 | SCE | RSD | CZ05 | New | 0.002 | new
2020 | SCE | RSD | CZ06 | 1975 | 3.533 | old
2020 | SCE | RSD | CZ06 | 1985 | 3.29 | old
2020 | SCE | RSD | CZ06 | 1996 | 1.299 | old
2020 | SCE | RSD | CZ06 | 2003 | 0.557 | ex
2020 | SCE | RSD | CZ06 | 2007 | 0.489 | ex
2020 | SCE | RSD | CZ06 | 2011 | 0.489 | ex
2020 | SCE | RSD | CZ06 | 2015 | 0.367 | ex
2020 | SCE | RSD | CZ06 | 2017 | 0.367 | rec
2020 | SCE | RSD | CZ06 | 2020 | 0.122 | rec
2020 | SCE | RSD | CZ06 | New | 0.122 | new
2020 | SCE | RSD | CZ08 | 1975 | 4.068 | old
2020 | SCE | RSD | CZ08 | 1985 | 3.777 | old
2020 | SCE | RSD | CZ08 | 1996 | 1.488 | old
2020 | SCE | RSD | CZ08 | 2003 | 0.664 | ex
2020 | SCE | RSD | CZ08 | 2007 | 0.552 | ex
2020 | SCE | RSD | CZ08 | 2011 | 0.552 | ex
2020 | SCE | RSD | CZ08 | 2015 | 0.414 | ex
2020 | SCE | RSD | CZ08 | 2017 | 0.414 | rec
2020 | SCE | RSD | CZ08 | 2020 | 0.138 | rec
2020 | SCE | RSD | CZ08 | New | 0.138 | new
2020 | SCE | RSD | CZ09 | 1975 | 2.281 | old
2020 | SCE | RSD | CZ09 | 1985 | 2.088 | old
2020 | SCE | RSD | CZ09 | 1996 | 0.812 | old
2020 | SCE | RSD | CZ09 | 2003 | 0.438 | ex
2020 | SCE | RSD | CZ09 | 2007 | 0.277 | ex
2020 | SCE | RSD | CZ09 | 2011 | 0.277 | ex
2020 | SCE | RSD | CZ09 | 2015 | 0.207 | ex
2020 | SCE | RSD | CZ09 | 2017 | 0.207 | rec
2020 | SCE | RSD | CZ09 | 2020 | 0.069 | rec
2020 | SCE | RSD | CZ09 | New | 0.069 | new
2020 | SCE | RSD | CZ10 | 1975 | 1.682 | old
2020 | SCE | RSD | CZ10 | 1985 | 3.155 | old
2020 | SCE | RSD | CZ10 | 1996 | 1.726 | old
2020 | SCE | RSD | CZ10 | 2003 | 1.892 | ex
2020 | SCE | RSD | CZ10 | 2007 | 0.643 | ex
2020 | SCE | RSD | CZ10 | 2011 | 0.643 | ex
2020 | SCE | RSD | CZ10 | 2015 | 0.482 | ex
2020 | SCE | RSD | CZ10 | 2017 | 0.482 | rec
2020 | SCE | RSD | CZ10 | 2020 | 0.161 | rec
2020 | SCE | RSD | CZ10 | New | 0.161 | new
2020 | SCE | RSD | CZ13 | 1975 | 0.209 | old
2020 | SCE | RSD | CZ13 | 1985 | 0.22 | old
2020 | SCE | RSD | CZ13 | 1996 | 0.17 | old
2020 | SCE | RSD | CZ13 | 2003 | 0.088 | ex
2020 | SCE | RSD | CZ13 | 2007 | 0.044 | ex
2020 | SCE | RSD | CZ13 | 2011 | 0.044 | ex
2020 | SCE | RSD | CZ13 | 2015 | 0.033 | ex
2020 | SCE | RSD | CZ13 | 2017 | 0.033 | rec
2020 | SCE | RSD | CZ13 | 2020 | 0.011 | rec
2020 | SCE | RSD | CZ13 | New | 0.011 | new
2020 | SCE | RSD | CZ14 | 1975 | 0.433 | old
2020 | SCE | RSD | CZ14 | 1985 | 0.659 | old
2020 | SCE | RSD | CZ14 | 1996 | 0.345 | old
2020 | SCE | RSD | CZ14 | 2003 | 0.348 | ex
2020 | SCE | RSD | CZ14 | 2007 | 0.123 | ex
2020 | SCE | RSD | CZ14 | 2011 | 0.123 | ex
2020 | SCE | RSD | CZ14 | 2015 | 0.092 | ex
2020 | SCE | RSD | CZ14 | 2017 | 0.092 | rec
2020 | SCE | RSD | CZ14 | 2020 | 0.031 | rec
2020 | SCE | RSD | CZ14 | New | 0.031 | new
2020 | SCE | RSD | CZ15 | 1975 | 0.329 | old
2020 | SCE | RSD | CZ15 | 1985 | 0.617 | old
2020 | SCE | RSD | CZ15 | 1996 | 0.338 | old
2020 | SCE | RSD | CZ15 | 2003 | 0.37 | ex
2020 | SCE | RSD | CZ15 | 2007 | 0.126 | ex
2020 | SCE | RSD | CZ15 | 2011 | 0.126 | ex
2020 | SCE | RSD | CZ15 | 2015 | 0.094 | ex
2020 | SCE | RSD | CZ15 | 2017 | 0.094 | rec
2020 | SCE | RSD | CZ15 | 2020 | 0.031 | rec
2020 | SCE | RSD | CZ15 | New | 0.031 | new
2020 | SCE | RSD | CZ16 | 1975 | 0.173 | old
2020 | SCE | RSD | CZ16 | 1985 | 0.248 | old
2020 | SCE | RSD | CZ16 | 1996 | 0.142 | old
2020 | SCE | RSD | CZ16 | 2003 | 0.127 | ex
2020 | SCE | RSD | CZ16 | 2007 | 0.047 | ex
2020 | SCE | RSD | CZ16 | 2011 | 0.047 | ex
2020 | SCE | RSD | CZ16 | 2015 | 0.035 | ex
2020 | SCE | RSD | CZ16 | 2017 | 0.035 | rec
2020 | SCE | RSD | CZ16 | 2020 | 0.012 | rec
2020 | SCE | RSD | CZ16 | New | 0.012 | new
2020 | SCE | Rt3 | CZ05 | 1975 | 0.256 | old
2020 | SCE | Rt3 | CZ05 | 1985 | 0.199 | old
2020 | SCE | Rt3 | CZ05 | 1996 | 0.102 | old
2020 | SCE | Rt3 | CZ05 | 2003 | 0.044 | ex
2020 | SCE | Rt3 | CZ05 | 2007 | 0.029 | ex
2020 | SCE | Rt3 | CZ05 | 2011 | 0.029 | ex
2020 | SCE | Rt3 | CZ05 | 2015 | 0.022 | ex
2020 | SCE | Rt3 | CZ05 | 2017 | 0.022 | rec
2020 | SCE | Rt3 | CZ05 | 2020 | 0.007 | rec
2020 | SCE | Rt3 | CZ05 | New | 0.007 | new
2020 | SCE | Rt3 | CZ06 | 1975 | 14.254 | old
2020 | SCE | Rt3 | CZ06 | 1985 | 11.102 | old
2020 | SCE | Rt3 | CZ06 | 1996 | 5.659 | old
2020 | SCE | Rt3 | CZ06 | 2003 | 2.502 | ex
2020 | SCE | Rt3 | CZ06 | 2007 | 1.611 | ex
2020 | SCE | Rt3 | CZ06 | 2011 | 1.611 | ex
2020 | SCE | Rt3 | CZ06 | 2015 | 1.208 | ex
2020 | SCE | Rt3 | CZ06 | 2017 | 1.208 | rec
2020 | SCE | Rt3 | CZ06 | 2020 | 0.403 | rec
2020 | SCE | Rt3 | CZ06 | New | 0.403 | new
2020 | SCE | Rt3 | CZ08 | 1975 | 16.087 | old
2020 | SCE | Rt3 | CZ08 | 1985 | 12.661 | old
2020 | SCE | Rt3 | CZ08 | 1996 | 6.424 | old
2020 | SCE | Rt3 | CZ08 | 2003 | 2.907 | ex
2020 | SCE | Rt3 | CZ08 | 2007 | 1.845 | ex
2020 | SCE | Rt3 | CZ08 | 2011 | 1.845 | ex
2020 | SCE | Rt3 | CZ08 | 2015 | 1.384 | ex
2020 | SCE | Rt3 | CZ08 | 2017 | 1.384 | rec
2020 | SCE | Rt3 | CZ08 | 2020 | 0.461 | rec
2020 | SCE | Rt3 | CZ08 | New | 0.461 | new
2020 | SCE | Rt3 | CZ09 | 1975 | 8.423 | old
2020 | SCE | Rt3 | CZ09 | 1985 | 6.891 | old
2020 | SCE | Rt3 | CZ09 | 1996 | 3.437 | old
2020 | SCE | Rt3 | CZ09 | 2003 | 1.688 | ex
2020 | SCE | Rt3 | CZ09 | 2007 | 1.021 | ex
2020 | SCE | Rt3 | CZ09 | 2011 | 1.021 | ex
2020 | SCE | Rt3 | CZ09 | 2015 | 0.766 | ex
2020 | SCE | Rt3 | CZ09 | 2017 | 0.766 | rec
2020 | SCE | Rt3 | CZ09 | 2020 | 0.255 | rec
2020 | SCE | Rt3 | CZ09 | New | 0.255 | new
2020 | SCE | Rt3 | CZ10 | 1975 | 5.212 | old
2020 | SCE | Rt3 | CZ10 | 1985 | 11.767 | old
2020 | SCE | Rt3 | CZ10 | 1996 | 5.962 | old
2020 | SCE | Rt3 | CZ10 | 2003 | 5.186 | ex
2020 | SCE | Rt3 | CZ10 | 2007 | 2.778 | ex
2020 | SCE | Rt3 | CZ10 | 2011 | 2.778 | ex
2020 | SCE | Rt3 | CZ10 | 2015 | 2.083 | ex
2020 | SCE | Rt3 | CZ10 | 2017 | 2.083 | rec
2020 | SCE | Rt3 | CZ10 | 2020 | 0.694 | rec
2020 | SCE | Rt3 | CZ10 | New | 0.694 | new
2020 | SCE | Rt3 | CZ13 | 1975 | 1.386 | old
2020 | SCE | Rt3 | CZ13 | 1985 | 0.996 | old
2020 | SCE | Rt3 | CZ13 | 1996 | 0.84 | old
2020 | SCE | Rt3 | CZ13 | 2003 | 0.473 | ex
2020 | SCE | Rt3 | CZ13 | 2007 | 0.306 | ex
2020 | SCE | Rt3 | CZ13 | 2011 | 0.306 | ex
2020 | SCE | Rt3 | CZ13 | 2015 | 0.229 | ex
2020 | SCE | Rt3 | CZ13 | 2017 | 0.229 | rec
2020 | SCE | Rt3 | CZ13 | 2020 | 0.076 | rec
2020 | SCE | Rt3 | CZ13 | New | 0.076 | new
2020 | SCE | Rt3 | CZ14 | 1975 | 1.455 | old
2020 | SCE | Rt3 | CZ14 | 1985 | 2.082 | old
2020 | SCE | Rt3 | CZ14 | 1996 | 1.047 | old
2020 | SCE | Rt3 | CZ14 | 2003 | 0.792 | ex
2020 | SCE | Rt3 | CZ14 | 2007 | 0.432 | ex
2020 | SCE | Rt3 | CZ14 | 2011 | 0.432 | ex
2020 | SCE | Rt3 | CZ14 | 2015 | 0.324 | ex
2020 | SCE | Rt3 | CZ14 | 2017 | 0.324 | rec
2020 | SCE | Rt3 | CZ14 | 2020 | 0.108 | rec
2020 | SCE | Rt3 | CZ14 | New | 0.108 | new
2020 | SCE | Rt3 | CZ15 | 1975 | 0.728 | old
2020 | SCE | Rt3 | CZ15 | 1985 | 1.643 | old
2020 | SCE | Rt3 | CZ15 | 1996 | 0.833 | old
2020 | SCE | Rt3 | CZ15 | 2003 | 0.724 | ex
2020 | SCE | Rt3 | CZ15 | 2007 | 0.388 | ex
2020 | SCE | Rt3 | CZ15 | 2011 | 0.388 | ex
2020 | SCE | Rt3 | CZ15 | 2015 | 0.291 | ex
2020 | SCE | Rt3 | CZ15 | 2017 | 0.291 | rec
2020 | SCE | Rt3 | CZ15 | 2020 | 0.097 | rec
2020 | SCE | Rt3 | CZ15 | New | 0.097 | new
2020 | SCE | Rt3 | CZ16 | 1975 | 0.337 | old
2020 | SCE | Rt3 | CZ16 | 1985 | 0.375 | old
2020 | SCE | Rt3 | CZ16 | 1996 | 0.234 | old
2020 | SCE | Rt3 | CZ16 | 2003 | 0.159 | ex
2020 | SCE | Rt3 | CZ16 | 2007 | 0.093 | ex
2020 | SCE | Rt3 | CZ16 | 2011 | 0.093 | ex
2020 | SCE | Rt3 | CZ16 | 2015 | 0.07 | ex
2020 | SCE | Rt3 | CZ16 | 2017 | 0.07 | rec
2020 | SCE | Rt3 | CZ16 | 2020 | 0.023 | rec
2020 | SCE | Rt3 | CZ16 | New | 0.023 | new
2020 | SCE | RtL | CZ05 | 1975 | 0.256 | old
2020 | SCE | RtL | CZ05 | 1985 | 0.199 | old
2020 | SCE | RtL | CZ05 | 1996 | 0.102 | old
2020 | SCE | RtL | CZ05 | 2003 | 0.044 | ex
2020 | SCE | RtL | CZ05 | 2007 | 0.029 | ex
2020 | SCE | RtL | CZ05 | 2011 | 0.029 | ex
2020 | SCE | RtL | CZ05 | 2015 | 0.022 | ex
2020 | SCE | RtL | CZ05 | 2017 | 0.022 | rec
2020 | SCE | RtL | CZ05 | 2020 | 0.007 | rec
2020 | SCE | RtL | CZ05 | New | 0.007 | new
2020 | SCE | RtL | CZ06 | 1975 | 14.254 | old
2020 | SCE | RtL | CZ06 | 1985 | 11.102 | old
2020 | SCE | RtL | CZ06 | 1996 | 5.659 | old
2020 | SCE | RtL | CZ06 | 2003 | 2.502 | ex
2020 | SCE | RtL | CZ06 | 2007 | 1.611 | ex
2020 | SCE | RtL | CZ06 | 2011 | 1.611 | ex
2020 | SCE | RtL | CZ06 | 2015 | 1.208 | ex
2020 | SCE | RtL | CZ06 | 2017 | 1.208 | rec
2020 | SCE | RtL | CZ06 | 2020 | 0.403 | rec
2020 | SCE | RtL | CZ06 | New | 0.403 | new
2020 | SCE | RtL | CZ08 | 1975 | 16.087 | old
2020 | SCE | RtL | CZ08 | 1985 | 12.661 | old
2020 | SCE | RtL | CZ08 | 1996 | 6.424 | old
2020 | SCE | RtL | CZ08 | 2003 | 2.907 | ex
2020 | SCE | RtL | CZ08 | 2007 | 1.845 | ex
2020 | SCE | RtL | CZ08 | 2011 | 1.845 | ex
2020 | SCE | RtL | CZ08 | 2015 | 1.384 | ex
2020 | SCE | RtL | CZ08 | 2017 | 1.384 | rec
2020 | SCE | RtL | CZ08 | 2020 | 0.461 | rec
2020 | SCE | RtL | CZ08 | New | 0.461 | new
2020 | SCE | RtL | CZ09 | 1975 | 8.423 | old
2020 | SCE | RtL | CZ09 | 1985 | 6.891 | old
2020 | SCE | RtL | CZ09 | 1996 | 3.437 | old
2020 | SCE | RtL | CZ09 | 2003 | 1.688 | ex
2020 | SCE | RtL | CZ09 | 2007 | 1.021 | ex
2020 | SCE | RtL | CZ09 | 2011 | 1.021 | ex
2020 | SCE | RtL | CZ09 | 2015 | 0.766 | ex
2020 | SCE | RtL | CZ09 | 2017 | 0.766 | rec
2020 | SCE | RtL | CZ09 | 2020 | 0.255 | rec
2020 | SCE | RtL | CZ09 | New | 0.255 | new
2020 | SCE | RtL | CZ10 | 1975 | 5.212 | old
2020 | SCE | RtL | CZ10 | 1985 | 11.767 | old
2020 | SCE | RtL | CZ10 | 1996 | 5.962 | old
2020 | SCE | RtL | CZ10 | 2003 | 5.186 | ex
2020 | SCE | RtL | CZ10 | 2007 | 2.778 | ex
2020 | SCE | RtL | CZ10 | 2011 | 2.778 | ex
2020 | SCE | RtL | CZ10 | 2015 | 2.083 | ex
2020 | SCE | RtL | CZ10 | 2017 | 2.083 | rec
2020 | SCE | RtL | CZ10 | 2020 | 0.694 | rec
2020 | SCE | RtL | CZ10 | New | 0.694 | new
2020 | SCE | RtL | CZ13 | 1975 | 1.386 | old
2020 | SCE | RtL | CZ13 | 1985 | 0.996 | old
2020 | SCE | RtL | CZ13 | 1996 | 0.84 | old
2020 | SCE | RtL | CZ13 | 2003 | 0.473 | ex
2020 | SCE | RtL | CZ13 | 2007 | 0.306 | ex
2020 | SCE | RtL | CZ13 | 2011 | 0.306 | ex
2020 | SCE | RtL | CZ13 | 2015 | 0.229 | ex
2020 | SCE | RtL | CZ13 | 2017 | 0.229 | rec
2020 | SCE | RtL | CZ13 | 2020 | 0.076 | rec
2020 | SCE | RtL | CZ13 | New | 0.076 | new
2020 | SCE | RtL | CZ14 | 1975 | 1.455 | old
2020 | SCE | RtL | CZ14 | 1985 | 2.082 | old
2020 | SCE | RtL | CZ14 | 1996 | 1.047 | old
2020 | SCE | RtL | CZ14 | 2003 | 0.792 | ex
2020 | SCE | RtL | CZ14 | 2007 | 0.432 | ex
2020 | SCE | RtL | CZ14 | 2011 | 0.432 | ex
2020 | SCE | RtL | CZ14 | 2015 | 0.324 | ex
2020 | SCE | RtL | CZ14 | 2017 | 0.324 | rec
2020 | SCE | RtL | CZ14 | 2020 | 0.108 | rec
2020 | SCE | RtL | CZ14 | New | 0.108 | new
2020 | SCE | RtL | CZ15 | 1975 | 0.728 | old
2020 | SCE | RtL | CZ15 | 1985 | 1.643 | old
2020 | SCE | RtL | CZ15 | 1996 | 0.833 | old
2020 | SCE | RtL | CZ15 | 2003 | 0.724 | ex
2020 | SCE | RtL | CZ15 | 2007 | 0.388 | ex
2020 | SCE | RtL | CZ15 | 2011 | 0.388 | ex
2020 | SCE | RtL | CZ15 | 2015 | 0.291 | ex
2020 | SCE | RtL | CZ15 | 2017 | 0.291 | rec
2020 | SCE | RtL | CZ15 | 2020 | 0.097 | rec
2020 | SCE | RtL | CZ15 | New | 0.097 | new
2020 | SCE | RtL | CZ16 | 1975 | 0.337 | old
2020 | SCE | RtL | CZ16 | 1985 | 0.375 | old
2020 | SCE | RtL | CZ16 | 1996 | 0.234 | old
2020 | SCE | RtL | CZ16 | 2003 | 0.159 | ex
2020 | SCE | RtL | CZ16 | 2007 | 0.093 | ex
2020 | SCE | RtL | CZ16 | 2011 | 0.093 | ex
2020 | SCE | RtL | CZ16 | 2015 | 0.07 | ex
2020 | SCE | RtL | CZ16 | 2017 | 0.07 | rec
2020 | SCE | RtL | CZ16 | 2020 | 0.023 | rec
2020 | SCE | RtL | CZ16 | New | 0.023 | new
2020 | SCE | RtS | CZ05 | 1975 | 0.256 | old
2020 | SCE | RtS | CZ05 | 1985 | 0.199 | old
2020 | SCE | RtS | CZ05 | 1996 | 0.102 | old
2020 | SCE | RtS | CZ05 | 2003 | 0.044 | ex
2020 | SCE | RtS | CZ05 | 2007 | 0.029 | ex
2020 | SCE | RtS | CZ05 | 2011 | 0.029 | ex
2020 | SCE | RtS | CZ05 | 2015 | 0.022 | ex
2020 | SCE | RtS | CZ05 | 2017 | 0.022 | rec
2020 | SCE | RtS | CZ05 | 2020 | 0.007 | rec
2020 | SCE | RtS | CZ05 | New | 0.007 | new
2020 | SCE | RtS | CZ06 | 1975 | 14.254 | old
2020 | SCE | RtS | CZ06 | 1985 | 11.102 | old
2020 | SCE | RtS | CZ06 | 1996 | 5.659 | old
2020 | SCE | RtS | CZ06 | 2003 | 2.502 | ex
2020 | SCE | RtS | CZ06 | 2007 | 1.611 | ex
2020 | SCE | RtS | CZ06 | 2011 | 1.611 | ex
2020 | SCE | RtS | CZ06 | 2015 | 1.208 | ex
2020 | SCE | RtS | CZ06 | 2017 | 1.208 | rec
2020 | SCE | RtS | CZ06 | 2020 | 0.403 | rec
2020 | SCE | RtS | CZ06 | New | 0.403 | new
2020 | SCE | RtS | CZ08 | 1975 | 16.087 | old
2020 | SCE | RtS | CZ08 | 1985 | 12.661 | old
2020 | SCE | RtS | CZ08 | 1996 | 6.424 | old
2020 | SCE | RtS | CZ08 | 2003 | 2.907 | ex
2020 | SCE | RtS | CZ08 | 2007 | 1.845 | ex
2020 | SCE | RtS | CZ08 | 2011 | 1.845 | ex
2020 | SCE | RtS | CZ08 | 2015 | 1.384 | ex
2020 | SCE | RtS | CZ08 | 2017 | 1.384 | rec
2020 | SCE | RtS | CZ08 | 2020 | 0.461 | rec
2020 | SCE | RtS | CZ08 | New | 0.461 | new
2020 | SCE | RtS | CZ09 | 1975 | 8.423 | old
2020 | SCE | RtS | CZ09 | 1985 | 6.891 | old
2020 | SCE | RtS | CZ09 | 1996 | 3.437 | old
2020 | SCE | RtS | CZ09 | 2003 | 1.688 | ex
2020 | SCE | RtS | CZ09 | 2007 | 1.021 | ex
2020 | SCE | RtS | CZ09 | 2011 | 1.021 | ex
2020 | SCE | RtS | CZ09 | 2015 | 0.766 | ex
2020 | SCE | RtS | CZ09 | 2017 | 0.766 | rec
2020 | SCE | RtS | CZ09 | 2020 | 0.255 | rec
2020 | SCE | RtS | CZ09 | New | 0.255 | new
2020 | SCE | RtS | CZ10 | 1975 | 5.212 | old
2020 | SCE | RtS | CZ10 | 1985 | 11.767 | old
2020 | SCE | RtS | CZ10 | 1996 | 5.962 | old
2020 | SCE | RtS | CZ10 | 2003 | 5.186 | ex
2020 | SCE | RtS | CZ10 | 2007 | 2.778 | ex
2020 | SCE | RtS | CZ10 | 2011 | 2.778 | ex
2020 | SCE | RtS | CZ10 | 2015 | 2.083 | ex
2020 | SCE | RtS | CZ10 | 2017 | 2.083 | rec
2020 | SCE | RtS | CZ10 | 2020 | 0.694 | rec
2020 | SCE | RtS | CZ10 | New | 0.694 | new
2020 | SCE | RtS | CZ13 | 1975 | 1.386 | old
2020 | SCE | RtS | CZ13 | 1985 | 0.996 | old
2020 | SCE | RtS | CZ13 | 1996 | 0.84 | old
2020 | SCE | RtS | CZ13 | 2003 | 0.473 | ex
2020 | SCE | RtS | CZ13 | 2007 | 0.306 | ex
2020 | SCE | RtS | CZ13 | 2011 | 0.306 | ex
2020 | SCE | RtS | CZ13 | 2015 | 0.229 | ex
2020 | SCE | RtS | CZ13 | 2017 | 0.229 | rec
2020 | SCE | RtS | CZ13 | 2020 | 0.076 | rec
2020 | SCE | RtS | CZ13 | New | 0.076 | new
2020 | SCE | RtS | CZ14 | 1975 | 1.455 | old
2020 | SCE | RtS | CZ14 | 1985 | 2.082 | old
2020 | SCE | RtS | CZ14 | 1996 | 1.047 | old
2020 | SCE | RtS | CZ14 | 2003 | 0.792 | ex
2020 | SCE | RtS | CZ14 | 2007 | 0.432 | ex
2020 | SCE | RtS | CZ14 | 2011 | 0.432 | ex
2020 | SCE | RtS | CZ14 | 2015 | 0.324 | ex
2020 | SCE | RtS | CZ14 | 2017 | 0.324 | rec
2020 | SCE | RtS | CZ14 | 2020 | 0.108 | rec
2020 | SCE | RtS | CZ14 | New | 0.108 | new
2020 | SCE | RtS | CZ15 | 1975 | 0.728 | old
2020 | SCE | RtS | CZ15 | 1985 | 1.643 | old
2020 | SCE | RtS | CZ15 | 1996 | 0.833 | old
2020 | SCE | RtS | CZ15 | 2003 | 0.724 | ex
2020 | SCE | RtS | CZ15 | 2007 | 0.388 | ex
2020 | SCE | RtS | CZ15 | 2011 | 0.388 | ex
2020 | SCE | RtS | CZ15 | 2015 | 0.291 | ex
2020 | SCE | RtS | CZ15 | 2017 | 0.291 | rec
2020 | SCE | RtS | CZ15 | 2020 | 0.097 | rec
2020 | SCE | RtS | CZ15 | New | 0.097 | new
2020 | SCE | RtS | CZ16 | 1975 | 0.337 | old
2020 | SCE | RtS | CZ16 | 1985 | 0.375 | old
2020 | SCE | RtS | CZ16 | 1996 | 0.234 | old
2020 | SCE | RtS | CZ16 | 2003 | 0.159 | ex
2020 | SCE | RtS | CZ16 | 2007 | 0.093 | ex
2020 | SCE | RtS | CZ16 | 2011 | 0.093 | ex
2020 | SCE | RtS | CZ16 | 2015 | 0.07 | ex
2020 | SCE | RtS | CZ16 | 2017 | 0.07 | rec
2020 | SCE | RtS | CZ16 | 2020 | 0.023 | rec
2020 | SCE | RtS | CZ16 | New | 0.023 | new
2020 | SCE | SCn | CZ05 | 1975 | 0.014 | old
2020 | SCE | SCn | CZ05 | 1985 | 0.01 | old
2020 | SCE | SCn | CZ05 | 1996 | 0.005 | old
2020 | SCE | SCn | CZ05 | 2003 | 0.003 | ex
2020 | SCE | SCn | CZ05 | 2007 | 0.001 | ex
2020 | SCE | SCn | CZ05 | 2011 | 0.001 | ex
2020 | SCE | SCn | CZ05 | 2015 | 0.001 | ex
2020 | SCE | SCn | CZ05 | 2017 | 0.001 | rec
2020 | SCE | SCn | CZ05 | 2020 | 0.001 | rec
2020 | SCE | SCn | CZ05 | New | 0.001 | new
2020 | SCE | SCn | CZ06 | 1975 | 11.912 | old
2020 | SCE | SCn | CZ06 | 1985 | 8.507 | old
2020 | SCE | SCn | CZ06 | 1996 | 4.015 | old
2020 | SCE | SCn | CZ06 | 2003 | 2.395 | ex
2020 | SCE | SCn | CZ06 | 2007 | 1.155 | ex
2020 | SCE | SCn | CZ06 | 2011 | 1.155 | ex
2020 | SCE | SCn | CZ06 | 2015 | 0.866 | ex
2020 | SCE | SCn | CZ06 | 2017 | 0.866 | rec
2020 | SCE | SCn | CZ06 | 2020 | 0.289 | rec
2020 | SCE | SCn | CZ06 | New | 0.289 | new
2020 | SCE | SCn | CZ08 | 1975 | 36.28 | old
2020 | SCE | SCn | CZ08 | 1985 | 25.658 | old
2020 | SCE | SCn | CZ08 | 1996 | 12.156 | old
2020 | SCE | SCn | CZ08 | 2003 | 7.047 | ex
2020 | SCE | SCn | CZ08 | 2007 | 3.436 | ex
2020 | SCE | SCn | CZ08 | 2011 | 3.436 | ex
2020 | SCE | SCn | CZ08 | 2015 | 2.577 | ex
2020 | SCE | SCn | CZ08 | 2017 | 2.577 | rec
2020 | SCE | SCn | CZ08 | 2020 | 0.859 | rec
2020 | SCE | SCn | CZ08 | New | 0.859 | new
2020 | SCE | SCn | CZ09 | 1975 | 8.688 | old
2020 | SCE | SCn | CZ09 | 1985 | 6.823 | old
2020 | SCE | SCn | CZ09 | 1996 | 3.109 | old
2020 | SCE | SCn | CZ09 | 2003 | 2.359 | ex
2020 | SCE | SCn | CZ09 | 2007 | 1.042 | ex
2020 | SCE | SCn | CZ09 | 2011 | 1.042 | ex
2020 | SCE | SCn | CZ09 | 2015 | 0.782 | ex
2020 | SCE | SCn | CZ09 | 2017 | 0.782 | rec
2020 | SCE | SCn | CZ09 | 2020 | 0.261 | rec
2020 | SCE | SCn | CZ09 | New | 0.261 | new
2020 | SCE | SCn | CZ10 | 1975 | 4.737 | old
2020 | SCE | SCn | CZ10 | 1985 | 22.896 | old
2020 | SCE | SCn | CZ10 | 1996 | 12.33 | old
2020 | SCE | SCn | CZ10 | 2003 | 16.819 | ex
2020 | SCE | SCn | CZ10 | 2007 | 11.107 | ex
2020 | SCE | SCn | CZ10 | 2011 | 11.107 | ex
2020 | SCE | SCn | CZ10 | 2015 | 8.331 | ex
2020 | SCE | SCn | CZ10 | 2017 | 8.331 | rec
2020 | SCE | SCn | CZ10 | 2020 | 2.777 | rec
2020 | SCE | SCn | CZ10 | New | 2.777 | new
2020 | SCE | SCn | CZ13 | 1975 | 0.504 | old
2020 | SCE | SCn | CZ13 | 1985 | 0.89 | old
2020 | SCE | SCn | CZ13 | 1996 | 0.971 | old
2020 | SCE | SCn | CZ13 | 2003 | 0.551 | ex
2020 | SCE | SCn | CZ13 | 2007 | 0.376 | ex
2020 | SCE | SCn | CZ13 | 2011 | 0.376 | ex
2020 | SCE | SCn | CZ13 | 2015 | 0.282 | ex
2020 | SCE | SCn | CZ13 | 2017 | 0.282 | rec
2020 | SCE | SCn | CZ13 | 2020 | 0.094 | rec
2020 | SCE | SCn | CZ13 | New | 0.094 | new
2020 | SCE | SCn | CZ14 | 1975 | 0.24 | old
2020 | SCE | SCn | CZ14 | 1985 | 0.522 | old
2020 | SCE | SCn | CZ14 | 1996 | 0.317 | old
2020 | SCE | SCn | CZ14 | 2003 | 0.337 | ex
2020 | SCE | SCn | CZ14 | 2007 | 0.215 | ex
2020 | SCE | SCn | CZ14 | 2011 | 0.215 | ex
2020 | SCE | SCn | CZ14 | 2015 | 0.161 | ex
2020 | SCE | SCn | CZ14 | 2017 | 0.161 | rec
2020 | SCE | SCn | CZ14 | 2020 | 0.054 | rec
2020 | SCE | SCn | CZ14 | New | 0.054 | new
2020 | SCE | SCn | CZ15 | 1975 | 0.087 | old
2020 | SCE | SCn | CZ15 | 1985 | 0.421 | old
2020 | SCE | SCn | CZ15 | 1996 | 0.227 | old
2020 | SCE | SCn | CZ15 | 2003 | 0.309 | ex
2020 | SCE | SCn | CZ15 | 2007 | 0.204 | ex
2020 | SCE | SCn | CZ15 | 2011 | 0.204 | ex
2020 | SCE | SCn | CZ15 | 2015 | 0.153 | ex
2020 | SCE | SCn | CZ15 | 2017 | 0.153 | rec
2020 | SCE | SCn | CZ15 | 2020 | 0.051 | rec
2020 | SCE | SCn | CZ15 | New | 0.051 | new
2020 | SCE | SCn | CZ16 | 1975 | 0.111 | old
2020 | SCE | SCn | CZ16 | 1985 | 0.427 | old
2020 | SCE | SCn | CZ16 | 1996 | 0.251 | old
2020 | SCE | SCn | CZ16 | 2003 | 0.306 | ex
2020 | SCE | SCn | CZ16 | 2007 | 0.202 | ex
2020 | SCE | SCn | CZ16 | 2011 | 0.202 | ex
2020 | SCE | SCn | CZ16 | 2015 | 0.152 | ex
2020 | SCE | SCn | CZ16 | 2017 | 0.152 | rec
2020 | SCE | SCn | CZ16 | 2020 | 0.051 | rec
2020 | SCE | SCn | CZ16 | New | 0.051 | new
2020 | SCE | SUn | CZ05 | 1975 | 0.014 | old
2020 | SCE | SUn | CZ05 | 1985 | 0.01 | old
2020 | SCE | SUn | CZ05 | 1996 | 0.005 | old
2020 | SCE | SUn | CZ05 | 2003 | 0.003 | ex
2020 | SCE | SUn | CZ05 | 2007 | 0.001 | ex
2020 | SCE | SUn | CZ05 | 2011 | 0.001 | ex
2020 | SCE | SUn | CZ05 | 2015 | 0.001 | ex
2020 | SCE | SUn | CZ05 | 2017 | 0.001 | rec
2020 | SCE | SUn | CZ05 | 2020 | 0.001 | rec
2020 | SCE | SUn | CZ05 | New | 0.001 | new
2020 | SCE | SUn | CZ06 | 1975 | 11.912 | old
2020 | SCE | SUn | CZ06 | 1985 | 8.507 | old
2020 | SCE | SUn | CZ06 | 1996 | 4.015 | old
2020 | SCE | SUn | CZ06 | 2003 | 2.395 | ex
2020 | SCE | SUn | CZ06 | 2007 | 1.155 | ex
2020 | SCE | SUn | CZ06 | 2011 | 1.155 | ex
2020 | SCE | SUn | CZ06 | 2015 | 0.866 | ex
2020 | SCE | SUn | CZ06 | 2017 | 0.866 | rec
2020 | SCE | SUn | CZ06 | 2020 | 0.289 | rec
2020 | SCE | SUn | CZ06 | New | 0.289 | new
2020 | SCE | SUn | CZ08 | 1975 | 36.28 | old
2020 | SCE | SUn | CZ08 | 1985 | 25.658 | old
2020 | SCE | SUn | CZ08 | 1996 | 12.156 | old
2020 | SCE | SUn | CZ08 | 2003 | 7.047 | ex
2020 | SCE | SUn | CZ08 | 2007 | 3.436 | ex
2020 | SCE | SUn | CZ08 | 2011 | 3.436 | ex
2020 | SCE | SUn | CZ08 | 2015 | 2.577 | ex
2020 | SCE | SUn | CZ08 | 2017 | 2.577 | rec
2020 | SCE | SUn | CZ08 | 2020 | 0.859 | rec
2020 | SCE | SUn | CZ08 | New | 0.859 | new
2020 | SCE | SUn | CZ09 | 1975 | 8.688 | old
2020 | SCE | SUn | CZ09 | 1985 | 6.823 | old
2020 | SCE | SUn | CZ09 | 1996 | 3.109 | old
2020 | SCE | SUn | CZ09 | 2003 | 2.359 | ex
2020 | SCE | SUn | CZ09 | 2007 | 1.042 | ex
2020 | SCE | SUn | CZ09 | 2011 | 1.042 | ex
2020 | SCE | SUn | CZ09 | 2015 | 0.782 | ex
2020 | SCE | SUn | CZ09 | 2017 | 0.782 | rec
2020 | SCE | SUn | CZ09 | 2020 | 0.261 | rec
2020 | SCE | SUn | CZ09 | New | 0.261 | new
2020 | SCE | SUn | CZ10 | 1975 | 4.737 | old
2020 | SCE | SUn | CZ10 | 1985 | 22.896 | old
2020 | SCE | SUn | CZ10 | 1996 | 12.33 | old
2020 | SCE | SUn | CZ10 | 2003 | 16.819 | ex
2020 | SCE | SUn | CZ10 | 2007 | 11.107 | ex
2020 | SCE | SUn | CZ10 | 2011 | 11.107 | ex
2020 | SCE | SUn | CZ10 | 2015 | 8.331 | ex
2020 | SCE | SUn | CZ10 | 2017 | 8.331 | rec
2020 | SCE | SUn | CZ10 | 2020 | 2.777 | rec
2020 | SCE | SUn | CZ10 | New | 2.777 | new
2020 | SCE | SUn | CZ13 | 1975 | 0.504 | old
2020 | SCE | SUn | CZ13 | 1985 | 0.89 | old
2020 | SCE | SUn | CZ13 | 1996 | 0.971 | old
2020 | SCE | SUn | CZ13 | 2003 | 0.551 | ex
2020 | SCE | SUn | CZ13 | 2007 | 0.376 | ex
2020 | SCE | SUn | CZ13 | 2011 | 0.376 | ex
2020 | SCE | SUn | CZ13 | 2015 | 0.282 | ex
2020 | SCE | SUn | CZ13 | 2017 | 0.282 | rec
2020 | SCE | SUn | CZ13 | 2020 | 0.094 | rec
2020 | SCE | SUn | CZ13 | New | 0.094 | new
2020 | SCE | SUn | CZ14 | 1975 | 0.24 | old
2020 | SCE | SUn | CZ14 | 1985 | 0.522 | old
2020 | SCE | SUn | CZ14 | 1996 | 0.317 | old
2020 | SCE | SUn | CZ14 | 2003 | 0.337 | ex
2020 | SCE | SUn | CZ14 | 2007 | 0.215 | ex
2020 | SCE | SUn | CZ14 | 2011 | 0.215 | ex
2020 | SCE | SUn | CZ14 | 2015 | 0.161 | ex
2020 | SCE | SUn | CZ14 | 2017 | 0.161 | rec
2020 | SCE | SUn | CZ14 | 2020 | 0.054 | rec
2020 | SCE | SUn | CZ14 | New | 0.054 | new
2020 | SCE | SUn | CZ15 | 1975 | 0.087 | old
2020 | SCE | SUn | CZ15 | 1985 | 0.421 | old
2020 | SCE | SUn | CZ15 | 1996 | 0.227 | old
2020 | SCE | SUn | CZ15 | 2003 | 0.309 | ex
2020 | SCE | SUn | CZ15 | 2007 | 0.204 | ex
2020 | SCE | SUn | CZ15 | 2011 | 0.204 | ex
2020 | SCE | SUn | CZ15 | 2015 | 0.153 | ex
2020 | SCE | SUn | CZ15 | 2017 | 0.153 | rec
2020 | SCE | SUn | CZ15 | 2020 | 0.051 | rec
2020 | SCE | SUn | CZ15 | New | 0.051 | new
2020 | SCE | SUn | CZ16 | 1975 | 0.111 | old
2020 | SCE | SUn | CZ16 | 1985 | 0.427 | old
2020 | SCE | SUn | CZ16 | 1996 | 0.251 | old
2020 | SCE | SUn | CZ16 | 2003 | 0.306 | ex
2020 | SCE | SUn | CZ16 | 2007 | 0.202 | ex
2020 | SCE | SUn | CZ16 | 2011 | 0.202 | ex
2020 | SCE | SUn | CZ16 | 2015 | 0.152 | ex
2020 | SCE | SUn | CZ16 | 2017 | 0.152 | rec
2020 | SCE | SUn | CZ16 | 2020 | 0.051 | rec
2020 | SCE | SUn | CZ16 | New | 0.051 | new
2020 | SCE | WRf | CZ06 | 1975 | 2.024 | old
2020 | SCE | WRf | CZ06 | 1985 | 0.872 | old
2020 | SCE | WRf | CZ06 | 1996 | 0.911 | old
2020 | SCE | WRf | CZ06 | 2003 | 0.341 | ex
2020 | SCE | WRf | CZ06 | 2007 | 0.213 | ex
2020 | SCE | WRf | CZ06 | 2011 | 0.213 | ex
2020 | SCE | WRf | CZ06 | 2015 | 0.16 | ex
2020 | SCE | WRf | CZ06 | 2017 | 0.16 | rec
2020 | SCE | WRf | CZ06 | 2020 | 0.053 | rec
2020 | SCE | WRf | CZ06 | New | 0.053 | new
2020 | SCE | WRf | CZ08 | 1975 | 2.688 | old
2020 | SCE | WRf | CZ08 | 1985 | 1.163 | old
2020 | SCE | WRf | CZ08 | 1996 | 1.218 | old
2020 | SCE | WRf | CZ08 | 2003 | 0.46 | ex
2020 | SCE | WRf | CZ08 | 2007 | 0.285 | ex
2020 | SCE | WRf | CZ08 | 2011 | 0.285 | ex
2020 | SCE | WRf | CZ08 | 2015 | 0.214 | ex
2020 | SCE | WRf | CZ08 | 2017 | 0.214 | rec
2020 | SCE | WRf | CZ08 | 2020 | 0.071 | rec
2020 | SCE | WRf | CZ08 | New | 0.071 | new
2020 | SCE | WRf | CZ09 | 1975 | 0.703 | old
2020 | SCE | WRf | CZ09 | 1985 | 0.335 | old
2020 | SCE | WRf | CZ09 | 1996 | 0.391 | old
2020 | SCE | WRf | CZ09 | 2003 | 0.182 | ex
2020 | SCE | WRf | CZ09 | 2007 | 0.092 | ex
2020 | SCE | WRf | CZ09 | 2011 | 0.092 | ex
2020 | SCE | WRf | CZ09 | 2015 | 0.069 | ex
2020 | SCE | WRf | CZ09 | 2017 | 0.069 | rec
2020 | SCE | WRf | CZ09 | 2020 | 0.023 | rec
2020 | SCE | WRf | CZ09 | New | 0.023 | new
2020 | SCE | WRf | CZ10 | 1975 | 0.581 | old
2020 | SCE | WRf | CZ10 | 1985 | 0.482 | old
2020 | SCE | WRf | CZ10 | 1996 | 1.763 | old
2020 | SCE | WRf | CZ10 | 2003 | 0.231 | ex
2020 | SCE | WRf | CZ10 | 2007 | 0.22 | ex
2020 | SCE | WRf | CZ10 | 2011 | 0.22 | ex
2020 | SCE | WRf | CZ10 | 2015 | 0.165 | ex
2020 | SCE | WRf | CZ10 | 2017 | 0.165 | rec
2020 | SCE | WRf | CZ10 | 2020 | 0.055 | rec
2020 | SCE | WRf | CZ10 | New | 0.055 | new
2020 | SCE | WRf | CZ13 | 1975 | 0.232 | old
2020 | SCE | WRf | CZ13 | 1985 | 1.295 | old
2020 | SCE | WRf | CZ13 | 1996 | 0.767 | old
2020 | SCE | WRf | CZ13 | 2003 | 0.211 | ex
2020 | SCE | WRf | CZ13 | 2007 | 0.298 | ex
2020 | SCE | WRf | CZ13 | 2011 | 0.298 | ex
2020 | SCE | WRf | CZ13 | 2015 | 0.224 | ex
2020 | SCE | WRf | CZ13 | 2017 | 0.224 | rec
2020 | SCE | WRf | CZ13 | 2020 | 0.075 | rec
2020 | SCE | WRf | CZ13 | New | 0.075 | new
2020 | SCE | WRf | CZ14 | 1975 | 0.009 | old
2020 | SCE | WRf | CZ14 | 1985 | 0.007 | old
2020 | SCE | WRf | CZ14 | 1996 | 0.022 | old
2020 | SCE | WRf | CZ14 | 2003 | 0.003 | ex
2020 | SCE | WRf | CZ14 | 2007 | 0.003 | ex
2020 | SCE | WRf | CZ14 | 2011 | 0.003 | ex
2020 | SCE | WRf | CZ14 | 2015 | 0.002 | ex
2020 | SCE | WRf | CZ14 | 2017 | 0.002 | rec
2020 | SCE | WRf | CZ14 | 2020 | 0.001 | rec
2020 | SCE | WRf | CZ14 | New | 0.001 | new
2020 | SCE | WRf | CZ15 | 1975 | 0.038 | old
2020 | SCE | WRf | CZ15 | 1985 | 0.031 | old
2020 | SCE | WRf | CZ15 | 1996 | 0.115 | old
2020 | SCE | WRf | CZ15 | 2003 | 0.015 | ex
2020 | SCE | WRf | CZ15 | 2007 | 0.014 | ex
2020 | SCE | WRf | CZ15 | 2011 | 0.014 | ex
2020 | SCE | WRf | CZ15 | 2015 | 0.011 | ex
2020 | SCE | WRf | CZ15 | 2017 | 0.011 | rec
2020 | SCE | WRf | CZ15 | 2020 | 0.004 | rec
2020 | SCE | WRf | CZ15 | New | 0.004 | new
2020 | SCE | WRf | CZ16 | 1975 | 0.006 | old
2020 | SCE | WRf | CZ16 | 1985 | 0.026 | old
2020 | SCE | WRf | CZ16 | 1996 | 0.016 | old
2020 | SCE | WRf | CZ16 | 2003 | 0.005 | ex
2020 | SCE | WRf | CZ16 | 2007 | 0.006 | ex
2020 | SCE | WRf | CZ16 | 2011 | 0.006 | ex
2020 | SCE | WRf | CZ16 | 2015 | 0.005 | ex
2020 | SCE | WRf | CZ16 | 2017 | 0.005 | rec
2020 | SCE | WRf | CZ16 | 2020 | 0.002 | rec
2020 | SCE | WRf | CZ16 | New | 0.002 | new
2020 | SCG | Asm | CZ05 | 1975 | 0.216 | old
2020 | SCG | Asm | CZ05 | 1985 | 0.115 | old
2020 | SCG | Asm | CZ05 | 1996 | 0.056 | old
2020 | SCG | Asm | CZ05 | 2003 | 0.028 | ex
2020 | SCG | Asm | CZ05 | 2007 | 0.018 | ex
2020 | SCG | Asm | CZ05 | 2011 | 0.018 | ex
2020 | SCG | Asm | CZ05 | 2015 | 0.013 | ex
2020 | SCG | Asm | CZ05 | 2017 | 0.013 | rec
2020 | SCG | Asm | CZ05 | 2020 | 0.004 | rec
2020 | SCG | Asm | CZ05 | New | 0.004 | new
2020 | SCG | Asm | CZ06 | 1975 | 19.932 | old
2020 | SCG | Asm | CZ06 | 1985 | 10.416 | old
2020 | SCG | Asm | CZ06 | 1996 | 5.177 | old
2020 | SCG | Asm | CZ06 | 2003 | 2.546 | ex
2020 | SCG | Asm | CZ06 | 2007 | 1.598 | ex
2020 | SCG | Asm | CZ06 | 2011 | 1.598 | ex
2020 | SCG | Asm | CZ06 | 2015 | 1.198 | ex
2020 | SCG | Asm | CZ06 | 2017 | 1.198 | rec
2020 | SCG | Asm | CZ06 | 2020 | 0.399 | rec
2020 | SCG | Asm | CZ06 | New | 0.399 | new
2020 | SCG | Asm | CZ08 | 1975 | 30.07 | old
2020 | SCG | Asm | CZ08 | 1985 | 15.594 | old
2020 | SCG | Asm | CZ08 | 1996 | 7.835 | old
2020 | SCG | Asm | CZ08 | 2003 | 3.85 | ex
2020 | SCG | Asm | CZ08 | 2007 | 2.397 | ex
2020 | SCG | Asm | CZ08 | 2011 | 2.397 | ex
2020 | SCG | Asm | CZ08 | 2015 | 1.798 | ex
2020 | SCG | Asm | CZ08 | 2017 | 1.798 | rec
2020 | SCG | Asm | CZ08 | 2020 | 0.599 | rec
2020 | SCG | Asm | CZ08 | New | 0.599 | new
2020 | SCG | Asm | CZ09 | 1975 | 25.899 | old
2020 | SCG | Asm | CZ09 | 1985 | 12.41 | old
2020 | SCG | Asm | CZ09 | 1996 | 7.291 | old
2020 | SCG | Asm | CZ09 | 2003 | 3.528 | ex
2020 | SCG | Asm | CZ09 | 2007 | 1.99 | ex
2020 | SCG | Asm | CZ09 | 2011 | 1.99 | ex
2020 | SCG | Asm | CZ09 | 2015 | 1.493 | ex
2020 | SCG | Asm | CZ09 | 2017 | 1.493 | rec
2020 | SCG | Asm | CZ09 | 2020 | 0.498 | rec
2020 | SCG | Asm | CZ09 | New | 0.498 | new
2020 | SCG | Asm | CZ10 | 1975 | 3.994 | old
2020 | SCG | Asm | CZ10 | 1985 | 9.306 | old
2020 | SCG | Asm | CZ10 | 1996 | 5.666 | old
2020 | SCG | Asm | CZ10 | 2003 | 5.288 | ex
2020 | SCG | Asm | CZ10 | 2007 | 2.938 | ex
2020 | SCG | Asm | CZ10 | 2011 | 2.938 | ex
2020 | SCG | Asm | CZ10 | 2015 | 2.204 | ex
2020 | SCG | Asm | CZ10 | 2017 | 2.204 | rec
2020 | SCG | Asm | CZ10 | 2020 | 0.735 | rec
2020 | SCG | Asm | CZ10 | New | 0.735 | new
2020 | SCG | Asm | CZ13 | 1975 | 0.899 | old
2020 | SCG | Asm | CZ13 | 1985 | 1.085 | old
2020 | SCG | Asm | CZ13 | 1996 | 0.903 | old
2020 | SCG | Asm | CZ13 | 2003 | 0.349 | ex
2020 | SCG | Asm | CZ13 | 2007 | 0.223 | ex
2020 | SCG | Asm | CZ13 | 2011 | 0.223 | ex
2020 | SCG | Asm | CZ13 | 2015 | 0.167 | ex
2020 | SCG | Asm | CZ13 | 2017 | 0.167 | rec
2020 | SCG | Asm | CZ13 | 2020 | 0.056 | rec
2020 | SCG | Asm | CZ13 | New | 0.056 | new
2020 | SCG | Asm | CZ14 | 1975 | 1.878 | old
2020 | SCG | Asm | CZ14 | 1985 | 1.916 | old
2020 | SCG | Asm | CZ14 | 1996 | 1.152 | old
2020 | SCG | Asm | CZ14 | 2003 | 0.877 | ex
2020 | SCG | Asm | CZ14 | 2007 | 0.486 | ex
2020 | SCG | Asm | CZ14 | 2011 | 0.486 | ex
2020 | SCG | Asm | CZ14 | 2015 | 0.364 | ex
2020 | SCG | Asm | CZ14 | 2017 | 0.364 | rec
2020 | SCG | Asm | CZ14 | 2020 | 0.122 | rec
2020 | SCG | Asm | CZ14 | New | 0.122 | new
2020 | SCG | Asm | CZ15 | 1975 | 1.446 | old
2020 | SCG | Asm | CZ15 | 1985 | 3.369 | old
2020 | SCG | Asm | CZ15 | 1996 | 2.051 | old
2020 | SCG | Asm | CZ15 | 2003 | 1.914 | ex
2020 | SCG | Asm | CZ15 | 2007 | 1.064 | ex
2020 | SCG | Asm | CZ15 | 2011 | 1.064 | ex
2020 | SCG | Asm | CZ15 | 2015 | 0.798 | ex
2020 | SCG | Asm | CZ15 | 2017 | 0.798 | rec
2020 | SCG | Asm | CZ15 | 2020 | 0.266 | rec
2020 | SCG | Asm | CZ15 | New | 0.266 | new
2020 | SCG | Asm | CZ16 | 1975 | 0.888 | old
2020 | SCG | Asm | CZ16 | 1985 | 1.175 | old
2020 | SCG | Asm | CZ16 | 1996 | 0.786 | old
2020 | SCG | Asm | CZ16 | 2003 | 0.535 | ex
2020 | SCG | Asm | CZ16 | 2007 | 0.306 | ex
2020 | SCG | Asm | CZ16 | 2011 | 0.306 | ex
2020 | SCG | Asm | CZ16 | 2015 | 0.23 | ex
2020 | SCG | Asm | CZ16 | 2017 | 0.23 | rec
2020 | SCG | Asm | CZ16 | 2020 | 0.077 | rec
2020 | SCG | Asm | CZ16 | New | 0.077 | new
2020 | SCG | ECC | CZ05 | 1975 | 0.009 | old
2020 | SCG | ECC | CZ05 | 1985 | 0.003 | old
2020 | SCG | ECC | CZ05 | 1996 | 0.002 | old
2020 | SCG | ECC | CZ05 | 2003 | 0.001 | ex
2020 | SCG | ECC | CZ05 | 2007 | 0.001 | ex
2020 | SCG | ECC | CZ05 | 2011 | 0.001 | ex
2020 | SCG | ECC | CZ05 | 2015 | 0.001 | ex
2020 | SCG | ECC | CZ05 | 2017 | 0.001 | rec
2020 | SCG | ECC | CZ05 | 2020 | 0.001 | rec
2020 | SCG | ECC | CZ05 | New | 0.001 | new
2020 | SCG | ECC | CZ06 | 1975 | 8.927 | old
2020 | SCG | ECC | CZ06 | 1985 | 2.669 | old
2020 | SCG | ECC | CZ06 | 1996 | 1.819 | old
2020 | SCG | ECC | CZ06 | 2003 | 1.066 | ex
2020 | SCG | ECC | CZ06 | 2007 | 0.47 | ex
2020 | SCG | ECC | CZ06 | 2011 | 0.47 | ex
2020 | SCG | ECC | CZ06 | 2015 | 0.353 | ex
2020 | SCG | ECC | CZ06 | 2017 | 0.353 | rec
2020 | SCG | ECC | CZ06 | 2020 | 0.118 | rec
2020 | SCG | ECC | CZ06 | New | 0.118 | new
2020 | SCG | ECC | CZ08 | 1975 | 15.19 | old
2020 | SCG | ECC | CZ08 | 1985 | 4.411 | old
2020 | SCG | ECC | CZ08 | 1996 | 2.942 | old
2020 | SCG | ECC | CZ08 | 2003 | 1.718 | ex
2020 | SCG | ECC | CZ08 | 2007 | 0.761 | ex
2020 | SCG | ECC | CZ08 | 2011 | 0.761 | ex
2020 | SCG | ECC | CZ08 | 2015 | 0.571 | ex
2020 | SCG | ECC | CZ08 | 2017 | 0.571 | rec
2020 | SCG | ECC | CZ08 | 2020 | 0.19 | rec
2020 | SCG | ECC | CZ08 | New | 0.19 | new
2020 | SCG | ECC | CZ09 | 1975 | 15.384 | old
2020 | SCG | ECC | CZ09 | 1985 | 2.253 | old
2020 | SCG | ECC | CZ09 | 1996 | 1.915 | old
2020 | SCG | ECC | CZ09 | 2003 | 1.181 | ex
2020 | SCG | ECC | CZ09 | 2007 | 0.474 | ex
2020 | SCG | ECC | CZ09 | 2011 | 0.474 | ex
2020 | SCG | ECC | CZ09 | 2015 | 0.356 | ex
2020 | SCG | ECC | CZ09 | 2017 | 0.356 | rec
2020 | SCG | ECC | CZ09 | 2020 | 0.119 | rec
2020 | SCG | ECC | CZ09 | New | 0.119 | new
2020 | SCG | ECC | CZ10 | 1975 | 2.219 | old
2020 | SCG | ECC | CZ10 | 1985 | 1.348 | old
2020 | SCG | ECC | CZ10 | 1996 | 0.934 | old
2020 | SCG | ECC | CZ10 | 2003 | 1.009 | ex
2020 | SCG | ECC | CZ10 | 2007 | 0.422 | ex
2020 | SCG | ECC | CZ10 | 2011 | 0.422 | ex
2020 | SCG | ECC | CZ10 | 2015 | 0.316 | ex
2020 | SCG | ECC | CZ10 | 2017 | 0.316 | rec
2020 | SCG | ECC | CZ10 | 2020 | 0.105 | rec
2020 | SCG | ECC | CZ10 | New | 0.105 | new
2020 | SCG | ECC | CZ13 | 1975 | 0.432 | old
2020 | SCG | ECC | CZ13 | 1985 | 0.256 | old
2020 | SCG | ECC | CZ13 | 1996 | 0.186 | old
2020 | SCG | ECC | CZ13 | 2003 | 0.208 | ex
2020 | SCG | ECC | CZ13 | 2007 | 0.112 | ex
2020 | SCG | ECC | CZ13 | 2011 | 0.112 | ex
2020 | SCG | ECC | CZ13 | 2015 | 0.084 | ex
2020 | SCG | ECC | CZ13 | 2017 | 0.084 | rec
2020 | SCG | ECC | CZ13 | 2020 | 0.028 | rec
2020 | SCG | ECC | CZ13 | New | 0.028 | new
2020 | SCG | ECC | CZ14 | 1975 | 0.823 | old
2020 | SCG | ECC | CZ14 | 1985 | 0.465 | old
2020 | SCG | ECC | CZ14 | 1996 | 0.329 | old
2020 | SCG | ECC | CZ14 | 2003 | 0.336 | ex
2020 | SCG | ECC | CZ14 | 2007 | 0.141 | ex
2020 | SCG | ECC | CZ14 | 2011 | 0.141 | ex
2020 | SCG | ECC | CZ14 | 2015 | 0.106 | ex
2020 | SCG | ECC | CZ14 | 2017 | 0.106 | rec
2020 | SCG | ECC | CZ14 | 2020 | 0.035 | rec
2020 | SCG | ECC | CZ14 | New | 0.035 | new
2020 | SCG | ECC | CZ15 | 1975 | 0.646 | old
2020 | SCG | ECC | CZ15 | 1985 | 0.392 | old
2020 | SCG | ECC | CZ15 | 1996 | 0.272 | old
2020 | SCG | ECC | CZ15 | 2003 | 0.294 | ex
2020 | SCG | ECC | CZ15 | 2007 | 0.123 | ex
2020 | SCG | ECC | CZ15 | 2011 | 0.123 | ex
2020 | SCG | ECC | CZ15 | 2015 | 0.092 | ex
2020 | SCG | ECC | CZ15 | 2017 | 0.092 | rec
2020 | SCG | ECC | CZ15 | 2020 | 0.031 | rec
2020 | SCG | ECC | CZ15 | New | 0.031 | new
2020 | SCG | ECC | CZ16 | 1975 | 1.447 | old
2020 | SCG | ECC | CZ16 | 1985 | 0.872 | old
2020 | SCG | ECC | CZ16 | 1996 | 0.607 | old
2020 | SCG | ECC | CZ16 | 2003 | 0.653 | ex
2020 | SCG | ECC | CZ16 | 2007 | 0.277 | ex
2020 | SCG | ECC | CZ16 | 2011 | 0.277 | ex
2020 | SCG | ECC | CZ16 | 2015 | 0.208 | ex
2020 | SCG | ECC | CZ16 | 2017 | 0.208 | rec
2020 | SCG | ECC | CZ16 | 2020 | 0.069 | rec
2020 | SCG | ECC | CZ16 | New | 0.069 | new
2020 | SCG | EPr | CZ05 | 1975 | 0.051 | old
2020 | SCG | EPr | CZ05 | 1985 | 0.006 | old
2020 | SCG | EPr | CZ05 | 1996 | 0.005 | old
2020 | SCG | EPr | CZ05 | 2003 | 0.004 | ex
2020 | SCG | EPr | CZ05 | 2007 | 0.001 | ex
2020 | SCG | EPr | CZ05 | 2011 | 0.001 | ex
2020 | SCG | EPr | CZ05 | 2015 | 0.001 | ex
2020 | SCG | EPr | CZ05 | 2017 | 0.001 | rec
2020 | SCG | EPr | CZ05 | 2020 | 0.001 | rec
2020 | SCG | EPr | CZ05 | New | 0.001 | new
2020 | SCG | EPr | CZ06 | 1975 | 10.282 | old
2020 | SCG | EPr | CZ06 | 1985 | 1.075 | old
2020 | SCG | EPr | CZ06 | 1996 | 0.948 | old
2020 | SCG | EPr | CZ06 | 2003 | 0.758 | ex
2020 | SCG | EPr | CZ06 | 2007 | 0.225 | ex
2020 | SCG | EPr | CZ06 | 2011 | 0.225 | ex
2020 | SCG | EPr | CZ06 | 2015 | 0.169 | ex
2020 | SCG | EPr | CZ06 | 2017 | 0.169 | rec
2020 | SCG | EPr | CZ06 | 2020 | 0.056 | rec
2020 | SCG | EPr | CZ06 | New | 0.056 | new
2020 | SCG | EPr | CZ08 | 1975 | 18.187 | old
2020 | SCG | EPr | CZ08 | 1985 | 1.882 | old
2020 | SCG | EPr | CZ08 | 1996 | 1.676 | old
2020 | SCG | EPr | CZ08 | 2003 | 1.39 | ex
2020 | SCG | EPr | CZ08 | 2007 | 0.403 | ex
2020 | SCG | EPr | CZ08 | 2011 | 0.403 | ex
2020 | SCG | EPr | CZ08 | 2015 | 0.303 | ex
2020 | SCG | EPr | CZ08 | 2017 | 0.303 | rec
2020 | SCG | EPr | CZ08 | 2020 | 0.101 | rec
2020 | SCG | EPr | CZ08 | New | 0.101 | new
2020 | SCG | EPr | CZ09 | 1975 | 17.43 | old
2020 | SCG | EPr | CZ09 | 1985 | 1.4 | old
2020 | SCG | EPr | CZ09 | 1996 | 1.408 | old
2020 | SCG | EPr | CZ09 | 2003 | 1.486 | ex
2020 | SCG | EPr | CZ09 | 2007 | 0.355 | ex
2020 | SCG | EPr | CZ09 | 2011 | 0.355 | ex
2020 | SCG | EPr | CZ09 | 2015 | 0.267 | ex
2020 | SCG | EPr | CZ09 | 2017 | 0.267 | rec
2020 | SCG | EPr | CZ09 | 2020 | 0.089 | rec
2020 | SCG | EPr | CZ09 | New | 0.089 | new
2020 | SCG | EPr | CZ10 | 1975 | 5.598 | old
2020 | SCG | EPr | CZ10 | 1985 | 2.398 | old
2020 | SCG | EPr | CZ10 | 1996 | 2.432 | old
2020 | SCG | EPr | CZ10 | 2003 | 2.248 | ex
2020 | SCG | EPr | CZ10 | 2007 | 0.57 | ex
2020 | SCG | EPr | CZ10 | 2011 | 0.57 | ex
2020 | SCG | EPr | CZ10 | 2015 | 0.427 | ex
2020 | SCG | EPr | CZ10 | 2017 | 0.427 | rec
2020 | SCG | EPr | CZ10 | 2020 | 0.142 | rec
2020 | SCG | EPr | CZ10 | New | 0.142 | new
2020 | SCG | EPr | CZ13 | 1975 | 1.468 | old
2020 | SCG | EPr | CZ13 | 1985 | 0.358 | old
2020 | SCG | EPr | CZ13 | 1996 | 0.458 | old
2020 | SCG | EPr | CZ13 | 2003 | 0.28 | ex
2020 | SCG | EPr | CZ13 | 2007 | 0.125 | ex
2020 | SCG | EPr | CZ13 | 2011 | 0.125 | ex
2020 | SCG | EPr | CZ13 | 2015 | 0.094 | ex
2020 | SCG | EPr | CZ13 | 2017 | 0.094 | rec
2020 | SCG | EPr | CZ13 | 2020 | 0.031 | rec
2020 | SCG | EPr | CZ13 | New | 0.031 | new
2020 | SCG | EPr | CZ14 | 1975 | 1.795 | old
2020 | SCG | EPr | CZ14 | 1985 | 0.528 | old
2020 | SCG | EPr | CZ14 | 1996 | 0.537 | old
2020 | SCG | EPr | CZ14 | 2003 | 0.495 | ex
2020 | SCG | EPr | CZ14 | 2007 | 0.129 | ex
2020 | SCG | EPr | CZ14 | 2011 | 0.129 | ex
2020 | SCG | EPr | CZ14 | 2015 | 0.097 | ex
2020 | SCG | EPr | CZ14 | 2017 | 0.097 | rec
2020 | SCG | EPr | CZ14 | 2020 | 0.032 | rec
2020 | SCG | EPr | CZ14 | New | 0.032 | new
2020 | SCG | EPr | CZ15 | 1975 | 0.499 | old
2020 | SCG | EPr | CZ15 | 1985 | 0.214 | old
2020 | SCG | EPr | CZ15 | 1996 | 0.217 | old
2020 | SCG | EPr | CZ15 | 2003 | 0.2 | ex
2020 | SCG | EPr | CZ15 | 2007 | 0.051 | ex
2020 | SCG | EPr | CZ15 | 2011 | 0.051 | ex
2020 | SCG | EPr | CZ15 | 2015 | 0.038 | ex
2020 | SCG | EPr | CZ15 | 2017 | 0.038 | rec
2020 | SCG | EPr | CZ15 | 2020 | 0.013 | rec
2020 | SCG | EPr | CZ15 | New | 0.013 | new
2020 | SCG | EPr | CZ16 | 1975 | 0.776 | old
2020 | SCG | EPr | CZ16 | 1985 | 0.261 | old
2020 | SCG | EPr | CZ16 | 1996 | 0.276 | old
2020 | SCG | EPr | CZ16 | 2003 | 0.238 | ex
2020 | SCG | EPr | CZ16 | 2007 | 0.067 | ex
2020 | SCG | EPr | CZ16 | 2011 | 0.067 | ex
2020 | SCG | EPr | CZ16 | 2015 | 0.05 | ex
2020 | SCG | EPr | CZ16 | 2017 | 0.05 | rec
2020 | SCG | EPr | CZ16 | 2020 | 0.017 | rec
2020 | SCG | EPr | CZ16 | New | 0.017 | new
2020 | SCG | ERC | CZ05 | 1975 | 0.051 | old
2020 | SCG | ERC | CZ05 | 1985 | 0.006 | old
2020 | SCG | ERC | CZ05 | 1996 | 0.005 | old
2020 | SCG | ERC | CZ05 | 2003 | 0.004 | ex
2020 | SCG | ERC | CZ05 | 2007 | 0.001 | ex
2020 | SCG | ERC | CZ05 | 2011 | 0.001 | ex
2020 | SCG | ERC | CZ05 | 2015 | 0.001 | ex
2020 | SCG | ERC | CZ05 | 2017 | 0.001 | rec
2020 | SCG | ERC | CZ05 | 2020 | 0.001 | rec
2020 | SCG | ERC | CZ05 | New | 0.001 | new
2020 | SCG | ERC | CZ06 | 1975 | 10.282 | old
2020 | SCG | ERC | CZ06 | 1985 | 1.075 | old
2020 | SCG | ERC | CZ06 | 1996 | 0.948 | old
2020 | SCG | ERC | CZ06 | 2003 | 0.758 | ex
2020 | SCG | ERC | CZ06 | 2007 | 0.225 | ex
2020 | SCG | ERC | CZ06 | 2011 | 0.225 | ex
2020 | SCG | ERC | CZ06 | 2015 | 0.169 | ex
2020 | SCG | ERC | CZ06 | 2017 | 0.169 | rec
2020 | SCG | ERC | CZ06 | 2020 | 0.056 | rec
2020 | SCG | ERC | CZ06 | New | 0.056 | new
2020 | SCG | ERC | CZ08 | 1975 | 18.187 | old
2020 | SCG | ERC | CZ08 | 1985 | 1.882 | old
2020 | SCG | ERC | CZ08 | 1996 | 1.676 | old
2020 | SCG | ERC | CZ08 | 2003 | 1.39 | ex
2020 | SCG | ERC | CZ08 | 2007 | 0.403 | ex
2020 | SCG | ERC | CZ08 | 2011 | 0.403 | ex
2020 | SCG | ERC | CZ08 | 2015 | 0.303 | ex
2020 | SCG | ERC | CZ08 | 2017 | 0.303 | rec
2020 | SCG | ERC | CZ08 | 2020 | 0.101 | rec
2020 | SCG | ERC | CZ08 | New | 0.101 | new
2020 | SCG | ERC | CZ09 | 1975 | 17.43 | old
2020 | SCG | ERC | CZ09 | 1985 | 1.4 | old
2020 | SCG | ERC | CZ09 | 1996 | 1.408 | old
2020 | SCG | ERC | CZ09 | 2003 | 1.486 | ex
2020 | SCG | ERC | CZ09 | 2007 | 0.355 | ex
2020 | SCG | ERC | CZ09 | 2011 | 0.355 | ex
2020 | SCG | ERC | CZ09 | 2015 | 0.267 | ex
2020 | SCG | ERC | CZ09 | 2017 | 0.267 | rec
2020 | SCG | ERC | CZ09 | 2020 | 0.089 | rec
2020 | SCG | ERC | CZ09 | New | 0.089 | new
2020 | SCG | ERC | CZ10 | 1975 | 5.598 | old
2020 | SCG | ERC | CZ10 | 1985 | 2.398 | old
2020 | SCG | ERC | CZ10 | 1996 | 2.432 | old
2020 | SCG | ERC | CZ10 | 2003 | 2.248 | ex
2020 | SCG | ERC | CZ10 | 2007 | 0.57 | ex
2020 | SCG | ERC | CZ10 | 2011 | 0.57 | ex
2020 | SCG | ERC | CZ10 | 2015 | 0.427 | ex
2020 | SCG | ERC | CZ10 | 2017 | 0.427 | rec
2020 | SCG | ERC | CZ10 | 2020 | 0.142 | rec
2020 | SCG | ERC | CZ10 | New | 0.142 | new
2020 | SCG | ERC | CZ13 | 1975 | 1.468 | old
2020 | SCG | ERC | CZ13 | 1985 | 0.358 | old
2020 | SCG | ERC | CZ13 | 1996 | 0.458 | old
2020 | SCG | ERC | CZ13 | 2003 | 0.28 | ex
2020 | SCG | ERC | CZ13 | 2007 | 0.125 | ex
2020 | SCG | ERC | CZ13 | 2011 | 0.125 | ex
2020 | SCG | ERC | CZ13 | 2015 | 0.094 | ex
2020 | SCG | ERC | CZ13 | 2017 | 0.094 | rec
2020 | SCG | ERC | CZ13 | 2020 | 0.031 | rec
2020 | SCG | ERC | CZ13 | New | 0.031 | new
2020 | SCG | ERC | CZ14 | 1975 | 1.795 | old
2020 | SCG | ERC | CZ14 | 1985 | 0.528 | old
2020 | SCG | ERC | CZ14 | 1996 | 0.537 | old
2020 | SCG | ERC | CZ14 | 2003 | 0.495 | ex
2020 | SCG | ERC | CZ14 | 2007 | 0.129 | ex
2020 | SCG | ERC | CZ14 | 2011 | 0.129 | ex
2020 | SCG | ERC | CZ14 | 2015 | 0.097 | ex
2020 | SCG | ERC | CZ14 | 2017 | 0.097 | rec
2020 | SCG | ERC | CZ14 | 2020 | 0.032 | rec
2020 | SCG | ERC | CZ14 | New | 0.032 | new
2020 | SCG | ERC | CZ15 | 1975 | 0.499 | old
2020 | SCG | ERC | CZ15 | 1985 | 0.214 | old
2020 | SCG | ERC | CZ15 | 1996 | 0.217 | old
2020 | SCG | ERC | CZ15 | 2003 | 0.2 | ex
2020 | SCG | ERC | CZ15 | 2007 | 0.051 | ex
2020 | SCG | ERC | CZ15 | 2011 | 0.051 | ex
2020 | SCG | ERC | CZ15 | 2015 | 0.038 | ex
2020 | SCG | ERC | CZ15 | 2017 | 0.038 | rec
2020 | SCG | ERC | CZ15 | 2020 | 0.013 | rec
2020 | SCG | ERC | CZ15 | New | 0.013 | new
2020 | SCG | ERC | CZ16 | 1975 | 0.776 | old
2020 | SCG | ERC | CZ16 | 1985 | 0.261 | old
2020 | SCG | ERC | CZ16 | 1996 | 0.276 | old
2020 | SCG | ERC | CZ16 | 2003 | 0.238 | ex
2020 | SCG | ERC | CZ16 | 2007 | 0.067 | ex
2020 | SCG | ERC | CZ16 | 2011 | 0.067 | ex
2020 | SCG | ERC | CZ16 | 2015 | 0.05 | ex
2020 | SCG | ERC | CZ16 | 2017 | 0.05 | rec
2020 | SCG | ERC | CZ16 | 2020 | 0.017 | rec
2020 | SCG | ERC | CZ16 | New | 0.017 | new
2020 | SCG | ESe | CZ05 | 1975 | 0.051 | old
2020 | SCG | ESe | CZ05 | 1985 | 0.006 | old
2020 | SCG | ESe | CZ05 | 1996 | 0.005 | old
2020 | SCG | ESe | CZ05 | 2003 | 0.004 | ex
2020 | SCG | ESe | CZ05 | 2007 | 0.001 | ex
2020 | SCG | ESe | CZ05 | 2011 | 0.001 | ex
2020 | SCG | ESe | CZ05 | 2015 | 0.001 | ex
2020 | SCG | ESe | CZ05 | 2017 | 0.001 | rec
2020 | SCG | ESe | CZ05 | 2020 | 0.001 | rec
2020 | SCG | ESe | CZ05 | New | 0.001 | new
2020 | SCG | ESe | CZ06 | 1975 | 10.282 | old
2020 | SCG | ESe | CZ06 | 1985 | 1.075 | old
2020 | SCG | ESe | CZ06 | 1996 | 0.948 | old
2020 | SCG | ESe | CZ06 | 2003 | 0.758 | ex
2020 | SCG | ESe | CZ06 | 2007 | 0.225 | ex
2020 | SCG | ESe | CZ06 | 2011 | 0.225 | ex
2020 | SCG | ESe | CZ06 | 2015 | 0.169 | ex
2020 | SCG | ESe | CZ06 | 2017 | 0.169 | rec
2020 | SCG | ESe | CZ06 | 2020 | 0.056 | rec
2020 | SCG | ESe | CZ06 | New | 0.056 | new
2020 | SCG | ESe | CZ08 | 1975 | 18.187 | old
2020 | SCG | ESe | CZ08 | 1985 | 1.882 | old
2020 | SCG | ESe | CZ08 | 1996 | 1.676 | old
2020 | SCG | ESe | CZ08 | 2003 | 1.39 | ex
2020 | SCG | ESe | CZ08 | 2007 | 0.403 | ex
2020 | SCG | ESe | CZ08 | 2011 | 0.403 | ex
2020 | SCG | ESe | CZ08 | 2015 | 0.303 | ex
2020 | SCG | ESe | CZ08 | 2017 | 0.303 | rec
2020 | SCG | ESe | CZ08 | 2020 | 0.101 | rec
2020 | SCG | ESe | CZ08 | New | 0.101 | new
2020 | SCG | ESe | CZ09 | 1975 | 17.43 | old
2020 | SCG | ESe | CZ09 | 1985 | 1.4 | old
2020 | SCG | ESe | CZ09 | 1996 | 1.408 | old
2020 | SCG | ESe | CZ09 | 2003 | 1.486 | ex
2020 | SCG | ESe | CZ09 | 2007 | 0.355 | ex
2020 | SCG | ESe | CZ09 | 2011 | 0.355 | ex
2020 | SCG | ESe | CZ09 | 2015 | 0.267 | ex
2020 | SCG | ESe | CZ09 | 2017 | 0.267 | rec
2020 | SCG | ESe | CZ09 | 2020 | 0.089 | rec
2020 | SCG | ESe | CZ09 | New | 0.089 | new
2020 | SCG | ESe | CZ10 | 1975 | 5.598 | old
2020 | SCG | ESe | CZ10 | 1985 | 2.398 | old
2020 | SCG | ESe | CZ10 | 1996 | 2.432 | old
2020 | SCG | ESe | CZ10 | 2003 | 2.248 | ex
2020 | SCG | ESe | CZ10 | 2007 | 0.57 | ex
2020 | SCG | ESe | CZ10 | 2011 | 0.57 | ex
2020 | SCG | ESe | CZ10 | 2015 | 0.427 | ex
2020 | SCG | ESe | CZ10 | 2017 | 0.427 | rec
2020 | SCG | ESe | CZ10 | 2020 | 0.142 | rec
2020 | SCG | ESe | CZ10 | New | 0.142 | new
2020 | SCG | ESe | CZ13 | 1975 | 1.468 | old
2020 | SCG | ESe | CZ13 | 1985 | 0.358 | old
2020 | SCG | ESe | CZ13 | 1996 | 0.458 | old
2020 | SCG | ESe | CZ13 | 2003 | 0.28 | ex
2020 | SCG | ESe | CZ13 | 2007 | 0.125 | ex
2020 | SCG | ESe | CZ13 | 2011 | 0.125 | ex
2020 | SCG | ESe | CZ13 | 2015 | 0.094 | ex
2020 | SCG | ESe | CZ13 | 2017 | 0.094 | rec
2020 | SCG | ESe | CZ13 | 2020 | 0.031 | rec
2020 | SCG | ESe | CZ13 | New | 0.031 | new
2020 | SCG | ESe | CZ14 | 1975 | 1.795 | old
2020 | SCG | ESe | CZ14 | 1985 | 0.528 | old
2020 | SCG | ESe | CZ14 | 1996 | 0.537 | old
2020 | SCG | ESe | CZ14 | 2003 | 0.495 | ex
2020 | SCG | ESe | CZ14 | 2007 | 0.129 | ex
2020 | SCG | ESe | CZ14 | 2011 | 0.129 | ex
2020 | SCG | ESe | CZ14 | 2015 | 0.097 | ex
2020 | SCG | ESe | CZ14 | 2017 | 0.097 | rec
2020 | SCG | ESe | CZ14 | 2020 | 0.032 | rec
2020 | SCG | ESe | CZ14 | New | 0.032 | new
2020 | SCG | ESe | CZ15 | 1975 | 0.499 | old
2020 | SCG | ESe | CZ15 | 1985 | 0.214 | old
2020 | SCG | ESe | CZ15 | 1996 | 0.217 | old
2020 | SCG | ESe | CZ15 | 2003 | 0.2 | ex
2020 | SCG | ESe | CZ15 | 2007 | 0.051 | ex
2020 | SCG | ESe | CZ15 | 2011 | 0.051 | ex
2020 | SCG | ESe | CZ15 | 2015 | 0.038 | ex
2020 | SCG | ESe | CZ15 | 2017 | 0.038 | rec
2020 | SCG | ESe | CZ15 | 2020 | 0.013 | rec
2020 | SCG | ESe | CZ15 | New | 0.013 | new
2020 | SCG | ESe | CZ16 | 1975 | 0.776 | old
2020 | SCG | ESe | CZ16 | 1985 | 0.261 | old
2020 | SCG | ESe | CZ16 | 1996 | 0.276 | old
2020 | SCG | ESe | CZ16 | 2003 | 0.238 | ex
2020 | SCG | ESe | CZ16 | 2007 | 0.067 | ex
2020 | SCG | ESe | CZ16 | 2011 | 0.067 | ex
2020 | SCG | ESe | CZ16 | 2015 | 0.05 | ex
2020 | SCG | ESe | CZ16 | 2017 | 0.05 | rec
2020 | SCG | ESe | CZ16 | 2020 | 0.017 | rec
2020 | SCG | ESe | CZ16 | New | 0.017 | new
2020 | SCG | EUD | CZ05 | 1975 | 0.009 | old
2020 | SCG | EUD | CZ05 | 1985 | 0.003 | old
2020 | SCG | EUD | CZ05 | 1996 | 0.002 | old
2020 | SCG | EUD | CZ05 | 2003 | 0.001 | ex
2020 | SCG | EUD | CZ05 | 2007 | 0.001 | ex
2020 | SCG | EUD | CZ05 | 2011 | 0.001 | ex
2020 | SCG | EUD | CZ05 | 2015 | 0.001 | ex
2020 | SCG | EUD | CZ05 | 2017 | 0.001 | rec
2020 | SCG | EUD | CZ05 | 2020 | 0.001 | rec
2020 | SCG | EUD | CZ05 | New | 0.001 | new
2020 | SCG | EUD | CZ06 | 1975 | 8.927 | old
2020 | SCG | EUD | CZ06 | 1985 | 2.669 | old
2020 | SCG | EUD | CZ06 | 1996 | 1.819 | old
2020 | SCG | EUD | CZ06 | 2003 | 1.066 | ex
2020 | SCG | EUD | CZ06 | 2007 | 0.47 | ex
2020 | SCG | EUD | CZ06 | 2011 | 0.47 | ex
2020 | SCG | EUD | CZ06 | 2015 | 0.353 | ex
2020 | SCG | EUD | CZ06 | 2017 | 0.353 | rec
2020 | SCG | EUD | CZ06 | 2020 | 0.118 | rec
2020 | SCG | EUD | CZ06 | New | 0.118 | new
2020 | SCG | EUD | CZ08 | 1975 | 15.19 | old
2020 | SCG | EUD | CZ08 | 1985 | 4.411 | old
2020 | SCG | EUD | CZ08 | 1996 | 2.942 | old
2020 | SCG | EUD | CZ08 | 2003 | 1.718 | ex
2020 | SCG | EUD | CZ08 | 2007 | 0.761 | ex
2020 | SCG | EUD | CZ08 | 2011 | 0.761 | ex
2020 | SCG | EUD | CZ08 | 2015 | 0.571 | ex
2020 | SCG | EUD | CZ08 | 2017 | 0.571 | rec
2020 | SCG | EUD | CZ08 | 2020 | 0.19 | rec
2020 | SCG | EUD | CZ08 | New | 0.19 | new
2020 | SCG | EUD | CZ09 | 1975 | 15.384 | old
2020 | SCG | EUD | CZ09 | 1985 | 2.253 | old
2020 | SCG | EUD | CZ09 | 1996 | 1.915 | old
2020 | SCG | EUD | CZ09 | 2003 | 1.181 | ex
2020 | SCG | EUD | CZ09 | 2007 | 0.474 | ex
2020 | SCG | EUD | CZ09 | 2011 | 0.474 | ex
2020 | SCG | EUD | CZ09 | 2015 | 0.356 | ex
2020 | SCG | EUD | CZ09 | 2017 | 0.356 | rec
2020 | SCG | EUD | CZ09 | 2020 | 0.119 | rec
2020 | SCG | EUD | CZ09 | New | 0.119 | new
2020 | SCG | EUD | CZ10 | 1975 | 2.219 | old
2020 | SCG | EUD | CZ10 | 1985 | 1.348 | old
2020 | SCG | EUD | CZ10 | 1996 | 0.934 | old
2020 | SCG | EUD | CZ10 | 2003 | 1.009 | ex
2020 | SCG | EUD | CZ10 | 2007 | 0.422 | ex
2020 | SCG | EUD | CZ10 | 2011 | 0.422 | ex
2020 | SCG | EUD | CZ10 | 2015 | 0.316 | ex
2020 | SCG | EUD | CZ10 | 2017 | 0.316 | rec
2020 | SCG | EUD | CZ10 | 2020 | 0.105 | rec
2020 | SCG | EUD | CZ10 | New | 0.105 | new
2020 | SCG | EUD | CZ13 | 1975 | 0.432 | old
2020 | SCG | EUD | CZ13 | 1985 | 0.256 | old
2020 | SCG | EUD | CZ13 | 1996 | 0.186 | old
2020 | SCG | EUD | CZ13 | 2003 | 0.208 | ex
2020 | SCG | EUD | CZ13 | 2007 | 0.112 | ex
2020 | SCG | EUD | CZ13 | 2011 | 0.112 | ex
2020 | SCG | EUD | CZ13 | 2015 | 0.084 | ex
2020 | SCG | EUD | CZ13 | 2017 | 0.084 | rec
2020 | SCG | EUD | CZ13 | 2020 | 0.028 | rec
2020 | SCG | EUD | CZ13 | New | 0.028 | new
2020 | SCG | EUD | CZ14 | 1975 | 0.823 | old
2020 | SCG | EUD | CZ14 | 1985 | 0.465 | old
2020 | SCG | EUD | CZ14 | 1996 | 0.329 | old
2020 | SCG | EUD | CZ14 | 2003 | 0.336 | ex
2020 | SCG | EUD | CZ14 | 2007 | 0.141 | ex
2020 | SCG | EUD | CZ14 | 2011 | 0.141 | ex
2020 | SCG | EUD | CZ14 | 2015 | 0.106 | ex
2020 | SCG | EUD | CZ14 | 2017 | 0.106 | rec
2020 | SCG | EUD | CZ14 | 2020 | 0.035 | rec
2020 | SCG | EUD | CZ14 | New | 0.035 | new
2020 | SCG | EUD | CZ15 | 1975 | 0.646 | old
2020 | SCG | EUD | CZ15 | 1985 | 0.392 | old
2020 | SCG | EUD | CZ15 | 1996 | 0.272 | old
2020 | SCG | EUD | CZ15 | 2003 | 0.294 | ex
2020 | SCG | EUD | CZ15 | 2007 | 0.123 | ex
2020 | SCG | EUD | CZ15 | 2011 | 0.123 | ex
2020 | SCG | EUD | CZ15 | 2015 | 0.092 | ex
2020 | SCG | EUD | CZ15 | 2017 | 0.092 | rec
2020 | SCG | EUD | CZ15 | 2020 | 0.031 | rec
2020 | SCG | EUD | CZ15 | New | 0.031 | new
2020 | SCG | EUD | CZ16 | 1975 | 1.447 | old
2020 | SCG | EUD | CZ16 | 1985 | 0.872 | old
2020 | SCG | EUD | CZ16 | 1996 | 0.607 | old
2020 | SCG | EUD | CZ16 | 2003 | 0.653 | ex
2020 | SCG | EUD | CZ16 | 2007 | 0.277 | ex
2020 | SCG | EUD | CZ16 | 2011 | 0.277 | ex
2020 | SCG | EUD | CZ16 | 2015 | 0.208 | ex
2020 | SCG | EUD | CZ16 | 2017 | 0.208 | rec
2020 | SCG | EUD | CZ16 | 2020 | 0.069 | rec
2020 | SCG | EUD | CZ16 | New | 0.069 | new
2020 | SCG | EUn | CZ05 | 1975 | 0.009 | old
2020 | SCG | EUn | CZ05 | 1985 | 0.003 | old
2020 | SCG | EUn | CZ05 | 1996 | 0.002 | old
2020 | SCG | EUn | CZ05 | 2003 | 0.001 | ex
2020 | SCG | EUn | CZ05 | 2007 | 0.001 | ex
2020 | SCG | EUn | CZ05 | 2011 | 0.001 | ex
2020 | SCG | EUn | CZ05 | 2015 | 0.001 | ex
2020 | SCG | EUn | CZ05 | 2017 | 0.001 | rec
2020 | SCG | EUn | CZ05 | 2020 | 0.001 | rec
2020 | SCG | EUn | CZ05 | New | 0.001 | new
2020 | SCG | EUn | CZ06 | 1975 | 8.927 | old
2020 | SCG | EUn | CZ06 | 1985 | 2.669 | old
2020 | SCG | EUn | CZ06 | 1996 | 1.819 | old
2020 | SCG | EUn | CZ06 | 2003 | 1.066 | ex
2020 | SCG | EUn | CZ06 | 2007 | 0.47 | ex
2020 | SCG | EUn | CZ06 | 2011 | 0.47 | ex
2020 | SCG | EUn | CZ06 | 2015 | 0.353 | ex
2020 | SCG | EUn | CZ06 | 2017 | 0.353 | rec
2020 | SCG | EUn | CZ06 | 2020 | 0.118 | rec
2020 | SCG | EUn | CZ06 | New | 0.118 | new
2020 | SCG | EUn | CZ08 | 1975 | 15.19 | old
2020 | SCG | EUn | CZ08 | 1985 | 4.411 | old
2020 | SCG | EUn | CZ08 | 1996 | 2.942 | old
2020 | SCG | EUn | CZ08 | 2003 | 1.718 | ex
2020 | SCG | EUn | CZ08 | 2007 | 0.761 | ex
2020 | SCG | EUn | CZ08 | 2011 | 0.761 | ex
2020 | SCG | EUn | CZ08 | 2015 | 0.571 | ex
2020 | SCG | EUn | CZ08 | 2017 | 0.571 | rec
2020 | SCG | EUn | CZ08 | 2020 | 0.19 | rec
2020 | SCG | EUn | CZ08 | New | 0.19 | new
2020 | SCG | EUn | CZ09 | 1975 | 15.384 | old
2020 | SCG | EUn | CZ09 | 1985 | 2.253 | old
2020 | SCG | EUn | CZ09 | 1996 | 1.915 | old
2020 | SCG | EUn | CZ09 | 2003 | 1.181 | ex
2020 | SCG | EUn | CZ09 | 2007 | 0.474 | ex
2020 | SCG | EUn | CZ09 | 2011 | 0.474 | ex
2020 | SCG | EUn | CZ09 | 2015 | 0.356 | ex
2020 | SCG | EUn | CZ09 | 2017 | 0.356 | rec
2020 | SCG | EUn | CZ09 | 2020 | 0.119 | rec
2020 | SCG | EUn | CZ09 | New | 0.119 | new
2020 | SCG | EUn | CZ10 | 1975 | 2.219 | old
2020 | SCG | EUn | CZ10 | 1985 | 1.348 | old
2020 | SCG | EUn | CZ10 | 1996 | 0.934 | old
2020 | SCG | EUn | CZ10 | 2003 | 1.009 | ex
2020 | SCG | EUn | CZ10 | 2007 | 0.422 | ex
2020 | SCG | EUn | CZ10 | 2011 | 0.422 | ex
2020 | SCG | EUn | CZ10 | 2015 | 0.316 | ex
2020 | SCG | EUn | CZ10 | 2017 | 0.316 | rec
2020 | SCG | EUn | CZ10 | 2020 | 0.105 | rec
2020 | SCG | EUn | CZ10 | New | 0.105 | new
2020 | SCG | EUn | CZ13 | 1975 | 0.432 | old
2020 | SCG | EUn | CZ13 | 1985 | 0.256 | old
2020 | SCG | EUn | CZ13 | 1996 | 0.186 | old
2020 | SCG | EUn | CZ13 | 2003 | 0.208 | ex
2020 | SCG | EUn | CZ13 | 2007 | 0.112 | ex
2020 | SCG | EUn | CZ13 | 2011 | 0.112 | ex
2020 | SCG | EUn | CZ13 | 2015 | 0.084 | ex
2020 | SCG | EUn | CZ13 | 2017 | 0.084 | rec
2020 | SCG | EUn | CZ13 | 2020 | 0.028 | rec
2020 | SCG | EUn | CZ13 | New | 0.028 | new
2020 | SCG | EUn | CZ14 | 1975 | 0.823 | old
2020 | SCG | EUn | CZ14 | 1985 | 0.465 | old
2020 | SCG | EUn | CZ14 | 1996 | 0.329 | old
2020 | SCG | EUn | CZ14 | 2003 | 0.336 | ex
2020 | SCG | EUn | CZ14 | 2007 | 0.141 | ex
2020 | SCG | EUn | CZ14 | 2011 | 0.141 | ex
2020 | SCG | EUn | CZ14 | 2015 | 0.106 | ex
2020 | SCG | EUn | CZ14 | 2017 | 0.106 | rec
2020 | SCG | EUn | CZ14 | 2020 | 0.035 | rec
2020 | SCG | EUn | CZ14 | New | 0.035 | new
2020 | SCG | EUn | CZ15 | 1975 | 0.646 | old
2020 | SCG | EUn | CZ15 | 1985 | 0.392 | old
2020 | SCG | EUn | CZ15 | 1996 | 0.272 | old
2020 | SCG | EUn | CZ15 | 2003 | 0.294 | ex
2020 | SCG | EUn | CZ15 | 2007 | 0.123 | ex
2020 | SCG | EUn | CZ15 | 2011 | 0.123 | ex
2020 | SCG | EUn | CZ15 | 2015 | 0.092 | ex
2020 | SCG | EUn | CZ15 | 2017 | 0.092 | rec
2020 | SCG | EUn | CZ15 | 2020 | 0.031 | rec
2020 | SCG | EUn | CZ15 | New | 0.031 | new
2020 | SCG | EUn | CZ16 | 1975 | 1.447 | old
2020 | SCG | EUn | CZ16 | 1985 | 0.872 | old
2020 | SCG | EUn | CZ16 | 1996 | 0.607 | old
2020 | SCG | EUn | CZ16 | 2003 | 0.653 | ex
2020 | SCG | EUn | CZ16 | 2007 | 0.277 | ex
2020 | SCG | EUn | CZ16 | 2011 | 0.277 | ex
2020 | SCG | EUn | CZ16 | 2015 | 0.208 | ex
2020 | SCG | EUn | CZ16 | 2017 | 0.208 | rec
2020 | SCG | EUn | CZ16 | 2020 | 0.069 | rec
2020 | SCG | EUn | CZ16 | New | 0.069 | new
2020 | SCG | Gro | CZ05 | 1975 | 0.206 | old
2020 | SCG | Gro | CZ05 | 1985 | 0.127 | old
2020 | SCG | Gro | CZ05 | 1996 | 0.072 | old
2020 | SCG | Gro | CZ05 | 2003 | 0.031 | ex
2020 | SCG | Gro | CZ05 | 2007 | 0.02 | ex
2020 | SCG | Gro | CZ05 | 2011 | 0.02 | ex
2020 | SCG | Gro | CZ05 | 2015 | 0.015 | ex
2020 | SCG | Gro | CZ05 | 2017 | 0.015 | rec
2020 | SCG | Gro | CZ05 | 2020 | 0.005 | rec
2020 | SCG | Gro | CZ05 | New | 0.005 | new
2020 | SCG | Gro | CZ06 | 1975 | 11.445 | old
2020 | SCG | Gro | CZ06 | 1985 | 7.024 | old
2020 | SCG | Gro | CZ06 | 1996 | 3.95 | old
2020 | SCG | Gro | CZ06 | 2003 | 1.734 | ex
2020 | SCG | Gro | CZ06 | 2007 | 1.12 | ex
2020 | SCG | Gro | CZ06 | 2011 | 1.12 | ex
2020 | SCG | Gro | CZ06 | 2015 | 0.84 | ex
2020 | SCG | Gro | CZ06 | 2017 | 0.84 | rec
2020 | SCG | Gro | CZ06 | 2020 | 0.28 | rec
2020 | SCG | Gro | CZ06 | New | 0.28 | new
2020 | SCG | Gro | CZ08 | 1975 | 17.378 | old
2020 | SCG | Gro | CZ08 | 1985 | 10.706 | old
2020 | SCG | Gro | CZ08 | 1996 | 5.98 | old
2020 | SCG | Gro | CZ08 | 2003 | 2.658 | ex
2020 | SCG | Gro | CZ08 | 2007 | 1.714 | ex
2020 | SCG | Gro | CZ08 | 2011 | 1.714 | ex
2020 | SCG | Gro | CZ08 | 2015 | 1.285 | ex
2020 | SCG | Gro | CZ08 | 2017 | 1.285 | rec
2020 | SCG | Gro | CZ08 | 2020 | 0.428 | rec
2020 | SCG | Gro | CZ08 | New | 0.428 | new
2020 | SCG | Gro | CZ09 | 1975 | 15.622 | old
2020 | SCG | Gro | CZ09 | 1985 | 10.044 | old
2020 | SCG | Gro | CZ09 | 1996 | 5.599 | old
2020 | SCG | Gro | CZ09 | 2003 | 2.702 | ex
2020 | SCG | Gro | CZ09 | 2007 | 1.66 | ex
2020 | SCG | Gro | CZ09 | 2011 | 1.66 | ex
2020 | SCG | Gro | CZ09 | 2015 | 1.245 | ex
2020 | SCG | Gro | CZ09 | 2017 | 1.245 | rec
2020 | SCG | Gro | CZ09 | 2020 | 0.415 | rec
2020 | SCG | Gro | CZ09 | New | 0.415 | new
2020 | SCG | Gro | CZ10 | 1975 | 5.339 | old
2020 | SCG | Gro | CZ10 | 1985 | 8.676 | old
2020 | SCG | Gro | CZ10 | 1996 | 4.536 | old
2020 | SCG | Gro | CZ10 | 2003 | 3.226 | ex
2020 | SCG | Gro | CZ10 | 2007 | 2.001 | ex
2020 | SCG | Gro | CZ10 | 2011 | 2.001 | ex
2020 | SCG | Gro | CZ10 | 2015 | 1.501 | ex
2020 | SCG | Gro | CZ10 | 2017 | 1.501 | rec
2020 | SCG | Gro | CZ10 | 2020 | 0.5 | rec
2020 | SCG | Gro | CZ10 | New | 0.5 | new
2020 | SCG | Gro | CZ13 | 1975 | 1.32 | old
2020 | SCG | Gro | CZ13 | 1985 | 0.834 | old
2020 | SCG | Gro | CZ13 | 1996 | 0.679 | old
2020 | SCG | Gro | CZ13 | 2003 | 0.382 | ex
2020 | SCG | Gro | CZ13 | 2007 | 0.25 | ex
2020 | SCG | Gro | CZ13 | 2011 | 0.25 | ex
2020 | SCG | Gro | CZ13 | 2015 | 0.187 | ex
2020 | SCG | Gro | CZ13 | 2017 | 0.187 | rec
2020 | SCG | Gro | CZ13 | 2020 | 0.063 | rec
2020 | SCG | Gro | CZ13 | New | 0.063 | new
2020 | SCG | Gro | CZ14 | 1975 | 1.531 | old
2020 | SCG | Gro | CZ14 | 1985 | 1.981 | old
2020 | SCG | Gro | CZ14 | 1996 | 1.06 | old
2020 | SCG | Gro | CZ14 | 2003 | 0.712 | ex
2020 | SCG | Gro | CZ14 | 2007 | 0.441 | ex
2020 | SCG | Gro | CZ14 | 2011 | 0.441 | ex
2020 | SCG | Gro | CZ14 | 2015 | 0.331 | ex
2020 | SCG | Gro | CZ14 | 2017 | 0.331 | rec
2020 | SCG | Gro | CZ14 | 2020 | 0.11 | rec
2020 | SCG | Gro | CZ14 | New | 0.11 | new
2020 | SCG | Gro | CZ15 | 1975 | 0.751 | old
2020 | SCG | Gro | CZ15 | 1985 | 1.22 | old
2020 | SCG | Gro | CZ15 | 1996 | 0.638 | old
2020 | SCG | Gro | CZ15 | 2003 | 0.454 | ex
2020 | SCG | Gro | CZ15 | 2007 | 0.281 | ex
2020 | SCG | Gro | CZ15 | 2011 | 0.281 | ex
2020 | SCG | Gro | CZ15 | 2015 | 0.211 | ex
2020 | SCG | Gro | CZ15 | 2017 | 0.211 | rec
2020 | SCG | Gro | CZ15 | 2020 | 0.07 | rec
2020 | SCG | Gro | CZ15 | New | 0.07 | new
2020 | SCG | Gro | CZ16 | 1975 | 0.677 | old
2020 | SCG | Gro | CZ16 | 1985 | 0.727 | old
2020 | SCG | Gro | CZ16 | 1996 | 0.433 | old
2020 | SCG | Gro | CZ16 | 2003 | 0.278 | ex
2020 | SCG | Gro | CZ16 | 2007 | 0.175 | ex
2020 | SCG | Gro | CZ16 | 2011 | 0.175 | ex
2020 | SCG | Gro | CZ16 | 2015 | 0.131 | ex
2020 | SCG | Gro | CZ16 | 2017 | 0.131 | rec
2020 | SCG | Gro | CZ16 | 2020 | 0.044 | rec
2020 | SCG | Gro | CZ16 | New | 0.044 | new
2020 | SCG | HGR | CZ05 | 1975 | 0.052 | old
2020 | SCG | HGR | CZ05 | 1985 | 0.067 | old
2020 | SCG | HGR | CZ05 | 1996 | 0.018 | old
2020 | SCG | HGR | CZ05 | 2003 | 0.01 | ex
2020 | SCG | HGR | CZ05 | 2007 | 0.004 | ex
2020 | SCG | HGR | CZ05 | 2011 | 0.004 | ex
2020 | SCG | HGR | CZ05 | 2015 | 0.003 | ex
2020 | SCG | HGR | CZ05 | 2017 | 0.003 | rec
2020 | SCG | HGR | CZ05 | 2020 | 0.001 | rec
2020 | SCG | HGR | CZ05 | New | 0.001 | new
2020 | SCG | HGR | CZ06 | 1975 | 6.781 | old
2020 | SCG | HGR | CZ06 | 1985 | 8.474 | old
2020 | SCG | HGR | CZ06 | 1996 | 2.309 | old
2020 | SCG | HGR | CZ06 | 2003 | 1.225 | ex
2020 | SCG | HGR | CZ06 | 2007 | 0.564 | ex
2020 | SCG | HGR | CZ06 | 2011 | 0.564 | ex
2020 | SCG | HGR | CZ06 | 2015 | 0.423 | ex
2020 | SCG | HGR | CZ06 | 2017 | 0.423 | rec
2020 | SCG | HGR | CZ06 | 2020 | 0.141 | rec
2020 | SCG | HGR | CZ06 | New | 0.141 | new
2020 | SCG | HGR | CZ08 | 1975 | 5.411 | old
2020 | SCG | HGR | CZ08 | 1985 | 6.279 | old
2020 | SCG | HGR | CZ08 | 1996 | 1.757 | old
2020 | SCG | HGR | CZ08 | 2003 | 0.904 | ex
2020 | SCG | HGR | CZ08 | 2007 | 0.473 | ex
2020 | SCG | HGR | CZ08 | 2011 | 0.473 | ex
2020 | SCG | HGR | CZ08 | 2015 | 0.355 | ex
2020 | SCG | HGR | CZ08 | 2017 | 0.355 | rec
2020 | SCG | HGR | CZ08 | 2020 | 0.118 | rec
2020 | SCG | HGR | CZ08 | New | 0.118 | new
2020 | SCG | HGR | CZ09 | 1975 | 8.182 | old
2020 | SCG | HGR | CZ09 | 1985 | 8.272 | old
2020 | SCG | HGR | CZ09 | 1996 | 2.426 | old
2020 | SCG | HGR | CZ09 | 2003 | 1.039 | ex
2020 | SCG | HGR | CZ09 | 2007 | 0.861 | ex
2020 | SCG | HGR | CZ09 | 2011 | 0.861 | ex
2020 | SCG | HGR | CZ09 | 2015 | 0.646 | ex
2020 | SCG | HGR | CZ09 | 2017 | 0.646 | rec
2020 | SCG | HGR | CZ09 | 2020 | 0.215 | rec
2020 | SCG | HGR | CZ09 | New | 0.215 | new
2020 | SCG | HGR | CZ10 | 1975 | 0.484 | old
2020 | SCG | HGR | CZ10 | 1985 | 1.441 | old
2020 | SCG | HGR | CZ10 | 1996 | 0.25 | old
2020 | SCG | HGR | CZ10 | 2003 | 0.395 | ex
2020 | SCG | HGR | CZ10 | 2007 | 0.215 | ex
2020 | SCG | HGR | CZ10 | 2011 | 0.215 | ex
2020 | SCG | HGR | CZ10 | 2015 | 0.161 | ex
2020 | SCG | HGR | CZ10 | 2017 | 0.161 | rec
2020 | SCG | HGR | CZ10 | 2020 | 0.054 | rec
2020 | SCG | HGR | CZ10 | New | 0.054 | new
2020 | SCG | HGR | CZ13 | 1975 | 0.163 | old
2020 | SCG | HGR | CZ13 | 1985 | 0.21 | old
2020 | SCG | HGR | CZ13 | 1996 | 0.101 | old
2020 | SCG | HGR | CZ13 | 2003 | 0.031 | ex
2020 | SCG | HGR | CZ13 | 2007 | 0.03 | ex
2020 | SCG | HGR | CZ13 | 2011 | 0.03 | ex
2020 | SCG | HGR | CZ13 | 2015 | 0.022 | ex
2020 | SCG | HGR | CZ13 | 2017 | 0.022 | rec
2020 | SCG | HGR | CZ13 | 2020 | 0.008 | rec
2020 | SCG | HGR | CZ13 | New | 0.008 | new
2020 | SCG | HGR | CZ14 | 1975 | 0.32 | old
2020 | SCG | HGR | CZ14 | 1985 | 0.671 | old
2020 | SCG | HGR | CZ14 | 1996 | 0.146 | old
2020 | SCG | HGR | CZ14 | 2003 | 0.138 | ex
2020 | SCG | HGR | CZ14 | 2007 | 0.097 | ex
2020 | SCG | HGR | CZ14 | 2011 | 0.097 | ex
2020 | SCG | HGR | CZ14 | 2015 | 0.073 | ex
2020 | SCG | HGR | CZ14 | 2017 | 0.073 | rec
2020 | SCG | HGR | CZ14 | 2020 | 0.024 | rec
2020 | SCG | HGR | CZ14 | New | 0.024 | new
2020 | SCG | HGR | CZ15 | 1975 | 1.238 | old
2020 | SCG | HGR | CZ15 | 1985 | 3.686 | old
2020 | SCG | HGR | CZ15 | 1996 | 0.639 | old
2020 | SCG | HGR | CZ15 | 2003 | 1.009 | ex
2020 | SCG | HGR | CZ15 | 2007 | 0.549 | ex
2020 | SCG | HGR | CZ15 | 2011 | 0.549 | ex
2020 | SCG | HGR | CZ15 | 2015 | 0.412 | ex
2020 | SCG | HGR | CZ15 | 2017 | 0.412 | rec
2020 | SCG | HGR | CZ15 | 2020 | 0.137 | rec
2020 | SCG | HGR | CZ15 | New | 0.137 | new
2020 | SCG | HGR | CZ16 | 1975 | 0.564 | old
2020 | SCG | HGR | CZ16 | 1985 | 0.83 | old
2020 | SCG | HGR | CZ16 | 1996 | 0.259 | old
2020 | SCG | HGR | CZ16 | 2003 | 0.103 | ex
2020 | SCG | HGR | CZ16 | 2007 | 0.116 | ex
2020 | SCG | HGR | CZ16 | 2011 | 0.116 | ex
2020 | SCG | HGR | CZ16 | 2015 | 0.087 | ex
2020 | SCG | HGR | CZ16 | 2017 | 0.087 | rec
2020 | SCG | HGR | CZ16 | 2020 | 0.029 | rec
2020 | SCG | HGR | CZ16 | New | 0.029 | new
2020 | SCG | Hsp | CZ05 | 1975 | 0.449 | old
2020 | SCG | Hsp | CZ05 | 1985 | 0.306 | old
2020 | SCG | Hsp | CZ05 | 1996 | 0.091 | old
2020 | SCG | Hsp | CZ05 | 2003 | 0.083 | ex
2020 | SCG | Hsp | CZ05 | 2007 | 0.025 | ex
2020 | SCG | Hsp | CZ05 | 2011 | 0.025 | ex
2020 | SCG | Hsp | CZ05 | 2015 | 0.019 | ex
2020 | SCG | Hsp | CZ05 | 2017 | 0.019 | rec
2020 | SCG | Hsp | CZ05 | 2020 | 0.006 | rec
2020 | SCG | Hsp | CZ05 | New | 0.006 | new
2020 | SCG | Hsp | CZ06 | 1975 | 7.763 | old
2020 | SCG | Hsp | CZ06 | 1985 | 4.908 | old
2020 | SCG | Hsp | CZ06 | 1996 | 1.489 | old
2020 | SCG | Hsp | CZ06 | 2003 | 1.375 | ex
2020 | SCG | Hsp | CZ06 | 2007 | 0.452 | ex
2020 | SCG | Hsp | CZ06 | 2011 | 0.452 | ex
2020 | SCG | Hsp | CZ06 | 2015 | 0.339 | ex
2020 | SCG | Hsp | CZ06 | 2017 | 0.339 | rec
2020 | SCG | Hsp | CZ06 | 2020 | 0.113 | rec
2020 | SCG | Hsp | CZ06 | New | 0.113 | new
2020 | SCG | Hsp | CZ08 | 1975 | 9.246 | old
2020 | SCG | Hsp | CZ08 | 1985 | 5.616 | old
2020 | SCG | Hsp | CZ08 | 1996 | 1.709 | old
2020 | SCG | Hsp | CZ08 | 2003 | 1.59 | ex
2020 | SCG | Hsp | CZ08 | 2007 | 0.545 | ex
2020 | SCG | Hsp | CZ08 | 2011 | 0.545 | ex
2020 | SCG | Hsp | CZ08 | 2015 | 0.409 | ex
2020 | SCG | Hsp | CZ08 | 2017 | 0.409 | rec
2020 | SCG | Hsp | CZ08 | 2020 | 0.136 | rec
2020 | SCG | Hsp | CZ08 | New | 0.136 | new
2020 | SCG | Hsp | CZ09 | 1975 | 11.309 | old
2020 | SCG | Hsp | CZ09 | 1985 | 5.791 | old
2020 | SCG | Hsp | CZ09 | 1996 | 1.94 | old
2020 | SCG | Hsp | CZ09 | 2003 | 1.894 | ex
2020 | SCG | Hsp | CZ09 | 2007 | 0.746 | ex
2020 | SCG | Hsp | CZ09 | 2011 | 0.746 | ex
2020 | SCG | Hsp | CZ09 | 2015 | 0.559 | ex
2020 | SCG | Hsp | CZ09 | 2017 | 0.559 | rec
2020 | SCG | Hsp | CZ09 | 2020 | 0.187 | rec
2020 | SCG | Hsp | CZ09 | New | 0.187 | new
2020 | SCG | Hsp | CZ10 | 1975 | 2.381 | old
2020 | SCG | Hsp | CZ10 | 1985 | 2.816 | old
2020 | SCG | Hsp | CZ10 | 1996 | 1.657 | old
2020 | SCG | Hsp | CZ10 | 2003 | 0.589 | ex
2020 | SCG | Hsp | CZ10 | 2007 | 0.463 | ex
2020 | SCG | Hsp | CZ10 | 2011 | 0.463 | ex
2020 | SCG | Hsp | CZ10 | 2015 | 0.347 | ex
2020 | SCG | Hsp | CZ10 | 2017 | 0.347 | rec
2020 | SCG | Hsp | CZ10 | 2020 | 0.116 | rec
2020 | SCG | Hsp | CZ10 | New | 0.116 | new
2020 | SCG | Hsp | CZ13 | 1975 | 0.438 | old
2020 | SCG | Hsp | CZ13 | 1985 | 0.51 | old
2020 | SCG | Hsp | CZ13 | 1996 | 0.423 | old
2020 | SCG | Hsp | CZ13 | 2003 | 0.077 | ex
2020 | SCG | Hsp | CZ13 | 2007 | 0.071 | ex
2020 | SCG | Hsp | CZ13 | 2011 | 0.071 | ex
2020 | SCG | Hsp | CZ13 | 2015 | 0.053 | ex
2020 | SCG | Hsp | CZ13 | 2017 | 0.053 | rec
2020 | SCG | Hsp | CZ13 | 2020 | 0.018 | rec
2020 | SCG | Hsp | CZ13 | New | 0.018 | new
2020 | SCG | Hsp | CZ14 | 1975 | 0.522 | old
2020 | SCG | Hsp | CZ14 | 1985 | 0.463 | old
2020 | SCG | Hsp | CZ14 | 1996 | 0.246 | old
2020 | SCG | Hsp | CZ14 | 2003 | 0.113 | ex
2020 | SCG | Hsp | CZ14 | 2007 | 0.074 | ex
2020 | SCG | Hsp | CZ14 | 2011 | 0.074 | ex
2020 | SCG | Hsp | CZ14 | 2015 | 0.056 | ex
2020 | SCG | Hsp | CZ14 | 2017 | 0.056 | rec
2020 | SCG | Hsp | CZ14 | 2020 | 0.019 | rec
2020 | SCG | Hsp | CZ14 | New | 0.019 | new
2020 | SCG | Hsp | CZ15 | 1975 | 0.493 | old
2020 | SCG | Hsp | CZ15 | 1985 | 0.583 | old
2020 | SCG | Hsp | CZ15 | 1996 | 0.343 | old
2020 | SCG | Hsp | CZ15 | 2003 | 0.122 | ex
2020 | SCG | Hsp | CZ15 | 2007 | 0.096 | ex
2020 | SCG | Hsp | CZ15 | 2011 | 0.096 | ex
2020 | SCG | Hsp | CZ15 | 2015 | 0.072 | ex
2020 | SCG | Hsp | CZ15 | 2017 | 0.072 | rec
2020 | SCG | Hsp | CZ15 | 2020 | 0.024 | rec
2020 | SCG | Hsp | CZ15 | New | 0.024 | new
2020 | SCG | Hsp | CZ16 | 1975 | 0.329 | old
2020 | SCG | Hsp | CZ16 | 1985 | 0.361 | old
2020 | SCG | Hsp | CZ16 | 1996 | 0.224 | old
2020 | SCG | Hsp | CZ16 | 2003 | 0.074 | ex
2020 | SCG | Hsp | CZ16 | 2007 | 0.057 | ex
2020 | SCG | Hsp | CZ16 | 2011 | 0.057 | ex
2020 | SCG | Hsp | CZ16 | 2015 | 0.043 | ex
2020 | SCG | Hsp | CZ16 | 2017 | 0.043 | rec
2020 | SCG | Hsp | CZ16 | 2020 | 0.014 | rec
2020 | SCG | Hsp | CZ16 | New | 0.014 | new
2020 | SCG | Htl | CZ05 | 1975 | 0.052 | old
2020 | SCG | Htl | CZ05 | 1985 | 0.067 | old
2020 | SCG | Htl | CZ05 | 1996 | 0.018 | old
2020 | SCG | Htl | CZ05 | 2003 | 0.01 | ex
2020 | SCG | Htl | CZ05 | 2007 | 0.004 | ex
2020 | SCG | Htl | CZ05 | 2011 | 0.004 | ex
2020 | SCG | Htl | CZ05 | 2015 | 0.003 | ex
2020 | SCG | Htl | CZ05 | 2017 | 0.003 | rec
2020 | SCG | Htl | CZ05 | 2020 | 0.001 | rec
2020 | SCG | Htl | CZ05 | New | 0.001 | new
2020 | SCG | Htl | CZ06 | 1975 | 6.781 | old
2020 | SCG | Htl | CZ06 | 1985 | 8.474 | old
2020 | SCG | Htl | CZ06 | 1996 | 2.309 | old
2020 | SCG | Htl | CZ06 | 2003 | 1.225 | ex
2020 | SCG | Htl | CZ06 | 2007 | 0.564 | ex
2020 | SCG | Htl | CZ06 | 2011 | 0.564 | ex
2020 | SCG | Htl | CZ06 | 2015 | 0.423 | ex
2020 | SCG | Htl | CZ06 | 2017 | 0.423 | rec
2020 | SCG | Htl | CZ06 | 2020 | 0.141 | rec
2020 | SCG | Htl | CZ06 | New | 0.141 | new
2020 | SCG | Htl | CZ08 | 1975 | 5.411 | old
2020 | SCG | Htl | CZ08 | 1985 | 6.279 | old
2020 | SCG | Htl | CZ08 | 1996 | 1.757 | old
2020 | SCG | Htl | CZ08 | 2003 | 0.904 | ex
2020 | SCG | Htl | CZ08 | 2007 | 0.473 | ex
2020 | SCG | Htl | CZ08 | 2011 | 0.473 | ex
2020 | SCG | Htl | CZ08 | 2015 | 0.355 | ex
2020 | SCG | Htl | CZ08 | 2017 | 0.355 | rec
2020 | SCG | Htl | CZ08 | 2020 | 0.118 | rec
2020 | SCG | Htl | CZ08 | New | 0.118 | new
2020 | SCG | Htl | CZ09 | 1975 | 8.182 | old
2020 | SCG | Htl | CZ09 | 1985 | 8.272 | old
2020 | SCG | Htl | CZ09 | 1996 | 2.426 | old
2020 | SCG | Htl | CZ09 | 2003 | 1.039 | ex
2020 | SCG | Htl | CZ09 | 2007 | 0.861 | ex
2020 | SCG | Htl | CZ09 | 2011 | 0.861 | ex
2020 | SCG | Htl | CZ09 | 2015 | 0.646 | ex
2020 | SCG | Htl | CZ09 | 2017 | 0.646 | rec
2020 | SCG | Htl | CZ09 | 2020 | 0.215 | rec
2020 | SCG | Htl | CZ09 | New | 0.215 | new
2020 | SCG | Htl | CZ10 | 1975 | 0.484 | old
2020 | SCG | Htl | CZ10 | 1985 | 1.441 | old
2020 | SCG | Htl | CZ10 | 1996 | 0.25 | old
2020 | SCG | Htl | CZ10 | 2003 | 0.395 | ex
2020 | SCG | Htl | CZ10 | 2007 | 0.215 | ex
2020 | SCG | Htl | CZ10 | 2011 | 0.215 | ex
2020 | SCG | Htl | CZ10 | 2015 | 0.161 | ex
2020 | SCG | Htl | CZ10 | 2017 | 0.161 | rec
2020 | SCG | Htl | CZ10 | 2020 | 0.054 | rec
2020 | SCG | Htl | CZ10 | New | 0.054 | new
2020 | SCG | Htl | CZ13 | 1975 | 0.163 | old
2020 | SCG | Htl | CZ13 | 1985 | 0.21 | old
2020 | SCG | Htl | CZ13 | 1996 | 0.101 | old
2020 | SCG | Htl | CZ13 | 2003 | 0.031 | ex
2020 | SCG | Htl | CZ13 | 2007 | 0.03 | ex
2020 | SCG | Htl | CZ13 | 2011 | 0.03 | ex
2020 | SCG | Htl | CZ13 | 2015 | 0.022 | ex
2020 | SCG | Htl | CZ13 | 2017 | 0.022 | rec
2020 | SCG | Htl | CZ13 | 2020 | 0.008 | rec
2020 | SCG | Htl | CZ13 | New | 0.008 | new
2020 | SCG | Htl | CZ14 | 1975 | 0.32 | old
2020 | SCG | Htl | CZ14 | 1985 | 0.671 | old
2020 | SCG | Htl | CZ14 | 1996 | 0.146 | old
2020 | SCG | Htl | CZ14 | 2003 | 0.138 | ex
2020 | SCG | Htl | CZ14 | 2007 | 0.097 | ex
2020 | SCG | Htl | CZ14 | 2011 | 0.097 | ex
2020 | SCG | Htl | CZ14 | 2015 | 0.073 | ex
2020 | SCG | Htl | CZ14 | 2017 | 0.073 | rec
2020 | SCG | Htl | CZ14 | 2020 | 0.024 | rec
2020 | SCG | Htl | CZ14 | New | 0.024 | new
2020 | SCG | Htl | CZ15 | 1975 | 1.238 | old
2020 | SCG | Htl | CZ15 | 1985 | 3.686 | old
2020 | SCG | Htl | CZ15 | 1996 | 0.639 | old
2020 | SCG | Htl | CZ15 | 2003 | 1.009 | ex
2020 | SCG | Htl | CZ15 | 2007 | 0.549 | ex
2020 | SCG | Htl | CZ15 | 2011 | 0.549 | ex
2020 | SCG | Htl | CZ15 | 2015 | 0.412 | ex
2020 | SCG | Htl | CZ15 | 2017 | 0.412 | rec
2020 | SCG | Htl | CZ15 | 2020 | 0.137 | rec
2020 | SCG | Htl | CZ15 | New | 0.137 | new
2020 | SCG | Htl | CZ16 | 1975 | 0.564 | old
2020 | SCG | Htl | CZ16 | 1985 | 0.83 | old
2020 | SCG | Htl | CZ16 | 1996 | 0.259 | old
2020 | SCG | Htl | CZ16 | 2003 | 0.103 | ex
2020 | SCG | Htl | CZ16 | 2007 | 0.116 | ex
2020 | SCG | Htl | CZ16 | 2011 | 0.116 | ex
2020 | SCG | Htl | CZ16 | 2015 | 0.087 | ex
2020 | SCG | Htl | CZ16 | 2017 | 0.087 | rec
2020 | SCG | Htl | CZ16 | 2020 | 0.029 | rec
2020 | SCG | Htl | CZ16 | New | 0.029 | new
2020 | SCG | MBT | CZ05 | 1975 | 0.216 | old
2020 | SCG | MBT | CZ05 | 1985 | 0.115 | old
2020 | SCG | MBT | CZ05 | 1996 | 0.056 | old
2020 | SCG | MBT | CZ05 | 2003 | 0.028 | ex
2020 | SCG | MBT | CZ05 | 2007 | 0.018 | ex
2020 | SCG | MBT | CZ05 | 2011 | 0.018 | ex
2020 | SCG | MBT | CZ05 | 2015 | 0.013 | ex
2020 | SCG | MBT | CZ05 | 2017 | 0.013 | rec
2020 | SCG | MBT | CZ05 | 2020 | 0.004 | rec
2020 | SCG | MBT | CZ05 | New | 0.004 | new
2020 | SCG | MBT | CZ06 | 1975 | 19.932 | old
2020 | SCG | MBT | CZ06 | 1985 | 10.416 | old
2020 | SCG | MBT | CZ06 | 1996 | 5.177 | old
2020 | SCG | MBT | CZ06 | 2003 | 2.546 | ex
2020 | SCG | MBT | CZ06 | 2007 | 1.598 | ex
2020 | SCG | MBT | CZ06 | 2011 | 1.598 | ex
2020 | SCG | MBT | CZ06 | 2015 | 1.198 | ex
2020 | SCG | MBT | CZ06 | 2017 | 1.198 | rec
2020 | SCG | MBT | CZ06 | 2020 | 0.399 | rec
2020 | SCG | MBT | CZ06 | New | 0.399 | new
2020 | SCG | MBT | CZ08 | 1975 | 30.07 | old
2020 | SCG | MBT | CZ08 | 1985 | 15.594 | old
2020 | SCG | MBT | CZ08 | 1996 | 7.835 | old
2020 | SCG | MBT | CZ08 | 2003 | 3.85 | ex
2020 | SCG | MBT | CZ08 | 2007 | 2.397 | ex
2020 | SCG | MBT | CZ08 | 2011 | 2.397 | ex
2020 | SCG | MBT | CZ08 | 2015 | 1.798 | ex
2020 | SCG | MBT | CZ08 | 2017 | 1.798 | rec
2020 | SCG | MBT | CZ08 | 2020 | 0.599 | rec
2020 | SCG | MBT | CZ08 | New | 0.599 | new
2020 | SCG | MBT | CZ09 | 1975 | 25.899 | old
2020 | SCG | MBT | CZ09 | 1985 | 12.41 | old
2020 | SCG | MBT | CZ09 | 1996 | 7.291 | old
2020 | SCG | MBT | CZ09 | 2003 | 3.528 | ex
2020 | SCG | MBT | CZ09 | 2007 | 1.99 | ex
2020 | SCG | MBT | CZ09 | 2011 | 1.99 | ex
2020 | SCG | MBT | CZ09 | 2015 | 1.493 | ex
2020 | SCG | MBT | CZ09 | 2017 | 1.493 | rec
2020 | SCG | MBT | CZ09 | 2020 | 0.498 | rec
2020 | SCG | MBT | CZ09 | New | 0.498 | new
2020 | SCG | MBT | CZ10 | 1975 | 3.994 | old
2020 | SCG | MBT | CZ10 | 1985 | 9.306 | old
2020 | SCG | MBT | CZ10 | 1996 | 5.666 | old
2020 | SCG | MBT | CZ10 | 2003 | 5.288 | ex
2020 | SCG | MBT | CZ10 | 2007 | 2.938 | ex
2020 | SCG | MBT | CZ10 | 2011 | 2.938 | ex
2020 | SCG | MBT | CZ10 | 2015 | 2.204 | ex
2020 | SCG | MBT | CZ10 | 2017 | 2.204 | rec
2020 | SCG | MBT | CZ10 | 2020 | 0.735 | rec
2020 | SCG | MBT | CZ10 | New | 0.735 | new
2020 | SCG | MBT | CZ13 | 1975 | 0.899 | old
2020 | SCG | MBT | CZ13 | 1985 | 1.085 | old
2020 | SCG | MBT | CZ13 | 1996 | 0.903 | old
2020 | SCG | MBT | CZ13 | 2003 | 0.349 | ex
2020 | SCG | MBT | CZ13 | 2007 | 0.223 | ex
2020 | SCG | MBT | CZ13 | 2011 | 0.223 | ex
2020 | SCG | MBT | CZ13 | 2015 | 0.167 | ex
2020 | SCG | MBT | CZ13 | 2017 | 0.167 | rec
2020 | SCG | MBT | CZ13 | 2020 | 0.056 | rec
2020 | SCG | MBT | CZ13 | New | 0.056 | new
2020 | SCG | MBT | CZ14 | 1975 | 1.878 | old
2020 | SCG | MBT | CZ14 | 1985 | 1.916 | old
2020 | SCG | MBT | CZ14 | 1996 | 1.152 | old
2020 | SCG | MBT | CZ14 | 2003 | 0.877 | ex
2020 | SCG | MBT | CZ14 | 2007 | 0.486 | ex
2020 | SCG | MBT | CZ14 | 2011 | 0.486 | ex
2020 | SCG | MBT | CZ14 | 2015 | 0.364 | ex
2020 | SCG | MBT | CZ14 | 2017 | 0.364 | rec
2020 | SCG | MBT | CZ14 | 2020 | 0.122 | rec
2020 | SCG | MBT | CZ14 | New | 0.122 | new
2020 | SCG | MBT | CZ15 | 1975 | 1.446 | old
2020 | SCG | MBT | CZ15 | 1985 | 3.369 | old
2020 | SCG | MBT | CZ15 | 1996 | 2.051 | old
2020 | SCG | MBT | CZ15 | 2003 | 1.914 | ex
2020 | SCG | MBT | CZ15 | 2007 | 1.064 | ex
2020 | SCG | MBT | CZ15 | 2011 | 1.064 | ex
2020 | SCG | MBT | CZ15 | 2015 | 0.798 | ex
2020 | SCG | MBT | CZ15 | 2017 | 0.798 | rec
2020 | SCG | MBT | CZ15 | 2020 | 0.266 | rec
2020 | SCG | MBT | CZ15 | New | 0.266 | new
2020 | SCG | MBT | CZ16 | 1975 | 0.888 | old
2020 | SCG | MBT | CZ16 | 1985 | 1.175 | old
2020 | SCG | MBT | CZ16 | 1996 | 0.786 | old
2020 | SCG | MBT | CZ16 | 2003 | 0.535 | ex
2020 | SCG | MBT | CZ16 | 2007 | 0.306 | ex
2020 | SCG | MBT | CZ16 | 2011 | 0.306 | ex
2020 | SCG | MBT | CZ16 | 2015 | 0.23 | ex
2020 | SCG | MBT | CZ16 | 2017 | 0.23 | rec
2020 | SCG | MBT | CZ16 | 2020 | 0.077 | rec
2020 | SCG | MBT | CZ16 | New | 0.077 | new
2020 | SCG | MLI | CZ05 | 1975 | 0.216 | old
2020 | SCG | MLI | CZ05 | 1985 | 0.115 | old
2020 | SCG | MLI | CZ05 | 1996 | 0.056 | old
2020 | SCG | MLI | CZ05 | 2003 | 0.028 | ex
2020 | SCG | MLI | CZ05 | 2007 | 0.018 | ex
2020 | SCG | MLI | CZ05 | 2011 | 0.018 | ex
2020 | SCG | MLI | CZ05 | 2015 | 0.013 | ex
2020 | SCG | MLI | CZ05 | 2017 | 0.013 | rec
2020 | SCG | MLI | CZ05 | 2020 | 0.004 | rec
2020 | SCG | MLI | CZ05 | New | 0.004 | new
2020 | SCG | MLI | CZ06 | 1975 | 19.932 | old
2020 | SCG | MLI | CZ06 | 1985 | 10.416 | old
2020 | SCG | MLI | CZ06 | 1996 | 5.177 | old
2020 | SCG | MLI | CZ06 | 2003 | 2.546 | ex
2020 | SCG | MLI | CZ06 | 2007 | 1.598 | ex
2020 | SCG | MLI | CZ06 | 2011 | 1.598 | ex
2020 | SCG | MLI | CZ06 | 2015 | 1.198 | ex
2020 | SCG | MLI | CZ06 | 2017 | 1.198 | rec
2020 | SCG | MLI | CZ06 | 2020 | 0.399 | rec
2020 | SCG | MLI | CZ06 | New | 0.399 | new
2020 | SCG | MLI | CZ08 | 1975 | 30.07 | old
2020 | SCG | MLI | CZ08 | 1985 | 15.594 | old
2020 | SCG | MLI | CZ08 | 1996 | 7.835 | old
2020 | SCG | MLI | CZ08 | 2003 | 3.85 | ex
2020 | SCG | MLI | CZ08 | 2007 | 2.397 | ex
2020 | SCG | MLI | CZ08 | 2011 | 2.397 | ex
2020 | SCG | MLI | CZ08 | 2015 | 1.798 | ex
2020 | SCG | MLI | CZ08 | 2017 | 1.798 | rec
2020 | SCG | MLI | CZ08 | 2020 | 0.599 | rec
2020 | SCG | MLI | CZ08 | New | 0.599 | new
2020 | SCG | MLI | CZ09 | 1975 | 25.899 | old
2020 | SCG | MLI | CZ09 | 1985 | 12.41 | old
2020 | SCG | MLI | CZ09 | 1996 | 7.291 | old
2020 | SCG | MLI | CZ09 | 2003 | 3.528 | ex
2020 | SCG | MLI | CZ09 | 2007 | 1.99 | ex
2020 | SCG | MLI | CZ09 | 2011 | 1.99 | ex
2020 | SCG | MLI | CZ09 | 2015 | 1.493 | ex
2020 | SCG | MLI | CZ09 | 2017 | 1.493 | rec
2020 | SCG | MLI | CZ09 | 2020 | 0.498 | rec
2020 | SCG | MLI | CZ09 | New | 0.498 | new
2020 | SCG | MLI | CZ10 | 1975 | 3.994 | old
2020 | SCG | MLI | CZ10 | 1985 | 9.306 | old
2020 | SCG | MLI | CZ10 | 1996 | 5.666 | old
2020 | SCG | MLI | CZ10 | 2003 | 5.288 | ex
2020 | SCG | MLI | CZ10 | 2007 | 2.938 | ex
2020 | SCG | MLI | CZ10 | 2011 | 2.938 | ex
2020 | SCG | MLI | CZ10 | 2015 | 2.204 | ex
2020 | SCG | MLI | CZ10 | 2017 | 2.204 | rec
2020 | SCG | MLI | CZ10 | 2020 | 0.735 | rec
2020 | SCG | MLI | CZ10 | New | 0.735 | new
2020 | SCG | MLI | CZ13 | 1975 | 0.899 | old
2020 | SCG | MLI | CZ13 | 1985 | 1.085 | old
2020 | SCG | MLI | CZ13 | 1996 | 0.903 | old
2020 | SCG | MLI | CZ13 | 2003 | 0.349 | ex
2020 | SCG | MLI | CZ13 | 2007 | 0.223 | ex
2020 | SCG | MLI | CZ13 | 2011 | 0.223 | ex
2020 | SCG | MLI | CZ13 | 2015 | 0.167 | ex
2020 | SCG | MLI | CZ13 | 2017 | 0.167 | rec
2020 | SCG | MLI | CZ13 | 2020 | 0.056 | rec
2020 | SCG | MLI | CZ13 | New | 0.056 | new
2020 | SCG | MLI | CZ14 | 1975 | 1.878 | old
2020 | SCG | MLI | CZ14 | 1985 | 1.916 | old
2020 | SCG | MLI | CZ14 | 1996 | 1.152 | old
2020 | SCG | MLI | CZ14 | 2003 | 0.877 | ex
2020 | SCG | MLI | CZ14 | 2007 | 0.486 | ex
2020 | SCG | MLI | CZ14 | 2011 | 0.486 | ex
2020 | SCG | MLI | CZ14 | 2015 | 0.364 | ex
2020 | SCG | MLI | CZ14 | 2017 | 0.364 | rec
2020 | SCG | MLI | CZ14 | 2020 | 0.122 | rec
2020 | SCG | MLI | CZ14 | New | 0.122 | new
2020 | SCG | MLI | CZ15 | 1975 | 1.446 | old
2020 | SCG | MLI | CZ15 | 1985 | 3.369 | old
2020 | SCG | MLI | CZ15 | 1996 | 2.051 | old
2020 | SCG | MLI | CZ15 | 2003 | 1.914 | ex
2020 | SCG | MLI | CZ15 | 2007 | 1.064 | ex
2020 | SCG | MLI | CZ15 | 2011 | 1.064 | ex
2020 | SCG | MLI | CZ15 | 2015 | 0.798 | ex
2020 | SCG | MLI | CZ15 | 2017 | 0.798 | rec
2020 | SCG | MLI | CZ15 | 2020 | 0.266 | rec
2020 | SCG | MLI | CZ15 | New | 0.266 | new
2020 | SCG | MLI | CZ16 | 1975 | 0.888 | old
2020 | SCG | MLI | CZ16 | 1985 | 1.175 | old
2020 | SCG | MLI | CZ16 | 1996 | 0.786 | old
2020 | SCG | MLI | CZ16 | 2003 | 0.535 | ex
2020 | SCG | MLI | CZ16 | 2007 | 0.306 | ex
2020 | SCG | MLI | CZ16 | 2011 | 0.306 | ex
2020 | SCG | MLI | CZ16 | 2015 | 0.23 | ex
2020 | SCG | MLI | CZ16 | 2017 | 0.23 | rec
2020 | SCG | MLI | CZ16 | 2020 | 0.077 | rec
2020 | SCG | MLI | CZ16 | New | 0.077 | new
2020 | SCG | Mtl | CZ05 | 1975 | 0.052 | old
2020 | SCG | Mtl | CZ05 | 1985 | 0.067 | old
2020 | SCG | Mtl | CZ05 | 1996 | 0.018 | old
2020 | SCG | Mtl | CZ05 | 2003 | 0.01 | ex
2020 | SCG | Mtl | CZ05 | 2007 | 0.004 | ex
2020 | SCG | Mtl | CZ05 | 2011 | 0.004 | ex
2020 | SCG | Mtl | CZ05 | 2015 | 0.003 | ex
2020 | SCG | Mtl | CZ05 | 2017 | 0.003 | rec
2020 | SCG | Mtl | CZ05 | 2020 | 0.001 | rec
2020 | SCG | Mtl | CZ05 | New | 0.001 | new
2020 | SCG | Mtl | CZ06 | 1975 | 6.781 | old
2020 | SCG | Mtl | CZ06 | 1985 | 8.474 | old
2020 | SCG | Mtl | CZ06 | 1996 | 2.309 | old
2020 | SCG | Mtl | CZ06 | 2003 | 1.225 | ex
2020 | SCG | Mtl | CZ06 | 2007 | 0.564 | ex
2020 | SCG | Mtl | CZ06 | 2011 | 0.564 | ex
2020 | SCG | Mtl | CZ06 | 2015 | 0.423 | ex
2020 | SCG | Mtl | CZ06 | 2017 | 0.423 | rec
2020 | SCG | Mtl | CZ06 | 2020 | 0.141 | rec
2020 | SCG | Mtl | CZ06 | New | 0.141 | new
2020 | SCG | Mtl | CZ08 | 1975 | 5.411 | old
2020 | SCG | Mtl | CZ08 | 1985 | 6.279 | old
2020 | SCG | Mtl | CZ08 | 1996 | 1.757 | old
2020 | SCG | Mtl | CZ08 | 2003 | 0.904 | ex
2020 | SCG | Mtl | CZ08 | 2007 | 0.473 | ex
2020 | SCG | Mtl | CZ08 | 2011 | 0.473 | ex
2020 | SCG | Mtl | CZ08 | 2015 | 0.355 | ex
2020 | SCG | Mtl | CZ08 | 2017 | 0.355 | rec
2020 | SCG | Mtl | CZ08 | 2020 | 0.118 | rec
2020 | SCG | Mtl | CZ08 | New | 0.118 | new
2020 | SCG | Mtl | CZ09 | 1975 | 8.182 | old
2020 | SCG | Mtl | CZ09 | 1985 | 8.272 | old
2020 | SCG | Mtl | CZ09 | 1996 | 2.426 | old
2020 | SCG | Mtl | CZ09 | 2003 | 1.039 | ex
2020 | SCG | Mtl | CZ09 | 2007 | 0.861 | ex
2020 | SCG | Mtl | CZ09 | 2011 | 0.861 | ex
2020 | SCG | Mtl | CZ09 | 2015 | 0.646 | ex
2020 | SCG | Mtl | CZ09 | 2017 | 0.646 | rec
2020 | SCG | Mtl | CZ09 | 2020 | 0.215 | rec
2020 | SCG | Mtl | CZ09 | New | 0.215 | new
2020 | SCG | Mtl | CZ10 | 1975 | 0.484 | old
2020 | SCG | Mtl | CZ10 | 1985 | 1.441 | old
2020 | SCG | Mtl | CZ10 | 1996 | 0.25 | old
2020 | SCG | Mtl | CZ10 | 2003 | 0.395 | ex
2020 | SCG | Mtl | CZ10 | 2007 | 0.215 | ex
2020 | SCG | Mtl | CZ10 | 2011 | 0.215 | ex
2020 | SCG | Mtl | CZ10 | 2015 | 0.161 | ex
2020 | SCG | Mtl | CZ10 | 2017 | 0.161 | rec
2020 | SCG | Mtl | CZ10 | 2020 | 0.054 | rec
2020 | SCG | Mtl | CZ10 | New | 0.054 | new
2020 | SCG | Mtl | CZ13 | 1975 | 0.163 | old
2020 | SCG | Mtl | CZ13 | 1985 | 0.21 | old
2020 | SCG | Mtl | CZ13 | 1996 | 0.101 | old
2020 | SCG | Mtl | CZ13 | 2003 | 0.031 | ex
2020 | SCG | Mtl | CZ13 | 2007 | 0.03 | ex
2020 | SCG | Mtl | CZ13 | 2011 | 0.03 | ex
2020 | SCG | Mtl | CZ13 | 2015 | 0.022 | ex
2020 | SCG | Mtl | CZ13 | 2017 | 0.022 | rec
2020 | SCG | Mtl | CZ13 | 2020 | 0.008 | rec
2020 | SCG | Mtl | CZ13 | New | 0.008 | new
2020 | SCG | Mtl | CZ14 | 1975 | 0.32 | old
2020 | SCG | Mtl | CZ14 | 1985 | 0.671 | old
2020 | SCG | Mtl | CZ14 | 1996 | 0.146 | old
2020 | SCG | Mtl | CZ14 | 2003 | 0.138 | ex
2020 | SCG | Mtl | CZ14 | 2007 | 0.097 | ex
2020 | SCG | Mtl | CZ14 | 2011 | 0.097 | ex
2020 | SCG | Mtl | CZ14 | 2015 | 0.073 | ex
2020 | SCG | Mtl | CZ14 | 2017 | 0.073 | rec
2020 | SCG | Mtl | CZ14 | 2020 | 0.024 | rec
2020 | SCG | Mtl | CZ14 | New | 0.024 | new
2020 | SCG | Mtl | CZ15 | 1975 | 1.238 | old
2020 | SCG | Mtl | CZ15 | 1985 | 3.686 | old
2020 | SCG | Mtl | CZ15 | 1996 | 0.639 | old
2020 | SCG | Mtl | CZ15 | 2003 | 1.009 | ex
2020 | SCG | Mtl | CZ15 | 2007 | 0.549 | ex
2020 | SCG | Mtl | CZ15 | 2011 | 0.549 | ex
2020 | SCG | Mtl | CZ15 | 2015 | 0.412 | ex
2020 | SCG | Mtl | CZ15 | 2017 | 0.412 | rec
2020 | SCG | Mtl | CZ15 | 2020 | 0.137 | rec
2020 | SCG | Mtl | CZ15 | New | 0.137 | new
2020 | SCG | Mtl | CZ16 | 1975 | 0.564 | old
2020 | SCG | Mtl | CZ16 | 1985 | 0.83 | old
2020 | SCG | Mtl | CZ16 | 1996 | 0.259 | old
2020 | SCG | Mtl | CZ16 | 2003 | 0.103 | ex
2020 | SCG | Mtl | CZ16 | 2007 | 0.116 | ex
2020 | SCG | Mtl | CZ16 | 2011 | 0.116 | ex
2020 | SCG | Mtl | CZ16 | 2015 | 0.087 | ex
2020 | SCG | Mtl | CZ16 | 2017 | 0.087 | rec
2020 | SCG | Mtl | CZ16 | 2020 | 0.029 | rec
2020 | SCG | Mtl | CZ16 | New | 0.029 | new
2020 | SCG | Nrs | CZ05 | 1975 | 0.449 | old
2020 | SCG | Nrs | CZ05 | 1985 | 0.306 | old
2020 | SCG | Nrs | CZ05 | 1996 | 0.091 | old
2020 | SCG | Nrs | CZ05 | 2003 | 0.083 | ex
2020 | SCG | Nrs | CZ05 | 2007 | 0.025 | ex
2020 | SCG | Nrs | CZ05 | 2011 | 0.025 | ex
2020 | SCG | Nrs | CZ05 | 2015 | 0.019 | ex
2020 | SCG | Nrs | CZ05 | 2017 | 0.019 | rec
2020 | SCG | Nrs | CZ05 | 2020 | 0.006 | rec
2020 | SCG | Nrs | CZ05 | New | 0.006 | new
2020 | SCG | Nrs | CZ06 | 1975 | 7.763 | old
2020 | SCG | Nrs | CZ06 | 1985 | 4.908 | old
2020 | SCG | Nrs | CZ06 | 1996 | 1.489 | old
2020 | SCG | Nrs | CZ06 | 2003 | 1.375 | ex
2020 | SCG | Nrs | CZ06 | 2007 | 0.452 | ex
2020 | SCG | Nrs | CZ06 | 2011 | 0.452 | ex
2020 | SCG | Nrs | CZ06 | 2015 | 0.339 | ex
2020 | SCG | Nrs | CZ06 | 2017 | 0.339 | rec
2020 | SCG | Nrs | CZ06 | 2020 | 0.113 | rec
2020 | SCG | Nrs | CZ06 | New | 0.113 | new
2020 | SCG | Nrs | CZ08 | 1975 | 9.246 | old
2020 | SCG | Nrs | CZ08 | 1985 | 5.616 | old
2020 | SCG | Nrs | CZ08 | 1996 | 1.709 | old
2020 | SCG | Nrs | CZ08 | 2003 | 1.59 | ex
2020 | SCG | Nrs | CZ08 | 2007 | 0.545 | ex
2020 | SCG | Nrs | CZ08 | 2011 | 0.545 | ex
2020 | SCG | Nrs | CZ08 | 2015 | 0.409 | ex
2020 | SCG | Nrs | CZ08 | 2017 | 0.409 | rec
2020 | SCG | Nrs | CZ08 | 2020 | 0.136 | rec
2020 | SCG | Nrs | CZ08 | New | 0.136 | new
2020 | SCG | Nrs | CZ09 | 1975 | 11.309 | old
2020 | SCG | Nrs | CZ09 | 1985 | 5.791 | old
2020 | SCG | Nrs | CZ09 | 1996 | 1.94 | old
2020 | SCG | Nrs | CZ09 | 2003 | 1.894 | ex
2020 | SCG | Nrs | CZ09 | 2007 | 0.746 | ex
2020 | SCG | Nrs | CZ09 | 2011 | 0.746 | ex
2020 | SCG | Nrs | CZ09 | 2015 | 0.559 | ex
2020 | SCG | Nrs | CZ09 | 2017 | 0.559 | rec
2020 | SCG | Nrs | CZ09 | 2020 | 0.187 | rec
2020 | SCG | Nrs | CZ09 | New | 0.187 | new
2020 | SCG | Nrs | CZ10 | 1975 | 2.381 | old
2020 | SCG | Nrs | CZ10 | 1985 | 2.816 | old
2020 | SCG | Nrs | CZ10 | 1996 | 1.657 | old
2020 | SCG | Nrs | CZ10 | 2003 | 0.589 | ex
2020 | SCG | Nrs | CZ10 | 2007 | 0.463 | ex
2020 | SCG | Nrs | CZ10 | 2011 | 0.463 | ex
2020 | SCG | Nrs | CZ10 | 2015 | 0.347 | ex
2020 | SCG | Nrs | CZ10 | 2017 | 0.347 | rec
2020 | SCG | Nrs | CZ10 | 2020 | 0.116 | rec
2020 | SCG | Nrs | CZ10 | New | 0.116 | new
2020 | SCG | Nrs | CZ13 | 1975 | 0.438 | old
2020 | SCG | Nrs | CZ13 | 1985 | 0.51 | old
2020 | SCG | Nrs | CZ13 | 1996 | 0.423 | old
2020 | SCG | Nrs | CZ13 | 2003 | 0.077 | ex
2020 | SCG | Nrs | CZ13 | 2007 | 0.071 | ex
2020 | SCG | Nrs | CZ13 | 2011 | 0.071 | ex
2020 | SCG | Nrs | CZ13 | 2015 | 0.053 | ex
2020 | SCG | Nrs | CZ13 | 2017 | 0.053 | rec
2020 | SCG | Nrs | CZ13 | 2020 | 0.018 | rec
2020 | SCG | Nrs | CZ13 | New | 0.018 | new
2020 | SCG | Nrs | CZ14 | 1975 | 0.522 | old
2020 | SCG | Nrs | CZ14 | 1985 | 0.463 | old
2020 | SCG | Nrs | CZ14 | 1996 | 0.246 | old
2020 | SCG | Nrs | CZ14 | 2003 | 0.113 | ex
2020 | SCG | Nrs | CZ14 | 2007 | 0.074 | ex
2020 | SCG | Nrs | CZ14 | 2011 | 0.074 | ex
2020 | SCG | Nrs | CZ14 | 2015 | 0.056 | ex
2020 | SCG | Nrs | CZ14 | 2017 | 0.056 | rec
2020 | SCG | Nrs | CZ14 | 2020 | 0.019 | rec
2020 | SCG | Nrs | CZ14 | New | 0.019 | new
2020 | SCG | Nrs | CZ15 | 1975 | 0.493 | old
2020 | SCG | Nrs | CZ15 | 1985 | 0.583 | old
2020 | SCG | Nrs | CZ15 | 1996 | 0.343 | old
2020 | SCG | Nrs | CZ15 | 2003 | 0.122 | ex
2020 | SCG | Nrs | CZ15 | 2007 | 0.096 | ex
2020 | SCG | Nrs | CZ15 | 2011 | 0.096 | ex
2020 | SCG | Nrs | CZ15 | 2015 | 0.072 | ex
2020 | SCG | Nrs | CZ15 | 2017 | 0.072 | rec
2020 | SCG | Nrs | CZ15 | 2020 | 0.024 | rec
2020 | SCG | Nrs | CZ15 | New | 0.024 | new
2020 | SCG | Nrs | CZ16 | 1975 | 0.329 | old
2020 | SCG | Nrs | CZ16 | 1985 | 0.361 | old
2020 | SCG | Nrs | CZ16 | 1996 | 0.224 | old
2020 | SCG | Nrs | CZ16 | 2003 | 0.074 | ex
2020 | SCG | Nrs | CZ16 | 2007 | 0.057 | ex
2020 | SCG | Nrs | CZ16 | 2011 | 0.057 | ex
2020 | SCG | Nrs | CZ16 | 2015 | 0.043 | ex
2020 | SCG | Nrs | CZ16 | 2017 | 0.043 | rec
2020 | SCG | Nrs | CZ16 | 2020 | 0.014 | rec
2020 | SCG | Nrs | CZ16 | New | 0.014 | new
2020 | SCG | OfL | CZ05 | 1975 | 0.491 | old
2020 | SCG | OfL | CZ05 | 1985 | 0.617 | old
2020 | SCG | OfL | CZ05 | 1996 | 0.117 | old
2020 | SCG | OfL | CZ05 | 2003 | 0.062 | ex
2020 | SCG | OfL | CZ05 | 2007 | 0.021 | ex
2020 | SCG | OfL | CZ05 | 2011 | 0.021 | ex
2020 | SCG | OfL | CZ05 | 2015 | 0.016 | ex
2020 | SCG | OfL | CZ05 | 2017 | 0.016 | rec
2020 | SCG | OfL | CZ05 | 2020 | 0.005 | rec
2020 | SCG | OfL | CZ05 | New | 0.005 | new
2020 | SCG | OfL | CZ06 | 1975 | 54.372 | old
2020 | SCG | OfL | CZ06 | 1985 | 62.471 | old
2020 | SCG | OfL | CZ06 | 1996 | 11.546 | old
2020 | SCG | OfL | CZ06 | 2003 | 6.225 | ex
2020 | SCG | OfL | CZ06 | 2007 | 2.851 | ex
2020 | SCG | OfL | CZ06 | 2011 | 2.851 | ex
2020 | SCG | OfL | CZ06 | 2015 | 2.139 | ex
2020 | SCG | OfL | CZ06 | 2017 | 2.139 | rec
2020 | SCG | OfL | CZ06 | 2020 | 0.713 | rec
2020 | SCG | OfL | CZ06 | New | 0.713 | new
2020 | SCG | OfL | CZ08 | 1975 | 74.314 | old
2020 | SCG | OfL | CZ08 | 1985 | 81.676 | old
2020 | SCG | OfL | CZ08 | 1996 | 15.024 | old
2020 | SCG | OfL | CZ08 | 2003 | 8.108 | ex
2020 | SCG | OfL | CZ08 | 2007 | 4.08 | ex
2020 | SCG | OfL | CZ08 | 2011 | 4.08 | ex
2020 | SCG | OfL | CZ08 | 2015 | 3.06 | ex
2020 | SCG | OfL | CZ08 | 2017 | 3.06 | rec
2020 | SCG | OfL | CZ08 | 2020 | 1.02 | rec
2020 | SCG | OfL | CZ08 | New | 1.02 | new
2020 | SCG | OfL | CZ09 | 1975 | 111.917 | old
2020 | SCG | OfL | CZ09 | 1985 | 95.452 | old
2020 | SCG | OfL | CZ09 | 1996 | 15.745 | old
2020 | SCG | OfL | CZ09 | 2003 | 9.073 | ex
2020 | SCG | OfL | CZ09 | 2007 | 5.925 | ex
2020 | SCG | OfL | CZ09 | 2011 | 5.925 | ex
2020 | SCG | OfL | CZ09 | 2015 | 4.444 | ex
2020 | SCG | OfL | CZ09 | 2017 | 4.444 | rec
2020 | SCG | OfL | CZ09 | 2020 | 1.481 | rec
2020 | SCG | OfL | CZ09 | New | 1.481 | new
2020 | SCG | OfL | CZ10 | 1975 | 8.506 | old
2020 | SCG | OfL | CZ10 | 1985 | 13.454 | old
2020 | SCG | OfL | CZ10 | 1996 | 3.573 | old
2020 | SCG | OfL | CZ10 | 2003 | 4.559 | ex
2020 | SCG | OfL | CZ10 | 2007 | 2.127 | ex
2020 | SCG | OfL | CZ10 | 2011 | 2.127 | ex
2020 | SCG | OfL | CZ10 | 2015 | 1.595 | ex
2020 | SCG | OfL | CZ10 | 2017 | 1.595 | rec
2020 | SCG | OfL | CZ10 | 2020 | 0.532 | rec
2020 | SCG | OfL | CZ10 | New | 0.532 | new
2020 | SCG | OfL | CZ13 | 1975 | 1.388 | old
2020 | SCG | OfL | CZ13 | 1985 | 1.545 | old
2020 | SCG | OfL | CZ13 | 1996 | 0.36 | old
2020 | SCG | OfL | CZ13 | 2003 | 0.167 | ex
2020 | SCG | OfL | CZ13 | 2007 | 0.196 | ex
2020 | SCG | OfL | CZ13 | 2011 | 0.196 | ex
2020 | SCG | OfL | CZ13 | 2015 | 0.147 | ex
2020 | SCG | OfL | CZ13 | 2017 | 0.147 | rec
2020 | SCG | OfL | CZ13 | 2020 | 0.049 | rec
2020 | SCG | OfL | CZ13 | New | 0.049 | new
2020 | SCG | OfL | CZ14 | 1975 | 2.454 | old
2020 | SCG | OfL | CZ14 | 1985 | 3.33 | old
2020 | SCG | OfL | CZ14 | 1996 | 0.664 | old
2020 | SCG | OfL | CZ14 | 2003 | 0.659 | ex
2020 | SCG | OfL | CZ14 | 2007 | 0.381 | ex
2020 | SCG | OfL | CZ14 | 2011 | 0.381 | ex
2020 | SCG | OfL | CZ14 | 2015 | 0.286 | ex
2020 | SCG | OfL | CZ14 | 2017 | 0.286 | rec
2020 | SCG | OfL | CZ14 | 2020 | 0.095 | rec
2020 | SCG | OfL | CZ14 | New | 0.095 | new
2020 | SCG | OfL | CZ15 | 1975 | 2.324 | old
2020 | SCG | OfL | CZ15 | 1985 | 3.677 | old
2020 | SCG | OfL | CZ15 | 1996 | 0.976 | old
2020 | SCG | OfL | CZ15 | 2003 | 1.246 | ex
2020 | SCG | OfL | CZ15 | 2007 | 0.581 | ex
2020 | SCG | OfL | CZ15 | 2011 | 0.581 | ex
2020 | SCG | OfL | CZ15 | 2015 | 0.436 | ex
2020 | SCG | OfL | CZ15 | 2017 | 0.436 | rec
2020 | SCG | OfL | CZ15 | 2020 | 0.145 | rec
2020 | SCG | OfL | CZ15 | New | 0.145 | new
2020 | SCG | OfL | CZ16 | 1975 | 1.177 | old
2020 | SCG | OfL | CZ16 | 1985 | 1.533 | old
2020 | SCG | OfL | CZ16 | 1996 | 0.302 | old
2020 | SCG | OfL | CZ16 | 2003 | 0.265 | ex
2020 | SCG | OfL | CZ16 | 2007 | 0.171 | ex
2020 | SCG | OfL | CZ16 | 2011 | 0.171 | ex
2020 | SCG | OfL | CZ16 | 2015 | 0.129 | ex
2020 | SCG | OfL | CZ16 | 2017 | 0.129 | rec
2020 | SCG | OfL | CZ16 | 2020 | 0.043 | rec
2020 | SCG | OfL | CZ16 | New | 0.043 | new
2020 | SCG | OfS | CZ05 | 1975 | 0.161 | old
2020 | SCG | OfS | CZ05 | 1985 | 0.09 | old
2020 | SCG | OfS | CZ05 | 1996 | 0.034 | old
2020 | SCG | OfS | CZ05 | 2003 | 0.013 | ex
2020 | SCG | OfS | CZ05 | 2007 | 0.012 | ex
2020 | SCG | OfS | CZ05 | 2011 | 0.012 | ex
2020 | SCG | OfS | CZ05 | 2015 | 0.009 | ex
2020 | SCG | OfS | CZ05 | 2017 | 0.009 | rec
2020 | SCG | OfS | CZ05 | 2020 | 0.003 | rec
2020 | SCG | OfS | CZ05 | New | 0.003 | new
2020 | SCG | OfS | CZ06 | 1975 | 16.018 | old
2020 | SCG | OfS | CZ06 | 1985 | 8.43 | old
2020 | SCG | OfS | CZ06 | 1996 | 3.293 | old
2020 | SCG | OfS | CZ06 | 2003 | 1.351 | ex
2020 | SCG | OfS | CZ06 | 2007 | 1.134 | ex
2020 | SCG | OfS | CZ06 | 2011 | 1.134 | ex
2020 | SCG | OfS | CZ06 | 2015 | 0.851 | ex
2020 | SCG | OfS | CZ06 | 2017 | 0.851 | rec
2020 | SCG | OfS | CZ06 | 2020 | 0.284 | rec
2020 | SCG | OfS | CZ06 | New | 0.284 | new
2020 | SCG | OfS | CZ08 | 1975 | 21.013 | old
2020 | SCG | OfS | CZ08 | 1985 | 10.705 | old
2020 | SCG | OfS | CZ08 | 1996 | 4.236 | old
2020 | SCG | OfS | CZ08 | 2003 | 1.757 | ex
2020 | SCG | OfS | CZ08 | 2007 | 1.446 | ex
2020 | SCG | OfS | CZ08 | 2011 | 1.446 | ex
2020 | SCG | OfS | CZ08 | 2015 | 1.084 | ex
2020 | SCG | OfS | CZ08 | 2017 | 1.084 | rec
2020 | SCG | OfS | CZ08 | 2020 | 0.362 | rec
2020 | SCG | OfS | CZ08 | New | 0.362 | new
2020 | SCG | OfS | CZ09 | 1975 | 23.86 | old
2020 | SCG | OfS | CZ09 | 1985 | 10.359 | old
2020 | SCG | OfS | CZ09 | 1996 | 4.853 | old
2020 | SCG | OfS | CZ09 | 2003 | 2.242 | ex
2020 | SCG | OfS | CZ09 | 2007 | 1.448 | ex
2020 | SCG | OfS | CZ09 | 2011 | 1.448 | ex
2020 | SCG | OfS | CZ09 | 2015 | 1.086 | ex
2020 | SCG | OfS | CZ09 | 2017 | 1.086 | rec
2020 | SCG | OfS | CZ09 | 2020 | 0.362 | rec
2020 | SCG | OfS | CZ09 | New | 0.362 | new
2020 | SCG | OfS | CZ10 | 1975 | 8.314 | old
2020 | SCG | OfS | CZ10 | 1985 | 7.781 | old
2020 | SCG | OfS | CZ10 | 1996 | 4.149 | old
2020 | SCG | OfS | CZ10 | 2003 | 3.04 | ex
2020 | SCG | OfS | CZ10 | 2007 | 1.581 | ex
2020 | SCG | OfS | CZ10 | 2011 | 1.581 | ex
2020 | SCG | OfS | CZ10 | 2015 | 1.186 | ex
2020 | SCG | OfS | CZ10 | 2017 | 1.186 | rec
2020 | SCG | OfS | CZ10 | 2020 | 0.395 | rec
2020 | SCG | OfS | CZ10 | New | 0.395 | new
2020 | SCG | OfS | CZ13 | 1975 | 2.712 | old
2020 | SCG | OfS | CZ13 | 1985 | 1.513 | old
2020 | SCG | OfS | CZ13 | 1996 | 0.856 | old
2020 | SCG | OfS | CZ13 | 2003 | 0.403 | ex
2020 | SCG | OfS | CZ13 | 2007 | 0.237 | ex
2020 | SCG | OfS | CZ13 | 2011 | 0.237 | ex
2020 | SCG | OfS | CZ13 | 2015 | 0.178 | ex
2020 | SCG | OfS | CZ13 | 2017 | 0.178 | rec
2020 | SCG | OfS | CZ13 | 2020 | 0.059 | rec
2020 | SCG | OfS | CZ13 | New | 0.059 | new
2020 | SCG | OfS | CZ14 | 1975 | 1.324 | old
2020 | SCG | OfS | CZ14 | 1985 | 1.066 | old
2020 | SCG | OfS | CZ14 | 1996 | 0.565 | old
2020 | SCG | OfS | CZ14 | 2003 | 0.383 | ex
2020 | SCG | OfS | CZ14 | 2007 | 0.203 | ex
2020 | SCG | OfS | CZ14 | 2011 | 0.203 | ex
2020 | SCG | OfS | CZ14 | 2015 | 0.152 | ex
2020 | SCG | OfS | CZ14 | 2017 | 0.152 | rec
2020 | SCG | OfS | CZ14 | 2020 | 0.051 | rec
2020 | SCG | OfS | CZ14 | New | 0.051 | new
2020 | SCG | OfS | CZ15 | 1975 | 2.272 | old
2020 | SCG | OfS | CZ15 | 1985 | 2.126 | old
2020 | SCG | OfS | CZ15 | 1996 | 1.134 | old
2020 | SCG | OfS | CZ15 | 2003 | 0.831 | ex
2020 | SCG | OfS | CZ15 | 2007 | 0.432 | ex
2020 | SCG | OfS | CZ15 | 2011 | 0.432 | ex
2020 | SCG | OfS | CZ15 | 2015 | 0.324 | ex
2020 | SCG | OfS | CZ15 | 2017 | 0.324 | rec
2020 | SCG | OfS | CZ15 | 2020 | 0.108 | rec
2020 | SCG | OfS | CZ15 | New | 0.108 | new
2020 | SCG | OfS | CZ16 | 1975 | 0.837 | old
2020 | SCG | OfS | CZ16 | 1985 | 0.578 | old
2020 | SCG | OfS | CZ16 | 1996 | 0.313 | old
2020 | SCG | OfS | CZ16 | 2003 | 0.188 | ex
2020 | SCG | OfS | CZ16 | 2007 | 0.103 | ex
2020 | SCG | OfS | CZ16 | 2011 | 0.103 | ex
2020 | SCG | OfS | CZ16 | 2015 | 0.077 | ex
2020 | SCG | OfS | CZ16 | 2017 | 0.077 | rec
2020 | SCG | OfS | CZ16 | 2020 | 0.026 | rec
2020 | SCG | OfS | CZ16 | New | 0.026 | new
2020 | SCG | RFF | CZ05 | 1975 | 0.051 | old
2020 | SCG | RFF | CZ05 | 1985 | 0.048 | old
2020 | SCG | RFF | CZ05 | 1996 | 0.019 | old
2020 | SCG | RFF | CZ05 | 2003 | 0.008 | ex
2020 | SCG | RFF | CZ05 | 2007 | 0.007 | ex
2020 | SCG | RFF | CZ05 | 2011 | 0.007 | ex
2020 | SCG | RFF | CZ05 | 2015 | 0.005 | ex
2020 | SCG | RFF | CZ05 | 2017 | 0.005 | rec
2020 | SCG | RFF | CZ05 | 2020 | 0.002 | rec
2020 | SCG | RFF | CZ05 | New | 0.002 | new
2020 | SCG | RFF | CZ06 | 1975 | 4.059 | old
2020 | SCG | RFF | CZ06 | 1985 | 3.597 | old
2020 | SCG | RFF | CZ06 | 1996 | 1.394 | old
2020 | SCG | RFF | CZ06 | 2003 | 0.623 | ex
2020 | SCG | RFF | CZ06 | 2007 | 0.533 | ex
2020 | SCG | RFF | CZ06 | 2011 | 0.533 | ex
2020 | SCG | RFF | CZ06 | 2015 | 0.4 | ex
2020 | SCG | RFF | CZ06 | 2017 | 0.4 | rec
2020 | SCG | RFF | CZ06 | 2020 | 0.133 | rec
2020 | SCG | RFF | CZ06 | New | 0.133 | new
2020 | SCG | RFF | CZ08 | 1975 | 5.125 | old
2020 | SCG | RFF | CZ08 | 1985 | 4.395 | old
2020 | SCG | RFF | CZ08 | 1996 | 1.679 | old
2020 | SCG | RFF | CZ08 | 2003 | 0.797 | ex
2020 | SCG | RFF | CZ08 | 2007 | 0.64 | ex
2020 | SCG | RFF | CZ08 | 2011 | 0.64 | ex
2020 | SCG | RFF | CZ08 | 2015 | 0.48 | ex
2020 | SCG | RFF | CZ08 | 2017 | 0.48 | rec
2020 | SCG | RFF | CZ08 | 2020 | 0.16 | rec
2020 | SCG | RFF | CZ08 | New | 0.16 | new
2020 | SCG | RFF | CZ09 | 1975 | 6.179 | old
2020 | SCG | RFF | CZ09 | 1985 | 4.596 | old
2020 | SCG | RFF | CZ09 | 1996 | 1.702 | old
2020 | SCG | RFF | CZ09 | 2003 | 1.057 | ex
2020 | SCG | RFF | CZ09 | 2007 | 0.55 | ex
2020 | SCG | RFF | CZ09 | 2011 | 0.55 | ex
2020 | SCG | RFF | CZ09 | 2015 | 0.412 | ex
2020 | SCG | RFF | CZ09 | 2017 | 0.412 | rec
2020 | SCG | RFF | CZ09 | 2020 | 0.138 | rec
2020 | SCG | RFF | CZ09 | New | 0.138 | new
2020 | SCG | RFF | CZ10 | 1975 | 1.682 | old
2020 | SCG | RFF | CZ10 | 1985 | 3.155 | old
2020 | SCG | RFF | CZ10 | 1996 | 1.726 | old
2020 | SCG | RFF | CZ10 | 2003 | 1.892 | ex
2020 | SCG | RFF | CZ10 | 2007 | 0.643 | ex
2020 | SCG | RFF | CZ10 | 2011 | 0.643 | ex
2020 | SCG | RFF | CZ10 | 2015 | 0.482 | ex
2020 | SCG | RFF | CZ10 | 2017 | 0.482 | rec
2020 | SCG | RFF | CZ10 | 2020 | 0.161 | rec
2020 | SCG | RFF | CZ10 | New | 0.161 | new
2020 | SCG | RFF | CZ13 | 1975 | 0.209 | old
2020 | SCG | RFF | CZ13 | 1985 | 0.22 | old
2020 | SCG | RFF | CZ13 | 1996 | 0.17 | old
2020 | SCG | RFF | CZ13 | 2003 | 0.088 | ex
2020 | SCG | RFF | CZ13 | 2007 | 0.044 | ex
2020 | SCG | RFF | CZ13 | 2011 | 0.044 | ex
2020 | SCG | RFF | CZ13 | 2015 | 0.033 | ex
2020 | SCG | RFF | CZ13 | 2017 | 0.033 | rec
2020 | SCG | RFF | CZ13 | 2020 | 0.011 | rec
2020 | SCG | RFF | CZ13 | New | 0.011 | new
2020 | SCG | RFF | CZ14 | 1975 | 0.433 | old
2020 | SCG | RFF | CZ14 | 1985 | 0.659 | old
2020 | SCG | RFF | CZ14 | 1996 | 0.345 | old
2020 | SCG | RFF | CZ14 | 2003 | 0.348 | ex
2020 | SCG | RFF | CZ14 | 2007 | 0.123 | ex
2020 | SCG | RFF | CZ14 | 2011 | 0.123 | ex
2020 | SCG | RFF | CZ14 | 2015 | 0.092 | ex
2020 | SCG | RFF | CZ14 | 2017 | 0.092 | rec
2020 | SCG | RFF | CZ14 | 2020 | 0.031 | rec
2020 | SCG | RFF | CZ14 | New | 0.031 | new
2020 | SCG | RFF | CZ15 | 1975 | 0.329 | old
2020 | SCG | RFF | CZ15 | 1985 | 0.617 | old
2020 | SCG | RFF | CZ15 | 1996 | 0.338 | old
2020 | SCG | RFF | CZ15 | 2003 | 0.37 | ex
2020 | SCG | RFF | CZ15 | 2007 | 0.126 | ex
2020 | SCG | RFF | CZ15 | 2011 | 0.126 | ex
2020 | SCG | RFF | CZ15 | 2015 | 0.094 | ex
2020 | SCG | RFF | CZ15 | 2017 | 0.094 | rec
2020 | SCG | RFF | CZ15 | 2020 | 0.031 | rec
2020 | SCG | RFF | CZ15 | New | 0.031 | new
2020 | SCG | RFF | CZ16 | 1975 | 0.173 | old
2020 | SCG | RFF | CZ16 | 1985 | 0.248 | old
2020 | SCG | RFF | CZ16 | 1996 | 0.142 | old
2020 | SCG | RFF | CZ16 | 2003 | 0.127 | ex
2020 | SCG | RFF | CZ16 | 2007 | 0.047 | ex
2020 | SCG | RFF | CZ16 | 2011 | 0.047 | ex
2020 | SCG | RFF | CZ16 | 2015 | 0.035 | ex
2020 | SCG | RFF | CZ16 | 2017 | 0.035 | rec
2020 | SCG | RFF | CZ16 | 2020 | 0.012 | rec
2020 | SCG | RFF | CZ16 | New | 0.012 | new
2020 | SCG | RSD | CZ05 | 1975 | 0.051 | old
2020 | SCG | RSD | CZ05 | 1985 | 0.048 | old
2020 | SCG | RSD | CZ05 | 1996 | 0.019 | old
2020 | SCG | RSD | CZ05 | 2003 | 0.008 | ex
2020 | SCG | RSD | CZ05 | 2007 | 0.007 | ex
2020 | SCG | RSD | CZ05 | 2011 | 0.007 | ex
2020 | SCG | RSD | CZ05 | 2015 | 0.005 | ex
2020 | SCG | RSD | CZ05 | 2017 | 0.005 | rec
2020 | SCG | RSD | CZ05 | 2020 | 0.002 | rec
2020 | SCG | RSD | CZ05 | New | 0.002 | new
2020 | SCG | RSD | CZ06 | 1975 | 4.059 | old
2020 | SCG | RSD | CZ06 | 1985 | 3.597 | old
2020 | SCG | RSD | CZ06 | 1996 | 1.394 | old
2020 | SCG | RSD | CZ06 | 2003 | 0.623 | ex
2020 | SCG | RSD | CZ06 | 2007 | 0.533 | ex
2020 | SCG | RSD | CZ06 | 2011 | 0.533 | ex
2020 | SCG | RSD | CZ06 | 2015 | 0.4 | ex
2020 | SCG | RSD | CZ06 | 2017 | 0.4 | rec
2020 | SCG | RSD | CZ06 | 2020 | 0.133 | rec
2020 | SCG | RSD | CZ06 | New | 0.133 | new
2020 | SCG | RSD | CZ08 | 1975 | 5.125 | old
2020 | SCG | RSD | CZ08 | 1985 | 4.395 | old
2020 | SCG | RSD | CZ08 | 1996 | 1.679 | old
2020 | SCG | RSD | CZ08 | 2003 | 0.797 | ex
2020 | SCG | RSD | CZ08 | 2007 | 0.64 | ex
2020 | SCG | RSD | CZ08 | 2011 | 0.64 | ex
2020 | SCG | RSD | CZ08 | 2015 | 0.48 | ex
2020 | SCG | RSD | CZ08 | 2017 | 0.48 | rec
2020 | SCG | RSD | CZ08 | 2020 | 0.16 | rec
2020 | SCG | RSD | CZ08 | New | 0.16 | new
2020 | SCG | RSD | CZ09 | 1975 | 6.179 | old
2020 | SCG | RSD | CZ09 | 1985 | 4.596 | old
2020 | SCG | RSD | CZ09 | 1996 | 1.702 | old
2020 | SCG | RSD | CZ09 | 2003 | 1.057 | ex
2020 | SCG | RSD | CZ09 | 2007 | 0.55 | ex
2020 | SCG | RSD | CZ09 | 2011 | 0.55 | ex
2020 | SCG | RSD | CZ09 | 2015 | 0.412 | ex
2020 | SCG | RSD | CZ09 | 2017 | 0.412 | rec
2020 | SCG | RSD | CZ09 | 2020 | 0.138 | rec
2020 | SCG | RSD | CZ09 | New | 0.138 | new
2020 | SCG | RSD | CZ10 | 1975 | 1.682 | old
2020 | SCG | RSD | CZ10 | 1985 | 3.155 | old
2020 | SCG | RSD | CZ10 | 1996 | 1.726 | old
2020 | SCG | RSD | CZ10 | 2003 | 1.892 | ex
2020 | SCG | RSD | CZ10 | 2007 | 0.643 | ex
2020 | SCG | RSD | CZ10 | 2011 | 0.643 | ex
2020 | SCG | RSD | CZ10 | 2015 | 0.482 | ex
2020 | SCG | RSD | CZ10 | 2017 | 0.482 | rec
2020 | SCG | RSD | CZ10 | 2020 | 0.161 | rec
2020 | SCG | RSD | CZ10 | New | 0.161 | new
2020 | SCG | RSD | CZ13 | 1975 | 0.209 | old
2020 | SCG | RSD | CZ13 | 1985 | 0.22 | old
2020 | SCG | RSD | CZ13 | 1996 | 0.17 | old
2020 | SCG | RSD | CZ13 | 2003 | 0.088 | ex
2020 | SCG | RSD | CZ13 | 2007 | 0.044 | ex
2020 | SCG | RSD | CZ13 | 2011 | 0.044 | ex
2020 | SCG | RSD | CZ13 | 2015 | 0.033 | ex
2020 | SCG | RSD | CZ13 | 2017 | 0.033 | rec
2020 | SCG | RSD | CZ13 | 2020 | 0.011 | rec
2020 | SCG | RSD | CZ13 | New | 0.011 | new
2020 | SCG | RSD | CZ14 | 1975 | 0.433 | old
2020 | SCG | RSD | CZ14 | 1985 | 0.659 | old
2020 | SCG | RSD | CZ14 | 1996 | 0.345 | old
2020 | SCG | RSD | CZ14 | 2003 | 0.348 | ex
2020 | SCG | RSD | CZ14 | 2007 | 0.123 | ex
2020 | SCG | RSD | CZ14 | 2011 | 0.123 | ex
2020 | SCG | RSD | CZ14 | 2015 | 0.092 | ex
2020 | SCG | RSD | CZ14 | 2017 | 0.092 | rec
2020 | SCG | RSD | CZ14 | 2020 | 0.031 | rec
2020 | SCG | RSD | CZ14 | New | 0.031 | new
2020 | SCG | RSD | CZ15 | 1975 | 0.329 | old
2020 | SCG | RSD | CZ15 | 1985 | 0.617 | old
2020 | SCG | RSD | CZ15 | 1996 | 0.338 | old
2020 | SCG | RSD | CZ15 | 2003 | 0.37 | ex
2020 | SCG | RSD | CZ15 | 2007 | 0.126 | ex
2020 | SCG | RSD | CZ15 | 2011 | 0.126 | ex
2020 | SCG | RSD | CZ15 | 2015 | 0.094 | ex
2020 | SCG | RSD | CZ15 | 2017 | 0.094 | rec
2020 | SCG | RSD | CZ15 | 2020 | 0.031 | rec
2020 | SCG | RSD | CZ15 | New | 0.031 | new
2020 | SCG | RSD | CZ16 | 1975 | 0.173 | old
2020 | SCG | RSD | CZ16 | 1985 | 0.248 | old
2020 | SCG | RSD | CZ16 | 1996 | 0.142 | old
2020 | SCG | RSD | CZ16 | 2003 | 0.127 | ex
2020 | SCG | RSD | CZ16 | 2007 | 0.047 | ex
2020 | SCG | RSD | CZ16 | 2011 | 0.047 | ex
2020 | SCG | RSD | CZ16 | 2015 | 0.035 | ex
2020 | SCG | RSD | CZ16 | 2017 | 0.035 | rec
2020 | SCG | RSD | CZ16 | 2020 | 0.012 | rec
2020 | SCG | RSD | CZ16 | New | 0.012 | new
2020 | SCG | Rt3 | CZ05 | 1975 | 0.256 | old
2020 | SCG | Rt3 | CZ05 | 1985 | 0.199 | old
2020 | SCG | Rt3 | CZ05 | 1996 | 0.102 | old
2020 | SCG | Rt3 | CZ05 | 2003 | 0.044 | ex
2020 | SCG | Rt3 | CZ05 | 2007 | 0.029 | ex
2020 | SCG | Rt3 | CZ05 | 2011 | 0.029 | ex
2020 | SCG | Rt3 | CZ05 | 2015 | 0.022 | ex
2020 | SCG | Rt3 | CZ05 | 2017 | 0.022 | rec
2020 | SCG | Rt3 | CZ05 | 2020 | 0.007 | rec
2020 | SCG | Rt3 | CZ05 | New | 0.007 | new
2020 | SCG | Rt3 | CZ06 | 1975 | 15.777 | old
2020 | SCG | Rt3 | CZ06 | 1985 | 12.086 | old
2020 | SCG | Rt3 | CZ06 | 1996 | 6.127 | old
2020 | SCG | Rt3 | CZ06 | 2003 | 2.742 | ex
2020 | SCG | Rt3 | CZ06 | 2007 | 1.777 | ex
2020 | SCG | Rt3 | CZ06 | 2011 | 1.777 | ex
2020 | SCG | Rt3 | CZ06 | 2015 | 1.333 | ex
2020 | SCG | Rt3 | CZ06 | 2017 | 1.333 | rec
2020 | SCG | Rt3 | CZ06 | 2020 | 0.444 | rec
2020 | SCG | Rt3 | CZ06 | New | 0.444 | new
2020 | SCG | Rt3 | CZ08 | 1975 | 19.147 | old
2020 | SCG | Rt3 | CZ08 | 1985 | 14.636 | old
2020 | SCG | Rt3 | CZ08 | 1996 | 7.364 | old
2020 | SCG | Rt3 | CZ08 | 2003 | 3.389 | ex
2020 | SCG | Rt3 | CZ08 | 2007 | 2.18 | ex
2020 | SCG | Rt3 | CZ08 | 2011 | 2.18 | ex
2020 | SCG | Rt3 | CZ08 | 2015 | 1.635 | ex
2020 | SCG | Rt3 | CZ08 | 2017 | 1.635 | rec
2020 | SCG | Rt3 | CZ08 | 2020 | 0.545 | rec
2020 | SCG | Rt3 | CZ08 | New | 0.545 | new
2020 | SCG | Rt3 | CZ09 | 1975 | 19.687 | old
2020 | SCG | Rt3 | CZ09 | 1985 | 15.035 | old
2020 | SCG | Rt3 | CZ09 | 1996 | 7.722 | old
2020 | SCG | Rt3 | CZ09 | 2003 | 3.937 | ex
2020 | SCG | Rt3 | CZ09 | 2007 | 2.36 | ex
2020 | SCG | Rt3 | CZ09 | 2011 | 2.36 | ex
2020 | SCG | Rt3 | CZ09 | 2015 | 1.77 | ex
2020 | SCG | Rt3 | CZ09 | 2017 | 1.77 | rec
2020 | SCG | Rt3 | CZ09 | 2020 | 0.59 | rec
2020 | SCG | Rt3 | CZ09 | New | 0.59 | new
2020 | SCG | Rt3 | CZ10 | 1975 | 5.212 | old
2020 | SCG | Rt3 | CZ10 | 1985 | 11.767 | old
2020 | SCG | Rt3 | CZ10 | 1996 | 5.962 | old
2020 | SCG | Rt3 | CZ10 | 2003 | 5.186 | ex
2020 | SCG | Rt3 | CZ10 | 2007 | 2.778 | ex
2020 | SCG | Rt3 | CZ10 | 2011 | 2.778 | ex
2020 | SCG | Rt3 | CZ10 | 2015 | 2.083 | ex
2020 | SCG | Rt3 | CZ10 | 2017 | 2.083 | rec
2020 | SCG | Rt3 | CZ10 | 2020 | 0.694 | rec
2020 | SCG | Rt3 | CZ10 | New | 0.694 | new
2020 | SCG | Rt3 | CZ13 | 1975 | 1.386 | old
2020 | SCG | Rt3 | CZ13 | 1985 | 0.996 | old
2020 | SCG | Rt3 | CZ13 | 1996 | 0.84 | old
2020 | SCG | Rt3 | CZ13 | 2003 | 0.473 | ex
2020 | SCG | Rt3 | CZ13 | 2007 | 0.306 | ex
2020 | SCG | Rt3 | CZ13 | 2011 | 0.306 | ex
2020 | SCG | Rt3 | CZ13 | 2015 | 0.229 | ex
2020 | SCG | Rt3 | CZ13 | 2017 | 0.229 | rec
2020 | SCG | Rt3 | CZ13 | 2020 | 0.076 | rec
2020 | SCG | Rt3 | CZ13 | New | 0.076 | new
2020 | SCG | Rt3 | CZ14 | 1975 | 1.455 | old
2020 | SCG | Rt3 | CZ14 | 1985 | 2.082 | old
2020 | SCG | Rt3 | CZ14 | 1996 | 1.047 | old
2020 | SCG | Rt3 | CZ14 | 2003 | 0.792 | ex
2020 | SCG | Rt3 | CZ14 | 2007 | 0.432 | ex
2020 | SCG | Rt3 | CZ14 | 2011 | 0.432 | ex
2020 | SCG | Rt3 | CZ14 | 2015 | 0.324 | ex
2020 | SCG | Rt3 | CZ14 | 2017 | 0.324 | rec
2020 | SCG | Rt3 | CZ14 | 2020 | 0.108 | rec
2020 | SCG | Rt3 | CZ14 | New | 0.108 | new
2020 | SCG | Rt3 | CZ15 | 1975 | 0.728 | old
2020 | SCG | Rt3 | CZ15 | 1985 | 1.643 | old
2020 | SCG | Rt3 | CZ15 | 1996 | 0.833 | old
2020 | SCG | Rt3 | CZ15 | 2003 | 0.724 | ex
2020 | SCG | Rt3 | CZ15 | 2007 | 0.388 | ex
2020 | SCG | Rt3 | CZ15 | 2011 | 0.388 | ex
2020 | SCG | Rt3 | CZ15 | 2015 | 0.291 | ex
2020 | SCG | Rt3 | CZ15 | 2017 | 0.291 | rec
2020 | SCG | Rt3 | CZ15 | 2020 | 0.097 | rec
2020 | SCG | Rt3 | CZ15 | New | 0.097 | new
2020 | SCG | Rt3 | CZ16 | 1975 | 0.337 | old
2020 | SCG | Rt3 | CZ16 | 1985 | 0.375 | old
2020 | SCG | Rt3 | CZ16 | 1996 | 0.234 | old
2020 | SCG | Rt3 | CZ16 | 2003 | 0.159 | ex
2020 | SCG | Rt3 | CZ16 | 2007 | 0.093 | ex
2020 | SCG | Rt3 | CZ16 | 2011 | 0.093 | ex
2020 | SCG | Rt3 | CZ16 | 2015 | 0.07 | ex
2020 | SCG | Rt3 | CZ16 | 2017 | 0.07 | rec
2020 | SCG | Rt3 | CZ16 | 2020 | 0.023 | rec
2020 | SCG | Rt3 | CZ16 | New | 0.023 | new
2020 | SCG | RtL | CZ05 | 1975 | 0.256 | old
2020 | SCG | RtL | CZ05 | 1985 | 0.199 | old
2020 | SCG | RtL | CZ05 | 1996 | 0.102 | old
2020 | SCG | RtL | CZ05 | 2003 | 0.044 | ex
2020 | SCG | RtL | CZ05 | 2007 | 0.029 | ex
2020 | SCG | RtL | CZ05 | 2011 | 0.029 | ex
2020 | SCG | RtL | CZ05 | 2015 | 0.022 | ex
2020 | SCG | RtL | CZ05 | 2017 | 0.022 | rec
2020 | SCG | RtL | CZ05 | 2020 | 0.007 | rec
2020 | SCG | RtL | CZ05 | New | 0.007 | new
2020 | SCG | RtL | CZ06 | 1975 | 15.777 | old
2020 | SCG | RtL | CZ06 | 1985 | 12.086 | old
2020 | SCG | RtL | CZ06 | 1996 | 6.127 | old
2020 | SCG | RtL | CZ06 | 2003 | 2.742 | ex
2020 | SCG | RtL | CZ06 | 2007 | 1.777 | ex
2020 | SCG | RtL | CZ06 | 2011 | 1.777 | ex
2020 | SCG | RtL | CZ06 | 2015 | 1.333 | ex
2020 | SCG | RtL | CZ06 | 2017 | 1.333 | rec
2020 | SCG | RtL | CZ06 | 2020 | 0.444 | rec
2020 | SCG | RtL | CZ06 | New | 0.444 | new
2020 | SCG | RtL | CZ08 | 1975 | 19.147 | old
2020 | SCG | RtL | CZ08 | 1985 | 14.636 | old
2020 | SCG | RtL | CZ08 | 1996 | 7.364 | old
2020 | SCG | RtL | CZ08 | 2003 | 3.389 | ex
2020 | SCG | RtL | CZ08 | 2007 | 2.18 | ex
2020 | SCG | RtL | CZ08 | 2011 | 2.18 | ex
2020 | SCG | RtL | CZ08 | 2015 | 1.635 | ex
2020 | SCG | RtL | CZ08 | 2017 | 1.635 | rec
2020 | SCG | RtL | CZ08 | 2020 | 0.545 | rec
2020 | SCG | RtL | CZ08 | New | 0.545 | new
2020 | SCG | RtL | CZ09 | 1975 | 19.687 | old
2020 | SCG | RtL | CZ09 | 1985 | 15.035 | old
2020 | SCG | RtL | CZ09 | 1996 | 7.722 | old
2020 | SCG | RtL | CZ09 | 2003 | 3.937 | ex
2020 | SCG | RtL | CZ09 | 2007 | 2.36 | ex
2020 | SCG | RtL | CZ09 | 2011 | 2.36 | ex
2020 | SCG | RtL | CZ09 | 2015 | 1.77 | ex
2020 | SCG | RtL | CZ09 | 2017 | 1.77 | rec
2020 | SCG | RtL | CZ09 | 2020 | 0.59 | rec
2020 | SCG | RtL | CZ09 | New | 0.59 | new
2020 | SCG | RtL | CZ10 | 1975 | 5.212 | old
2020 | SCG | RtL | CZ10 | 1985 | 11.767 | old
2020 | SCG | RtL | CZ10 | 1996 | 5.962 | old
2020 | SCG | RtL | CZ10 | 2003 | 5.186 | ex
2020 | SCG | RtL | CZ10 | 2007 | 2.778 | ex
2020 | SCG | RtL | CZ10 | 2011 | 2.778 | ex
2020 | SCG | RtL | CZ10 | 2015 | 2.083 | ex
2020 | SCG | RtL | CZ10 | 2017 | 2.083 | rec
2020 | SCG | RtL | CZ10 | 2020 | 0.694 | rec
2020 | SCG | RtL | CZ10 | New | 0.694 | new
2020 | SCG | RtL | CZ13 | 1975 | 1.386 | old
2020 | SCG | RtL | CZ13 | 1985 | 0.996 | old
2020 | SCG | RtL | CZ13 | 1996 | 0.84 | old
2020 | SCG | RtL | CZ13 | 2003 | 0.473 | ex
2020 | SCG | RtL | CZ13 | 2007 | 0.306 | ex
2020 | SCG | RtL | CZ13 | 2011 | 0.306 | ex
2020 | SCG | RtL | CZ13 | 2015 | 0.229 | ex
2020 | SCG | RtL | CZ13 | 2017 | 0.229 | rec
2020 | SCG | RtL | CZ13 | 2020 | 0.076 | rec
2020 | SCG | RtL | CZ13 | New | 0.076 | new
2020 | SCG | RtL | CZ14 | 1975 | 1.455 | old
2020 | SCG | RtL | CZ14 | 1985 | 2.082 | old
2020 | SCG | RtL | CZ14 | 1996 | 1.047 | old
2020 | SCG | RtL | CZ14 | 2003 | 0.792 | ex
2020 | SCG | RtL | CZ14 | 2007 | 0.432 | ex
2020 | SCG | RtL | CZ14 | 2011 | 0.432 | ex
2020 | SCG | RtL | CZ14 | 2015 | 0.324 | ex
2020 | SCG | RtL | CZ14 | 2017 | 0.324 | rec
2020 | SCG | RtL | CZ14 | 2020 | 0.108 | rec
2020 | SCG | RtL | CZ14 | New | 0.108 | new
2020 | SCG | RtL | CZ15 | 1975 | 0.728 | old
2020 | SCG | RtL | CZ15 | 1985 | 1.643 | old
2020 | SCG | RtL | CZ15 | 1996 | 0.833 | old
2020 | SCG | RtL | CZ15 | 2003 | 0.724 | ex
2020 | SCG | RtL | CZ15 | 2007 | 0.388 | ex
2020 | SCG | RtL | CZ15 | 2011 | 0.388 | ex
2020 | SCG | RtL | CZ15 | 2015 | 0.291 | ex
2020 | SCG | RtL | CZ15 | 2017 | 0.291 | rec
2020 | SCG | RtL | CZ15 | 2020 | 0.097 | rec
2020 | SCG | RtL | CZ15 | New | 0.097 | new
2020 | SCG | RtL | CZ16 | 1975 | 0.337 | old
2020 | SCG | RtL | CZ16 | 1985 | 0.375 | old
2020 | SCG | RtL | CZ16 | 1996 | 0.234 | old
2020 | SCG | RtL | CZ16 | 2003 | 0.159 | ex
2020 | SCG | RtL | CZ16 | 2007 | 0.093 | ex
2020 | SCG | RtL | CZ16 | 2011 | 0.093 | ex
2020 | SCG | RtL | CZ16 | 2015 | 0.07 | ex
2020 | SCG | RtL | CZ16 | 2017 | 0.07 | rec
2020 | SCG | RtL | CZ16 | 2020 | 0.023 | rec
2020 | SCG | RtL | CZ16 | New | 0.023 | new
2020 | SCG | RtS | CZ05 | 1975 | 0.256 | old
2020 | SCG | RtS | CZ05 | 1985 | 0.199 | old
2020 | SCG | RtS | CZ05 | 1996 | 0.102 | old
2020 | SCG | RtS | CZ05 | 2003 | 0.044 | ex
2020 | SCG | RtS | CZ05 | 2007 | 0.029 | ex
2020 | SCG | RtS | CZ05 | 2011 | 0.029 | ex
2020 | SCG | RtS | CZ05 | 2015 | 0.022 | ex
2020 | SCG | RtS | CZ05 | 2017 | 0.022 | rec
2020 | SCG | RtS | CZ05 | 2020 | 0.007 | rec
2020 | SCG | RtS | CZ05 | New | 0.007 | new
2020 | SCG | RtS | CZ06 | 1975 | 15.777 | old
2020 | SCG | RtS | CZ06 | 1985 | 12.086 | old
2020 | SCG | RtS | CZ06 | 1996 | 6.127 | old
2020 | SCG | RtS | CZ06 | 2003 | 2.742 | ex
2020 | SCG | RtS | CZ06 | 2007 | 1.777 | ex
2020 | SCG | RtS | CZ06 | 2011 | 1.777 | ex
2020 | SCG | RtS | CZ06 | 2015 | 1.333 | ex
2020 | SCG | RtS | CZ06 | 2017 | 1.333 | rec
2020 | SCG | RtS | CZ06 | 2020 | 0.444 | rec
2020 | SCG | RtS | CZ06 | New | 0.444 | new
2020 | SCG | RtS | CZ08 | 1975 | 19.147 | old
2020 | SCG | RtS | CZ08 | 1985 | 14.636 | old
2020 | SCG | RtS | CZ08 | 1996 | 7.364 | old
2020 | SCG | RtS | CZ08 | 2003 | 3.389 | ex
2020 | SCG | RtS | CZ08 | 2007 | 2.18 | ex
2020 | SCG | RtS | CZ08 | 2011 | 2.18 | ex
2020 | SCG | RtS | CZ08 | 2015 | 1.635 | ex
2020 | SCG | RtS | CZ08 | 2017 | 1.635 | rec
2020 | SCG | RtS | CZ08 | 2020 | 0.545 | rec
2020 | SCG | RtS | CZ08 | New | 0.545 | new
2020 | SCG | RtS | CZ09 | 1975 | 19.687 | old
2020 | SCG | RtS | CZ09 | 1985 | 15.035 | old
2020 | SCG | RtS | CZ09 | 1996 | 7.722 | old
2020 | SCG | RtS | CZ09 | 2003 | 3.937 | ex
2020 | SCG | RtS | CZ09 | 2007 | 2.36 | ex
2020 | SCG | RtS | CZ09 | 2011 | 2.36 | ex
2020 | SCG | RtS | CZ09 | 2015 | 1.77 | ex
2020 | SCG | RtS | CZ09 | 2017 | 1.77 | rec
2020 | SCG | RtS | CZ09 | 2020 | 0.59 | rec
2020 | SCG | RtS | CZ09 | New | 0.59 | new
2020 | SCG | RtS | CZ10 | 1975 | 5.212 | old
2020 | SCG | RtS | CZ10 | 1985 | 11.767 | old
2020 | SCG | RtS | CZ10 | 1996 | 5.962 | old
2020 | SCG | RtS | CZ10 | 2003 | 5.186 | ex
2020 | SCG | RtS | CZ10 | 2007 | 2.778 | ex
2020 | SCG | RtS | CZ10 | 2011 | 2.778 | ex
2020 | SCG | RtS | CZ10 | 2015 | 2.083 | ex
2020 | SCG | RtS | CZ10 | 2017 | 2.083 | rec
2020 | SCG | RtS | CZ10 | 2020 | 0.694 | rec
2020 | SCG | RtS | CZ10 | New | 0.694 | new
2020 | SCG | RtS | CZ13 | 1975 | 1.386 | old
2020 | SCG | RtS | CZ13 | 1985 | 0.996 | old
2020 | SCG | RtS | CZ13 | 1996 | 0.84 | old
2020 | SCG | RtS | CZ13 | 2003 | 0.473 | ex
2020 | SCG | RtS | CZ13 | 2007 | 0.306 | ex
2020 | SCG | RtS | CZ13 | 2011 | 0.306 | ex
2020 | SCG | RtS | CZ13 | 2015 | 0.229 | ex
2020 | SCG | RtS | CZ13 | 2017 | 0.229 | rec
2020 | SCG | RtS | CZ13 | 2020 | 0.076 | rec
2020 | SCG | RtS | CZ13 | New | 0.076 | new
2020 | SCG | RtS | CZ14 | 1975 | 1.455 | old
2020 | SCG | RtS | CZ14 | 1985 | 2.082 | old
2020 | SCG | RtS | CZ14 | 1996 | 1.047 | old
2020 | SCG | RtS | CZ14 | 2003 | 0.792 | ex
2020 | SCG | RtS | CZ14 | 2007 | 0.432 | ex
2020 | SCG | RtS | CZ14 | 2011 | 0.432 | ex
2020 | SCG | RtS | CZ14 | 2015 | 0.324 | ex
2020 | SCG | RtS | CZ14 | 2017 | 0.324 | rec
2020 | SCG | RtS | CZ14 | 2020 | 0.108 | rec
2020 | SCG | RtS | CZ14 | New | 0.108 | new
2020 | SCG | RtS | CZ15 | 1975 | 0.728 | old
2020 | SCG | RtS | CZ15 | 1985 | 1.643 | old
2020 | SCG | RtS | CZ15 | 1996 | 0.833 | old
2020 | SCG | RtS | CZ15 | 2003 | 0.724 | ex
2020 | SCG | RtS | CZ15 | 2007 | 0.388 | ex
2020 | SCG | RtS | CZ15 | 2011 | 0.388 | ex
2020 | SCG | RtS | CZ15 | 2015 | 0.291 | ex
2020 | SCG | RtS | CZ15 | 2017 | 0.291 | rec
2020 | SCG | RtS | CZ15 | 2020 | 0.097 | rec
2020 | SCG | RtS | CZ15 | New | 0.097 | new
2020 | SCG | RtS | CZ16 | 1975 | 0.337 | old
2020 | SCG | RtS | CZ16 | 1985 | 0.375 | old
2020 | SCG | RtS | CZ16 | 1996 | 0.234 | old
2020 | SCG | RtS | CZ16 | 2003 | 0.159 | ex
2020 | SCG | RtS | CZ16 | 2007 | 0.093 | ex
2020 | SCG | RtS | CZ16 | 2011 | 0.093 | ex
2020 | SCG | RtS | CZ16 | 2015 | 0.07 | ex
2020 | SCG | RtS | CZ16 | 2017 | 0.07 | rec
2020 | SCG | RtS | CZ16 | 2020 | 0.023 | rec
2020 | SCG | RtS | CZ16 | New | 0.023 | new
2020 | SCG | SCn | CZ05 | 1975 | 0.014 | old
2020 | SCG | SCn | CZ05 | 1985 | 0.01 | old
2020 | SCG | SCn | CZ05 | 1996 | 0.005 | old
2020 | SCG | SCn | CZ05 | 2003 | 0.003 | ex
2020 | SCG | SCn | CZ05 | 2007 | 0.001 | ex
2020 | SCG | SCn | CZ05 | 2011 | 0.001 | ex
2020 | SCG | SCn | CZ05 | 2015 | 0.001 | ex
2020 | SCG | SCn | CZ05 | 2017 | 0.001 | rec
2020 | SCG | SCn | CZ05 | 2020 | 0.001 | rec
2020 | SCG | SCn | CZ05 | New | 0.001 | new
2020 | SCG | SCn | CZ06 | 1975 | 14.232 | old
2020 | SCG | SCn | CZ06 | 1985 | 9.975 | old
2020 | SCG | SCn | CZ06 | 1996 | 4.625 | old
2020 | SCG | SCn | CZ06 | 2003 | 2.858 | ex
2020 | SCG | SCn | CZ06 | 2007 | 1.382 | ex
2020 | SCG | SCn | CZ06 | 2011 | 1.382 | ex
2020 | SCG | SCn | CZ06 | 2015 | 1.037 | ex
2020 | SCG | SCn | CZ06 | 2017 | 1.037 | rec
2020 | SCG | SCn | CZ06 | 2020 | 0.346 | rec
2020 | SCG | SCn | CZ06 | New | 0.346 | new
2020 | SCG | SCn | CZ08 | 1975 | 40.94 | old
2020 | SCG | SCn | CZ08 | 1985 | 28.608 | old
2020 | SCG | SCn | CZ08 | 1996 | 13.381 | old
2020 | SCG | SCn | CZ08 | 2003 | 7.977 | ex
2020 | SCG | SCn | CZ08 | 2007 | 3.893 | ex
2020 | SCG | SCn | CZ08 | 2011 | 3.893 | ex
2020 | SCG | SCn | CZ08 | 2015 | 2.92 | ex
2020 | SCG | SCn | CZ08 | 2017 | 2.92 | rec
2020 | SCG | SCn | CZ08 | 2020 | 0.973 | rec
2020 | SCG | SCn | CZ08 | New | 0.973 | new
2020 | SCG | SCn | CZ09 | 1975 | 24.952 | old
2020 | SCG | SCn | CZ09 | 1985 | 18.779 | old
2020 | SCG | SCn | CZ09 | 1996 | 8.489 | old
2020 | SCG | SCn | CZ09 | 2003 | 6.558 | ex
2020 | SCG | SCn | CZ09 | 2007 | 2.792 | ex
2020 | SCG | SCn | CZ09 | 2011 | 2.792 | ex
2020 | SCG | SCn | CZ09 | 2015 | 2.094 | ex
2020 | SCG | SCn | CZ09 | 2017 | 2.094 | rec
2020 | SCG | SCn | CZ09 | 2020 | 0.698 | rec
2020 | SCG | SCn | CZ09 | New | 0.698 | new
2020 | SCG | SCn | CZ10 | 1975 | 4.737 | old
2020 | SCG | SCn | CZ10 | 1985 | 22.896 | old
2020 | SCG | SCn | CZ10 | 1996 | 12.33 | old
2020 | SCG | SCn | CZ10 | 2003 | 16.819 | ex
2020 | SCG | SCn | CZ10 | 2007 | 11.107 | ex
2020 | SCG | SCn | CZ10 | 2011 | 11.107 | ex
2020 | SCG | SCn | CZ10 | 2015 | 8.331 | ex
2020 | SCG | SCn | CZ10 | 2017 | 8.331 | rec
2020 | SCG | SCn | CZ10 | 2020 | 2.777 | rec
2020 | SCG | SCn | CZ10 | New | 2.777 | new
2020 | SCG | SCn | CZ13 | 1975 | 0.504 | old
2020 | SCG | SCn | CZ13 | 1985 | 0.89 | old
2020 | SCG | SCn | CZ13 | 1996 | 0.971 | old
2020 | SCG | SCn | CZ13 | 2003 | 0.551 | ex
2020 | SCG | SCn | CZ13 | 2007 | 0.376 | ex
2020 | SCG | SCn | CZ13 | 2011 | 0.376 | ex
2020 | SCG | SCn | CZ13 | 2015 | 0.282 | ex
2020 | SCG | SCn | CZ13 | 2017 | 0.282 | rec
2020 | SCG | SCn | CZ13 | 2020 | 0.094 | rec
2020 | SCG | SCn | CZ13 | New | 0.094 | new
2020 | SCG | SCn | CZ14 | 1975 | 0.24 | old
2020 | SCG | SCn | CZ14 | 1985 | 0.522 | old
2020 | SCG | SCn | CZ14 | 1996 | 0.317 | old
2020 | SCG | SCn | CZ14 | 2003 | 0.337 | ex
2020 | SCG | SCn | CZ14 | 2007 | 0.215 | ex
2020 | SCG | SCn | CZ14 | 2011 | 0.215 | ex
2020 | SCG | SCn | CZ14 | 2015 | 0.161 | ex
2020 | SCG | SCn | CZ14 | 2017 | 0.161 | rec
2020 | SCG | SCn | CZ14 | 2020 | 0.054 | rec
2020 | SCG | SCn | CZ14 | New | 0.054 | new
2020 | SCG | SCn | CZ15 | 1975 | 0.087 | old
2020 | SCG | SCn | CZ15 | 1985 | 0.421 | old
2020 | SCG | SCn | CZ15 | 1996 | 0.227 | old
2020 | SCG | SCn | CZ15 | 2003 | 0.309 | ex
2020 | SCG | SCn | CZ15 | 2007 | 0.204 | ex
2020 | SCG | SCn | CZ15 | 2011 | 0.204 | ex
2020 | SCG | SCn | CZ15 | 2015 | 0.153 | ex
2020 | SCG | SCn | CZ15 | 2017 | 0.153 | rec
2020 | SCG | SCn | CZ15 | 2020 | 0.051 | rec
2020 | SCG | SCn | CZ15 | New | 0.051 | new
2020 | SCG | SCn | CZ16 | 1975 | 0.111 | old
2020 | SCG | SCn | CZ16 | 1985 | 0.427 | old
2020 | SCG | SCn | CZ16 | 1996 | 0.251 | old
2020 | SCG | SCn | CZ16 | 2003 | 0.306 | ex
2020 | SCG | SCn | CZ16 | 2007 | 0.202 | ex
2020 | SCG | SCn | CZ16 | 2011 | 0.202 | ex
2020 | SCG | SCn | CZ16 | 2015 | 0.152 | ex
2020 | SCG | SCn | CZ16 | 2017 | 0.152 | rec
2020 | SCG | SCn | CZ16 | 2020 | 0.051 | rec
2020 | SCG | SCn | CZ16 | New | 0.051 | new
2020 | SCG | SUn | CZ05 | 1975 | 0.014 | old
2020 | SCG | SUn | CZ05 | 1985 | 0.01 | old
2020 | SCG | SUn | CZ05 | 1996 | 0.005 | old
2020 | SCG | SUn | CZ05 | 2003 | 0.003 | ex
2020 | SCG | SUn | CZ05 | 2007 | 0.001 | ex
2020 | SCG | SUn | CZ05 | 2011 | 0.001 | ex
2020 | SCG | SUn | CZ05 | 2015 | 0.001 | ex
2020 | SCG | SUn | CZ05 | 2017 | 0.001 | rec
2020 | SCG | SUn | CZ05 | 2020 | 0.001 | rec
2020 | SCG | SUn | CZ05 | New | 0.001 | new
2020 | SCG | SUn | CZ06 | 1975 | 14.232 | old
2020 | SCG | SUn | CZ06 | 1985 | 9.975 | old
2020 | SCG | SUn | CZ06 | 1996 | 4.625 | old
2020 | SCG | SUn | CZ06 | 2003 | 2.858 | ex
2020 | SCG | SUn | CZ06 | 2007 | 1.382 | ex
2020 | SCG | SUn | CZ06 | 2011 | 1.382 | ex
2020 | SCG | SUn | CZ06 | 2015 | 1.037 | ex
2020 | SCG | SUn | CZ06 | 2017 | 1.037 | rec
2020 | SCG | SUn | CZ06 | 2020 | 0.346 | rec
2020 | SCG | SUn | CZ06 | New | 0.346 | new
2020 | SCG | SUn | CZ08 | 1975 | 40.94 | old
2020 | SCG | SUn | CZ08 | 1985 | 28.608 | old
2020 | SCG | SUn | CZ08 | 1996 | 13.381 | old
2020 | SCG | SUn | CZ08 | 2003 | 7.977 | ex
2020 | SCG | SUn | CZ08 | 2007 | 3.893 | ex
2020 | SCG | SUn | CZ08 | 2011 | 3.893 | ex
2020 | SCG | SUn | CZ08 | 2015 | 2.92 | ex
2020 | SCG | SUn | CZ08 | 2017 | 2.92 | rec
2020 | SCG | SUn | CZ08 | 2020 | 0.973 | rec
2020 | SCG | SUn | CZ08 | New | 0.973 | new
2020 | SCG | SUn | CZ09 | 1975 | 24.952 | old
2020 | SCG | SUn | CZ09 | 1985 | 18.779 | old
2020 | SCG | SUn | CZ09 | 1996 | 8.489 | old
2020 | SCG | SUn | CZ09 | 2003 | 6.558 | ex
2020 | SCG | SUn | CZ09 | 2007 | 2.792 | ex
2020 | SCG | SUn | CZ09 | 2011 | 2.792 | ex
2020 | SCG | SUn | CZ09 | 2015 | 2.094 | ex
2020 | SCG | SUn | CZ09 | 2017 | 2.094 | rec
2020 | SCG | SUn | CZ09 | 2020 | 0.698 | rec
2020 | SCG | SUn | CZ09 | New | 0.698 | new
2020 | SCG | SUn | CZ10 | 1975 | 4.737 | old
2020 | SCG | SUn | CZ10 | 1985 | 22.896 | old
2020 | SCG | SUn | CZ10 | 1996 | 12.33 | old
2020 | SCG | SUn | CZ10 | 2003 | 16.819 | ex
2020 | SCG | SUn | CZ10 | 2007 | 11.107 | ex
2020 | SCG | SUn | CZ10 | 2011 | 11.107 | ex
2020 | SCG | SUn | CZ10 | 2015 | 8.331 | ex
2020 | SCG | SUn | CZ10 | 2017 | 8.331 | rec
2020 | SCG | SUn | CZ10 | 2020 | 2.777 | rec
2020 | SCG | SUn | CZ10 | New | 2.777 | new
2020 | SCG | SUn | CZ13 | 1975 | 0.504 | old
2020 | SCG | SUn | CZ13 | 1985 | 0.89 | old
2020 | SCG | SUn | CZ13 | 1996 | 0.971 | old
2020 | SCG | SUn | CZ13 | 2003 | 0.551 | ex
2020 | SCG | SUn | CZ13 | 2007 | 0.376 | ex
2020 | SCG | SUn | CZ13 | 2011 | 0.376 | ex
2020 | SCG | SUn | CZ13 | 2015 | 0.282 | ex
2020 | SCG | SUn | CZ13 | 2017 | 0.282 | rec
2020 | SCG | SUn | CZ13 | 2020 | 0.094 | rec
2020 | SCG | SUn | CZ13 | New | 0.094 | new
2020 | SCG | SUn | CZ14 | 1975 | 0.24 | old
2020 | SCG | SUn | CZ14 | 1985 | 0.522 | old
2020 | SCG | SUn | CZ14 | 1996 | 0.317 | old
2020 | SCG | SUn | CZ14 | 2003 | 0.337 | ex
2020 | SCG | SUn | CZ14 | 2007 | 0.215 | ex
2020 | SCG | SUn | CZ14 | 2011 | 0.215 | ex
2020 | SCG | SUn | CZ14 | 2015 | 0.161 | ex
2020 | SCG | SUn | CZ14 | 2017 | 0.161 | rec
2020 | SCG | SUn | CZ14 | 2020 | 0.054 | rec
2020 | SCG | SUn | CZ14 | New | 0.054 | new
2020 | SCG | SUn | CZ15 | 1975 | 0.087 | old
2020 | SCG | SUn | CZ15 | 1985 | 0.421 | old
2020 | SCG | SUn | CZ15 | 1996 | 0.227 | old
2020 | SCG | SUn | CZ15 | 2003 | 0.309 | ex
2020 | SCG | SUn | CZ15 | 2007 | 0.204 | ex
2020 | SCG | SUn | CZ15 | 2011 | 0.204 | ex
2020 | SCG | SUn | CZ15 | 2015 | 0.153 | ex
2020 | SCG | SUn | CZ15 | 2017 | 0.153 | rec
2020 | SCG | SUn | CZ15 | 2020 | 0.051 | rec
2020 | SCG | SUn | CZ15 | New | 0.051 | new
2020 | SCG | SUn | CZ16 | 1975 | 0.111 | old
2020 | SCG | SUn | CZ16 | 1985 | 0.427 | old
2020 | SCG | SUn | CZ16 | 1996 | 0.251 | old
2020 | SCG | SUn | CZ16 | 2003 | 0.306 | ex
2020 | SCG | SUn | CZ16 | 2007 | 0.202 | ex
2020 | SCG | SUn | CZ16 | 2011 | 0.202 | ex
2020 | SCG | SUn | CZ16 | 2015 | 0.152 | ex
2020 | SCG | SUn | CZ16 | 2017 | 0.152 | rec
2020 | SCG | SUn | CZ16 | 2020 | 0.051 | rec
2020 | SCG | SUn | CZ16 | New | 0.051 | new
2020 | SCG | WRf | CZ06 | 1975 | 2.208 | old
2020 | SCG | WRf | CZ06 | 1985 | 0.946 | old
2020 | SCG | WRf | CZ06 | 1996 | 0.991 | old
2020 | SCG | WRf | CZ06 | 2003 | 0.378 | ex
2020 | SCG | WRf | CZ06 | 2007 | 0.233 | ex
2020 | SCG | WRf | CZ06 | 2011 | 0.233 | ex
2020 | SCG | WRf | CZ06 | 2015 | 0.175 | ex
2020 | SCG | WRf | CZ06 | 2017 | 0.175 | rec
2020 | SCG | WRf | CZ06 | 2020 | 0.058 | rec
2020 | SCG | WRf | CZ06 | New | 0.058 | new
2020 | SCG | WRf | CZ08 | 1975 | 3.058 | old
2020 | SCG | WRf | CZ08 | 1985 | 1.31 | old
2020 | SCG | WRf | CZ08 | 1996 | 1.38 | old
2020 | SCG | WRf | CZ08 | 2003 | 0.534 | ex
2020 | SCG | WRf | CZ08 | 2007 | 0.325 | ex
2020 | SCG | WRf | CZ08 | 2011 | 0.325 | ex
2020 | SCG | WRf | CZ08 | 2015 | 0.244 | ex
2020 | SCG | WRf | CZ08 | 2017 | 0.244 | rec
2020 | SCG | WRf | CZ08 | 2020 | 0.081 | rec
2020 | SCG | WRf | CZ08 | New | 0.081 | new
2020 | SCG | WRf | CZ09 | 1975 | 2.009 | old
2020 | SCG | WRf | CZ09 | 1985 | 0.854 | old
2020 | SCG | WRf | CZ09 | 1996 | 1.026 | old
2020 | SCG | WRf | CZ09 | 2003 | 0.474 | ex
2020 | SCG | WRf | CZ09 | 2007 | 0.237 | ex
2020 | SCG | WRf | CZ09 | 2011 | 0.237 | ex
2020 | SCG | WRf | CZ09 | 2015 | 0.178 | ex
2020 | SCG | WRf | CZ09 | 2017 | 0.178 | rec
2020 | SCG | WRf | CZ09 | 2020 | 0.059 | rec
2020 | SCG | WRf | CZ09 | New | 0.059 | new
2020 | SCG | WRf | CZ10 | 1975 | 0.581 | old
2020 | SCG | WRf | CZ10 | 1985 | 0.482 | old
2020 | SCG | WRf | CZ10 | 1996 | 1.763 | old
2020 | SCG | WRf | CZ10 | 2003 | 0.231 | ex
2020 | SCG | WRf | CZ10 | 2007 | 0.22 | ex
2020 | SCG | WRf | CZ10 | 2011 | 0.22 | ex
2020 | SCG | WRf | CZ10 | 2015 | 0.165 | ex
2020 | SCG | WRf | CZ10 | 2017 | 0.165 | rec
2020 | SCG | WRf | CZ10 | 2020 | 0.055 | rec
2020 | SCG | WRf | CZ10 | New | 0.055 | new
2020 | SCG | WRf | CZ13 | 1975 | 0.232 | old
2020 | SCG | WRf | CZ13 | 1985 | 1.295 | old
2020 | SCG | WRf | CZ13 | 1996 | 0.767 | old
2020 | SCG | WRf | CZ13 | 2003 | 0.211 | ex
2020 | SCG | WRf | CZ13 | 2007 | 0.298 | ex
2020 | SCG | WRf | CZ13 | 2011 | 0.298 | ex
2020 | SCG | WRf | CZ13 | 2015 | 0.224 | ex
2020 | SCG | WRf | CZ13 | 2017 | 0.224 | rec
2020 | SCG | WRf | CZ13 | 2020 | 0.075 | rec
2020 | SCG | WRf | CZ13 | New | 0.075 | new
2020 | SCG | WRf | CZ14 | 1975 | 0.009 | old
2020 | SCG | WRf | CZ14 | 1985 | 0.007 | old
2020 | SCG | WRf | CZ14 | 1996 | 0.022 | old
2020 | SCG | WRf | CZ14 | 2003 | 0.003 | ex
2020 | SCG | WRf | CZ14 | 2007 | 0.003 | ex
2020 | SCG | WRf | CZ14 | 2011 | 0.003 | ex
2020 | SCG | WRf | CZ14 | 2015 | 0.002 | ex
2020 | SCG | WRf | CZ14 | 2017 | 0.002 | rec
2020 | SCG | WRf | CZ14 | 2020 | 0.001 | rec
2020 | SCG | WRf | CZ14 | New | 0.001 | new
2020 | SCG | WRf | CZ15 | 1975 | 0.038 | old
2020 | SCG | WRf | CZ15 | 1985 | 0.031 | old
2020 | SCG | WRf | CZ15 | 1996 | 0.115 | old
2020 | SCG | WRf | CZ15 | 2003 | 0.015 | ex
2020 | SCG | WRf | CZ15 | 2007 | 0.014 | ex
2020 | SCG | WRf | CZ15 | 2011 | 0.014 | ex
2020 | SCG | WRf | CZ15 | 2015 | 0.011 | ex
2020 | SCG | WRf | CZ15 | 2017 | 0.011 | rec
2020 | SCG | WRf | CZ15 | 2020 | 0.004 | rec
2020 | SCG | WRf | CZ15 | New | 0.004 | new
2020 | SCG | WRf | CZ16 | 1975 | 0.006 | old
2020 | SCG | WRf | CZ16 | 1985 | 0.026 | old
2020 | SCG | WRf | CZ16 | 1996 | 0.016 | old
2020 | SCG | WRf | CZ16 | 2003 | 0.005 | ex
2020 | SCG | WRf | CZ16 | 2007 | 0.006 | ex
2020 | SCG | WRf | CZ16 | 2011 | 0.006 | ex
2020 | SCG | WRf | CZ16 | 2015 | 0.005 | ex
2020 | SCG | WRf | CZ16 | 2017 | 0.005 | rec
2020 | SCG | WRf | CZ16 | 2020 | 0.002 | rec
2020 | SCG | WRf | CZ16 | New | 0.002 | new
2020 | SDG | Asm | CZ06 | 1975 | 0.201 | old
2020 | SDG | Asm | CZ06 | 1985 | 0.307 | old
2020 | SDG | Asm | CZ06 | 1996 | 0.201 | old
2020 | SDG | Asm | CZ06 | 2003 | 0.1 | ex
2020 | SDG | Asm | CZ06 | 2007 | 0.059 | ex
2020 | SDG | Asm | CZ06 | 2011 | 0.059 | ex
2020 | SDG | Asm | CZ06 | 2015 | 0.044 | ex
2020 | SDG | Asm | CZ06 | 2017 | 0.044 | rec
2020 | SDG | Asm | CZ06 | 2020 | 0.015 | rec
2020 | SDG | Asm | CZ06 | New | 0.015 | new
2020 | SDG | Asm | CZ07 | 1975 | 3.896 | old
2020 | SDG | Asm | CZ07 | 1985 | 5.952 | old
2020 | SDG | Asm | CZ07 | 1996 | 3.888 | old
2020 | SDG | Asm | CZ07 | 2003 | 1.935 | ex
2020 | SDG | Asm | CZ07 | 2007 | 1.142 | ex
2020 | SDG | Asm | CZ07 | 2011 | 1.142 | ex
2020 | SDG | Asm | CZ07 | 2015 | 0.856 | ex
2020 | SDG | Asm | CZ07 | 2017 | 0.856 | rec
2020 | SDG | Asm | CZ07 | 2020 | 0.286 | rec
2020 | SDG | Asm | CZ07 | New | 0.286 | new
2020 | SDG | Asm | CZ08 | 1975 | 0.123 | old
2020 | SDG | Asm | CZ08 | 1985 | 0.189 | old
2020 | SDG | Asm | CZ08 | 1996 | 0.123 | old
2020 | SDG | Asm | CZ08 | 2003 | 0.061 | ex
2020 | SDG | Asm | CZ08 | 2007 | 0.036 | ex
2020 | SDG | Asm | CZ08 | 2011 | 0.036 | ex
2020 | SDG | Asm | CZ08 | 2015 | 0.027 | ex
2020 | SDG | Asm | CZ08 | 2017 | 0.027 | rec
2020 | SDG | Asm | CZ08 | 2020 | 0.009 | rec
2020 | SDG | Asm | CZ08 | New | 0.009 | new
2020 | SDG | Asm | CZ10 | 1975 | 1.872 | old
2020 | SDG | Asm | CZ10 | 1985 | 2.86 | old
2020 | SDG | Asm | CZ10 | 1996 | 1.868 | old
2020 | SDG | Asm | CZ10 | 2003 | 0.93 | ex
2020 | SDG | Asm | CZ10 | 2007 | 0.549 | ex
2020 | SDG | Asm | CZ10 | 2011 | 0.549 | ex
2020 | SDG | Asm | CZ10 | 2015 | 0.412 | ex
2020 | SDG | Asm | CZ10 | 2017 | 0.412 | rec
2020 | SDG | Asm | CZ10 | 2020 | 0.137 | rec
2020 | SDG | Asm | CZ10 | New | 0.137 | new
2020 | SDG | Asm | CZ14 | 1975 | 0.059 | old
2020 | SDG | Asm | CZ14 | 1985 | 0.09 | old
2020 | SDG | Asm | CZ14 | 1996 | 0.059 | old
2020 | SDG | Asm | CZ14 | 2003 | 0.029 | ex
2020 | SDG | Asm | CZ14 | 2007 | 0.017 | ex
2020 | SDG | Asm | CZ14 | 2011 | 0.017 | ex
2020 | SDG | Asm | CZ14 | 2015 | 0.013 | ex
2020 | SDG | Asm | CZ14 | 2017 | 0.013 | rec
2020 | SDG | Asm | CZ14 | 2020 | 0.004 | rec
2020 | SDG | Asm | CZ14 | New | 0.004 | new
2020 | SDG | Asm | CZ15 | 1975 | 0.019 | old
2020 | SDG | Asm | CZ15 | 1985 | 0.029 | old
2020 | SDG | Asm | CZ15 | 1996 | 0.019 | old
2020 | SDG | Asm | CZ15 | 2003 | 0.01 | ex
2020 | SDG | Asm | CZ15 | 2007 | 0.006 | ex
2020 | SDG | Asm | CZ15 | 2011 | 0.006 | ex
2020 | SDG | Asm | CZ15 | 2015 | 0.004 | ex
2020 | SDG | Asm | CZ15 | 2017 | 0.004 | rec
2020 | SDG | Asm | CZ15 | 2020 | 0.001 | rec
2020 | SDG | Asm | CZ15 | New | 0.001 | new
2020 | SDG | ECC | CZ06 | 1975 | 0.025 | old
2020 | SDG | ECC | CZ06 | 1985 | 0.022 | old
2020 | SDG | ECC | CZ06 | 1996 | 0.013 | old
2020 | SDG | ECC | CZ06 | 2003 | 0.011 | ex
2020 | SDG | ECC | CZ06 | 2007 | 0.003 | ex
2020 | SDG | ECC | CZ06 | 2011 | 0.003 | ex
2020 | SDG | ECC | CZ06 | 2015 | 0.003 | ex
2020 | SDG | ECC | CZ06 | 2017 | 0.003 | rec
2020 | SDG | ECC | CZ06 | 2020 | 0.001 | rec
2020 | SDG | ECC | CZ06 | New | 0.001 | new
2020 | SDG | ECC | CZ07 | 1975 | 3.617 | old
2020 | SDG | ECC | CZ07 | 1985 | 3.151 | old
2020 | SDG | ECC | CZ07 | 1996 | 1.792 | old
2020 | SDG | ECC | CZ07 | 2003 | 1.584 | ex
2020 | SDG | ECC | CZ07 | 2007 | 0.473 | ex
2020 | SDG | ECC | CZ07 | 2011 | 0.473 | ex
2020 | SDG | ECC | CZ07 | 2015 | 0.355 | ex
2020 | SDG | ECC | CZ07 | 2017 | 0.355 | rec
2020 | SDG | ECC | CZ07 | 2020 | 0.118 | rec
2020 | SDG | ECC | CZ07 | New | 0.118 | new
2020 | SDG | ECC | CZ08 | 1975 | 0.043 | old
2020 | SDG | ECC | CZ08 | 1985 | 0.038 | old
2020 | SDG | ECC | CZ08 | 1996 | 0.021 | old
2020 | SDG | ECC | CZ08 | 2003 | 0.019 | ex
2020 | SDG | ECC | CZ08 | 2007 | 0.006 | ex
2020 | SDG | ECC | CZ08 | 2011 | 0.006 | ex
2020 | SDG | ECC | CZ08 | 2015 | 0.004 | ex
2020 | SDG | ECC | CZ08 | 2017 | 0.004 | rec
2020 | SDG | ECC | CZ08 | 2020 | 0.001 | rec
2020 | SDG | ECC | CZ08 | New | 0.001 | new
2020 | SDG | ECC | CZ10 | 1975 | 1.14 | old
2020 | SDG | ECC | CZ10 | 1985 | 0.993 | old
2020 | SDG | ECC | CZ10 | 1996 | 0.565 | old
2020 | SDG | ECC | CZ10 | 2003 | 0.499 | ex
2020 | SDG | ECC | CZ10 | 2007 | 0.149 | ex
2020 | SDG | ECC | CZ10 | 2011 | 0.149 | ex
2020 | SDG | ECC | CZ10 | 2015 | 0.112 | ex
2020 | SDG | ECC | CZ10 | 2017 | 0.112 | rec
2020 | SDG | ECC | CZ10 | 2020 | 0.037 | rec
2020 | SDG | ECC | CZ10 | New | 0.037 | new
2020 | SDG | ECC | CZ14 | 1975 | 0.025 | old
2020 | SDG | ECC | CZ14 | 1985 | 0.022 | old
2020 | SDG | ECC | CZ14 | 1996 | 0.013 | old
2020 | SDG | ECC | CZ14 | 2003 | 0.011 | ex
2020 | SDG | ECC | CZ14 | 2007 | 0.003 | ex
2020 | SDG | ECC | CZ14 | 2011 | 0.003 | ex
2020 | SDG | ECC | CZ14 | 2015 | 0.003 | ex
2020 | SDG | ECC | CZ14 | 2017 | 0.003 | rec
2020 | SDG | ECC | CZ14 | 2020 | 0.001 | rec
2020 | SDG | ECC | CZ14 | New | 0.001 | new
2020 | SDG | EPr | CZ06 | 1975 | 0.39 | old
2020 | SDG | EPr | CZ06 | 1985 | 0.101 | old
2020 | SDG | EPr | CZ06 | 1996 | 0.104 | old
2020 | SDG | EPr | CZ06 | 2003 | 0.076 | ex
2020 | SDG | EPr | CZ06 | 2007 | 0.017 | ex
2020 | SDG | EPr | CZ06 | 2011 | 0.017 | ex
2020 | SDG | EPr | CZ06 | 2015 | 0.013 | ex
2020 | SDG | EPr | CZ06 | 2017 | 0.013 | rec
2020 | SDG | EPr | CZ06 | 2020 | 0.004 | rec
2020 | SDG | EPr | CZ06 | New | 0.004 | new
2020 | SDG | EPr | CZ07 | 1975 | 4.474 | old
2020 | SDG | EPr | CZ07 | 1985 | 1.161 | old
2020 | SDG | EPr | CZ07 | 1996 | 1.194 | old
2020 | SDG | EPr | CZ07 | 2003 | 0.874 | ex
2020 | SDG | EPr | CZ07 | 2007 | 0.194 | ex
2020 | SDG | EPr | CZ07 | 2011 | 0.194 | ex
2020 | SDG | EPr | CZ07 | 2015 | 0.145 | ex
2020 | SDG | EPr | CZ07 | 2017 | 0.145 | rec
2020 | SDG | EPr | CZ07 | 2020 | 0.048 | rec
2020 | SDG | EPr | CZ07 | New | 0.048 | new
2020 | SDG | EPr | CZ08 | 1975 | 0.44 | old
2020 | SDG | EPr | CZ08 | 1985 | 0.114 | old
2020 | SDG | EPr | CZ08 | 1996 | 0.117 | old
2020 | SDG | EPr | CZ08 | 2003 | 0.086 | ex
2020 | SDG | EPr | CZ08 | 2007 | 0.019 | ex
2020 | SDG | EPr | CZ08 | 2011 | 0.019 | ex
2020 | SDG | EPr | CZ08 | 2015 | 0.014 | ex
2020 | SDG | EPr | CZ08 | 2017 | 0.014 | rec
2020 | SDG | EPr | CZ08 | 2020 | 0.005 | rec
2020 | SDG | EPr | CZ08 | New | 0.005 | new
2020 | SDG | EPr | CZ10 | 1975 | 2.606 | old
2020 | SDG | EPr | CZ10 | 1985 | 0.676 | old
2020 | SDG | EPr | CZ10 | 1996 | 0.696 | old
2020 | SDG | EPr | CZ10 | 2003 | 0.509 | ex
2020 | SDG | EPr | CZ10 | 2007 | 0.113 | ex
2020 | SDG | EPr | CZ10 | 2011 | 0.113 | ex
2020 | SDG | EPr | CZ10 | 2015 | 0.085 | ex
2020 | SDG | EPr | CZ10 | 2017 | 0.085 | rec
2020 | SDG | EPr | CZ10 | 2020 | 0.028 | rec
2020 | SDG | EPr | CZ10 | New | 0.028 | new
2020 | SDG | EPr | CZ14 | 1975 | 0.071 | old
2020 | SDG | EPr | CZ14 | 1985 | 0.019 | old
2020 | SDG | EPr | CZ14 | 1996 | 0.019 | old
2020 | SDG | EPr | CZ14 | 2003 | 0.014 | ex
2020 | SDG | EPr | CZ14 | 2007 | 0.003 | ex
2020 | SDG | EPr | CZ14 | 2011 | 0.003 | ex
2020 | SDG | EPr | CZ14 | 2015 | 0.002 | ex
2020 | SDG | EPr | CZ14 | 2017 | 0.002 | rec
2020 | SDG | EPr | CZ14 | 2020 | 0.001 | rec
2020 | SDG | EPr | CZ14 | New | 0.001 | new
2020 | SDG | EPr | CZ15 | 1975 | 0.019 | old
2020 | SDG | EPr | CZ15 | 1985 | 0.005 | old
2020 | SDG | EPr | CZ15 | 1996 | 0.005 | old
2020 | SDG | EPr | CZ15 | 2003 | 0.004 | ex
2020 | SDG | EPr | CZ15 | 2007 | 0.001 | ex
2020 | SDG | EPr | CZ15 | 2011 | 0.001 | ex
2020 | SDG | EPr | CZ15 | 2015 | 0.001 | ex
2020 | SDG | EPr | CZ15 | 2017 | 0.001 | rec
2020 | SDG | EPr | CZ15 | 2020 | 0.001 | rec
2020 | SDG | EPr | CZ15 | New | 0.001 | new
2020 | SDG | ERC | CZ06 | 1975 | 0.39 | old
2020 | SDG | ERC | CZ06 | 1985 | 0.101 | old
2020 | SDG | ERC | CZ06 | 1996 | 0.104 | old
2020 | SDG | ERC | CZ06 | 2003 | 0.076 | ex
2020 | SDG | ERC | CZ06 | 2007 | 0.017 | ex
2020 | SDG | ERC | CZ06 | 2011 | 0.017 | ex
2020 | SDG | ERC | CZ06 | 2015 | 0.013 | ex
2020 | SDG | ERC | CZ06 | 2017 | 0.013 | rec
2020 | SDG | ERC | CZ06 | 2020 | 0.004 | rec
2020 | SDG | ERC | CZ06 | New | 0.004 | new
2020 | SDG | ERC | CZ07 | 1975 | 4.474 | old
2020 | SDG | ERC | CZ07 | 1985 | 1.161 | old
2020 | SDG | ERC | CZ07 | 1996 | 1.194 | old
2020 | SDG | ERC | CZ07 | 2003 | 0.874 | ex
2020 | SDG | ERC | CZ07 | 2007 | 0.194 | ex
2020 | SDG | ERC | CZ07 | 2011 | 0.194 | ex
2020 | SDG | ERC | CZ07 | 2015 | 0.145 | ex
2020 | SDG | ERC | CZ07 | 2017 | 0.145 | rec
2020 | SDG | ERC | CZ07 | 2020 | 0.048 | rec
2020 | SDG | ERC | CZ07 | New | 0.048 | new
2020 | SDG | ERC | CZ08 | 1975 | 0.44 | old
2020 | SDG | ERC | CZ08 | 1985 | 0.114 | old
2020 | SDG | ERC | CZ08 | 1996 | 0.117 | old
2020 | SDG | ERC | CZ08 | 2003 | 0.086 | ex
2020 | SDG | ERC | CZ08 | 2007 | 0.019 | ex
2020 | SDG | ERC | CZ08 | 2011 | 0.019 | ex
2020 | SDG | ERC | CZ08 | 2015 | 0.014 | ex
2020 | SDG | ERC | CZ08 | 2017 | 0.014 | rec
2020 | SDG | ERC | CZ08 | 2020 | 0.005 | rec
2020 | SDG | ERC | CZ08 | New | 0.005 | new
2020 | SDG | ERC | CZ10 | 1975 | 2.606 | old
2020 | SDG | ERC | CZ10 | 1985 | 0.676 | old
2020 | SDG | ERC | CZ10 | 1996 | 0.696 | old
2020 | SDG | ERC | CZ10 | 2003 | 0.509 | ex
2020 | SDG | ERC | CZ10 | 2007 | 0.113 | ex
2020 | SDG | ERC | CZ10 | 2011 | 0.113 | ex
2020 | SDG | ERC | CZ10 | 2015 | 0.085 | ex
2020 | SDG | ERC | CZ10 | 2017 | 0.085 | rec
2020 | SDG | ERC | CZ10 | 2020 | 0.028 | rec
2020 | SDG | ERC | CZ10 | New | 0.028 | new
2020 | SDG | ERC | CZ14 | 1975 | 0.071 | old
2020 | SDG | ERC | CZ14 | 1985 | 0.019 | old
2020 | SDG | ERC | CZ14 | 1996 | 0.019 | old
2020 | SDG | ERC | CZ14 | 2003 | 0.014 | ex
2020 | SDG | ERC | CZ14 | 2007 | 0.003 | ex
2020 | SDG | ERC | CZ14 | 2011 | 0.003 | ex
2020 | SDG | ERC | CZ14 | 2015 | 0.002 | ex
2020 | SDG | ERC | CZ14 | 2017 | 0.002 | rec
2020 | SDG | ERC | CZ14 | 2020 | 0.001 | rec
2020 | SDG | ERC | CZ14 | New | 0.001 | new
2020 | SDG | ERC | CZ15 | 1975 | 0.019 | old
2020 | SDG | ERC | CZ15 | 1985 | 0.005 | old
2020 | SDG | ERC | CZ15 | 1996 | 0.005 | old
2020 | SDG | ERC | CZ15 | 2003 | 0.004 | ex
2020 | SDG | ERC | CZ15 | 2007 | 0.001 | ex
2020 | SDG | ERC | CZ15 | 2011 | 0.001 | ex
2020 | SDG | ERC | CZ15 | 2015 | 0.001 | ex
2020 | SDG | ERC | CZ15 | 2017 | 0.001 | rec
2020 | SDG | ERC | CZ15 | 2020 | 0.001 | rec
2020 | SDG | ERC | CZ15 | New | 0.001 | new
2020 | SDG | ESe | CZ06 | 1975 | 0.39 | old
2020 | SDG | ESe | CZ06 | 1985 | 0.101 | old
2020 | SDG | ESe | CZ06 | 1996 | 0.104 | old
2020 | SDG | ESe | CZ06 | 2003 | 0.076 | ex
2020 | SDG | ESe | CZ06 | 2007 | 0.017 | ex
2020 | SDG | ESe | CZ06 | 2011 | 0.017 | ex
2020 | SDG | ESe | CZ06 | 2015 | 0.013 | ex
2020 | SDG | ESe | CZ06 | 2017 | 0.013 | rec
2020 | SDG | ESe | CZ06 | 2020 | 0.004 | rec
2020 | SDG | ESe | CZ06 | New | 0.004 | new
2020 | SDG | ESe | CZ07 | 1975 | 4.474 | old
2020 | SDG | ESe | CZ07 | 1985 | 1.161 | old
2020 | SDG | ESe | CZ07 | 1996 | 1.194 | old
2020 | SDG | ESe | CZ07 | 2003 | 0.874 | ex
2020 | SDG | ESe | CZ07 | 2007 | 0.194 | ex
2020 | SDG | ESe | CZ07 | 2011 | 0.194 | ex
2020 | SDG | ESe | CZ07 | 2015 | 0.145 | ex
2020 | SDG | ESe | CZ07 | 2017 | 0.145 | rec
2020 | SDG | ESe | CZ07 | 2020 | 0.048 | rec
2020 | SDG | ESe | CZ07 | New | 0.048 | new
2020 | SDG | ESe | CZ08 | 1975 | 0.44 | old
2020 | SDG | ESe | CZ08 | 1985 | 0.114 | old
2020 | SDG | ESe | CZ08 | 1996 | 0.117 | old
2020 | SDG | ESe | CZ08 | 2003 | 0.086 | ex
2020 | SDG | ESe | CZ08 | 2007 | 0.019 | ex
2020 | SDG | ESe | CZ08 | 2011 | 0.019 | ex
2020 | SDG | ESe | CZ08 | 2015 | 0.014 | ex
2020 | SDG | ESe | CZ08 | 2017 | 0.014 | rec
2020 | SDG | ESe | CZ08 | 2020 | 0.005 | rec
2020 | SDG | ESe | CZ08 | New | 0.005 | new
2020 | SDG | ESe | CZ10 | 1975 | 2.606 | old
2020 | SDG | ESe | CZ10 | 1985 | 0.676 | old
2020 | SDG | ESe | CZ10 | 1996 | 0.696 | old
2020 | SDG | ESe | CZ10 | 2003 | 0.509 | ex
2020 | SDG | ESe | CZ10 | 2007 | 0.113 | ex
2020 | SDG | ESe | CZ10 | 2011 | 0.113 | ex
2020 | SDG | ESe | CZ10 | 2015 | 0.085 | ex
2020 | SDG | ESe | CZ10 | 2017 | 0.085 | rec
2020 | SDG | ESe | CZ10 | 2020 | 0.028 | rec
2020 | SDG | ESe | CZ10 | New | 0.028 | new
2020 | SDG | ESe | CZ14 | 1975 | 0.071 | old
2020 | SDG | ESe | CZ14 | 1985 | 0.019 | old
2020 | SDG | ESe | CZ14 | 1996 | 0.019 | old
2020 | SDG | ESe | CZ14 | 2003 | 0.014 | ex
2020 | SDG | ESe | CZ14 | 2007 | 0.003 | ex
2020 | SDG | ESe | CZ14 | 2011 | 0.003 | ex
2020 | SDG | ESe | CZ14 | 2015 | 0.002 | ex
2020 | SDG | ESe | CZ14 | 2017 | 0.002 | rec
2020 | SDG | ESe | CZ14 | 2020 | 0.001 | rec
2020 | SDG | ESe | CZ14 | New | 0.001 | new
2020 | SDG | ESe | CZ15 | 1975 | 0.019 | old
2020 | SDG | ESe | CZ15 | 1985 | 0.005 | old
2020 | SDG | ESe | CZ15 | 1996 | 0.005 | old
2020 | SDG | ESe | CZ15 | 2003 | 0.004 | ex
2020 | SDG | ESe | CZ15 | 2007 | 0.001 | ex
2020 | SDG | ESe | CZ15 | 2011 | 0.001 | ex
2020 | SDG | ESe | CZ15 | 2015 | 0.001 | ex
2020 | SDG | ESe | CZ15 | 2017 | 0.001 | rec
2020 | SDG | ESe | CZ15 | 2020 | 0.001 | rec
2020 | SDG | ESe | CZ15 | New | 0.001 | new
2020 | SDG | EUD | CZ06 | 1975 | 0.025 | old
2020 | SDG | EUD | CZ06 | 1985 | 0.022 | old
2020 | SDG | EUD | CZ06 | 1996 | 0.013 | old
2020 | SDG | EUD | CZ06 | 2003 | 0.011 | ex
2020 | SDG | EUD | CZ06 | 2007 | 0.003 | ex
2020 | SDG | EUD | CZ06 | 2011 | 0.003 | ex
2020 | SDG | EUD | CZ06 | 2015 | 0.003 | ex
2020 | SDG | EUD | CZ06 | 2017 | 0.003 | rec
2020 | SDG | EUD | CZ06 | 2020 | 0.001 | rec
2020 | SDG | EUD | CZ06 | New | 0.001 | new
2020 | SDG | EUD | CZ07 | 1975 | 3.617 | old
2020 | SDG | EUD | CZ07 | 1985 | 3.151 | old
2020 | SDG | EUD | CZ07 | 1996 | 1.792 | old
2020 | SDG | EUD | CZ07 | 2003 | 1.584 | ex
2020 | SDG | EUD | CZ07 | 2007 | 0.473 | ex
2020 | SDG | EUD | CZ07 | 2011 | 0.473 | ex
2020 | SDG | EUD | CZ07 | 2015 | 0.355 | ex
2020 | SDG | EUD | CZ07 | 2017 | 0.355 | rec
2020 | SDG | EUD | CZ07 | 2020 | 0.118 | rec
2020 | SDG | EUD | CZ07 | New | 0.118 | new
2020 | SDG | EUD | CZ08 | 1975 | 0.043 | old
2020 | SDG | EUD | CZ08 | 1985 | 0.038 | old
2020 | SDG | EUD | CZ08 | 1996 | 0.021 | old
2020 | SDG | EUD | CZ08 | 2003 | 0.019 | ex
2020 | SDG | EUD | CZ08 | 2007 | 0.006 | ex
2020 | SDG | EUD | CZ08 | 2011 | 0.006 | ex
2020 | SDG | EUD | CZ08 | 2015 | 0.004 | ex
2020 | SDG | EUD | CZ08 | 2017 | 0.004 | rec
2020 | SDG | EUD | CZ08 | 2020 | 0.001 | rec
2020 | SDG | EUD | CZ08 | New | 0.001 | new
2020 | SDG | EUD | CZ10 | 1975 | 1.14 | old
2020 | SDG | EUD | CZ10 | 1985 | 0.993 | old
2020 | SDG | EUD | CZ10 | 1996 | 0.565 | old
2020 | SDG | EUD | CZ10 | 2003 | 0.499 | ex
2020 | SDG | EUD | CZ10 | 2007 | 0.149 | ex
2020 | SDG | EUD | CZ10 | 2011 | 0.149 | ex
2020 | SDG | EUD | CZ10 | 2015 | 0.112 | ex
2020 | SDG | EUD | CZ10 | 2017 | 0.112 | rec
2020 | SDG | EUD | CZ10 | 2020 | 0.037 | rec
2020 | SDG | EUD | CZ10 | New | 0.037 | new
2020 | SDG | EUD | CZ14 | 1975 | 0.025 | old
2020 | SDG | EUD | CZ14 | 1985 | 0.022 | old
2020 | SDG | EUD | CZ14 | 1996 | 0.013 | old
2020 | SDG | EUD | CZ14 | 2003 | 0.011 | ex
2020 | SDG | EUD | CZ14 | 2007 | 0.003 | ex
2020 | SDG | EUD | CZ14 | 2011 | 0.003 | ex
2020 | SDG | EUD | CZ14 | 2015 | 0.003 | ex
2020 | SDG | EUD | CZ14 | 2017 | 0.003 | rec
2020 | SDG | EUD | CZ14 | 2020 | 0.001 | rec
2020 | SDG | EUD | CZ14 | New | 0.001 | new
2020 | SDG | EUn | CZ06 | 1975 | 0.025 | old
2020 | SDG | EUn | CZ06 | 1985 | 0.022 | old
2020 | SDG | EUn | CZ06 | 1996 | 0.013 | old
2020 | SDG | EUn | CZ06 | 2003 | 0.011 | ex
2020 | SDG | EUn | CZ06 | 2007 | 0.003 | ex
2020 | SDG | EUn | CZ06 | 2011 | 0.003 | ex
2020 | SDG | EUn | CZ06 | 2015 | 0.003 | ex
2020 | SDG | EUn | CZ06 | 2017 | 0.003 | rec
2020 | SDG | EUn | CZ06 | 2020 | 0.001 | rec
2020 | SDG | EUn | CZ06 | New | 0.001 | new
2020 | SDG | EUn | CZ07 | 1975 | 3.617 | old
2020 | SDG | EUn | CZ07 | 1985 | 3.151 | old
2020 | SDG | EUn | CZ07 | 1996 | 1.792 | old
2020 | SDG | EUn | CZ07 | 2003 | 1.584 | ex
2020 | SDG | EUn | CZ07 | 2007 | 0.473 | ex
2020 | SDG | EUn | CZ07 | 2011 | 0.473 | ex
2020 | SDG | EUn | CZ07 | 2015 | 0.355 | ex
2020 | SDG | EUn | CZ07 | 2017 | 0.355 | rec
2020 | SDG | EUn | CZ07 | 2020 | 0.118 | rec
2020 | SDG | EUn | CZ07 | New | 0.118 | new
2020 | SDG | EUn | CZ08 | 1975 | 0.043 | old
2020 | SDG | EUn | CZ08 | 1985 | 0.038 | old
2020 | SDG | EUn | CZ08 | 1996 | 0.021 | old
2020 | SDG | EUn | CZ08 | 2003 | 0.019 | ex
2020 | SDG | EUn | CZ08 | 2007 | 0.006 | ex
2020 | SDG | EUn | CZ08 | 2011 | 0.006 | ex
2020 | SDG | EUn | CZ08 | 2015 | 0.004 | ex
2020 | SDG | EUn | CZ08 | 2017 | 0.004 | rec
2020 | SDG | EUn | CZ08 | 2020 | 0.001 | rec
2020 | SDG | EUn | CZ08 | New | 0.001 | new
2020 | SDG | EUn | CZ10 | 1975 | 1.14 | old
2020 | SDG | EUn | CZ10 | 1985 | 0.993 | old
2020 | SDG | EUn | CZ10 | 1996 | 0.565 | old
2020 | SDG | EUn | CZ10 | 2003 | 0.499 | ex
2020 | SDG | EUn | CZ10 | 2007 | 0.149 | ex
2020 | SDG | EUn | CZ10 | 2011 | 0.149 | ex
2020 | SDG | EUn | CZ10 | 2015 | 0.112 | ex
2020 | SDG | EUn | CZ10 | 2017 | 0.112 | rec
2020 | SDG | EUn | CZ10 | 2020 | 0.037 | rec
2020 | SDG | EUn | CZ10 | New | 0.037 | new
2020 | SDG | EUn | CZ14 | 1975 | 0.025 | old
2020 | SDG | EUn | CZ14 | 1985 | 0.022 | old
2020 | SDG | EUn | CZ14 | 1996 | 0.013 | old
2020 | SDG | EUn | CZ14 | 2003 | 0.011 | ex
2020 | SDG | EUn | CZ14 | 2007 | 0.003 | ex
2020 | SDG | EUn | CZ14 | 2011 | 0.003 | ex
2020 | SDG | EUn | CZ14 | 2015 | 0.003 | ex
2020 | SDG | EUn | CZ14 | 2017 | 0.003 | rec
2020 | SDG | EUn | CZ14 | 2020 | 0.001 | rec
2020 | SDG | EUn | CZ14 | New | 0.001 | new
2020 | SDG | Gro | CZ06 | 1975 | 0.312 | old
2020 | SDG | Gro | CZ06 | 1985 | 0.771 | old
2020 | SDG | Gro | CZ06 | 1996 | 0.369 | old
2020 | SDG | Gro | CZ06 | 2003 | 0.185 | ex
2020 | SDG | Gro | CZ06 | 2007 | 0.107 | ex
2020 | SDG | Gro | CZ06 | 2011 | 0.107 | ex
2020 | SDG | Gro | CZ06 | 2015 | 0.08 | ex
2020 | SDG | Gro | CZ06 | 2017 | 0.08 | rec
2020 | SDG | Gro | CZ06 | 2020 | 0.027 | rec
2020 | SDG | Gro | CZ06 | New | 0.027 | new
2020 | SDG | Gro | CZ07 | 1975 | 3.364 | old
2020 | SDG | Gro | CZ07 | 1985 | 8.306 | old
2020 | SDG | Gro | CZ07 | 1996 | 3.977 | old
2020 | SDG | Gro | CZ07 | 2003 | 1.995 | ex
2020 | SDG | Gro | CZ07 | 2007 | 1.153 | ex
2020 | SDG | Gro | CZ07 | 2011 | 1.153 | ex
2020 | SDG | Gro | CZ07 | 2015 | 0.865 | ex
2020 | SDG | Gro | CZ07 | 2017 | 0.865 | rec
2020 | SDG | Gro | CZ07 | 2020 | 0.288 | rec
2020 | SDG | Gro | CZ07 | New | 0.288 | new
2020 | SDG | Gro | CZ08 | 1975 | 0.129 | old
2020 | SDG | Gro | CZ08 | 1985 | 0.319 | old
2020 | SDG | Gro | CZ08 | 1996 | 0.153 | old
2020 | SDG | Gro | CZ08 | 2003 | 0.077 | ex
2020 | SDG | Gro | CZ08 | 2007 | 0.044 | ex
2020 | SDG | Gro | CZ08 | 2011 | 0.044 | ex
2020 | SDG | Gro | CZ08 | 2015 | 0.033 | ex
2020 | SDG | Gro | CZ08 | 2017 | 0.033 | rec
2020 | SDG | Gro | CZ08 | 2020 | 0.011 | rec
2020 | SDG | Gro | CZ08 | New | 0.011 | new
2020 | SDG | Gro | CZ10 | 1975 | 1.423 | old
2020 | SDG | Gro | CZ10 | 1985 | 3.513 | old
2020 | SDG | Gro | CZ10 | 1996 | 1.682 | old
2020 | SDG | Gro | CZ10 | 2003 | 0.844 | ex
2020 | SDG | Gro | CZ10 | 2007 | 0.488 | ex
2020 | SDG | Gro | CZ10 | 2011 | 0.488 | ex
2020 | SDG | Gro | CZ10 | 2015 | 0.366 | ex
2020 | SDG | Gro | CZ10 | 2017 | 0.366 | rec
2020 | SDG | Gro | CZ10 | 2020 | 0.122 | rec
2020 | SDG | Gro | CZ10 | New | 0.122 | new
2020 | SDG | Gro | CZ14 | 1975 | 0.02 | old
2020 | SDG | Gro | CZ14 | 1985 | 0.049 | old
2020 | SDG | Gro | CZ14 | 1996 | 0.024 | old
2020 | SDG | Gro | CZ14 | 2003 | 0.012 | ex
2020 | SDG | Gro | CZ14 | 2007 | 0.007 | ex
2020 | SDG | Gro | CZ14 | 2011 | 0.007 | ex
2020 | SDG | Gro | CZ14 | 2015 | 0.005 | ex
2020 | SDG | Gro | CZ14 | 2017 | 0.005 | rec
2020 | SDG | Gro | CZ14 | 2020 | 0.002 | rec
2020 | SDG | Gro | CZ14 | New | 0.002 | new
2020 | SDG | Gro | CZ15 | 1975 | 0.006 | old
2020 | SDG | Gro | CZ15 | 1985 | 0.014 | old
2020 | SDG | Gro | CZ15 | 1996 | 0.007 | old
2020 | SDG | Gro | CZ15 | 2003 | 0.003 | ex
2020 | SDG | Gro | CZ15 | 2007 | 0.002 | ex
2020 | SDG | Gro | CZ15 | 2011 | 0.002 | ex
2020 | SDG | Gro | CZ15 | 2015 | 0.002 | ex
2020 | SDG | Gro | CZ15 | 2017 | 0.002 | rec
2020 | SDG | Gro | CZ15 | 2020 | 0.001 | rec
2020 | SDG | Gro | CZ15 | New | 0.001 | new
2020 | SDG | HGR | CZ06 | 1975 | 0.23 | old
2020 | SDG | HGR | CZ06 | 1985 | 0.436 | old
2020 | SDG | HGR | CZ06 | 1996 | 0.094 | old
2020 | SDG | HGR | CZ06 | 2003 | 0.135 | ex
2020 | SDG | HGR | CZ06 | 2007 | 0.075 | ex
2020 | SDG | HGR | CZ06 | 2011 | 0.075 | ex
2020 | SDG | HGR | CZ06 | 2015 | 0.056 | ex
2020 | SDG | HGR | CZ06 | 2017 | 0.056 | rec
2020 | SDG | HGR | CZ06 | 2020 | 0.019 | rec
2020 | SDG | HGR | CZ06 | New | 0.019 | new
2020 | SDG | HGR | CZ07 | 1975 | 3.981 | old
2020 | SDG | HGR | CZ07 | 1985 | 7.554 | old
2020 | SDG | HGR | CZ07 | 1996 | 1.63 | old
2020 | SDG | HGR | CZ07 | 2003 | 2.344 | ex
2020 | SDG | HGR | CZ07 | 2007 | 1.292 | ex
2020 | SDG | HGR | CZ07 | 2011 | 1.292 | ex
2020 | SDG | HGR | CZ07 | 2015 | 0.969 | ex
2020 | SDG | HGR | CZ07 | 2017 | 0.969 | rec
2020 | SDG | HGR | CZ07 | 2020 | 0.323 | rec
2020 | SDG | HGR | CZ07 | New | 0.323 | new
2020 | SDG | HGR | CZ08 | 1975 | 0.015 | old
2020 | SDG | HGR | CZ08 | 1985 | 0.028 | old
2020 | SDG | HGR | CZ08 | 1996 | 0.006 | old
2020 | SDG | HGR | CZ08 | 2003 | 0.009 | ex
2020 | SDG | HGR | CZ08 | 2007 | 0.005 | ex
2020 | SDG | HGR | CZ08 | 2011 | 0.005 | ex
2020 | SDG | HGR | CZ08 | 2015 | 0.004 | ex
2020 | SDG | HGR | CZ08 | 2017 | 0.004 | rec
2020 | SDG | HGR | CZ08 | 2020 | 0.001 | rec
2020 | SDG | HGR | CZ08 | New | 0.001 | new
2020 | SDG | HGR | CZ10 | 1975 | 0.451 | old
2020 | SDG | HGR | CZ10 | 1985 | 0.857 | old
2020 | SDG | HGR | CZ10 | 1996 | 0.185 | old
2020 | SDG | HGR | CZ10 | 2003 | 0.266 | ex
2020 | SDG | HGR | CZ10 | 2007 | 0.147 | ex
2020 | SDG | HGR | CZ10 | 2011 | 0.147 | ex
2020 | SDG | HGR | CZ10 | 2015 | 0.11 | ex
2020 | SDG | HGR | CZ10 | 2017 | 0.11 | rec
2020 | SDG | HGR | CZ10 | 2020 | 0.037 | rec
2020 | SDG | HGR | CZ10 | New | 0.037 | new
2020 | SDG | HGR | CZ14 | 1975 | 0.045 | old
2020 | SDG | HGR | CZ14 | 1985 | 0.085 | old
2020 | SDG | HGR | CZ14 | 1996 | 0.018 | old
2020 | SDG | HGR | CZ14 | 2003 | 0.027 | ex
2020 | SDG | HGR | CZ14 | 2007 | 0.015 | ex
2020 | SDG | HGR | CZ14 | 2011 | 0.015 | ex
2020 | SDG | HGR | CZ14 | 2015 | 0.011 | ex
2020 | SDG | HGR | CZ14 | 2017 | 0.011 | rec
2020 | SDG | HGR | CZ14 | 2020 | 0.004 | rec
2020 | SDG | HGR | CZ14 | New | 0.004 | new
2020 | SDG | HGR | CZ15 | 1975 | 0.055 | old
2020 | SDG | HGR | CZ15 | 1985 | 0.103 | old
2020 | SDG | HGR | CZ15 | 1996 | 0.022 | old
2020 | SDG | HGR | CZ15 | 2003 | 0.032 | ex
2020 | SDG | HGR | CZ15 | 2007 | 0.018 | ex
2020 | SDG | HGR | CZ15 | 2011 | 0.018 | ex
2020 | SDG | HGR | CZ15 | 2015 | 0.013 | ex
2020 | SDG | HGR | CZ15 | 2017 | 0.013 | rec
2020 | SDG | HGR | CZ15 | 2020 | 0.004 | rec
2020 | SDG | HGR | CZ15 | New | 0.004 | new
2020 | SDG | Hsp | CZ06 | 1975 | 0.144 | old
2020 | SDG | Hsp | CZ06 | 1985 | 0.143 | old
2020 | SDG | Hsp | CZ06 | 1996 | 0.047 | old
2020 | SDG | Hsp | CZ06 | 2003 | 0.029 | ex
2020 | SDG | Hsp | CZ06 | 2007 | 0.01 | ex
2020 | SDG | Hsp | CZ06 | 2011 | 0.01 | ex
2020 | SDG | Hsp | CZ06 | 2015 | 0.008 | ex
2020 | SDG | Hsp | CZ06 | 2017 | 0.008 | rec
2020 | SDG | Hsp | CZ06 | 2020 | 0.003 | rec
2020 | SDG | Hsp | CZ06 | New | 0.003 | new
2020 | SDG | Hsp | CZ07 | 1975 | 4.645 | old
2020 | SDG | Hsp | CZ07 | 1985 | 4.609 | old
2020 | SDG | Hsp | CZ07 | 1996 | 1.501 | old
2020 | SDG | Hsp | CZ07 | 2003 | 0.928 | ex
2020 | SDG | Hsp | CZ07 | 2007 | 0.334 | ex
2020 | SDG | Hsp | CZ07 | 2011 | 0.334 | ex
2020 | SDG | Hsp | CZ07 | 2015 | 0.25 | ex
2020 | SDG | Hsp | CZ07 | 2017 | 0.25 | rec
2020 | SDG | Hsp | CZ07 | 2020 | 0.083 | rec
2020 | SDG | Hsp | CZ07 | New | 0.083 | new
2020 | SDG | Hsp | CZ08 | 1975 | 0.261 | old
2020 | SDG | Hsp | CZ08 | 1985 | 0.259 | old
2020 | SDG | Hsp | CZ08 | 1996 | 0.084 | old
2020 | SDG | Hsp | CZ08 | 2003 | 0.052 | ex
2020 | SDG | Hsp | CZ08 | 2007 | 0.019 | ex
2020 | SDG | Hsp | CZ08 | 2011 | 0.019 | ex
2020 | SDG | Hsp | CZ08 | 2015 | 0.014 | ex
2020 | SDG | Hsp | CZ08 | 2017 | 0.014 | rec
2020 | SDG | Hsp | CZ08 | 2020 | 0.005 | rec
2020 | SDG | Hsp | CZ08 | New | 0.005 | new
2020 | SDG | Hsp | CZ10 | 1975 | 0.826 | old
2020 | SDG | Hsp | CZ10 | 1985 | 0.819 | old
2020 | SDG | Hsp | CZ10 | 1996 | 0.267 | old
2020 | SDG | Hsp | CZ10 | 2003 | 0.165 | ex
2020 | SDG | Hsp | CZ10 | 2007 | 0.059 | ex
2020 | SDG | Hsp | CZ10 | 2011 | 0.059 | ex
2020 | SDG | Hsp | CZ10 | 2015 | 0.045 | ex
2020 | SDG | Hsp | CZ10 | 2017 | 0.045 | rec
2020 | SDG | Hsp | CZ10 | 2020 | 0.015 | rec
2020 | SDG | Hsp | CZ10 | New | 0.015 | new
2020 | SDG | Hsp | CZ14 | 1975 | 0.004 | old
2020 | SDG | Hsp | CZ14 | 1985 | 0.004 | old
2020 | SDG | Hsp | CZ14 | 1996 | 0.001 | old
2020 | SDG | Hsp | CZ14 | 2003 | 0.001 | ex
2020 | SDG | Hsp | CZ14 | 2007 | 0.001 | ex
2020 | SDG | Hsp | CZ14 | 2011 | 0.001 | ex
2020 | SDG | Hsp | CZ14 | 2015 | 0.001 | ex
2020 | SDG | Hsp | CZ14 | 2017 | 0.001 | rec
2020 | SDG | Hsp | CZ14 | 2020 | 0.001 | rec
2020 | SDG | Hsp | CZ14 | New | 0.001 | new
2020 | SDG | Htl | CZ06 | 1975 | 0.23 | old
2020 | SDG | Htl | CZ06 | 1985 | 0.436 | old
2020 | SDG | Htl | CZ06 | 1996 | 0.094 | old
2020 | SDG | Htl | CZ06 | 2003 | 0.135 | ex
2020 | SDG | Htl | CZ06 | 2007 | 0.075 | ex
2020 | SDG | Htl | CZ06 | 2011 | 0.075 | ex
2020 | SDG | Htl | CZ06 | 2015 | 0.056 | ex
2020 | SDG | Htl | CZ06 | 2017 | 0.056 | rec
2020 | SDG | Htl | CZ06 | 2020 | 0.019 | rec
2020 | SDG | Htl | CZ06 | New | 0.019 | new
2020 | SDG | Htl | CZ07 | 1975 | 3.981 | old
2020 | SDG | Htl | CZ07 | 1985 | 7.554 | old
2020 | SDG | Htl | CZ07 | 1996 | 1.63 | old
2020 | SDG | Htl | CZ07 | 2003 | 2.344 | ex
2020 | SDG | Htl | CZ07 | 2007 | 1.292 | ex
2020 | SDG | Htl | CZ07 | 2011 | 1.292 | ex
2020 | SDG | Htl | CZ07 | 2015 | 0.969 | ex
2020 | SDG | Htl | CZ07 | 2017 | 0.969 | rec
2020 | SDG | Htl | CZ07 | 2020 | 0.323 | rec
2020 | SDG | Htl | CZ07 | New | 0.323 | new
2020 | SDG | Htl | CZ08 | 1975 | 0.015 | old
2020 | SDG | Htl | CZ08 | 1985 | 0.028 | old
2020 | SDG | Htl | CZ08 | 1996 | 0.006 | old
2020 | SDG | Htl | CZ08 | 2003 | 0.009 | ex
2020 | SDG | Htl | CZ08 | 2007 | 0.005 | ex
2020 | SDG | Htl | CZ08 | 2011 | 0.005 | ex
2020 | SDG | Htl | CZ08 | 2015 | 0.004 | ex
2020 | SDG | Htl | CZ08 | 2017 | 0.004 | rec
2020 | SDG | Htl | CZ08 | 2020 | 0.001 | rec
2020 | SDG | Htl | CZ08 | New | 0.001 | new
2020 | SDG | Htl | CZ10 | 1975 | 0.451 | old
2020 | SDG | Htl | CZ10 | 1985 | 0.857 | old
2020 | SDG | Htl | CZ10 | 1996 | 0.185 | old
2020 | SDG | Htl | CZ10 | 2003 | 0.266 | ex
2020 | SDG | Htl | CZ10 | 2007 | 0.147 | ex
2020 | SDG | Htl | CZ10 | 2011 | 0.147 | ex
2020 | SDG | Htl | CZ10 | 2015 | 0.11 | ex
2020 | SDG | Htl | CZ10 | 2017 | 0.11 | rec
2020 | SDG | Htl | CZ10 | 2020 | 0.037 | rec
2020 | SDG | Htl | CZ10 | New | 0.037 | new
2020 | SDG | Htl | CZ14 | 1975 | 0.045 | old
2020 | SDG | Htl | CZ14 | 1985 | 0.085 | old
2020 | SDG | Htl | CZ14 | 1996 | 0.018 | old
2020 | SDG | Htl | CZ14 | 2003 | 0.027 | ex
2020 | SDG | Htl | CZ14 | 2007 | 0.015 | ex
2020 | SDG | Htl | CZ14 | 2011 | 0.015 | ex
2020 | SDG | Htl | CZ14 | 2015 | 0.011 | ex
2020 | SDG | Htl | CZ14 | 2017 | 0.011 | rec
2020 | SDG | Htl | CZ14 | 2020 | 0.004 | rec
2020 | SDG | Htl | CZ14 | New | 0.004 | new
2020 | SDG | Htl | CZ15 | 1975 | 0.055 | old
2020 | SDG | Htl | CZ15 | 1985 | 0.103 | old
2020 | SDG | Htl | CZ15 | 1996 | 0.022 | old
2020 | SDG | Htl | CZ15 | 2003 | 0.032 | ex
2020 | SDG | Htl | CZ15 | 2007 | 0.018 | ex
2020 | SDG | Htl | CZ15 | 2011 | 0.018 | ex
2020 | SDG | Htl | CZ15 | 2015 | 0.013 | ex
2020 | SDG | Htl | CZ15 | 2017 | 0.013 | rec
2020 | SDG | Htl | CZ15 | 2020 | 0.004 | rec
2020 | SDG | Htl | CZ15 | New | 0.004 | new
2020 | SDG | MBT | CZ06 | 1975 | 0.201 | old
2020 | SDG | MBT | CZ06 | 1985 | 0.307 | old
2020 | SDG | MBT | CZ06 | 1996 | 0.201 | old
2020 | SDG | MBT | CZ06 | 2003 | 0.1 | ex
2020 | SDG | MBT | CZ06 | 2007 | 0.059 | ex
2020 | SDG | MBT | CZ06 | 2011 | 0.059 | ex
2020 | SDG | MBT | CZ06 | 2015 | 0.044 | ex
2020 | SDG | MBT | CZ06 | 2017 | 0.044 | rec
2020 | SDG | MBT | CZ06 | 2020 | 0.015 | rec
2020 | SDG | MBT | CZ06 | New | 0.015 | new
2020 | SDG | MBT | CZ07 | 1975 | 3.896 | old
2020 | SDG | MBT | CZ07 | 1985 | 5.952 | old
2020 | SDG | MBT | CZ07 | 1996 | 3.888 | old
2020 | SDG | MBT | CZ07 | 2003 | 1.935 | ex
2020 | SDG | MBT | CZ07 | 2007 | 1.142 | ex
2020 | SDG | MBT | CZ07 | 2011 | 1.142 | ex
2020 | SDG | MBT | CZ07 | 2015 | 0.856 | ex
2020 | SDG | MBT | CZ07 | 2017 | 0.856 | rec
2020 | SDG | MBT | CZ07 | 2020 | 0.286 | rec
2020 | SDG | MBT | CZ07 | New | 0.286 | new
2020 | SDG | MBT | CZ08 | 1975 | 0.123 | old
2020 | SDG | MBT | CZ08 | 1985 | 0.189 | old
2020 | SDG | MBT | CZ08 | 1996 | 0.123 | old
2020 | SDG | MBT | CZ08 | 2003 | 0.061 | ex
2020 | SDG | MBT | CZ08 | 2007 | 0.036 | ex
2020 | SDG | MBT | CZ08 | 2011 | 0.036 | ex
2020 | SDG | MBT | CZ08 | 2015 | 0.027 | ex
2020 | SDG | MBT | CZ08 | 2017 | 0.027 | rec
2020 | SDG | MBT | CZ08 | 2020 | 0.009 | rec
2020 | SDG | MBT | CZ08 | New | 0.009 | new
2020 | SDG | MBT | CZ10 | 1975 | 1.872 | old
2020 | SDG | MBT | CZ10 | 1985 | 2.86 | old
2020 | SDG | MBT | CZ10 | 1996 | 1.868 | old
2020 | SDG | MBT | CZ10 | 2003 | 0.93 | ex
2020 | SDG | MBT | CZ10 | 2007 | 0.549 | ex
2020 | SDG | MBT | CZ10 | 2011 | 0.549 | ex
2020 | SDG | MBT | CZ10 | 2015 | 0.412 | ex
2020 | SDG | MBT | CZ10 | 2017 | 0.412 | rec
2020 | SDG | MBT | CZ10 | 2020 | 0.137 | rec
2020 | SDG | MBT | CZ10 | New | 0.137 | new
2020 | SDG | MBT | CZ14 | 1975 | 0.059 | old
2020 | SDG | MBT | CZ14 | 1985 | 0.09 | old
2020 | SDG | MBT | CZ14 | 1996 | 0.059 | old
2020 | SDG | MBT | CZ14 | 2003 | 0.029 | ex
2020 | SDG | MBT | CZ14 | 2007 | 0.017 | ex
2020 | SDG | MBT | CZ14 | 2011 | 0.017 | ex
2020 | SDG | MBT | CZ14 | 2015 | 0.013 | ex
2020 | SDG | MBT | CZ14 | 2017 | 0.013 | rec
2020 | SDG | MBT | CZ14 | 2020 | 0.004 | rec
2020 | SDG | MBT | CZ14 | New | 0.004 | new
2020 | SDG | MBT | CZ15 | 1975 | 0.019 | old
2020 | SDG | MBT | CZ15 | 1985 | 0.029 | old
2020 | SDG | MBT | CZ15 | 1996 | 0.019 | old
2020 | SDG | MBT | CZ15 | 2003 | 0.01 | ex
2020 | SDG | MBT | CZ15 | 2007 | 0.006 | ex
2020 | SDG | MBT | CZ15 | 2011 | 0.006 | ex
2020 | SDG | MBT | CZ15 | 2015 | 0.004 | ex
2020 | SDG | MBT | CZ15 | 2017 | 0.004 | rec
2020 | SDG | MBT | CZ15 | 2020 | 0.001 | rec
2020 | SDG | MBT | CZ15 | New | 0.001 | new
2020 | SDG | MLI | CZ06 | 1975 | 0.201 | old
2020 | SDG | MLI | CZ06 | 1985 | 0.307 | old
2020 | SDG | MLI | CZ06 | 1996 | 0.201 | old
2020 | SDG | MLI | CZ06 | 2003 | 0.1 | ex
2020 | SDG | MLI | CZ06 | 2007 | 0.059 | ex
2020 | SDG | MLI | CZ06 | 2011 | 0.059 | ex
2020 | SDG | MLI | CZ06 | 2015 | 0.044 | ex
2020 | SDG | MLI | CZ06 | 2017 | 0.044 | rec
2020 | SDG | MLI | CZ06 | 2020 | 0.015 | rec
2020 | SDG | MLI | CZ06 | New | 0.015 | new
2020 | SDG | MLI | CZ07 | 1975 | 3.896 | old
2020 | SDG | MLI | CZ07 | 1985 | 5.952 | old
2020 | SDG | MLI | CZ07 | 1996 | 3.888 | old
2020 | SDG | MLI | CZ07 | 2003 | 1.935 | ex
2020 | SDG | MLI | CZ07 | 2007 | 1.142 | ex
2020 | SDG | MLI | CZ07 | 2011 | 1.142 | ex
2020 | SDG | MLI | CZ07 | 2015 | 0.856 | ex
2020 | SDG | MLI | CZ07 | 2017 | 0.856 | rec
2020 | SDG | MLI | CZ07 | 2020 | 0.286 | rec
2020 | SDG | MLI | CZ07 | New | 0.286 | new
2020 | SDG | MLI | CZ08 | 1975 | 0.123 | old
2020 | SDG | MLI | CZ08 | 1985 | 0.189 | old
2020 | SDG | MLI | CZ08 | 1996 | 0.123 | old
2020 | SDG | MLI | CZ08 | 2003 | 0.061 | ex
2020 | SDG | MLI | CZ08 | 2007 | 0.036 | ex
2020 | SDG | MLI | CZ08 | 2011 | 0.036 | ex
2020 | SDG | MLI | CZ08 | 2015 | 0.027 | ex
2020 | SDG | MLI | CZ08 | 2017 | 0.027 | rec
2020 | SDG | MLI | CZ08 | 2020 | 0.009 | rec
2020 | SDG | MLI | CZ08 | New | 0.009 | new
2020 | SDG | MLI | CZ10 | 1975 | 1.872 | old
2020 | SDG | MLI | CZ10 | 1985 | 2.86 | old
2020 | SDG | MLI | CZ10 | 1996 | 1.868 | old
2020 | SDG | MLI | CZ10 | 2003 | 0.93 | ex
2020 | SDG | MLI | CZ10 | 2007 | 0.549 | ex
2020 | SDG | MLI | CZ10 | 2011 | 0.549 | ex
2020 | SDG | MLI | CZ10 | 2015 | 0.412 | ex
2020 | SDG | MLI | CZ10 | 2017 | 0.412 | rec
2020 | SDG | MLI | CZ10 | 2020 | 0.137 | rec
2020 | SDG | MLI | CZ10 | New | 0.137 | new
2020 | SDG | MLI | CZ14 | 1975 | 0.059 | old
2020 | SDG | MLI | CZ14 | 1985 | 0.09 | old
2020 | SDG | MLI | CZ14 | 1996 | 0.059 | old
2020 | SDG | MLI | CZ14 | 2003 | 0.029 | ex
2020 | SDG | MLI | CZ14 | 2007 | 0.017 | ex
2020 | SDG | MLI | CZ14 | 2011 | 0.017 | ex
2020 | SDG | MLI | CZ14 | 2015 | 0.013 | ex
2020 | SDG | MLI | CZ14 | 2017 | 0.013 | rec
2020 | SDG | MLI | CZ14 | 2020 | 0.004 | rec
2020 | SDG | MLI | CZ14 | New | 0.004 | new
2020 | SDG | MLI | CZ15 | 1975 | 0.019 | old
2020 | SDG | MLI | CZ15 | 1985 | 0.029 | old
2020 | SDG | MLI | CZ15 | 1996 | 0.019 | old
2020 | SDG | MLI | CZ15 | 2003 | 0.01 | ex
2020 | SDG | MLI | CZ15 | 2007 | 0.006 | ex
2020 | SDG | MLI | CZ15 | 2011 | 0.006 | ex
2020 | SDG | MLI | CZ15 | 2015 | 0.004 | ex
2020 | SDG | MLI | CZ15 | 2017 | 0.004 | rec
2020 | SDG | MLI | CZ15 | 2020 | 0.001 | rec
2020 | SDG | MLI | CZ15 | New | 0.001 | new
2020 | SDG | Mtl | CZ06 | 1975 | 0.23 | old
2020 | SDG | Mtl | CZ06 | 1985 | 0.436 | old
2020 | SDG | Mtl | CZ06 | 1996 | 0.094 | old
2020 | SDG | Mtl | CZ06 | 2003 | 0.135 | ex
2020 | SDG | Mtl | CZ06 | 2007 | 0.075 | ex
2020 | SDG | Mtl | CZ06 | 2011 | 0.075 | ex
2020 | SDG | Mtl | CZ06 | 2015 | 0.056 | ex
2020 | SDG | Mtl | CZ06 | 2017 | 0.056 | rec
2020 | SDG | Mtl | CZ06 | 2020 | 0.019 | rec
2020 | SDG | Mtl | CZ06 | New | 0.019 | new
2020 | SDG | Mtl | CZ07 | 1975 | 3.981 | old
2020 | SDG | Mtl | CZ07 | 1985 | 7.554 | old
2020 | SDG | Mtl | CZ07 | 1996 | 1.63 | old
2020 | SDG | Mtl | CZ07 | 2003 | 2.344 | ex
2020 | SDG | Mtl | CZ07 | 2007 | 1.292 | ex
2020 | SDG | Mtl | CZ07 | 2011 | 1.292 | ex
2020 | SDG | Mtl | CZ07 | 2015 | 0.969 | ex
2020 | SDG | Mtl | CZ07 | 2017 | 0.969 | rec
2020 | SDG | Mtl | CZ07 | 2020 | 0.323 | rec
2020 | SDG | Mtl | CZ07 | New | 0.323 | new
2020 | SDG | Mtl | CZ08 | 1975 | 0.015 | old
2020 | SDG | Mtl | CZ08 | 1985 | 0.028 | old
2020 | SDG | Mtl | CZ08 | 1996 | 0.006 | old
2020 | SDG | Mtl | CZ08 | 2003 | 0.009 | ex
2020 | SDG | Mtl | CZ08 | 2007 | 0.005 | ex
2020 | SDG | Mtl | CZ08 | 2011 | 0.005 | ex
2020 | SDG | Mtl | CZ08 | 2015 | 0.004 | ex
2020 | SDG | Mtl | CZ08 | 2017 | 0.004 | rec
2020 | SDG | Mtl | CZ08 | 2020 | 0.001 | rec
2020 | SDG | Mtl | CZ08 | New | 0.001 | new
2020 | SDG | Mtl | CZ10 | 1975 | 0.451 | old
2020 | SDG | Mtl | CZ10 | 1985 | 0.857 | old
2020 | SDG | Mtl | CZ10 | 1996 | 0.185 | old
2020 | SDG | Mtl | CZ10 | 2003 | 0.266 | ex
2020 | SDG | Mtl | CZ10 | 2007 | 0.147 | ex
2020 | SDG | Mtl | CZ10 | 2011 | 0.147 | ex
2020 | SDG | Mtl | CZ10 | 2015 | 0.11 | ex
2020 | SDG | Mtl | CZ10 | 2017 | 0.11 | rec
2020 | SDG | Mtl | CZ10 | 2020 | 0.037 | rec
2020 | SDG | Mtl | CZ10 | New | 0.037 | new
2020 | SDG | Mtl | CZ14 | 1975 | 0.045 | old
2020 | SDG | Mtl | CZ14 | 1985 | 0.085 | old
2020 | SDG | Mtl | CZ14 | 1996 | 0.018 | old
2020 | SDG | Mtl | CZ14 | 2003 | 0.027 | ex
2020 | SDG | Mtl | CZ14 | 2007 | 0.015 | ex
2020 | SDG | Mtl | CZ14 | 2011 | 0.015 | ex
2020 | SDG | Mtl | CZ14 | 2015 | 0.011 | ex
2020 | SDG | Mtl | CZ14 | 2017 | 0.011 | rec
2020 | SDG | Mtl | CZ14 | 2020 | 0.004 | rec
2020 | SDG | Mtl | CZ14 | New | 0.004 | new
2020 | SDG | Mtl | CZ15 | 1975 | 0.055 | old
2020 | SDG | Mtl | CZ15 | 1985 | 0.103 | old
2020 | SDG | Mtl | CZ15 | 1996 | 0.022 | old
2020 | SDG | Mtl | CZ15 | 2003 | 0.032 | ex
2020 | SDG | Mtl | CZ15 | 2007 | 0.018 | ex
2020 | SDG | Mtl | CZ15 | 2011 | 0.018 | ex
2020 | SDG | Mtl | CZ15 | 2015 | 0.013 | ex
2020 | SDG | Mtl | CZ15 | 2017 | 0.013 | rec
2020 | SDG | Mtl | CZ15 | 2020 | 0.004 | rec
2020 | SDG | Mtl | CZ15 | New | 0.004 | new
2020 | SDG | Nrs | CZ06 | 1975 | 0.144 | old
2020 | SDG | Nrs | CZ06 | 1985 | 0.143 | old
2020 | SDG | Nrs | CZ06 | 1996 | 0.047 | old
2020 | SDG | Nrs | CZ06 | 2003 | 0.029 | ex
2020 | SDG | Nrs | CZ06 | 2007 | 0.01 | ex
2020 | SDG | Nrs | CZ06 | 2011 | 0.01 | ex
2020 | SDG | Nrs | CZ06 | 2015 | 0.008 | ex
2020 | SDG | Nrs | CZ06 | 2017 | 0.008 | rec
2020 | SDG | Nrs | CZ06 | 2020 | 0.003 | rec
2020 | SDG | Nrs | CZ06 | New | 0.003 | new
2020 | SDG | Nrs | CZ07 | 1975 | 4.645 | old
2020 | SDG | Nrs | CZ07 | 1985 | 4.609 | old
2020 | SDG | Nrs | CZ07 | 1996 | 1.501 | old
2020 | SDG | Nrs | CZ07 | 2003 | 0.928 | ex
2020 | SDG | Nrs | CZ07 | 2007 | 0.334 | ex
2020 | SDG | Nrs | CZ07 | 2011 | 0.334 | ex
2020 | SDG | Nrs | CZ07 | 2015 | 0.25 | ex
2020 | SDG | Nrs | CZ07 | 2017 | 0.25 | rec
2020 | SDG | Nrs | CZ07 | 2020 | 0.083 | rec
2020 | SDG | Nrs | CZ07 | New | 0.083 | new
2020 | SDG | Nrs | CZ08 | 1975 | 0.261 | old
2020 | SDG | Nrs | CZ08 | 1985 | 0.259 | old
2020 | SDG | Nrs | CZ08 | 1996 | 0.084 | old
2020 | SDG | Nrs | CZ08 | 2003 | 0.052 | ex
2020 | SDG | Nrs | CZ08 | 2007 | 0.019 | ex
2020 | SDG | Nrs | CZ08 | 2011 | 0.019 | ex
2020 | SDG | Nrs | CZ08 | 2015 | 0.014 | ex
2020 | SDG | Nrs | CZ08 | 2017 | 0.014 | rec
2020 | SDG | Nrs | CZ08 | 2020 | 0.005 | rec
2020 | SDG | Nrs | CZ08 | New | 0.005 | new
2020 | SDG | Nrs | CZ10 | 1975 | 0.826 | old
2020 | SDG | Nrs | CZ10 | 1985 | 0.819 | old
2020 | SDG | Nrs | CZ10 | 1996 | 0.267 | old
2020 | SDG | Nrs | CZ10 | 2003 | 0.165 | ex
2020 | SDG | Nrs | CZ10 | 2007 | 0.059 | ex
2020 | SDG | Nrs | CZ10 | 2011 | 0.059 | ex
2020 | SDG | Nrs | CZ10 | 2015 | 0.045 | ex
2020 | SDG | Nrs | CZ10 | 2017 | 0.045 | rec
2020 | SDG | Nrs | CZ10 | 2020 | 0.015 | rec
2020 | SDG | Nrs | CZ10 | New | 0.015 | new
2020 | SDG | Nrs | CZ14 | 1975 | 0.004 | old
2020 | SDG | Nrs | CZ14 | 1985 | 0.004 | old
2020 | SDG | Nrs | CZ14 | 1996 | 0.001 | old
2020 | SDG | Nrs | CZ14 | 2003 | 0.001 | ex
2020 | SDG | Nrs | CZ14 | 2007 | 0.001 | ex
2020 | SDG | Nrs | CZ14 | 2011 | 0.001 | ex
2020 | SDG | Nrs | CZ14 | 2015 | 0.001 | ex
2020 | SDG | Nrs | CZ14 | 2017 | 0.001 | rec
2020 | SDG | Nrs | CZ14 | 2020 | 0.001 | rec
2020 | SDG | Nrs | CZ14 | New | 0.001 | new
2020 | SDG | OfL | CZ06 | 1975 | 0.233 | old
2020 | SDG | OfL | CZ06 | 1985 | 1.281 | old
2020 | SDG | OfL | CZ06 | 1996 | 0.35 | old
2020 | SDG | OfL | CZ06 | 2003 | 0.203 | ex
2020 | SDG | OfL | CZ06 | 2007 | 0.082 | ex
2020 | SDG | OfL | CZ06 | 2011 | 0.082 | ex
2020 | SDG | OfL | CZ06 | 2015 | 0.061 | ex
2020 | SDG | OfL | CZ06 | 2017 | 0.061 | rec
2020 | SDG | OfL | CZ06 | 2020 | 0.02 | rec
2020 | SDG | OfL | CZ06 | New | 0.02 | new
2020 | SDG | OfL | CZ07 | 1975 | 8.368 | old
2020 | SDG | OfL | CZ07 | 1985 | 45.981 | old
2020 | SDG | OfL | CZ07 | 1996 | 12.559 | old
2020 | SDG | OfL | CZ07 | 2003 | 7.284 | ex
2020 | SDG | OfL | CZ07 | 2007 | 2.934 | ex
2020 | SDG | OfL | CZ07 | 2011 | 2.934 | ex
2020 | SDG | OfL | CZ07 | 2015 | 2.201 | ex
2020 | SDG | OfL | CZ07 | 2017 | 2.201 | rec
2020 | SDG | OfL | CZ07 | 2020 | 0.734 | rec
2020 | SDG | OfL | CZ07 | New | 0.734 | new
2020 | SDG | OfL | CZ08 | 1975 | 0.218 | old
2020 | SDG | OfL | CZ08 | 1985 | 1.198 | old
2020 | SDG | OfL | CZ08 | 1996 | 0.327 | old
2020 | SDG | OfL | CZ08 | 2003 | 0.19 | ex
2020 | SDG | OfL | CZ08 | 2007 | 0.077 | ex
2020 | SDG | OfL | CZ08 | 2011 | 0.077 | ex
2020 | SDG | OfL | CZ08 | 2015 | 0.057 | ex
2020 | SDG | OfL | CZ08 | 2017 | 0.057 | rec
2020 | SDG | OfL | CZ08 | 2020 | 0.019 | rec
2020 | SDG | OfL | CZ08 | New | 0.019 | new
2020 | SDG | OfL | CZ10 | 1975 | 1.863 | old
2020 | SDG | OfL | CZ10 | 1985 | 10.235 | old
2020 | SDG | OfL | CZ10 | 1996 | 2.796 | old
2020 | SDG | OfL | CZ10 | 2003 | 1.621 | ex
2020 | SDG | OfL | CZ10 | 2007 | 0.653 | ex
2020 | SDG | OfL | CZ10 | 2011 | 0.653 | ex
2020 | SDG | OfL | CZ10 | 2015 | 0.49 | ex
2020 | SDG | OfL | CZ10 | 2017 | 0.49 | rec
2020 | SDG | OfL | CZ10 | 2020 | 0.163 | rec
2020 | SDG | OfL | CZ10 | New | 0.163 | new
2020 | SDG | OfL | CZ14 | 1975 | 0.045 | old
2020 | SDG | OfL | CZ14 | 1985 | 0.248 | old
2020 | SDG | OfL | CZ14 | 1996 | 0.068 | old
2020 | SDG | OfL | CZ14 | 2003 | 0.039 | ex
2020 | SDG | OfL | CZ14 | 2007 | 0.016 | ex
2020 | SDG | OfL | CZ14 | 2011 | 0.016 | ex
2020 | SDG | OfL | CZ14 | 2015 | 0.012 | ex
2020 | SDG | OfL | CZ14 | 2017 | 0.012 | rec
2020 | SDG | OfL | CZ14 | 2020 | 0.004 | rec
2020 | SDG | OfL | CZ14 | New | 0.004 | new
2020 | SDG | OfL | CZ15 | 1975 | 0.014 | old
2020 | SDG | OfL | CZ15 | 1985 | 0.077 | old
2020 | SDG | OfL | CZ15 | 1996 | 0.021 | old
2020 | SDG | OfL | CZ15 | 2003 | 0.012 | ex
2020 | SDG | OfL | CZ15 | 2007 | 0.005 | ex
2020 | SDG | OfL | CZ15 | 2011 | 0.005 | ex
2020 | SDG | OfL | CZ15 | 2015 | 0.004 | ex
2020 | SDG | OfL | CZ15 | 2017 | 0.004 | rec
2020 | SDG | OfL | CZ15 | 2020 | 0.001 | rec
2020 | SDG | OfL | CZ15 | New | 0.001 | new
2020 | SDG | OfS | CZ06 | 1975 | 0.657 | old
2020 | SDG | OfS | CZ06 | 1985 | 0.253 | old
2020 | SDG | OfS | CZ06 | 1996 | 0.134 | old
2020 | SDG | OfS | CZ06 | 2003 | 0.063 | ex
2020 | SDG | OfS | CZ06 | 2007 | 0.038 | ex
2020 | SDG | OfS | CZ06 | 2011 | 0.038 | ex
2020 | SDG | OfS | CZ06 | 2015 | 0.028 | ex
2020 | SDG | OfS | CZ06 | 2017 | 0.028 | rec
2020 | SDG | OfS | CZ06 | 2020 | 0.009 | rec
2020 | SDG | OfS | CZ06 | New | 0.009 | new
2020 | SDG | OfS | CZ07 | 1975 | 23.568 | old
2020 | SDG | OfS | CZ07 | 1985 | 9.098 | old
2020 | SDG | OfS | CZ07 | 1996 | 4.797 | old
2020 | SDG | OfS | CZ07 | 2003 | 2.264 | ex
2020 | SDG | OfS | CZ07 | 2007 | 1.345 | ex
2020 | SDG | OfS | CZ07 | 2011 | 1.345 | ex
2020 | SDG | OfS | CZ07 | 2015 | 1.009 | ex
2020 | SDG | OfS | CZ07 | 2017 | 1.009 | rec
2020 | SDG | OfS | CZ07 | 2020 | 0.336 | rec
2020 | SDG | OfS | CZ07 | New | 0.336 | new
2020 | SDG | OfS | CZ08 | 1975 | 0.614 | old
2020 | SDG | OfS | CZ08 | 1985 | 0.237 | old
2020 | SDG | OfS | CZ08 | 1996 | 0.125 | old
2020 | SDG | OfS | CZ08 | 2003 | 0.059 | ex
2020 | SDG | OfS | CZ08 | 2007 | 0.035 | ex
2020 | SDG | OfS | CZ08 | 2011 | 0.035 | ex
2020 | SDG | OfS | CZ08 | 2015 | 0.026 | ex
2020 | SDG | OfS | CZ08 | 2017 | 0.026 | rec
2020 | SDG | OfS | CZ08 | 2020 | 0.009 | rec
2020 | SDG | OfS | CZ08 | New | 0.009 | new
2020 | SDG | OfS | CZ10 | 1975 | 5.246 | old
2020 | SDG | OfS | CZ10 | 1985 | 2.025 | old
2020 | SDG | OfS | CZ10 | 1996 | 1.068 | old
2020 | SDG | OfS | CZ10 | 2003 | 0.504 | ex
2020 | SDG | OfS | CZ10 | 2007 | 0.299 | ex
2020 | SDG | OfS | CZ10 | 2011 | 0.299 | ex
2020 | SDG | OfS | CZ10 | 2015 | 0.225 | ex
2020 | SDG | OfS | CZ10 | 2017 | 0.225 | rec
2020 | SDG | OfS | CZ10 | 2020 | 0.075 | rec
2020 | SDG | OfS | CZ10 | New | 0.075 | new
2020 | SDG | OfS | CZ14 | 1975 | 0.127 | old
2020 | SDG | OfS | CZ14 | 1985 | 0.049 | old
2020 | SDG | OfS | CZ14 | 1996 | 0.026 | old
2020 | SDG | OfS | CZ14 | 2003 | 0.012 | ex
2020 | SDG | OfS | CZ14 | 2007 | 0.007 | ex
2020 | SDG | OfS | CZ14 | 2011 | 0.007 | ex
2020 | SDG | OfS | CZ14 | 2015 | 0.006 | ex
2020 | SDG | OfS | CZ14 | 2017 | 0.006 | rec
2020 | SDG | OfS | CZ14 | 2020 | 0.002 | rec
2020 | SDG | OfS | CZ14 | New | 0.002 | new
2020 | SDG | OfS | CZ15 | 1975 | 0.039 | old
2020 | SDG | OfS | CZ15 | 1985 | 0.015 | old
2020 | SDG | OfS | CZ15 | 1996 | 0.008 | old
2020 | SDG | OfS | CZ15 | 2003 | 0.004 | ex
2020 | SDG | OfS | CZ15 | 2007 | 0.002 | ex
2020 | SDG | OfS | CZ15 | 2011 | 0.002 | ex
2020 | SDG | OfS | CZ15 | 2015 | 0.002 | ex
2020 | SDG | OfS | CZ15 | 2017 | 0.002 | rec
2020 | SDG | OfS | CZ15 | 2020 | 0.001 | rec
2020 | SDG | OfS | CZ15 | New | 0.001 | new
2020 | SDG | RFF | CZ06 | 1975 | 0.186 | old
2020 | SDG | RFF | CZ06 | 1985 | 0.073 | old
2020 | SDG | RFF | CZ06 | 1996 | 0.048 | old
2020 | SDG | RFF | CZ06 | 2003 | 0.019 | ex
2020 | SDG | RFF | CZ06 | 2007 | 0.013 | ex
2020 | SDG | RFF | CZ06 | 2011 | 0.013 | ex
2020 | SDG | RFF | CZ06 | 2015 | 0.01 | ex
2020 | SDG | RFF | CZ06 | 2017 | 0.01 | rec
2020 | SDG | RFF | CZ06 | 2020 | 0.003 | rec
2020 | SDG | RFF | CZ06 | New | 0.003 | new
2020 | SDG | RFF | CZ07 | 1975 | 2.854 | old
2020 | SDG | RFF | CZ07 | 1985 | 1.125 | old
2020 | SDG | RFF | CZ07 | 1996 | 0.738 | old
2020 | SDG | RFF | CZ07 | 2003 | 0.296 | ex
2020 | SDG | RFF | CZ07 | 2007 | 0.201 | ex
2020 | SDG | RFF | CZ07 | 2011 | 0.201 | ex
2020 | SDG | RFF | CZ07 | 2015 | 0.151 | ex
2020 | SDG | RFF | CZ07 | 2017 | 0.151 | rec
2020 | SDG | RFF | CZ07 | 2020 | 0.05 | rec
2020 | SDG | RFF | CZ07 | New | 0.05 | new
2020 | SDG | RFF | CZ08 | 1975 | 0.125 | old
2020 | SDG | RFF | CZ08 | 1985 | 0.049 | old
2020 | SDG | RFF | CZ08 | 1996 | 0.032 | old
2020 | SDG | RFF | CZ08 | 2003 | 0.013 | ex
2020 | SDG | RFF | CZ08 | 2007 | 0.009 | ex
2020 | SDG | RFF | CZ08 | 2011 | 0.009 | ex
2020 | SDG | RFF | CZ08 | 2015 | 0.007 | ex
2020 | SDG | RFF | CZ08 | 2017 | 0.007 | rec
2020 | SDG | RFF | CZ08 | 2020 | 0.002 | rec
2020 | SDG | RFF | CZ08 | New | 0.002 | new
2020 | SDG | RFF | CZ10 | 1975 | 0.894 | old
2020 | SDG | RFF | CZ10 | 1985 | 0.352 | old
2020 | SDG | RFF | CZ10 | 1996 | 0.231 | old
2020 | SDG | RFF | CZ10 | 2003 | 0.093 | ex
2020 | SDG | RFF | CZ10 | 2007 | 0.063 | ex
2020 | SDG | RFF | CZ10 | 2011 | 0.063 | ex
2020 | SDG | RFF | CZ10 | 2015 | 0.047 | ex
2020 | SDG | RFF | CZ10 | 2017 | 0.047 | rec
2020 | SDG | RFF | CZ10 | 2020 | 0.016 | rec
2020 | SDG | RFF | CZ10 | New | 0.016 | new
2020 | SDG | RFF | CZ14 | 1975 | 0.009 | old
2020 | SDG | RFF | CZ14 | 1985 | 0.003 | old
2020 | SDG | RFF | CZ14 | 1996 | 0.002 | old
2020 | SDG | RFF | CZ14 | 2003 | 0.001 | ex
2020 | SDG | RFF | CZ14 | 2007 | 0.001 | ex
2020 | SDG | RFF | CZ14 | 2011 | 0.001 | ex
2020 | SDG | RFF | CZ14 | 2015 | 0.001 | ex
2020 | SDG | RFF | CZ14 | 2017 | 0.001 | rec
2020 | SDG | RFF | CZ14 | 2020 | 0.001 | rec
2020 | SDG | RFF | CZ14 | New | 0.001 | new
2020 | SDG | RFF | CZ15 | 1975 | 0.004 | old
2020 | SDG | RFF | CZ15 | 1985 | 0.002 | old
2020 | SDG | RFF | CZ15 | 1996 | 0.001 | old
2020 | SDG | RFF | CZ15 | 2003 | 0.001 | ex
2020 | SDG | RFF | CZ15 | 2007 | 0.001 | ex
2020 | SDG | RFF | CZ15 | 2011 | 0.001 | ex
2020 | SDG | RFF | CZ15 | 2015 | 0.001 | ex
2020 | SDG | RFF | CZ15 | 2017 | 0.001 | rec
2020 | SDG | RFF | CZ15 | 2020 | 0.001 | rec
2020 | SDG | RFF | CZ15 | New | 0.001 | new
2020 | SDG | RSD | CZ06 | 1975 | 0.186 | old
2020 | SDG | RSD | CZ06 | 1985 | 0.073 | old
2020 | SDG | RSD | CZ06 | 1996 | 0.048 | old
2020 | SDG | RSD | CZ06 | 2003 | 0.019 | ex
2020 | SDG | RSD | CZ06 | 2007 | 0.013 | ex
2020 | SDG | RSD | CZ06 | 2011 | 0.013 | ex
2020 | SDG | RSD | CZ06 | 2015 | 0.01 | ex
2020 | SDG | RSD | CZ06 | 2017 | 0.01 | rec
2020 | SDG | RSD | CZ06 | 2020 | 0.003 | rec
2020 | SDG | RSD | CZ06 | New | 0.003 | new
2020 | SDG | RSD | CZ07 | 1975 | 2.854 | old
2020 | SDG | RSD | CZ07 | 1985 | 1.125 | old
2020 | SDG | RSD | CZ07 | 1996 | 0.738 | old
2020 | SDG | RSD | CZ07 | 2003 | 0.296 | ex
2020 | SDG | RSD | CZ07 | 2007 | 0.201 | ex
2020 | SDG | RSD | CZ07 | 2011 | 0.201 | ex
2020 | SDG | RSD | CZ07 | 2015 | 0.151 | ex
2020 | SDG | RSD | CZ07 | 2017 | 0.151 | rec
2020 | SDG | RSD | CZ07 | 2020 | 0.05 | rec
2020 | SDG | RSD | CZ07 | New | 0.05 | new
2020 | SDG | RSD | CZ08 | 1975 | 0.125 | old
2020 | SDG | RSD | CZ08 | 1985 | 0.049 | old
2020 | SDG | RSD | CZ08 | 1996 | 0.032 | old
2020 | SDG | RSD | CZ08 | 2003 | 0.013 | ex
2020 | SDG | RSD | CZ08 | 2007 | 0.009 | ex
2020 | SDG | RSD | CZ08 | 2011 | 0.009 | ex
2020 | SDG | RSD | CZ08 | 2015 | 0.007 | ex
2020 | SDG | RSD | CZ08 | 2017 | 0.007 | rec
2020 | SDG | RSD | CZ08 | 2020 | 0.002 | rec
2020 | SDG | RSD | CZ08 | New | 0.002 | new
2020 | SDG | RSD | CZ10 | 1975 | 0.894 | old
2020 | SDG | RSD | CZ10 | 1985 | 0.352 | old
2020 | SDG | RSD | CZ10 | 1996 | 0.231 | old
2020 | SDG | RSD | CZ10 | 2003 | 0.093 | ex
2020 | SDG | RSD | CZ10 | 2007 | 0.063 | ex
2020 | SDG | RSD | CZ10 | 2011 | 0.063 | ex
2020 | SDG | RSD | CZ10 | 2015 | 0.047 | ex
2020 | SDG | RSD | CZ10 | 2017 | 0.047 | rec
2020 | SDG | RSD | CZ10 | 2020 | 0.016 | rec
2020 | SDG | RSD | CZ10 | New | 0.016 | new
2020 | SDG | RSD | CZ14 | 1975 | 0.009 | old
2020 | SDG | RSD | CZ14 | 1985 | 0.003 | old
2020 | SDG | RSD | CZ14 | 1996 | 0.002 | old
2020 | SDG | RSD | CZ14 | 2003 | 0.001 | ex
2020 | SDG | RSD | CZ14 | 2007 | 0.001 | ex
2020 | SDG | RSD | CZ14 | 2011 | 0.001 | ex
2020 | SDG | RSD | CZ14 | 2015 | 0.001 | ex
2020 | SDG | RSD | CZ14 | 2017 | 0.001 | rec
2020 | SDG | RSD | CZ14 | 2020 | 0.001 | rec
2020 | SDG | RSD | CZ14 | New | 0.001 | new
2020 | SDG | RSD | CZ15 | 1975 | 0.004 | old
2020 | SDG | RSD | CZ15 | 1985 | 0.002 | old
2020 | SDG | RSD | CZ15 | 1996 | 0.001 | old
2020 | SDG | RSD | CZ15 | 2003 | 0.001 | ex
2020 | SDG | RSD | CZ15 | 2007 | 0.001 | ex
2020 | SDG | RSD | CZ15 | 2011 | 0.001 | ex
2020 | SDG | RSD | CZ15 | 2015 | 0.001 | ex
2020 | SDG | RSD | CZ15 | 2017 | 0.001 | rec
2020 | SDG | RSD | CZ15 | 2020 | 0.001 | rec
2020 | SDG | RSD | CZ15 | New | 0.001 | new
2020 | SDG | Rt3 | CZ06 | 1975 | 0.328 | old
2020 | SDG | Rt3 | CZ06 | 1985 | 0.412 | old
2020 | SDG | Rt3 | CZ06 | 1996 | 0.209 | old
2020 | SDG | Rt3 | CZ06 | 2003 | 0.1 | ex
2020 | SDG | Rt3 | CZ06 | 2007 | 0.058 | ex
2020 | SDG | Rt3 | CZ06 | 2011 | 0.058 | ex
2020 | SDG | Rt3 | CZ06 | 2015 | 0.043 | ex
2020 | SDG | Rt3 | CZ06 | 2017 | 0.043 | rec
2020 | SDG | Rt3 | CZ06 | 2020 | 0.014 | rec
2020 | SDG | Rt3 | CZ06 | New | 0.014 | new
2020 | SDG | Rt3 | CZ07 | 1975 | 6.4 | old
2020 | SDG | Rt3 | CZ07 | 1985 | 8.036 | old
2020 | SDG | Rt3 | CZ07 | 1996 | 4.075 | old
2020 | SDG | Rt3 | CZ07 | 2003 | 1.957 | ex
2020 | SDG | Rt3 | CZ07 | 2007 | 1.122 | ex
2020 | SDG | Rt3 | CZ07 | 2011 | 1.122 | ex
2020 | SDG | Rt3 | CZ07 | 2015 | 0.841 | ex
2020 | SDG | Rt3 | CZ07 | 2017 | 0.841 | rec
2020 | SDG | Rt3 | CZ07 | 2020 | 0.281 | rec
2020 | SDG | Rt3 | CZ07 | New | 0.281 | new
2020 | SDG | Rt3 | CZ08 | 1975 | 0.589 | old
2020 | SDG | Rt3 | CZ08 | 1985 | 0.739 | old
2020 | SDG | Rt3 | CZ08 | 1996 | 0.375 | old
2020 | SDG | Rt3 | CZ08 | 2003 | 0.18 | ex
2020 | SDG | Rt3 | CZ08 | 2007 | 0.103 | ex
2020 | SDG | Rt3 | CZ08 | 2011 | 0.103 | ex
2020 | SDG | Rt3 | CZ08 | 2015 | 0.077 | ex
2020 | SDG | Rt3 | CZ08 | 2017 | 0.077 | rec
2020 | SDG | Rt3 | CZ08 | 2020 | 0.026 | rec
2020 | SDG | Rt3 | CZ08 | New | 0.026 | new
2020 | SDG | Rt3 | CZ10 | 1975 | 2.383 | old
2020 | SDG | Rt3 | CZ10 | 1985 | 2.993 | old
2020 | SDG | Rt3 | CZ10 | 1996 | 1.518 | old
2020 | SDG | Rt3 | CZ10 | 2003 | 0.729 | ex
2020 | SDG | Rt3 | CZ10 | 2007 | 0.418 | ex
2020 | SDG | Rt3 | CZ10 | 2011 | 0.418 | ex
2020 | SDG | Rt3 | CZ10 | 2015 | 0.313 | ex
2020 | SDG | Rt3 | CZ10 | 2017 | 0.313 | rec
2020 | SDG | Rt3 | CZ10 | 2020 | 0.105 | rec
2020 | SDG | Rt3 | CZ10 | New | 0.105 | new
2020 | SDG | Rt3 | CZ14 | 1975 | 0.009 | old
2020 | SDG | Rt3 | CZ14 | 1985 | 0.011 | old
2020 | SDG | Rt3 | CZ14 | 1996 | 0.006 | old
2020 | SDG | Rt3 | CZ14 | 2003 | 0.003 | ex
2020 | SDG | Rt3 | CZ14 | 2007 | 0.002 | ex
2020 | SDG | Rt3 | CZ14 | 2011 | 0.002 | ex
2020 | SDG | Rt3 | CZ14 | 2015 | 0.001 | ex
2020 | SDG | Rt3 | CZ14 | 2017 | 0.001 | rec
2020 | SDG | Rt3 | CZ14 | 2020 | 0.001 | rec
2020 | SDG | Rt3 | CZ14 | New | 0.001 | new
2020 | SDG | Rt3 | CZ15 | 1975 | 0.003 | old
2020 | SDG | Rt3 | CZ15 | 1985 | 0.004 | old
2020 | SDG | Rt3 | CZ15 | 1996 | 0.002 | old
2020 | SDG | Rt3 | CZ15 | 2003 | 0.001 | ex
2020 | SDG | Rt3 | CZ15 | 2007 | 0.001 | ex
2020 | SDG | Rt3 | CZ15 | 2011 | 0.001 | ex
2020 | SDG | Rt3 | CZ15 | 2015 | 0.001 | ex
2020 | SDG | Rt3 | CZ15 | 2017 | 0.001 | rec
2020 | SDG | Rt3 | CZ15 | 2020 | 0.001 | rec
2020 | SDG | Rt3 | CZ15 | New | 0.001 | new
2020 | SDG | RtL | CZ06 | 1975 | 0.328 | old
2020 | SDG | RtL | CZ06 | 1985 | 0.412 | old
2020 | SDG | RtL | CZ06 | 1996 | 0.209 | old
2020 | SDG | RtL | CZ06 | 2003 | 0.1 | ex
2020 | SDG | RtL | CZ06 | 2007 | 0.058 | ex
2020 | SDG | RtL | CZ06 | 2011 | 0.058 | ex
2020 | SDG | RtL | CZ06 | 2015 | 0.043 | ex
2020 | SDG | RtL | CZ06 | 2017 | 0.043 | rec
2020 | SDG | RtL | CZ06 | 2020 | 0.014 | rec
2020 | SDG | RtL | CZ06 | New | 0.014 | new
2020 | SDG | RtL | CZ07 | 1975 | 6.4 | old
2020 | SDG | RtL | CZ07 | 1985 | 8.036 | old
2020 | SDG | RtL | CZ07 | 1996 | 4.075 | old
2020 | SDG | RtL | CZ07 | 2003 | 1.957 | ex
2020 | SDG | RtL | CZ07 | 2007 | 1.122 | ex
2020 | SDG | RtL | CZ07 | 2011 | 1.122 | ex
2020 | SDG | RtL | CZ07 | 2015 | 0.841 | ex
2020 | SDG | RtL | CZ07 | 2017 | 0.841 | rec
2020 | SDG | RtL | CZ07 | 2020 | 0.281 | rec
2020 | SDG | RtL | CZ07 | New | 0.281 | new
2020 | SDG | RtL | CZ08 | 1975 | 0.589 | old
2020 | SDG | RtL | CZ08 | 1985 | 0.739 | old
2020 | SDG | RtL | CZ08 | 1996 | 0.375 | old
2020 | SDG | RtL | CZ08 | 2003 | 0.18 | ex
2020 | SDG | RtL | CZ08 | 2007 | 0.103 | ex
2020 | SDG | RtL | CZ08 | 2011 | 0.103 | ex
2020 | SDG | RtL | CZ08 | 2015 | 0.077 | ex
2020 | SDG | RtL | CZ08 | 2017 | 0.077 | rec
2020 | SDG | RtL | CZ08 | 2020 | 0.026 | rec
2020 | SDG | RtL | CZ08 | New | 0.026 | new
2020 | SDG | RtL | CZ10 | 1975 | 2.383 | old
2020 | SDG | RtL | CZ10 | 1985 | 2.993 | old
2020 | SDG | RtL | CZ10 | 1996 | 1.518 | old
2020 | SDG | RtL | CZ10 | 2003 | 0.729 | ex
2020 | SDG | RtL | CZ10 | 2007 | 0.418 | ex
2020 | SDG | RtL | CZ10 | 2011 | 0.418 | ex
2020 | SDG | RtL | CZ10 | 2015 | 0.313 | ex
2020 | SDG | RtL | CZ10 | 2017 | 0.313 | rec
2020 | SDG | RtL | CZ10 | 2020 | 0.105 | rec
2020 | SDG | RtL | CZ10 | New | 0.105 | new
2020 | SDG | RtL | CZ14 | 1975 | 0.009 | old
2020 | SDG | RtL | CZ14 | 1985 | 0.011 | old
2020 | SDG | RtL | CZ14 | 1996 | 0.006 | old
2020 | SDG | RtL | CZ14 | 2003 | 0.003 | ex
2020 | SDG | RtL | CZ14 | 2007 | 0.002 | ex
2020 | SDG | RtL | CZ14 | 2011 | 0.002 | ex
2020 | SDG | RtL | CZ14 | 2015 | 0.001 | ex
2020 | SDG | RtL | CZ14 | 2017 | 0.001 | rec
2020 | SDG | RtL | CZ14 | 2020 | 0.001 | rec
2020 | SDG | RtL | CZ14 | New | 0.001 | new
2020 | SDG | RtL | CZ15 | 1975 | 0.003 | old
2020 | SDG | RtL | CZ15 | 1985 | 0.004 | old
2020 | SDG | RtL | CZ15 | 1996 | 0.002 | old
2020 | SDG | RtL | CZ15 | 2003 | 0.001 | ex
2020 | SDG | RtL | CZ15 | 2007 | 0.001 | ex
2020 | SDG | RtL | CZ15 | 2011 | 0.001 | ex
2020 | SDG | RtL | CZ15 | 2015 | 0.001 | ex
2020 | SDG | RtL | CZ15 | 2017 | 0.001 | rec
2020 | SDG | RtL | CZ15 | 2020 | 0.001 | rec
2020 | SDG | RtL | CZ15 | New | 0.001 | new
2020 | SDG | RtS | CZ06 | 1975 | 0.328 | old
2020 | SDG | RtS | CZ06 | 1985 | 0.412 | old
2020 | SDG | RtS | CZ06 | 1996 | 0.209 | old
2020 | SDG | RtS | CZ06 | 2003 | 0.1 | ex
2020 | SDG | RtS | CZ06 | 2007 | 0.058 | ex
2020 | SDG | RtS | CZ06 | 2011 | 0.058 | ex
2020 | SDG | RtS | CZ06 | 2015 | 0.043 | ex
2020 | SDG | RtS | CZ06 | 2017 | 0.043 | rec
2020 | SDG | RtS | CZ06 | 2020 | 0.014 | rec
2020 | SDG | RtS | CZ06 | New | 0.014 | new
2020 | SDG | RtS | CZ07 | 1975 | 6.4 | old
2020 | SDG | RtS | CZ07 | 1985 | 8.036 | old
2020 | SDG | RtS | CZ07 | 1996 | 4.075 | old
2020 | SDG | RtS | CZ07 | 2003 | 1.957 | ex
2020 | SDG | RtS | CZ07 | 2007 | 1.122 | ex
2020 | SDG | RtS | CZ07 | 2011 | 1.122 | ex
2020 | SDG | RtS | CZ07 | 2015 | 0.841 | ex
2020 | SDG | RtS | CZ07 | 2017 | 0.841 | rec
2020 | SDG | RtS | CZ07 | 2020 | 0.281 | rec
2020 | SDG | RtS | CZ07 | New | 0.281 | new
2020 | SDG | RtS | CZ08 | 1975 | 0.589 | old
2020 | SDG | RtS | CZ08 | 1985 | 0.739 | old
2020 | SDG | RtS | CZ08 | 1996 | 0.375 | old
2020 | SDG | RtS | CZ08 | 2003 | 0.18 | ex
2020 | SDG | RtS | CZ08 | 2007 | 0.103 | ex
2020 | SDG | RtS | CZ08 | 2011 | 0.103 | ex
2020 | SDG | RtS | CZ08 | 2015 | 0.077 | ex
2020 | SDG | RtS | CZ08 | 2017 | 0.077 | rec
2020 | SDG | RtS | CZ08 | 2020 | 0.026 | rec
2020 | SDG | RtS | CZ08 | New | 0.026 | new
2020 | SDG | RtS | CZ10 | 1975 | 2.383 | old
2020 | SDG | RtS | CZ10 | 1985 | 2.993 | old
2020 | SDG | RtS | CZ10 | 1996 | 1.518 | old
2020 | SDG | RtS | CZ10 | 2003 | 0.729 | ex
2020 | SDG | RtS | CZ10 | 2007 | 0.418 | ex
2020 | SDG | RtS | CZ10 | 2011 | 0.418 | ex
2020 | SDG | RtS | CZ10 | 2015 | 0.313 | ex
2020 | SDG | RtS | CZ10 | 2017 | 0.313 | rec
2020 | SDG | RtS | CZ10 | 2020 | 0.105 | rec
2020 | SDG | RtS | CZ10 | New | 0.105 | new
2020 | SDG | RtS | CZ14 | 1975 | 0.009 | old
2020 | SDG | RtS | CZ14 | 1985 | 0.011 | old
2020 | SDG | RtS | CZ14 | 1996 | 0.006 | old
2020 | SDG | RtS | CZ14 | 2003 | 0.003 | ex
2020 | SDG | RtS | CZ14 | 2007 | 0.002 | ex
2020 | SDG | RtS | CZ14 | 2011 | 0.002 | ex
2020 | SDG | RtS | CZ14 | 2015 | 0.001 | ex
2020 | SDG | RtS | CZ14 | 2017 | 0.001 | rec
2020 | SDG | RtS | CZ14 | 2020 | 0.001 | rec
2020 | SDG | RtS | CZ14 | New | 0.001 | new
2020 | SDG | RtS | CZ15 | 1975 | 0.003 | old
2020 | SDG | RtS | CZ15 | 1985 | 0.004 | old
2020 | SDG | RtS | CZ15 | 1996 | 0.002 | old
2020 | SDG | RtS | CZ15 | 2003 | 0.001 | ex
2020 | SDG | RtS | CZ15 | 2007 | 0.001 | ex
2020 | SDG | RtS | CZ15 | 2011 | 0.001 | ex
2020 | SDG | RtS | CZ15 | 2015 | 0.001 | ex
2020 | SDG | RtS | CZ15 | 2017 | 0.001 | rec
2020 | SDG | RtS | CZ15 | 2020 | 0.001 | rec
2020 | SDG | RtS | CZ15 | New | 0.001 | new
2020 | SDG | SCn | CZ06 | 1975 | 0.164 | old
2020 | SDG | SCn | CZ06 | 1985 | 0.382 | old
2020 | SDG | SCn | CZ06 | 1996 | 0.166 | old
2020 | SDG | SCn | CZ06 | 2003 | 0.091 | ex
2020 | SDG | SCn | CZ06 | 2007 | 0.04 | ex
2020 | SDG | SCn | CZ06 | 2011 | 0.04 | ex
2020 | SDG | SCn | CZ06 | 2015 | 0.03 | ex
2020 | SDG | SCn | CZ06 | 2017 | 0.03 | rec
2020 | SDG | SCn | CZ06 | 2020 | 0.01 | rec
2020 | SDG | SCn | CZ06 | New | 0.01 | new
2020 | SDG | SCn | CZ07 | 1975 | 4.264 | old
2020 | SDG | SCn | CZ07 | 1985 | 9.927 | old
2020 | SDG | SCn | CZ07 | 1996 | 4.314 | old
2020 | SDG | SCn | CZ07 | 2003 | 2.377 | ex
2020 | SDG | SCn | CZ07 | 2007 | 1.039 | ex
2020 | SDG | SCn | CZ07 | 2011 | 1.039 | ex
2020 | SDG | SCn | CZ07 | 2015 | 0.78 | ex
2020 | SDG | SCn | CZ07 | 2017 | 0.78 | rec
2020 | SDG | SCn | CZ07 | 2020 | 0.26 | rec
2020 | SDG | SCn | CZ07 | New | 0.26 | new
2020 | SDG | SCn | CZ08 | 1975 | 0.1 | old
2020 | SDG | SCn | CZ08 | 1985 | 0.232 | old
2020 | SDG | SCn | CZ08 | 1996 | 0.101 | old
2020 | SDG | SCn | CZ08 | 2003 | 0.056 | ex
2020 | SDG | SCn | CZ08 | 2007 | 0.024 | ex
2020 | SDG | SCn | CZ08 | 2011 | 0.024 | ex
2020 | SDG | SCn | CZ08 | 2015 | 0.018 | ex
2020 | SDG | SCn | CZ08 | 2017 | 0.018 | rec
2020 | SDG | SCn | CZ08 | 2020 | 0.006 | rec
2020 | SDG | SCn | CZ08 | New | 0.006 | new
2020 | SDG | SCn | CZ10 | 1975 | 1.947 | old
2020 | SDG | SCn | CZ10 | 1985 | 4.533 | old
2020 | SDG | SCn | CZ10 | 1996 | 1.97 | old
2020 | SDG | SCn | CZ10 | 2003 | 1.085 | ex
2020 | SDG | SCn | CZ10 | 2007 | 0.475 | ex
2020 | SDG | SCn | CZ10 | 2011 | 0.475 | ex
2020 | SDG | SCn | CZ10 | 2015 | 0.356 | ex
2020 | SDG | SCn | CZ10 | 2017 | 0.356 | rec
2020 | SDG | SCn | CZ10 | 2020 | 0.119 | rec
2020 | SDG | SCn | CZ10 | New | 0.119 | new
2020 | SDG | SCn | CZ14 | 1975 | 0.019 | old
2020 | SDG | SCn | CZ14 | 1985 | 0.044 | old
2020 | SDG | SCn | CZ14 | 1996 | 0.019 | old
2020 | SDG | SCn | CZ14 | 2003 | 0.011 | ex
2020 | SDG | SCn | CZ14 | 2007 | 0.005 | ex
2020 | SDG | SCn | CZ14 | 2011 | 0.005 | ex
2020 | SDG | SCn | CZ14 | 2015 | 0.004 | ex
2020 | SDG | SCn | CZ14 | 2017 | 0.004 | rec
2020 | SDG | SCn | CZ14 | 2020 | 0.001 | rec
2020 | SDG | SCn | CZ14 | New | 0.001 | new
2020 | SDG | SCn | CZ15 | 1975 | 0.009 | old
2020 | SDG | SCn | CZ15 | 1985 | 0.021 | old
2020 | SDG | SCn | CZ15 | 1996 | 0.009 | old
2020 | SDG | SCn | CZ15 | 2003 | 0.005 | ex
2020 | SDG | SCn | CZ15 | 2007 | 0.002 | ex
2020 | SDG | SCn | CZ15 | 2011 | 0.002 | ex
2020 | SDG | SCn | CZ15 | 2015 | 0.002 | ex
2020 | SDG | SCn | CZ15 | 2017 | 0.002 | rec
2020 | SDG | SCn | CZ15 | 2020 | 0.001 | rec
2020 | SDG | SCn | CZ15 | New | 0.001 | new
2020 | SDG | SUn | CZ06 | 1975 | 0.164 | old
2020 | SDG | SUn | CZ06 | 1985 | 0.382 | old
2020 | SDG | SUn | CZ06 | 1996 | 0.166 | old
2020 | SDG | SUn | CZ06 | 2003 | 0.091 | ex
2020 | SDG | SUn | CZ06 | 2007 | 0.04 | ex
2020 | SDG | SUn | CZ06 | 2011 | 0.04 | ex
2020 | SDG | SUn | CZ06 | 2015 | 0.03 | ex
2020 | SDG | SUn | CZ06 | 2017 | 0.03 | rec
2020 | SDG | SUn | CZ06 | 2020 | 0.01 | rec
2020 | SDG | SUn | CZ06 | New | 0.01 | new
2020 | SDG | SUn | CZ07 | 1975 | 4.264 | old
2020 | SDG | SUn | CZ07 | 1985 | 9.927 | old
2020 | SDG | SUn | CZ07 | 1996 | 4.314 | old
2020 | SDG | SUn | CZ07 | 2003 | 2.377 | ex
2020 | SDG | SUn | CZ07 | 2007 | 1.039 | ex
2020 | SDG | SUn | CZ07 | 2011 | 1.039 | ex
2020 | SDG | SUn | CZ07 | 2015 | 0.78 | ex
2020 | SDG | SUn | CZ07 | 2017 | 0.78 | rec
2020 | SDG | SUn | CZ07 | 2020 | 0.26 | rec
2020 | SDG | SUn | CZ07 | New | 0.26 | new
2020 | SDG | SUn | CZ08 | 1975 | 0.1 | old
2020 | SDG | SUn | CZ08 | 1985 | 0.232 | old
2020 | SDG | SUn | CZ08 | 1996 | 0.101 | old
2020 | SDG | SUn | CZ08 | 2003 | 0.056 | ex
2020 | SDG | SUn | CZ08 | 2007 | 0.024 | ex
2020 | SDG | SUn | CZ08 | 2011 | 0.024 | ex
2020 | SDG | SUn | CZ08 | 2015 | 0.018 | ex
2020 | SDG | SUn | CZ08 | 2017 | 0.018 | rec
2020 | SDG | SUn | CZ08 | 2020 | 0.006 | rec
2020 | SDG | SUn | CZ08 | New | 0.006 | new
2020 | SDG | SUn | CZ10 | 1975 | 1.947 | old
2020 | SDG | SUn | CZ10 | 1985 | 4.533 | old
2020 | SDG | SUn | CZ10 | 1996 | 1.97 | old
2020 | SDG | SUn | CZ10 | 2003 | 1.085 | ex
2020 | SDG | SUn | CZ10 | 2007 | 0.475 | ex
2020 | SDG | SUn | CZ10 | 2011 | 0.475 | ex
2020 | SDG | SUn | CZ10 | 2015 | 0.356 | ex
2020 | SDG | SUn | CZ10 | 2017 | 0.356 | rec
2020 | SDG | SUn | CZ10 | 2020 | 0.119 | rec
2020 | SDG | SUn | CZ10 | New | 0.119 | new
2020 | SDG | SUn | CZ14 | 1975 | 0.019 | old
2020 | SDG | SUn | CZ14 | 1985 | 0.044 | old
2020 | SDG | SUn | CZ14 | 1996 | 0.019 | old
2020 | SDG | SUn | CZ14 | 2003 | 0.011 | ex
2020 | SDG | SUn | CZ14 | 2007 | 0.005 | ex
2020 | SDG | SUn | CZ14 | 2011 | 0.005 | ex
2020 | SDG | SUn | CZ14 | 2015 | 0.004 | ex
2020 | SDG | SUn | CZ14 | 2017 | 0.004 | rec
2020 | SDG | SUn | CZ14 | 2020 | 0.001 | rec
2020 | SDG | SUn | CZ14 | New | 0.001 | new
2020 | SDG | SUn | CZ15 | 1975 | 0.009 | old
2020 | SDG | SUn | CZ15 | 1985 | 0.021 | old
2020 | SDG | SUn | CZ15 | 1996 | 0.009 | old
2020 | SDG | SUn | CZ15 | 2003 | 0.005 | ex
2020 | SDG | SUn | CZ15 | 2007 | 0.002 | ex
2020 | SDG | SUn | CZ15 | 2011 | 0.002 | ex
2020 | SDG | SUn | CZ15 | 2015 | 0.002 | ex
2020 | SDG | SUn | CZ15 | 2017 | 0.002 | rec
2020 | SDG | SUn | CZ15 | 2020 | 0.001 | rec
2020 | SDG | SUn | CZ15 | New | 0.001 | new
2020 | SDG | WRf | CZ06 | 1975 | 0.002 | old
2020 | SDG | WRf | CZ06 | 1985 | 0.001 | old
2020 | SDG | WRf | CZ06 | 1996 | 0.003 | old
2020 | SDG | WRf | CZ06 | 2003 | 0.001 | ex
2020 | SDG | WRf | CZ06 | 2007 | 0.001 | ex
2020 | SDG | WRf | CZ06 | 2011 | 0.001 | ex
2020 | SDG | WRf | CZ06 | 2015 | 0.001 | ex
2020 | SDG | WRf | CZ06 | 2017 | 0.001 | rec
2020 | SDG | WRf | CZ06 | 2020 | 0.001 | rec
2020 | SDG | WRf | CZ06 | New | 0.001 | new
2020 | SDG | WRf | CZ07 | 1975 | 0.126 | old
2020 | SDG | WRf | CZ07 | 1985 | 0.06 | old
2020 | SDG | WRf | CZ07 | 1996 | 0.265 | old
2020 | SDG | WRf | CZ07 | 2003 | 0.028 | ex
2020 | SDG | WRf | CZ07 | 2007 | 0.03 | ex
2020 | SDG | WRf | CZ07 | 2011 | 0.03 | ex
2020 | SDG | WRf | CZ07 | 2015 | 0.022 | ex
2020 | SDG | WRf | CZ07 | 2017 | 0.022 | rec
2020 | SDG | WRf | CZ07 | 2020 | 0.008 | rec
2020 | SDG | WRf | CZ07 | New | 0.008 | new
2020 | SDG | WRf | CZ10 | 1975 | 0.036 | old
2020 | SDG | WRf | CZ10 | 1985 | 0.017 | old
2020 | SDG | WRf | CZ10 | 1996 | 0.076 | old
2020 | SDG | WRf | CZ10 | 2003 | 0.008 | ex
2020 | SDG | WRf | CZ10 | 2007 | 0.009 | ex
2020 | SDG | WRf | CZ10 | 2011 | 0.009 | ex
2020 | SDG | WRf | CZ10 | 2015 | 0.006 | ex
2020 | SDG | WRf | CZ10 | 2017 | 0.006 | rec
2020 | SDG | WRf | CZ10 | 2020 | 0.002 | rec
2020 | SDG | WRf | CZ10 | New | 0.002 | new

## DEER2020 wts_Consolidated
DEER2020 Commercial Weights (in millions of square feet)
minimum set to 1000 sqft
ver | pa | pa revised | bldgtype | bldgloc | wts_consolidated | era
2020 | PGE | PGE | Asm | CZ01 | 0.882 | old
2020 | PGE | PGE | Asm | CZ01 | 0.167 | ex
2020 | PGE | PGE | Asm | CZ01 | 0.035 | rec
2020 | PGE | Any | Asm | CZ01 | 0.009 | new
2020 | PGE | PGE | Asm | CZ02 | 8.734 | old
2020 | PGE | PGE | Asm | CZ02 | 1.337 | ex
2020 | PGE | PGE | Asm | CZ02 | 0.269 | rec
2020 | PGE | Any | Asm | CZ02 | 0.067 | new
2020 | PGE | PGE | Asm | CZ03 | 44.501 | old
2020 | PGE | PGE | Asm | CZ03 | 5.908 | ex
2020 | PGE | PGE | Asm | CZ03 | 1.045 | rec
2020 | PGE | Any | Asm | CZ03 | 0.261 | new
2020 | PGE | PGE | Asm | CZ04 | 23.473 | old
2020 | PGE | PGE | Asm | CZ04 | 3.753 | ex
2020 | PGE | PGE | Asm | CZ04 | 0.796 | rec
2020 | PGE | Any | Asm | CZ04 | 0.199 | new
2020 | PGE | PGE | Asm | CZ05 | 2.802 | old
2020 | PGE | PGE | Asm | CZ05 | 0.448 | ex
2020 | PGE | PGE | Asm | CZ05 | 0.095 | rec
2020 | PGE | Any | Asm | CZ05 | 0.032 | new
2020 | PGE | PGE | Asm | CZ11 | 6.029 | old
2020 | PGE | PGE | Asm | CZ11 | 1.473 | ex
2020 | PGE | PGE | Asm | CZ11 | 0.324 | rec
2020 | PGE | Any | Asm | CZ11 | 0.081 | new
2020 | PGE | PGE | Asm | CZ12 | 24.051 | old
2020 | PGE | PGE | Asm | CZ12 | 4.929 | ex
2020 | PGE | PGE | Asm | CZ12 | 1.04 | rec
2020 | PGE | Any | Asm | CZ12 | 0.26 | new
2020 | PGE | PGE | Asm | CZ13 | 15.196 | old
2020 | PGE | PGE | Asm | CZ13 | 3.331 | ex
2020 | PGE | PGE | Asm | CZ13 | 0.767 | rec
2020 | PGE | Any | Asm | CZ13 | 0.304 | new
2020 | PGE | PGE | Asm | CZ16 | 1.351 | old
2020 | PGE | PGE | Asm | CZ16 | 0.286 | ex
2020 | PGE | PGE | Asm | CZ16 | 0.061 | rec
2020 | PGE | Any | Asm | CZ16 | 0.169 | new
2020 | PGE | PGE | ECC | CZ01 | 1.653 | old
2020 | PGE | PGE | ECC | CZ01 | 0.131 | ex
2020 | PGE | PGE | ECC | CZ01 | 0.032 | rec
2020 | PGE | Any | ECC | CZ01 | 0.008 | new
2020 | PGE | PGE | ECC | CZ02 | 3.935 | old
2020 | PGE | PGE | ECC | CZ02 | 0.802 | ex
2020 | PGE | PGE | ECC | CZ02 | 0.151 | rec
2020 | PGE | Any | ECC | CZ02 | 0.038 | new
2020 | PGE | PGE | ECC | CZ03 | 20.346 | old
2020 | PGE | PGE | ECC | CZ03 | 3.221 | ex
2020 | PGE | PGE | ECC | CZ03 | 0.573 | rec
2020 | PGE | Any | ECC | CZ03 | 0.143 | new
2020 | PGE | PGE | ECC | CZ04 | 4.805 | old
2020 | PGE | PGE | ECC | CZ04 | 1.088 | ex
2020 | PGE | PGE | ECC | CZ04 | 0.203 | rec
2020 | PGE | Any | ECC | CZ04 | 0.051 | new
2020 | PGE | PGE | ECC | CZ05 | 3.633 | old
2020 | PGE | PGE | ECC | CZ05 | 0.821 | ex
2020 | PGE | PGE | ECC | CZ05 | 0.153 | rec
2020 | PGE | Any | ECC | CZ05 | 0.04 | new
2020 | PGE | PGE | ECC | CZ11 | 4.639 | old
2020 | PGE | PGE | ECC | CZ11 | 1.197 | ex
2020 | PGE | PGE | ECC | CZ11 | 0.233 | rec
2020 | PGE | Any | ECC | CZ11 | 0.058 | new
2020 | PGE | PGE | ECC | CZ12 | 6.613 | old
2020 | PGE | PGE | ECC | CZ12 | 1.674 | ex
2020 | PGE | PGE | ECC | CZ12 | 0.319 | rec
2020 | PGE | Any | ECC | CZ12 | 0.08 | new
2020 | PGE | PGE | ECC | CZ13 | 7.046 | old
2020 | PGE | PGE | ECC | CZ13 | 1.809 | ex
2020 | PGE | PGE | ECC | CZ13 | 0.352 | rec
2020 | PGE | Any | ECC | CZ13 | 0.144 | new
2020 | PGE | PGE | ECC | CZ16 | 0.155 | old
2020 | PGE | PGE | ECC | CZ16 | 0.025 | ex
2020 | PGE | PGE | ECC | CZ16 | 0.005 | rec
2020 | PGE | Any | ECC | CZ16 | 0.139 | new
2020 | PGE | PGE | EPr | CZ01 | 0.602 | old
2020 | PGE | PGE | EPr | CZ01 | 0.096 | ex
2020 | PGE | PGE | EPr | CZ01 | 0.017 | rec
2020 | PGE | Any | EPr | CZ01 | 0.004 | new
2020 | PGE | PGE | EPr | CZ02 | 4.515 | old
2020 | PGE | PGE | EPr | CZ02 | 0.622 | ex
2020 | PGE | PGE | EPr | CZ02 | 0.105 | rec
2020 | PGE | Any | EPr | CZ02 | 0.026 | new
2020 | PGE | PGE | EPr | CZ03 | 17.783 | old
2020 | PGE | PGE | EPr | CZ03 | 1.819 | ex
2020 | PGE | PGE | EPr | CZ03 | 0.313 | rec
2020 | PGE | Any | EPr | CZ03 | 0.078 | new
2020 | PGE | PGE | EPr | CZ04 | 8.74 | old
2020 | PGE | PGE | EPr | CZ04 | 1.301 | ex
2020 | PGE | PGE | EPr | CZ04 | 0.212 | rec
2020 | PGE | Any | EPr | CZ04 | 0.053 | new
2020 | PGE | PGE | EPr | CZ05 | 1.209 | old
2020 | PGE | PGE | EPr | CZ05 | 0.18 | ex
2020 | PGE | PGE | EPr | CZ05 | 0.029 | rec
2020 | PGE | Any | EPr | CZ05 | 0.009 | new
2020 | PGE | PGE | EPr | CZ11 | 3.527 | old
2020 | PGE | PGE | EPr | CZ11 | 0.941 | ex
2020 | PGE | PGE | EPr | CZ11 | 0.175 | rec
2020 | PGE | Any | EPr | CZ11 | 0.044 | new
2020 | PGE | PGE | EPr | CZ12 | 12.518 | old
2020 | PGE | PGE | EPr | CZ12 | 3.103 | ex
2020 | PGE | PGE | EPr | CZ12 | 0.535 | rec
2020 | PGE | Any | EPr | CZ12 | 0.134 | new
2020 | PGE | PGE | EPr | CZ13 | 9.743 | old
2020 | PGE | PGE | EPr | CZ13 | 2.178 | ex
2020 | PGE | PGE | EPr | CZ13 | 0.421 | rec
2020 | PGE | Any | EPr | CZ13 | 0.167 | new
2020 | PGE | PGE | EPr | CZ16 | 0.548 | old
2020 | PGE | PGE | EPr | CZ16 | 0.131 | ex
2020 | PGE | PGE | EPr | CZ16 | 0.024 | rec
2020 | PGE | Any | EPr | CZ16 | 0.04 | new
2020 | PGE | PGE | ERC | CZ01 | 0.602 | old
2020 | PGE | PGE | ERC | CZ01 | 0.096 | ex
2020 | PGE | PGE | ERC | CZ01 | 0.017 | rec
2020 | PGE | Any | ERC | CZ01 | 0.004 | new
2020 | PGE | PGE | ERC | CZ02 | 4.515 | old
2020 | PGE | PGE | ERC | CZ02 | 0.622 | ex
2020 | PGE | PGE | ERC | CZ02 | 0.105 | rec
2020 | PGE | Any | ERC | CZ02 | 0.026 | new
2020 | PGE | PGE | ERC | CZ03 | 17.783 | old
2020 | PGE | PGE | ERC | CZ03 | 1.819 | ex
2020 | PGE | PGE | ERC | CZ03 | 0.313 | rec
2020 | PGE | Any | ERC | CZ03 | 0.078 | new
2020 | PGE | PGE | ERC | CZ04 | 8.74 | old
2020 | PGE | PGE | ERC | CZ04 | 1.301 | ex
2020 | PGE | PGE | ERC | CZ04 | 0.212 | rec
2020 | PGE | Any | ERC | CZ04 | 0.053 | new
2020 | PGE | PGE | ERC | CZ05 | 1.209 | old
2020 | PGE | PGE | ERC | CZ05 | 0.18 | ex
2020 | PGE | PGE | ERC | CZ05 | 0.029 | rec
2020 | PGE | Any | ERC | CZ05 | 0.009 | new
2020 | PGE | PGE | ERC | CZ11 | 3.527 | old
2020 | PGE | PGE | ERC | CZ11 | 0.941 | ex
2020 | PGE | PGE | ERC | CZ11 | 0.175 | rec
2020 | PGE | Any | ERC | CZ11 | 0.044 | new
2020 | PGE | PGE | ERC | CZ12 | 12.518 | old
2020 | PGE | PGE | ERC | CZ12 | 3.103 | ex
2020 | PGE | PGE | ERC | CZ12 | 0.535 | rec
2020 | PGE | Any | ERC | CZ12 | 0.134 | new
2020 | PGE | PGE | ERC | CZ13 | 9.743 | old
2020 | PGE | PGE | ERC | CZ13 | 2.178 | ex
2020 | PGE | PGE | ERC | CZ13 | 0.421 | rec
2020 | PGE | Any | ERC | CZ13 | 0.167 | new
2020 | PGE | PGE | ERC | CZ16 | 0.548 | old
2020 | PGE | PGE | ERC | CZ16 | 0.131 | ex
2020 | PGE | PGE | ERC | CZ16 | 0.024 | rec
2020 | PGE | Any | ERC | CZ16 | 0.04 | new
2020 | PGE | PGE | ESe | CZ01 | 0.602 | old
2020 | PGE | PGE | ESe | CZ01 | 0.096 | ex
2020 | PGE | PGE | ESe | CZ01 | 0.017 | rec
2020 | PGE | Any | ESe | CZ01 | 0.004 | new
2020 | PGE | PGE | ESe | CZ02 | 4.515 | old
2020 | PGE | PGE | ESe | CZ02 | 0.622 | ex
2020 | PGE | PGE | ESe | CZ02 | 0.105 | rec
2020 | PGE | Any | ESe | CZ02 | 0.026 | new
2020 | PGE | PGE | ESe | CZ03 | 17.783 | old
2020 | PGE | PGE | ESe | CZ03 | 1.819 | ex
2020 | PGE | PGE | ESe | CZ03 | 0.313 | rec
2020 | PGE | Any | ESe | CZ03 | 0.078 | new
2020 | PGE | PGE | ESe | CZ04 | 8.74 | old
2020 | PGE | PGE | ESe | CZ04 | 1.301 | ex
2020 | PGE | PGE | ESe | CZ04 | 0.212 | rec
2020 | PGE | Any | ESe | CZ04 | 0.053 | new
2020 | PGE | PGE | ESe | CZ05 | 1.209 | old
2020 | PGE | PGE | ESe | CZ05 | 0.18 | ex
2020 | PGE | PGE | ESe | CZ05 | 0.029 | rec
2020 | PGE | Any | ESe | CZ05 | 0.009 | new
2020 | PGE | PGE | ESe | CZ11 | 3.527 | old
2020 | PGE | PGE | ESe | CZ11 | 0.941 | ex
2020 | PGE | PGE | ESe | CZ11 | 0.175 | rec
2020 | PGE | Any | ESe | CZ11 | 0.044 | new
2020 | PGE | PGE | ESe | CZ12 | 12.518 | old
2020 | PGE | PGE | ESe | CZ12 | 3.103 | ex
2020 | PGE | PGE | ESe | CZ12 | 0.535 | rec
2020 | PGE | Any | ESe | CZ12 | 0.134 | new
2020 | PGE | PGE | ESe | CZ13 | 9.743 | old
2020 | PGE | PGE | ESe | CZ13 | 2.178 | ex
2020 | PGE | PGE | ESe | CZ13 | 0.421 | rec
2020 | PGE | Any | ESe | CZ13 | 0.167 | new
2020 | PGE | PGE | ESe | CZ16 | 0.548 | old
2020 | PGE | PGE | ESe | CZ16 | 0.131 | ex
2020 | PGE | PGE | ESe | CZ16 | 0.024 | rec
2020 | PGE | Any | ESe | CZ16 | 0.04 | new
2020 | PGE | PGE | EUD | CZ01 | 1.653 | old
2020 | PGE | PGE | EUD | CZ01 | 0.131 | ex
2020 | PGE | PGE | EUD | CZ01 | 0.032 | rec
2020 | PGE | Any | EUD | CZ01 | 0.008 | new
2020 | PGE | PGE | EUD | CZ02 | 3.935 | old
2020 | PGE | PGE | EUD | CZ02 | 0.802 | ex
2020 | PGE | PGE | EUD | CZ02 | 0.151 | rec
2020 | PGE | Any | EUD | CZ02 | 0.038 | new
2020 | PGE | PGE | EUD | CZ03 | 20.346 | old
2020 | PGE | PGE | EUD | CZ03 | 3.221 | ex
2020 | PGE | PGE | EUD | CZ03 | 0.573 | rec
2020 | PGE | Any | EUD | CZ03 | 0.143 | new
2020 | PGE | PGE | EUD | CZ04 | 4.805 | old
2020 | PGE | PGE | EUD | CZ04 | 1.088 | ex
2020 | PGE | PGE | EUD | CZ04 | 0.203 | rec
2020 | PGE | Any | EUD | CZ04 | 0.051 | new
2020 | PGE | PGE | EUD | CZ05 | 3.633 | old
2020 | PGE | PGE | EUD | CZ05 | 0.821 | ex
2020 | PGE | PGE | EUD | CZ05 | 0.153 | rec
2020 | PGE | Any | EUD | CZ05 | 0.04 | new
2020 | PGE | PGE | EUD | CZ11 | 4.639 | old
2020 | PGE | PGE | EUD | CZ11 | 1.197 | ex
2020 | PGE | PGE | EUD | CZ11 | 0.233 | rec
2020 | PGE | Any | EUD | CZ11 | 0.058 | new
2020 | PGE | PGE | EUD | CZ12 | 6.613 | old
2020 | PGE | PGE | EUD | CZ12 | 1.674 | ex
2020 | PGE | PGE | EUD | CZ12 | 0.319 | rec
2020 | PGE | Any | EUD | CZ12 | 0.08 | new
2020 | PGE | PGE | EUD | CZ13 | 7.046 | old
2020 | PGE | PGE | EUD | CZ13 | 1.809 | ex
2020 | PGE | PGE | EUD | CZ13 | 0.352 | rec
2020 | PGE | Any | EUD | CZ13 | 0.144 | new
2020 | PGE | PGE | EUD | CZ16 | 0.155 | old
2020 | PGE | PGE | EUD | CZ16 | 0.025 | ex
2020 | PGE | PGE | EUD | CZ16 | 0.005 | rec
2020 | PGE | Any | EUD | CZ16 | 0.139 | new
2020 | PGE | PGE | EUn | CZ01 | 1.653 | old
2020 | PGE | PGE | EUn | CZ01 | 0.131 | ex
2020 | PGE | PGE | EUn | CZ01 | 0.032 | rec
2020 | PGE | Any | EUn | CZ01 | 0.008 | new
2020 | PGE | PGE | EUn | CZ02 | 3.935 | old
2020 | PGE | PGE | EUn | CZ02 | 0.802 | ex
2020 | PGE | PGE | EUn | CZ02 | 0.151 | rec
2020 | PGE | Any | EUn | CZ02 | 0.038 | new
2020 | PGE | PGE | EUn | CZ03 | 20.346 | old
2020 | PGE | PGE | EUn | CZ03 | 3.221 | ex
2020 | PGE | PGE | EUn | CZ03 | 0.573 | rec
2020 | PGE | Any | EUn | CZ03 | 0.143 | new
2020 | PGE | PGE | EUn | CZ04 | 4.805 | old
2020 | PGE | PGE | EUn | CZ04 | 1.088 | ex
2020 | PGE | PGE | EUn | CZ04 | 0.203 | rec
2020 | PGE | Any | EUn | CZ04 | 0.051 | new
2020 | PGE | PGE | EUn | CZ05 | 3.633 | old
2020 | PGE | PGE | EUn | CZ05 | 0.821 | ex
2020 | PGE | PGE | EUn | CZ05 | 0.153 | rec
2020 | PGE | Any | EUn | CZ05 | 0.04 | new
2020 | PGE | PGE | EUn | CZ11 | 4.639 | old
2020 | PGE | PGE | EUn | CZ11 | 1.197 | ex
2020 | PGE | PGE | EUn | CZ11 | 0.233 | rec
2020 | PGE | Any | EUn | CZ11 | 0.058 | new
2020 | PGE | PGE | EUn | CZ12 | 6.613 | old
2020 | PGE | PGE | EUn | CZ12 | 1.674 | ex
2020 | PGE | PGE | EUn | CZ12 | 0.319 | rec
2020 | PGE | Any | EUn | CZ12 | 0.08 | new
2020 | PGE | PGE | EUn | CZ13 | 7.046 | old
2020 | PGE | PGE | EUn | CZ13 | 1.809 | ex
2020 | PGE | PGE | EUn | CZ13 | 0.352 | rec
2020 | PGE | Any | EUn | CZ13 | 0.144 | new
2020 | PGE | PGE | EUn | CZ16 | 0.155 | old
2020 | PGE | PGE | EUn | CZ16 | 0.025 | ex
2020 | PGE | PGE | EUn | CZ16 | 0.005 | rec
2020 | PGE | Any | EUn | CZ16 | 0.139 | new
2020 | PGE | PGE | Gro | CZ01 | 0.996 | old
2020 | PGE | PGE | Gro | CZ01 | 0.154 | ex
2020 | PGE | PGE | Gro | CZ01 | 0.035 | rec
2020 | PGE | Any | Gro | CZ01 | 0.009 | new
2020 | PGE | PGE | Gro | CZ02 | 7.153 | old
2020 | PGE | PGE | Gro | CZ02 | 1.228 | ex
2020 | PGE | PGE | Gro | CZ02 | 0.272 | rec
2020 | PGE | Any | Gro | CZ02 | 0.068 | new
2020 | PGE | PGE | Gro | CZ03 | 25.454 | old
2020 | PGE | PGE | Gro | CZ03 | 3.773 | ex
2020 | PGE | PGE | Gro | CZ03 | 0.873 | rec
2020 | PGE | Any | Gro | CZ03 | 0.218 | new
2020 | PGE | PGE | Gro | CZ04 | 11.06 | old
2020 | PGE | PGE | Gro | CZ04 | 2.005 | ex
2020 | PGE | PGE | Gro | CZ04 | 0.439 | rec
2020 | PGE | Any | Gro | CZ04 | 0.11 | new
2020 | PGE | PGE | Gro | CZ05 | 2.505 | old
2020 | PGE | PGE | Gro | CZ05 | 0.455 | ex
2020 | PGE | PGE | Gro | CZ05 | 0.1 | rec
2020 | PGE | Any | Gro | CZ05 | 0.035 | new
2020 | PGE | PGE | Gro | CZ11 | 6.117 | old
2020 | PGE | PGE | Gro | CZ11 | 1.719 | ex
2020 | PGE | PGE | Gro | CZ11 | 0.381 | rec
2020 | PGE | Any | Gro | CZ11 | 0.095 | new
2020 | PGE | PGE | Gro | CZ12 | 19.867 | old
2020 | PGE | PGE | Gro | CZ12 | 5.344 | ex
2020 | PGE | PGE | Gro | CZ12 | 1.084 | rec
2020 | PGE | Any | Gro | CZ12 | 0.271 | new
2020 | PGE | PGE | Gro | CZ13 | 14.037 | old
2020 | PGE | PGE | Gro | CZ13 | 3.699 | ex
2020 | PGE | PGE | Gro | CZ13 | 0.876 | rec
2020 | PGE | Any | Gro | CZ13 | 0.345 | new
2020 | PGE | PGE | Gro | CZ16 | 1.054 | old
2020 | PGE | PGE | Gro | CZ16 | 0.263 | ex
2020 | PGE | PGE | Gro | CZ16 | 0.057 | rec
2020 | PGE | Any | Gro | CZ16 | 0.102 | new
2020 | PGE | PGE | HGR | CZ01 | 0.705 | old
2020 | PGE | PGE | HGR | CZ01 | 0.224 | ex
2020 | PGE | PGE | HGR | CZ01 | 0.039 | rec
2020 | PGE | Any | HGR | CZ01 | 0.01 | new
2020 | PGE | PGE | HGR | CZ02 | 3.489 | old
2020 | PGE | PGE | HGR | CZ02 | 0.824 | ex
2020 | PGE | PGE | HGR | CZ02 | 0.168 | rec
2020 | PGE | Any | HGR | CZ02 | 0.042 | new
2020 | PGE | PGE | HGR | CZ03 | 23.105 | old
2020 | PGE | PGE | HGR | CZ03 | 3.374 | ex
2020 | PGE | PGE | HGR | CZ03 | 0.501 | rec
2020 | PGE | Any | HGR | CZ03 | 0.125 | new
2020 | PGE | PGE | HGR | CZ04 | 7.366 | old
2020 | PGE | PGE | HGR | CZ04 | 1.722 | ex
2020 | PGE | PGE | HGR | CZ04 | 0.372 | rec
2020 | PGE | Any | HGR | CZ04 | 0.093 | new
2020 | PGE | PGE | HGR | CZ05 | 3.074 | old
2020 | PGE | PGE | HGR | CZ05 | 0.721 | ex
2020 | PGE | PGE | HGR | CZ05 | 0.156 | rec
2020 | PGE | Any | HGR | CZ05 | 0.041 | new
2020 | PGE | PGE | HGR | CZ11 | 1.924 | old
2020 | PGE | PGE | HGR | CZ11 | 0.508 | ex
2020 | PGE | PGE | HGR | CZ11 | 0.109 | rec
2020 | PGE | Any | HGR | CZ11 | 0.027 | new
2020 | PGE | PGE | HGR | CZ12 | 6.437 | old
2020 | PGE | PGE | HGR | CZ12 | 1.914 | ex
2020 | PGE | PGE | HGR | CZ12 | 0.421 | rec
2020 | PGE | Any | HGR | CZ12 | 0.105 | new
2020 | PGE | PGE | HGR | CZ13 | 4.253 | old
2020 | PGE | PGE | HGR | CZ13 | 1.052 | ex
2020 | PGE | PGE | HGR | CZ13 | 0.231 | rec
2020 | PGE | Any | HGR | CZ13 | 0.074 | new
2020 | PGE | PGE | HGR | CZ16 | 0.78 | old
2020 | PGE | PGE | HGR | CZ16 | 0.236 | ex
2020 | PGE | PGE | HGR | CZ16 | 0.044 | rec
2020 | PGE | Any | HGR | CZ16 | 0.069 | new
2020 | PGE | PGE | Hsp | CZ01 | 0.614 | old
2020 | PGE | PGE | Hsp | CZ01 | 0.141 | ex
2020 | PGE | PGE | Hsp | CZ01 | 0.023 | rec
2020 | PGE | Any | Hsp | CZ01 | 0.006 | new
2020 | PGE | PGE | Hsp | CZ02 | 5.289 | old
2020 | PGE | PGE | Hsp | CZ02 | 1.019 | ex
2020 | PGE | PGE | Hsp | CZ02 | 0.213 | rec
2020 | PGE | Any | Hsp | CZ02 | 0.053 | new
2020 | PGE | PGE | Hsp | CZ03 | 16.544 | old
2020 | PGE | PGE | Hsp | CZ03 | 2.179 | ex
2020 | PGE | PGE | Hsp | CZ03 | 0.583 | rec
2020 | PGE | Any | Hsp | CZ03 | 0.146 | new
2020 | PGE | PGE | Hsp | CZ04 | 7.099 | old
2020 | PGE | PGE | Hsp | CZ04 | 1.448 | ex
2020 | PGE | PGE | Hsp | CZ04 | 0.298 | rec
2020 | PGE | Any | Hsp | CZ04 | 0.075 | new
2020 | PGE | PGE | Hsp | CZ05 | 1.081 | old
2020 | PGE | PGE | Hsp | CZ05 | 0.22 | ex
2020 | PGE | PGE | Hsp | CZ05 | 0.045 | rec
2020 | PGE | Any | Hsp | CZ05 | 0.023 | new
2020 | PGE | PGE | Hsp | CZ11 | 3.449 | old
2020 | PGE | PGE | Hsp | CZ11 | 0.918 | ex
2020 | PGE | PGE | Hsp | CZ11 | 0.18 | rec
2020 | PGE | Any | Hsp | CZ11 | 0.045 | new
2020 | PGE | PGE | Hsp | CZ12 | 11.659 | old
2020 | PGE | PGE | Hsp | CZ12 | 2.681 | ex
2020 | PGE | PGE | Hsp | CZ12 | 0.593 | rec
2020 | PGE | Any | Hsp | CZ12 | 0.148 | new
2020 | PGE | PGE | Hsp | CZ13 | 8.773 | old
2020 | PGE | PGE | Hsp | CZ13 | 2.404 | ex
2020 | PGE | PGE | Hsp | CZ13 | 0.467 | rec
2020 | PGE | Any | Hsp | CZ13 | 0.153 | new
2020 | PGE | PGE | Hsp | CZ16 | 0.2 | old
2020 | PGE | PGE | Hsp | CZ16 | 0.051 | ex
2020 | PGE | PGE | Hsp | CZ16 | 0.009 | rec
2020 | PGE | Any | Hsp | CZ16 | 0.03 | new
2020 | PGE | PGE | Htl | CZ01 | 0.705 | old
2020 | PGE | PGE | Htl | CZ01 | 0.224 | ex
2020 | PGE | PGE | Htl | CZ01 | 0.039 | rec
2020 | PGE | Any | Htl | CZ01 | 0.01 | new
2020 | PGE | PGE | Htl | CZ02 | 3.489 | old
2020 | PGE | PGE | Htl | CZ02 | 0.824 | ex
2020 | PGE | PGE | Htl | CZ02 | 0.168 | rec
2020 | PGE | Any | Htl | CZ02 | 0.042 | new
2020 | PGE | PGE | Htl | CZ03 | 23.105 | old
2020 | PGE | PGE | Htl | CZ03 | 3.374 | ex
2020 | PGE | PGE | Htl | CZ03 | 0.501 | rec
2020 | PGE | Any | Htl | CZ03 | 0.125 | new
2020 | PGE | PGE | Htl | CZ04 | 7.366 | old
2020 | PGE | PGE | Htl | CZ04 | 1.722 | ex
2020 | PGE | PGE | Htl | CZ04 | 0.372 | rec
2020 | PGE | Any | Htl | CZ04 | 0.093 | new
2020 | PGE | PGE | Htl | CZ05 | 3.074 | old
2020 | PGE | PGE | Htl | CZ05 | 0.721 | ex
2020 | PGE | PGE | Htl | CZ05 | 0.156 | rec
2020 | PGE | Any | Htl | CZ05 | 0.041 | new
2020 | PGE | PGE | Htl | CZ11 | 1.924 | old
2020 | PGE | PGE | Htl | CZ11 | 0.508 | ex
2020 | PGE | PGE | Htl | CZ11 | 0.109 | rec
2020 | PGE | Any | Htl | CZ11 | 0.027 | new
2020 | PGE | PGE | Htl | CZ12 | 6.437 | old
2020 | PGE | PGE | Htl | CZ12 | 1.914 | ex
2020 | PGE | PGE | Htl | CZ12 | 0.421 | rec
2020 | PGE | Any | Htl | CZ12 | 0.105 | new
2020 | PGE | PGE | Htl | CZ13 | 4.253 | old
2020 | PGE | PGE | Htl | CZ13 | 1.052 | ex
2020 | PGE | PGE | Htl | CZ13 | 0.231 | rec
2020 | PGE | Any | Htl | CZ13 | 0.074 | new
2020 | PGE | PGE | Htl | CZ16 | 0.78 | old
2020 | PGE | PGE | Htl | CZ16 | 0.236 | ex
2020 | PGE | PGE | Htl | CZ16 | 0.044 | rec
2020 | PGE | Any | Htl | CZ16 | 0.069 | new
2020 | PGE | PGE | MBT | CZ01 | 0.882 | old
2020 | PGE | PGE | MBT | CZ01 | 0.167 | ex
2020 | PGE | PGE | MBT | CZ01 | 0.035 | rec
2020 | PGE | Any | MBT | CZ01 | 0.009 | new
2020 | PGE | PGE | MBT | CZ02 | 8.734 | old
2020 | PGE | PGE | MBT | CZ02 | 1.337 | ex
2020 | PGE | PGE | MBT | CZ02 | 0.269 | rec
2020 | PGE | Any | MBT | CZ02 | 0.067 | new
2020 | PGE | PGE | MBT | CZ03 | 44.501 | old
2020 | PGE | PGE | MBT | CZ03 | 5.908 | ex
2020 | PGE | PGE | MBT | CZ03 | 1.045 | rec
2020 | PGE | Any | MBT | CZ03 | 0.261 | new
2020 | PGE | PGE | MBT | CZ04 | 23.473 | old
2020 | PGE | PGE | MBT | CZ04 | 3.753 | ex
2020 | PGE | PGE | MBT | CZ04 | 0.796 | rec
2020 | PGE | Any | MBT | CZ04 | 0.199 | new
2020 | PGE | PGE | MBT | CZ05 | 2.802 | old
2020 | PGE | PGE | MBT | CZ05 | 0.448 | ex
2020 | PGE | PGE | MBT | CZ05 | 0.095 | rec
2020 | PGE | Any | MBT | CZ05 | 0.032 | new
2020 | PGE | PGE | MBT | CZ11 | 6.029 | old
2020 | PGE | PGE | MBT | CZ11 | 1.473 | ex
2020 | PGE | PGE | MBT | CZ11 | 0.324 | rec
2020 | PGE | Any | MBT | CZ11 | 0.081 | new
2020 | PGE | PGE | MBT | CZ12 | 24.051 | old
2020 | PGE | PGE | MBT | CZ12 | 4.929 | ex
2020 | PGE | PGE | MBT | CZ12 | 1.04 | rec
2020 | PGE | Any | MBT | CZ12 | 0.26 | new
2020 | PGE | PGE | MBT | CZ13 | 15.196 | old
2020 | PGE | PGE | MBT | CZ13 | 3.331 | ex
2020 | PGE | PGE | MBT | CZ13 | 0.767 | rec
2020 | PGE | Any | MBT | CZ13 | 0.304 | new
2020 | PGE | PGE | MBT | CZ16 | 1.351 | old
2020 | PGE | PGE | MBT | CZ16 | 0.286 | ex
2020 | PGE | PGE | MBT | CZ16 | 0.061 | rec
2020 | PGE | Any | MBT | CZ16 | 0.169 | new
2020 | PGE | PGE | MLI | CZ01 | 0.882 | old
2020 | PGE | PGE | MLI | CZ01 | 0.167 | ex
2020 | PGE | PGE | MLI | CZ01 | 0.035 | rec
2020 | PGE | Any | MLI | CZ01 | 0.009 | new
2020 | PGE | PGE | MLI | CZ02 | 8.734 | old
2020 | PGE | PGE | MLI | CZ02 | 1.337 | ex
2020 | PGE | PGE | MLI | CZ02 | 0.269 | rec
2020 | PGE | Any | MLI | CZ02 | 0.067 | new
2020 | PGE | PGE | MLI | CZ03 | 44.501 | old
2020 | PGE | PGE | MLI | CZ03 | 5.908 | ex
2020 | PGE | PGE | MLI | CZ03 | 1.045 | rec
2020 | PGE | Any | MLI | CZ03 | 0.261 | new
2020 | PGE | PGE | MLI | CZ04 | 23.473 | old
2020 | PGE | PGE | MLI | CZ04 | 3.753 | ex
2020 | PGE | PGE | MLI | CZ04 | 0.796 | rec
2020 | PGE | Any | MLI | CZ04 | 0.199 | new
2020 | PGE | PGE | MLI | CZ05 | 2.802 | old
2020 | PGE | PGE | MLI | CZ05 | 0.448 | ex
2020 | PGE | PGE | MLI | CZ05 | 0.095 | rec
2020 | PGE | Any | MLI | CZ05 | 0.032 | new
2020 | PGE | PGE | MLI | CZ11 | 6.029 | old
2020 | PGE | PGE | MLI | CZ11 | 1.473 | ex
2020 | PGE | PGE | MLI | CZ11 | 0.324 | rec
2020 | PGE | Any | MLI | CZ11 | 0.081 | new
2020 | PGE | PGE | MLI | CZ12 | 24.051 | old
2020 | PGE | PGE | MLI | CZ12 | 4.929 | ex
2020 | PGE | PGE | MLI | CZ12 | 1.04 | rec
2020 | PGE | Any | MLI | CZ12 | 0.26 | new
2020 | PGE | PGE | MLI | CZ13 | 15.196 | old
2020 | PGE | PGE | MLI | CZ13 | 3.331 | ex
2020 | PGE | PGE | MLI | CZ13 | 0.767 | rec
2020 | PGE | Any | MLI | CZ13 | 0.304 | new
2020 | PGE | PGE | MLI | CZ16 | 1.351 | old
2020 | PGE | PGE | MLI | CZ16 | 0.286 | ex
2020 | PGE | PGE | MLI | CZ16 | 0.061 | rec
2020 | PGE | Any | MLI | CZ16 | 0.169 | new
2020 | PGE | PGE | Mtl | CZ01 | 0.705 | old
2020 | PGE | PGE | Mtl | CZ01 | 0.224 | ex
2020 | PGE | PGE | Mtl | CZ01 | 0.039 | rec
2020 | PGE | Any | Mtl | CZ01 | 0.01 | new
2020 | PGE | PGE | Mtl | CZ02 | 3.489 | old
2020 | PGE | PGE | Mtl | CZ02 | 0.824 | ex
2020 | PGE | PGE | Mtl | CZ02 | 0.168 | rec
2020 | PGE | Any | Mtl | CZ02 | 0.042 | new
2020 | PGE | PGE | Mtl | CZ03 | 23.105 | old
2020 | PGE | PGE | Mtl | CZ03 | 3.374 | ex
2020 | PGE | PGE | Mtl | CZ03 | 0.501 | rec
2020 | PGE | Any | Mtl | CZ03 | 0.125 | new
2020 | PGE | PGE | Mtl | CZ04 | 7.366 | old
2020 | PGE | PGE | Mtl | CZ04 | 1.722 | ex
2020 | PGE | PGE | Mtl | CZ04 | 0.372 | rec
2020 | PGE | Any | Mtl | CZ04 | 0.093 | new
2020 | PGE | PGE | Mtl | CZ05 | 3.074 | old
2020 | PGE | PGE | Mtl | CZ05 | 0.721 | ex
2020 | PGE | PGE | Mtl | CZ05 | 0.156 | rec
2020 | PGE | Any | Mtl | CZ05 | 0.041 | new
2020 | PGE | PGE | Mtl | CZ11 | 1.924 | old
2020 | PGE | PGE | Mtl | CZ11 | 0.508 | ex
2020 | PGE | PGE | Mtl | CZ11 | 0.109 | rec
2020 | PGE | Any | Mtl | CZ11 | 0.027 | new
2020 | PGE | PGE | Mtl | CZ12 | 6.437 | old
2020 | PGE | PGE | Mtl | CZ12 | 1.914 | ex
2020 | PGE | PGE | Mtl | CZ12 | 0.421 | rec
2020 | PGE | Any | Mtl | CZ12 | 0.105 | new
2020 | PGE | PGE | Mtl | CZ13 | 4.253 | old
2020 | PGE | PGE | Mtl | CZ13 | 1.052 | ex
2020 | PGE | PGE | Mtl | CZ13 | 0.231 | rec
2020 | PGE | Any | Mtl | CZ13 | 0.074 | new
2020 | PGE | PGE | Mtl | CZ16 | 0.78 | old
2020 | PGE | PGE | Mtl | CZ16 | 0.236 | ex
2020 | PGE | PGE | Mtl | CZ16 | 0.044 | rec
2020 | PGE | Any | Mtl | CZ16 | 0.069 | new
2020 | PGE | PGE | Nrs | CZ01 | 0.614 | old
2020 | PGE | PGE | Nrs | CZ01 | 0.141 | ex
2020 | PGE | PGE | Nrs | CZ01 | 0.023 | rec
2020 | PGE | Any | Nrs | CZ01 | 0.006 | new
2020 | PGE | PGE | Nrs | CZ02 | 5.289 | old
2020 | PGE | PGE | Nrs | CZ02 | 1.019 | ex
2020 | PGE | PGE | Nrs | CZ02 | 0.213 | rec
2020 | PGE | Any | Nrs | CZ02 | 0.053 | new
2020 | PGE | PGE | Nrs | CZ03 | 16.544 | old
2020 | PGE | PGE | Nrs | CZ03 | 2.179 | ex
2020 | PGE | PGE | Nrs | CZ03 | 0.583 | rec
2020 | PGE | Any | Nrs | CZ03 | 0.146 | new
2020 | PGE | PGE | Nrs | CZ04 | 7.099 | old
2020 | PGE | PGE | Nrs | CZ04 | 1.448 | ex
2020 | PGE | PGE | Nrs | CZ04 | 0.298 | rec
2020 | PGE | Any | Nrs | CZ04 | 0.075 | new
2020 | PGE | PGE | Nrs | CZ05 | 1.081 | old
2020 | PGE | PGE | Nrs | CZ05 | 0.22 | ex
2020 | PGE | PGE | Nrs | CZ05 | 0.045 | rec
2020 | PGE | Any | Nrs | CZ05 | 0.023 | new
2020 | PGE | PGE | Nrs | CZ11 | 3.449 | old
2020 | PGE | PGE | Nrs | CZ11 | 0.918 | ex
2020 | PGE | PGE | Nrs | CZ11 | 0.18 | rec
2020 | PGE | Any | Nrs | CZ11 | 0.045 | new
2020 | PGE | PGE | Nrs | CZ12 | 11.659 | old
2020 | PGE | PGE | Nrs | CZ12 | 2.681 | ex
2020 | PGE | PGE | Nrs | CZ12 | 0.593 | rec
2020 | PGE | Any | Nrs | CZ12 | 0.148 | new
2020 | PGE | PGE | Nrs | CZ13 | 8.773 | old
2020 | PGE | PGE | Nrs | CZ13 | 2.404 | ex
2020 | PGE | PGE | Nrs | CZ13 | 0.467 | rec
2020 | PGE | Any | Nrs | CZ13 | 0.153 | new
2020 | PGE | PGE | Nrs | CZ16 | 0.2 | old
2020 | PGE | PGE | Nrs | CZ16 | 0.051 | ex
2020 | PGE | PGE | Nrs | CZ16 | 0.009 | rec
2020 | PGE | Any | Nrs | CZ16 | 0.03 | new
2020 | PGE | PGE | OfL | CZ01 | 1.322 | old
2020 | PGE | PGE | OfL | CZ01 | 0.353 | ex
2020 | PGE | PGE | OfL | CZ01 | 0.048 | rec
2020 | PGE | Any | OfL | CZ01 | 0.012 | new
2020 | PGE | PGE | OfL | CZ02 | 15.845 | old
2020 | PGE | PGE | OfL | CZ02 | 3.833 | ex
2020 | PGE | PGE | OfL | CZ02 | 0.711 | rec
2020 | PGE | Any | OfL | CZ02 | 0.178 | new
2020 | PGE | PGE | OfL | CZ03 | 174.648 | old
2020 | PGE | PGE | OfL | CZ03 | 34.557 | ex
2020 | PGE | PGE | OfL | CZ03 | 6.492 | rec
2020 | PGE | Any | OfL | CZ03 | 1.623 | new
2020 | PGE | PGE | OfL | CZ04 | 69.341 | old
2020 | PGE | PGE | OfL | CZ04 | 19.239 | ex
2020 | PGE | PGE | OfL | CZ04 | 3.61 | rec
2020 | PGE | Any | OfL | CZ04 | 0.903 | new
2020 | PGE | PGE | OfL | CZ05 | 4.865 | old
2020 | PGE | PGE | OfL | CZ05 | 1.353 | ex
2020 | PGE | PGE | OfL | CZ05 | 0.254 | rec
2020 | PGE | Any | OfL | CZ05 | 0.074 | new
2020 | PGE | PGE | OfL | CZ11 | 5.743 | old
2020 | PGE | PGE | OfL | CZ11 | 1.943 | ex
2020 | PGE | PGE | OfL | CZ11 | 0.411 | rec
2020 | PGE | Any | OfL | CZ11 | 0.103 | new
2020 | PGE | PGE | OfL | CZ12 | 47.841 | old
2020 | PGE | PGE | OfL | CZ12 | 17.611 | ex
2020 | PGE | PGE | OfL | CZ12 | 3.387 | rec
2020 | PGE | Any | OfL | CZ12 | 0.847 | new
2020 | PGE | PGE | OfL | CZ13 | 21.008 | old
2020 | PGE | PGE | OfL | CZ13 | 5.978 | ex
2020 | PGE | PGE | OfL | CZ13 | 1.397 | rec
2020 | PGE | Any | OfL | CZ13 | 0.447 | new
2020 | PGE | PGE | OfL | CZ16 | 0.673 | old
2020 | PGE | PGE | OfL | CZ16 | 0.208 | ex
2020 | PGE | PGE | OfL | CZ16 | 0.035 | rec
2020 | PGE | Any | OfL | CZ16 | 0.095 | new
2020 | PGE | PGE | OfS | CZ01 | 1.898 | old
2020 | PGE | PGE | OfS | CZ01 | 0.325 | ex
2020 | PGE | PGE | OfS | CZ01 | 0.071 | rec
2020 | PGE | Any | OfS | CZ01 | 0.018 | new
2020 | PGE | PGE | OfS | CZ02 | 4.572 | old
2020 | PGE | PGE | OfS | CZ02 | 0.847 | ex
2020 | PGE | PGE | OfS | CZ02 | 0.199 | rec
2020 | PGE | Any | OfS | CZ02 | 0.05 | new
2020 | PGE | PGE | OfS | CZ03 | 27.509 | old
2020 | PGE | PGE | OfS | CZ03 | 4.797 | ex
2020 | PGE | PGE | OfS | CZ03 | 1.205 | rec
2020 | PGE | Any | OfS | CZ03 | 0.301 | new
2020 | PGE | PGE | OfS | CZ04 | 21.136 | old
2020 | PGE | PGE | OfS | CZ04 | 4.129 | ex
2020 | PGE | PGE | OfS | CZ04 | 0.971 | rec
2020 | PGE | Any | OfS | CZ04 | 0.243 | new
2020 | PGE | PGE | OfS | CZ05 | 1.488 | old
2020 | PGE | PGE | OfS | CZ05 | 0.29 | ex
2020 | PGE | PGE | OfS | CZ05 | 0.068 | rec
2020 | PGE | Any | OfS | CZ05 | 0.023 | new
2020 | PGE | PGE | OfS | CZ11 | 6.587 | old
2020 | PGE | PGE | OfS | CZ11 | 1.408 | ex
2020 | PGE | PGE | OfS | CZ11 | 0.3 | rec
2020 | PGE | Any | OfS | CZ11 | 0.075 | new
2020 | PGE | PGE | OfS | CZ12 | 25.803 | old
2020 | PGE | PGE | OfS | CZ12 | 5.65 | ex
2020 | PGE | PGE | OfS | CZ12 | 1.248 | rec
2020 | PGE | Any | OfS | CZ12 | 0.312 | new
2020 | PGE | PGE | OfS | CZ13 | 22.844 | old
2020 | PGE | PGE | OfS | CZ13 | 5.019 | ex
2020 | PGE | PGE | OfS | CZ13 | 1.065 | rec
2020 | PGE | Any | OfS | CZ13 | 0.384 | new
2020 | PGE | PGE | OfS | CZ16 | 0.939 | old
2020 | PGE | PGE | OfS | CZ16 | 0.173 | ex
2020 | PGE | PGE | OfS | CZ16 | 0.037 | rec
2020 | PGE | Any | OfS | CZ16 | 0.061 | new
2020 | PGE | PGE | RFF | CZ01 | 0.355 | old
2020 | PGE | PGE | RFF | CZ01 | 0.026 | ex
2020 | PGE | PGE | RFF | CZ01 | 0.007 | rec
2020 | PGE | Any | RFF | CZ01 | 0.002 | new
2020 | PGE | PGE | RFF | CZ02 | 1.574 | old
2020 | PGE | PGE | RFF | CZ02 | 0.163 | ex
2020 | PGE | PGE | RFF | CZ02 | 0.039 | rec
2020 | PGE | Any | RFF | CZ02 | 0.01 | new
2020 | PGE | PGE | RFF | CZ03 | 7.188 | old
2020 | PGE | PGE | RFF | CZ03 | 0.774 | ex
2020 | PGE | PGE | RFF | CZ03 | 0.192 | rec
2020 | PGE | Any | RFF | CZ03 | 0.048 | new
2020 | PGE | PGE | RFF | CZ04 | 3.147 | old
2020 | PGE | PGE | RFF | CZ04 | 0.343 | ex
2020 | PGE | PGE | RFF | CZ04 | 0.077 | rec
2020 | PGE | Any | RFF | CZ04 | 0.019 | new
2020 | PGE | PGE | RFF | CZ05 | 0.618 | old
2020 | PGE | PGE | RFF | CZ05 | 0.067 | ex
2020 | PGE | PGE | RFF | CZ05 | 0.015 | rec
2020 | PGE | Any | RFF | CZ05 | 0.008 | new
2020 | PGE | PGE | RFF | CZ11 | 1.374 | old
2020 | PGE | PGE | RFF | CZ11 | 0.18 | ex
2020 | PGE | PGE | RFF | CZ11 | 0.04 | rec
2020 | PGE | Any | RFF | CZ11 | 0.01 | new
2020 | PGE | PGE | RFF | CZ12 | 4.717 | old
2020 | PGE | PGE | RFF | CZ12 | 0.659 | ex
2020 | PGE | PGE | RFF | CZ12 | 0.139 | rec
2020 | PGE | Any | RFF | CZ12 | 0.035 | new
2020 | PGE | PGE | RFF | CZ13 | 3.329 | old
2020 | PGE | PGE | RFF | CZ13 | 0.435 | ex
2020 | PGE | PGE | RFF | CZ13 | 0.096 | rec
2020 | PGE | Any | RFF | CZ13 | 0.046 | new
2020 | PGE | PGE | RFF | CZ16 | 0.284 | old
2020 | PGE | PGE | RFF | CZ16 | 0.031 | ex
2020 | PGE | PGE | RFF | CZ16 | 0.007 | rec
2020 | PGE | Any | RFF | CZ16 | 0.026 | new
2020 | PGE | PGE | RSD | CZ01 | 0.355 | old
2020 | PGE | PGE | RSD | CZ01 | 0.026 | ex
2020 | PGE | PGE | RSD | CZ01 | 0.007 | rec
2020 | PGE | Any | RSD | CZ01 | 0.002 | new
2020 | PGE | PGE | RSD | CZ02 | 1.574 | old
2020 | PGE | PGE | RSD | CZ02 | 0.163 | ex
2020 | PGE | PGE | RSD | CZ02 | 0.039 | rec
2020 | PGE | Any | RSD | CZ02 | 0.01 | new
2020 | PGE | PGE | RSD | CZ03 | 7.188 | old
2020 | PGE | PGE | RSD | CZ03 | 0.774 | ex
2020 | PGE | PGE | RSD | CZ03 | 0.192 | rec
2020 | PGE | Any | RSD | CZ03 | 0.048 | new
2020 | PGE | PGE | RSD | CZ04 | 3.147 | old
2020 | PGE | PGE | RSD | CZ04 | 0.343 | ex
2020 | PGE | PGE | RSD | CZ04 | 0.077 | rec
2020 | PGE | Any | RSD | CZ04 | 0.019 | new
2020 | PGE | PGE | RSD | CZ05 | 0.618 | old
2020 | PGE | PGE | RSD | CZ05 | 0.067 | ex
2020 | PGE | PGE | RSD | CZ05 | 0.015 | rec
2020 | PGE | Any | RSD | CZ05 | 0.008 | new
2020 | PGE | PGE | RSD | CZ11 | 1.374 | old
2020 | PGE | PGE | RSD | CZ11 | 0.18 | ex
2020 | PGE | PGE | RSD | CZ11 | 0.04 | rec
2020 | PGE | Any | RSD | CZ11 | 0.01 | new
2020 | PGE | PGE | RSD | CZ12 | 4.717 | old
2020 | PGE | PGE | RSD | CZ12 | 0.659 | ex
2020 | PGE | PGE | RSD | CZ12 | 0.139 | rec
2020 | PGE | Any | RSD | CZ12 | 0.035 | new
2020 | PGE | PGE | RSD | CZ13 | 3.329 | old
2020 | PGE | PGE | RSD | CZ13 | 0.435 | ex
2020 | PGE | PGE | RSD | CZ13 | 0.096 | rec
2020 | PGE | Any | RSD | CZ13 | 0.046 | new
2020 | PGE | PGE | RSD | CZ16 | 0.284 | old
2020 | PGE | PGE | RSD | CZ16 | 0.031 | ex
2020 | PGE | PGE | RSD | CZ16 | 0.007 | rec
2020 | PGE | Any | RSD | CZ16 | 0.026 | new
2020 | PGE | PGE | Rt3 | CZ01 | 1.136 | old
2020 | PGE | PGE | Rt3 | CZ01 | 0.176 | ex
2020 | PGE | PGE | Rt3 | CZ01 | 0.04 | rec
2020 | PGE | Any | Rt3 | CZ01 | 0.01 | new
2020 | PGE | PGE | Rt3 | CZ02 | 7.537 | old
2020 | PGE | PGE | Rt3 | CZ02 | 1.284 | ex
2020 | PGE | PGE | Rt3 | CZ02 | 0.285 | rec
2020 | PGE | Any | Rt3 | CZ02 | 0.071 | new
2020 | PGE | PGE | Rt3 | CZ03 | 35.701 | old
2020 | PGE | PGE | Rt3 | CZ03 | 5.258 | ex
2020 | PGE | PGE | Rt3 | CZ03 | 1.22 | rec
2020 | PGE | Any | Rt3 | CZ03 | 0.305 | new
2020 | PGE | PGE | Rt3 | CZ04 | 15.221 | old
2020 | PGE | PGE | Rt3 | CZ04 | 2.747 | ex
2020 | PGE | PGE | Rt3 | CZ04 | 0.601 | rec
2020 | PGE | Any | Rt3 | CZ04 | 0.15 | new
2020 | PGE | PGE | Rt3 | CZ05 | 2.617 | old
2020 | PGE | PGE | Rt3 | CZ05 | 0.476 | ex
2020 | PGE | PGE | Rt3 | CZ05 | 0.104 | rec
2020 | PGE | Any | Rt3 | CZ05 | 0.04 | new
2020 | PGE | PGE | Rt3 | CZ11 | 5.724 | old
2020 | PGE | PGE | Rt3 | CZ11 | 1.474 | ex
2020 | PGE | PGE | Rt3 | CZ11 | 0.325 | rec
2020 | PGE | Any | Rt3 | CZ11 | 0.081 | new
2020 | PGE | PGE | Rt3 | CZ12 | 24.052 | old
2020 | PGE | PGE | Rt3 | CZ12 | 6.103 | ex
2020 | PGE | PGE | Rt3 | CZ12 | 1.236 | rec
2020 | PGE | Any | Rt3 | CZ12 | 0.309 | new
2020 | PGE | PGE | Rt3 | CZ13 | 14.777 | old
2020 | PGE | PGE | Rt3 | CZ13 | 3.701 | ex
2020 | PGE | PGE | Rt3 | CZ13 | 0.852 | rec
2020 | PGE | Any | Rt3 | CZ13 | 0.365 | new
2020 | PGE | PGE | Rt3 | CZ16 | 0.338 | old
2020 | PGE | PGE | Rt3 | CZ16 | 0.069 | ex
2020 | PGE | PGE | Rt3 | CZ16 | 0.016 | rec
2020 | PGE | Any | Rt3 | CZ16 | 0.05 | new
2020 | PGE | PGE | RtL | CZ01 | 1.136 | old
2020 | PGE | PGE | RtL | CZ01 | 0.176 | ex
2020 | PGE | PGE | RtL | CZ01 | 0.04 | rec
2020 | PGE | Any | RtL | CZ01 | 0.01 | new
2020 | PGE | PGE | RtL | CZ02 | 7.537 | old
2020 | PGE | PGE | RtL | CZ02 | 1.284 | ex
2020 | PGE | PGE | RtL | CZ02 | 0.285 | rec
2020 | PGE | Any | RtL | CZ02 | 0.071 | new
2020 | PGE | PGE | RtL | CZ03 | 35.701 | old
2020 | PGE | PGE | RtL | CZ03 | 5.258 | ex
2020 | PGE | PGE | RtL | CZ03 | 1.22 | rec
2020 | PGE | Any | RtL | CZ03 | 0.305 | new
2020 | PGE | PGE | RtL | CZ04 | 15.221 | old
2020 | PGE | PGE | RtL | CZ04 | 2.747 | ex
2020 | PGE | PGE | RtL | CZ04 | 0.601 | rec
2020 | PGE | Any | RtL | CZ04 | 0.15 | new
2020 | PGE | PGE | RtL | CZ05 | 2.617 | old
2020 | PGE | PGE | RtL | CZ05 | 0.476 | ex
2020 | PGE | PGE | RtL | CZ05 | 0.104 | rec
2020 | PGE | Any | RtL | CZ05 | 0.04 | new
2020 | PGE | PGE | RtL | CZ11 | 5.724 | old
2020 | PGE | PGE | RtL | CZ11 | 1.474 | ex
2020 | PGE | PGE | RtL | CZ11 | 0.325 | rec
2020 | PGE | Any | RtL | CZ11 | 0.081 | new
2020 | PGE | PGE | RtL | CZ12 | 24.052 | old
2020 | PGE | PGE | RtL | CZ12 | 6.103 | ex
2020 | PGE | PGE | RtL | CZ12 | 1.236 | rec
2020 | PGE | Any | RtL | CZ12 | 0.309 | new
2020 | PGE | PGE | RtL | CZ13 | 14.777 | old
2020 | PGE | PGE | RtL | CZ13 | 3.701 | ex
2020 | PGE | PGE | RtL | CZ13 | 0.852 | rec
2020 | PGE | Any | RtL | CZ13 | 0.365 | new
2020 | PGE | PGE | RtL | CZ16 | 0.338 | old
2020 | PGE | PGE | RtL | CZ16 | 0.069 | ex
2020 | PGE | PGE | RtL | CZ16 | 0.016 | rec
2020 | PGE | Any | RtL | CZ16 | 0.05 | new
2020 | PGE | PGE | RtS | CZ01 | 1.136 | old
2020 | PGE | PGE | RtS | CZ01 | 0.176 | ex
2020 | PGE | PGE | RtS | CZ01 | 0.04 | rec
2020 | PGE | Any | RtS | CZ01 | 0.01 | new
2020 | PGE | PGE | RtS | CZ02 | 7.537 | old
2020 | PGE | PGE | RtS | CZ02 | 1.284 | ex
2020 | PGE | PGE | RtS | CZ02 | 0.285 | rec
2020 | PGE | Any | RtS | CZ02 | 0.071 | new
2020 | PGE | PGE | RtS | CZ03 | 35.701 | old
2020 | PGE | PGE | RtS | CZ03 | 5.258 | ex
2020 | PGE | PGE | RtS | CZ03 | 1.22 | rec
2020 | PGE | Any | RtS | CZ03 | 0.305 | new
2020 | PGE | PGE | RtS | CZ04 | 15.221 | old
2020 | PGE | PGE | RtS | CZ04 | 2.747 | ex
2020 | PGE | PGE | RtS | CZ04 | 0.601 | rec
2020 | PGE | Any | RtS | CZ04 | 0.15 | new
2020 | PGE | PGE | RtS | CZ05 | 2.617 | old
2020 | PGE | PGE | RtS | CZ05 | 0.476 | ex
2020 | PGE | PGE | RtS | CZ05 | 0.104 | rec
2020 | PGE | Any | RtS | CZ05 | 0.04 | new
2020 | PGE | PGE | RtS | CZ11 | 5.724 | old
2020 | PGE | PGE | RtS | CZ11 | 1.474 | ex
2020 | PGE | PGE | RtS | CZ11 | 0.325 | rec
2020 | PGE | Any | RtS | CZ11 | 0.081 | new
2020 | PGE | PGE | RtS | CZ12 | 24.052 | old
2020 | PGE | PGE | RtS | CZ12 | 6.103 | ex
2020 | PGE | PGE | RtS | CZ12 | 1.236 | rec
2020 | PGE | Any | RtS | CZ12 | 0.309 | new
2020 | PGE | PGE | RtS | CZ13 | 14.777 | old
2020 | PGE | PGE | RtS | CZ13 | 3.701 | ex
2020 | PGE | PGE | RtS | CZ13 | 0.852 | rec
2020 | PGE | Any | RtS | CZ13 | 0.365 | new
2020 | PGE | PGE | RtS | CZ16 | 0.338 | old
2020 | PGE | PGE | RtS | CZ16 | 0.069 | ex
2020 | PGE | PGE | RtS | CZ16 | 0.016 | rec
2020 | PGE | Any | RtS | CZ16 | 0.05 | new
2020 | PGE | PGE | SCn | CZ01 | 1.011 | old
2020 | PGE | PGE | SCn | CZ01 | 0.376 | ex
2020 | PGE | PGE | SCn | CZ01 | 0.06 | rec
2020 | PGE | Any | SCn | CZ01 | 0.015 | new
2020 | PGE | PGE | SCn | CZ02 | 8.752 | old
2020 | PGE | PGE | SCn | CZ02 | 1.786 | ex
2020 | PGE | PGE | SCn | CZ02 | 0.355 | rec
2020 | PGE | Any | SCn | CZ02 | 0.089 | new
2020 | PGE | PGE | SCn | CZ03 | 49.141 | old
2020 | PGE | PGE | SCn | CZ03 | 6.94 | ex
2020 | PGE | PGE | SCn | CZ03 | 1.868 | rec
2020 | PGE | Any | SCn | CZ03 | 0.467 | new
2020 | PGE | PGE | SCn | CZ04 | 17.135 | old
2020 | PGE | PGE | SCn | CZ04 | 3.447 | ex
2020 | PGE | PGE | SCn | CZ04 | 0.68 | rec
2020 | PGE | Any | SCn | CZ04 | 0.17 | new
2020 | PGE | PGE | SCn | CZ05 | 1.3 | old
2020 | PGE | PGE | SCn | CZ05 | 0.265 | ex
2020 | PGE | PGE | SCn | CZ05 | 0.052 | rec
2020 | PGE | Any | SCn | CZ05 | 0.015 | new
2020 | PGE | PGE | SCn | CZ11 | 6.795 | old
2020 | PGE | PGE | SCn | CZ11 | 3.41 | ex
2020 | PGE | PGE | SCn | CZ11 | 0.684 | rec
2020 | PGE | Any | SCn | CZ11 | 0.171 | new
2020 | PGE | PGE | SCn | CZ12 | 28.584 | old
2020 | PGE | PGE | SCn | CZ12 | 12.215 | ex
2020 | PGE | PGE | SCn | CZ12 | 2.588 | rec
2020 | PGE | Any | SCn | CZ12 | 0.647 | new
2020 | PGE | PGE | SCn | CZ13 | 17.275 | old
2020 | PGE | PGE | SCn | CZ13 | 8.141 | ex
2020 | PGE | PGE | SCn | CZ13 | 1.585 | rec
2020 | PGE | Any | SCn | CZ13 | 0.584 | new
2020 | PGE | PGE | SCn | CZ16 | 0.876 | old
2020 | PGE | PGE | SCn | CZ16 | 0.406 | ex
2020 | PGE | PGE | SCn | CZ16 | 0.079 | rec
2020 | PGE | Any | SCn | CZ16 | 0.122 | new
2020 | PGE | PGE | SUn | CZ01 | 1.011 | old
2020 | PGE | PGE | SUn | CZ01 | 0.376 | ex
2020 | PGE | PGE | SUn | CZ01 | 0.06 | rec
2020 | PGE | Any | SUn | CZ01 | 0.015 | new
2020 | PGE | PGE | SUn | CZ02 | 8.752 | old
2020 | PGE | PGE | SUn | CZ02 | 1.786 | ex
2020 | PGE | PGE | SUn | CZ02 | 0.355 | rec
2020 | PGE | Any | SUn | CZ02 | 0.089 | new
2020 | PGE | PGE | SUn | CZ03 | 49.141 | old
2020 | PGE | PGE | SUn | CZ03 | 6.94 | ex
2020 | PGE | PGE | SUn | CZ03 | 1.868 | rec
2020 | PGE | Any | SUn | CZ03 | 0.467 | new
2020 | PGE | PGE | SUn | CZ04 | 17.135 | old
2020 | PGE | PGE | SUn | CZ04 | 3.447 | ex
2020 | PGE | PGE | SUn | CZ04 | 0.68 | rec
2020 | PGE | Any | SUn | CZ04 | 0.17 | new
2020 | PGE | PGE | SUn | CZ05 | 1.3 | old
2020 | PGE | PGE | SUn | CZ05 | 0.265 | ex
2020 | PGE | PGE | SUn | CZ05 | 0.052 | rec
2020 | PGE | Any | SUn | CZ05 | 0.015 | new
2020 | PGE | PGE | SUn | CZ11 | 6.795 | old
2020 | PGE | PGE | SUn | CZ11 | 3.41 | ex
2020 | PGE | PGE | SUn | CZ11 | 0.684 | rec
2020 | PGE | Any | SUn | CZ11 | 0.171 | new
2020 | PGE | PGE | SUn | CZ12 | 28.584 | old
2020 | PGE | PGE | SUn | CZ12 | 12.215 | ex
2020 | PGE | PGE | SUn | CZ12 | 2.588 | rec
2020 | PGE | Any | SUn | CZ12 | 0.647 | new
2020 | PGE | PGE | SUn | CZ13 | 17.275 | old
2020 | PGE | PGE | SUn | CZ13 | 8.141 | ex
2020 | PGE | PGE | SUn | CZ13 | 1.585 | rec
2020 | PGE | Any | SUn | CZ13 | 0.584 | new
2020 | PGE | PGE | SUn | CZ16 | 0.876 | old
2020 | PGE | PGE | SUn | CZ16 | 0.406 | ex
2020 | PGE | PGE | SUn | CZ16 | 0.079 | rec
2020 | PGE | Any | SUn | CZ16 | 0.122 | new
2020 | PGE | PGE | WRf | CZ01 | 0.104 | old
2020 | PGE | PGE | WRf | CZ01 | 0.044 | ex
2020 | PGE | PGE | WRf | CZ01 | 0.007 | rec
2020 | PGE | Any | WRf | CZ01 | 0.002 | new
2020 | PGE | PGE | WRf | CZ02 | 0.761 | old
2020 | PGE | PGE | WRf | CZ02 | 0.168 | ex
2020 | PGE | PGE | WRf | CZ02 | 0.035 | rec
2020 | PGE | Any | WRf | CZ02 | 0.009 | new
2020 | PGE | PGE | WRf | CZ03 | 8.838 | old
2020 | PGE | PGE | WRf | CZ03 | 1.4 | ex
2020 | PGE | PGE | WRf | CZ03 | 0.368 | rec
2020 | PGE | Any | WRf | CZ03 | 0.092 | new
2020 | PGE | PGE | WRf | CZ04 | 1.603 | old
2020 | PGE | PGE | WRf | CZ04 | 0.306 | ex
2020 | PGE | PGE | WRf | CZ04 | 0.067 | rec
2020 | PGE | Any | WRf | CZ04 | 0.017 | new
2020 | PGE | PGE | WRf | CZ05 | 0.942 | old
2020 | PGE | PGE | WRf | CZ05 | 0.18 | ex
2020 | PGE | PGE | WRf | CZ05 | 0.04 | rec
2020 | PGE | Any | WRf | CZ05 | 0.01 | new
2020 | PGE | PGE | WRf | CZ11 | 1 | old
2020 | PGE | PGE | WRf | CZ11 | 0.386 | ex
2020 | PGE | PGE | WRf | CZ11 | 0.091 | rec
2020 | PGE | Any | WRf | CZ11 | 0.023 | new
2020 | PGE | PGE | WRf | CZ12 | 4.529 | old
2020 | PGE | PGE | WRf | CZ12 | 1.965 | ex
2020 | PGE | PGE | WRf | CZ12 | 0.528 | rec
2020 | PGE | Any | WRf | CZ12 | 0.132 | new
2020 | PGE | PGE | WRf | CZ13 | 6.717 | old
2020 | PGE | PGE | WRf | CZ13 | 2.448 | ex
2020 | PGE | PGE | WRf | CZ13 | 0.553 | rec
2020 | PGE | Any | WRf | CZ13 | 0.288 | new
2020 | PGE | PGE | WRf | CZ16 | 0.009 | old
2020 | PGE | PGE | WRf | CZ16 | 0.004 | ex
2020 | PGE | PGE | WRf | CZ16 | 0.002 | rec
2020 | PGE | Any | WRf | CZ16 | 0.005 | new
2020 | SCE | SCE | Asm | CZ05 | 0.387 | old
2020 | SCE | SCE | Asm | CZ05 | 0.077 | ex
2020 | SCE | SCE | Asm | CZ05 | 0.017 | rec
2020 | SCE | SCE | Asm | CZ06 | 32.51 | old
2020 | SCE | SCE | Asm | CZ06 | 6.365 | ex
2020 | SCE | SCE | Asm | CZ06 | 1.467 | rec
2020 | SCE | Any | Asm | CZ06 | 0.781 | new
2020 | SCE | SCE | Asm | CZ08 | 47.444 | old
2020 | SCE | SCE | Asm | CZ08 | 9.289 | ex
2020 | SCE | SCE | Asm | CZ08 | 2.135 | rec
2020 | SCE | Any | Asm | CZ08 | 1.142 | new
2020 | SCE | SCE | Asm | CZ09 | 22.149 | old
2020 | SCE | SCE | Asm | CZ09 | 4.334 | ex
2020 | SCE | SCE | Asm | CZ09 | 0.967 | rec
2020 | SCE | Any | Asm | CZ09 | 0.74 | new
2020 | SCE | SCE | Asm | CZ10 | 18.966 | old
2020 | SCE | SCE | Asm | CZ10 | 13.368 | ex
2020 | SCE | SCE | Asm | CZ10 | 2.939 | rec
2020 | SCE | Any | Asm | CZ10 | 1.607 | new
2020 | SCE | SCE | Asm | CZ13 | 2.887 | old
2020 | SCE | SCE | Asm | CZ13 | 0.962 | ex
2020 | SCE | SCE | Asm | CZ13 | 0.223 | rec
2020 | SCE | SCE | Asm | CZ14 | 4.946 | old
2020 | SCE | SCE | Asm | CZ14 | 2.213 | ex
2020 | SCE | SCE | Asm | CZ14 | 0.486 | rec
2020 | SCE | Any | Asm | CZ14 | 0.248 | new
2020 | SCE | SCE | Asm | CZ15 | 6.866 | old
2020 | SCE | SCE | Asm | CZ15 | 4.84 | ex
2020 | SCE | SCE | Asm | CZ15 | 1.064 | rec
2020 | SCE | Any | Asm | CZ15 | 0.533 | new
2020 | SCE | SCE | Asm | CZ16 | 2.849 | old
2020 | SCE | SCE | Asm | CZ16 | 1.377 | ex
2020 | SCE | SCE | Asm | CZ16 | 0.307 | rec
2020 | SCE | SCE | ECC | CZ05 | 0.014 | old
2020 | SCE | SCE | ECC | CZ05 | 0.004 | ex
2020 | SCE | SCE | ECC | CZ05 | 0.002 | rec
2020 | SCE | SCE | ECC | CZ06 | 11.375 | old
2020 | SCE | SCE | ECC | CZ06 | 2.175 | ex
2020 | SCE | SCE | ECC | CZ06 | 0.435 | rec
2020 | SCE | Any | ECC | CZ06 | 0.228 | new
2020 | SCE | SCE | ECC | CZ08 | 18.447 | old
2020 | SCE | SCE | ECC | CZ08 | 3.438 | ex
2020 | SCE | SCE | ECC | CZ08 | 0.689 | rec
2020 | SCE | Any | ECC | CZ08 | 0.363 | new
2020 | SCE | SCE | ECC | CZ09 | 3.959 | old
2020 | SCE | SCE | ECC | CZ09 | 0.895 | ex
2020 | SCE | SCE | ECC | CZ09 | 0.176 | rec
2020 | SCE | Any | ECC | CZ09 | 0.163 | new
2020 | SCE | SCE | ECC | CZ10 | 4.501 | old
2020 | SCE | SCE | ECC | CZ10 | 2.169 | ex
2020 | SCE | SCE | ECC | CZ10 | 0.421 | rec
2020 | SCE | Any | ECC | CZ10 | 0.247 | new
2020 | SCE | SCE | ECC | CZ13 | 0.874 | old
2020 | SCE | SCE | ECC | CZ13 | 0.516 | ex
2020 | SCE | SCE | ECC | CZ13 | 0.112 | rec
2020 | SCE | SCE | ECC | CZ14 | 1.617 | old
2020 | SCE | SCE | ECC | CZ14 | 0.724 | ex
2020 | SCE | SCE | ECC | CZ14 | 0.141 | rec
2020 | SCE | Any | ECC | CZ14 | 0.071 | new
2020 | SCE | SCE | ECC | CZ15 | 1.31 | old
2020 | SCE | SCE | ECC | CZ15 | 0.632 | ex
2020 | SCE | SCE | ECC | CZ15 | 0.123 | rec
2020 | SCE | Any | ECC | CZ15 | 0.062 | new
2020 | SCE | SCE | ECC | CZ16 | 2.926 | old
2020 | SCE | SCE | ECC | CZ16 | 1.415 | ex
2020 | SCE | SCE | ECC | CZ16 | 0.277 | rec
2020 | SCE | SCE | EPr | CZ05 | 0.062 | old
2020 | SCE | SCE | EPr | CZ05 | 0.007 | ex
2020 | SCE | SCE | EPr | CZ05 | 0.002 | rec
2020 | SCE | SCE | EPr | CZ06 | 10.902 | old
2020 | SCE | SCE | EPr | CZ06 | 1.241 | ex
2020 | SCE | SCE | EPr | CZ06 | 0.204 | rec
2020 | SCE | Any | EPr | CZ06 | 0.111 | new
2020 | SCE | SCE | EPr | CZ08 | 18.927 | old
2020 | SCE | SCE | EPr | CZ08 | 2.23 | ex
2020 | SCE | SCE | EPr | CZ08 | 0.363 | rec
2020 | SCE | Any | EPr | CZ08 | 0.197 | new
2020 | SCE | SCE | EPr | CZ09 | 9.851 | old
2020 | SCE | SCE | EPr | CZ09 | 1.305 | ex
2020 | SCE | SCE | EPr | CZ09 | 0.204 | rec
2020 | SCE | Any | EPr | CZ09 | 0.14 | new
2020 | SCE | SCE | EPr | CZ10 | 10.428 | old
2020 | SCE | SCE | EPr | CZ10 | 3.815 | ex
2020 | SCE | SCE | EPr | CZ10 | 0.569 | rec
2020 | SCE | Any | EPr | CZ10 | 0.312 | new
2020 | SCE | SCE | EPr | CZ13 | 2.284 | old
2020 | SCE | SCE | EPr | CZ13 | 0.624 | ex
2020 | SCE | SCE | EPr | CZ13 | 0.125 | rec
2020 | SCE | SCE | EPr | CZ14 | 2.86 | old
2020 | SCE | SCE | EPr | CZ14 | 0.85 | ex
2020 | SCE | SCE | EPr | CZ14 | 0.129 | rec
2020 | SCE | Any | EPr | CZ14 | 0.065 | new
2020 | SCE | SCE | EPr | CZ15 | 0.93 | old
2020 | SCE | SCE | EPr | CZ15 | 0.34 | ex
2020 | SCE | SCE | EPr | CZ15 | 0.051 | rec
2020 | SCE | Any | EPr | CZ15 | 0.027 | new
2020 | SCE | SCE | EPr | CZ16 | 1.313 | old
2020 | SCE | SCE | EPr | CZ16 | 0.422 | ex
2020 | SCE | SCE | EPr | CZ16 | 0.067 | rec
2020 | SCE | SCE | ERC | CZ05 | 0.062 | old
2020 | SCE | SCE | ERC | CZ05 | 0.007 | ex
2020 | SCE | SCE | ERC | CZ05 | 0.002 | rec
2020 | SCE | SCE | ERC | CZ06 | 10.902 | old
2020 | SCE | SCE | ERC | CZ06 | 1.241 | ex
2020 | SCE | SCE | ERC | CZ06 | 0.204 | rec
2020 | SCE | Any | ERC | CZ06 | 0.111 | new
2020 | SCE | SCE | ERC | CZ08 | 18.927 | old
2020 | SCE | SCE | ERC | CZ08 | 2.23 | ex
2020 | SCE | SCE | ERC | CZ08 | 0.363 | rec
2020 | SCE | Any | ERC | CZ08 | 0.197 | new
2020 | SCE | SCE | ERC | CZ09 | 9.851 | old
2020 | SCE | SCE | ERC | CZ09 | 1.305 | ex
2020 | SCE | SCE | ERC | CZ09 | 0.204 | rec
2020 | SCE | Any | ERC | CZ09 | 0.14 | new
2020 | SCE | SCE | ERC | CZ10 | 10.428 | old
2020 | SCE | SCE | ERC | CZ10 | 3.815 | ex
2020 | SCE | SCE | ERC | CZ10 | 0.569 | rec
2020 | SCE | Any | ERC | CZ10 | 0.312 | new
2020 | SCE | SCE | ERC | CZ13 | 2.284 | old
2020 | SCE | SCE | ERC | CZ13 | 0.624 | ex
2020 | SCE | SCE | ERC | CZ13 | 0.125 | rec
2020 | SCE | SCE | ERC | CZ14 | 2.86 | old
2020 | SCE | SCE | ERC | CZ14 | 0.85 | ex
2020 | SCE | SCE | ERC | CZ14 | 0.129 | rec
2020 | SCE | Any | ERC | CZ14 | 0.065 | new
2020 | SCE | SCE | ERC | CZ15 | 0.93 | old
2020 | SCE | SCE | ERC | CZ15 | 0.34 | ex
2020 | SCE | SCE | ERC | CZ15 | 0.051 | rec
2020 | SCE | Any | ERC | CZ15 | 0.027 | new
2020 | SCE | SCE | ERC | CZ16 | 1.313 | old
2020 | SCE | SCE | ERC | CZ16 | 0.422 | ex
2020 | SCE | SCE | ERC | CZ16 | 0.067 | rec
2020 | SCE | SCE | ESe | CZ05 | 0.062 | old
2020 | SCE | SCE | ESe | CZ05 | 0.007 | ex
2020 | SCE | SCE | ESe | CZ05 | 0.002 | rec
2020 | SCE | SCE | ESe | CZ06 | 10.902 | old
2020 | SCE | SCE | ESe | CZ06 | 1.241 | ex
2020 | SCE | SCE | ESe | CZ06 | 0.204 | rec
2020 | SCE | Any | ESe | CZ06 | 0.111 | new
2020 | SCE | SCE | ESe | CZ08 | 18.927 | old
2020 | SCE | SCE | ESe | CZ08 | 2.23 | ex
2020 | SCE | SCE | ESe | CZ08 | 0.363 | rec
2020 | SCE | Any | ESe | CZ08 | 0.197 | new
2020 | SCE | SCE | ESe | CZ09 | 9.851 | old
2020 | SCE | SCE | ESe | CZ09 | 1.305 | ex
2020 | SCE | SCE | ESe | CZ09 | 0.204 | rec
2020 | SCE | Any | ESe | CZ09 | 0.14 | new
2020 | SCE | SCE | ESe | CZ10 | 10.428 | old
2020 | SCE | SCE | ESe | CZ10 | 3.815 | ex
2020 | SCE | SCE | ESe | CZ10 | 0.569 | rec
2020 | SCE | Any | ESe | CZ10 | 0.312 | new
2020 | SCE | SCE | ESe | CZ13 | 2.284 | old
2020 | SCE | SCE | ESe | CZ13 | 0.624 | ex
2020 | SCE | SCE | ESe | CZ13 | 0.125 | rec
2020 | SCE | SCE | ESe | CZ14 | 2.86 | old
2020 | SCE | SCE | ESe | CZ14 | 0.85 | ex
2020 | SCE | SCE | ESe | CZ14 | 0.129 | rec
2020 | SCE | Any | ESe | CZ14 | 0.065 | new
2020 | SCE | SCE | ESe | CZ15 | 0.93 | old
2020 | SCE | SCE | ESe | CZ15 | 0.34 | ex
2020 | SCE | SCE | ESe | CZ15 | 0.051 | rec
2020 | SCE | Any | ESe | CZ15 | 0.027 | new
2020 | SCE | SCE | ESe | CZ16 | 1.313 | old
2020 | SCE | SCE | ESe | CZ16 | 0.422 | ex
2020 | SCE | SCE | ESe | CZ16 | 0.067 | rec
2020 | SCE | SCE | EUD | CZ05 | 0.014 | old
2020 | SCE | SCE | EUD | CZ05 | 0.004 | ex
2020 | SCE | SCE | EUD | CZ05 | 0.002 | rec
2020 | SCE | SCE | EUD | CZ06 | 11.375 | old
2020 | SCE | SCE | EUD | CZ06 | 2.175 | ex
2020 | SCE | SCE | EUD | CZ06 | 0.435 | rec
2020 | SCE | Any | EUD | CZ06 | 0.228 | new
2020 | SCE | SCE | EUD | CZ08 | 18.447 | old
2020 | SCE | SCE | EUD | CZ08 | 3.438 | ex
2020 | SCE | SCE | EUD | CZ08 | 0.689 | rec
2020 | SCE | Any | EUD | CZ08 | 0.363 | new
2020 | SCE | SCE | EUD | CZ09 | 3.959 | old
2020 | SCE | SCE | EUD | CZ09 | 0.895 | ex
2020 | SCE | SCE | EUD | CZ09 | 0.176 | rec
2020 | SCE | Any | EUD | CZ09 | 0.163 | new
2020 | SCE | SCE | EUD | CZ10 | 4.501 | old
2020 | SCE | SCE | EUD | CZ10 | 2.169 | ex
2020 | SCE | SCE | EUD | CZ10 | 0.421 | rec
2020 | SCE | Any | EUD | CZ10 | 0.247 | new
2020 | SCE | SCE | EUD | CZ13 | 0.874 | old
2020 | SCE | SCE | EUD | CZ13 | 0.516 | ex
2020 | SCE | SCE | EUD | CZ13 | 0.112 | rec
2020 | SCE | SCE | EUD | CZ14 | 1.617 | old
2020 | SCE | SCE | EUD | CZ14 | 0.724 | ex
2020 | SCE | SCE | EUD | CZ14 | 0.141 | rec
2020 | SCE | Any | EUD | CZ14 | 0.071 | new
2020 | SCE | SCE | EUD | CZ15 | 1.31 | old
2020 | SCE | SCE | EUD | CZ15 | 0.632 | ex
2020 | SCE | SCE | EUD | CZ15 | 0.123 | rec
2020 | SCE | Any | EUD | CZ15 | 0.062 | new
2020 | SCE | SCE | EUD | CZ16 | 2.926 | old
2020 | SCE | SCE | EUD | CZ16 | 1.415 | ex
2020 | SCE | SCE | EUD | CZ16 | 0.277 | rec
2020 | SCE | SCE | EUn | CZ05 | 0.014 | old
2020 | SCE | SCE | EUn | CZ05 | 0.004 | ex
2020 | SCE | SCE | EUn | CZ05 | 0.002 | rec
2020 | SCE | SCE | EUn | CZ06 | 11.375 | old
2020 | SCE | SCE | EUn | CZ06 | 2.175 | ex
2020 | SCE | SCE | EUn | CZ06 | 0.435 | rec
2020 | SCE | Any | EUn | CZ06 | 0.228 | new
2020 | SCE | SCE | EUn | CZ08 | 18.447 | old
2020 | SCE | SCE | EUn | CZ08 | 3.438 | ex
2020 | SCE | SCE | EUn | CZ08 | 0.689 | rec
2020 | SCE | Any | EUn | CZ08 | 0.363 | new
2020 | SCE | SCE | EUn | CZ09 | 3.959 | old
2020 | SCE | SCE | EUn | CZ09 | 0.895 | ex
2020 | SCE | SCE | EUn | CZ09 | 0.176 | rec
2020 | SCE | Any | EUn | CZ09 | 0.163 | new
2020 | SCE | SCE | EUn | CZ10 | 4.501 | old
2020 | SCE | SCE | EUn | CZ10 | 2.169 | ex
2020 | SCE | SCE | EUn | CZ10 | 0.421 | rec
2020 | SCE | Any | EUn | CZ10 | 0.247 | new
2020 | SCE | SCE | EUn | CZ13 | 0.874 | old
2020 | SCE | SCE | EUn | CZ13 | 0.516 | ex
2020 | SCE | SCE | EUn | CZ13 | 0.112 | rec
2020 | SCE | SCE | EUn | CZ14 | 1.617 | old
2020 | SCE | SCE | EUn | CZ14 | 0.724 | ex
2020 | SCE | SCE | EUn | CZ14 | 0.141 | rec
2020 | SCE | Any | EUn | CZ14 | 0.071 | new
2020 | SCE | SCE | EUn | CZ15 | 1.31 | old
2020 | SCE | SCE | EUn | CZ15 | 0.632 | ex
2020 | SCE | SCE | EUn | CZ15 | 0.123 | rec
2020 | SCE | Any | EUn | CZ15 | 0.062 | new
2020 | SCE | SCE | EUn | CZ16 | 2.926 | old
2020 | SCE | SCE | EUn | CZ16 | 1.415 | ex
2020 | SCE | SCE | EUn | CZ16 | 0.277 | rec
2020 | SCE | SCE | Gro | CZ05 | 0.405 | old
2020 | SCE | SCE | Gro | CZ05 | 0.086 | ex
2020 | SCE | SCE | Gro | CZ05 | 0.02 | rec
2020 | SCE | SCE | Gro | CZ06 | 20.222 | old
2020 | SCE | SCE | Gro | CZ06 | 4.329 | ex
2020 | SCE | SCE | Gro | CZ06 | 1.004 | rec
2020 | SCE | Any | Gro | CZ06 | 0.558 | new
2020 | SCE | SCE | Gro | CZ08 | 29.653 | old
2020 | SCE | SCE | Gro | CZ08 | 6.398 | ex
2020 | SCE | SCE | Gro | CZ08 | 1.481 | rec
2020 | SCE | Any | Gro | CZ08 | 0.809 | new
2020 | SCE | SCE | Gro | CZ09 | 13.584 | old
2020 | SCE | SCE | Gro | CZ09 | 3.051 | ex
2020 | SCE | SCE | Gro | CZ09 | 0.699 | rec
2020 | SCE | Any | Gro | CZ09 | 0.59 | new
2020 | SCE | SCE | Gro | CZ10 | 18.551 | old
2020 | SCE | SCE | Gro | CZ10 | 8.729 | ex
2020 | SCE | SCE | Gro | CZ10 | 2.001 | rec
2020 | SCE | Any | Gro | CZ10 | 1.122 | new
2020 | SCE | SCE | Gro | CZ13 | 2.833 | old
2020 | SCE | SCE | Gro | CZ13 | 1.069 | ex
2020 | SCE | SCE | Gro | CZ13 | 0.25 | rec
2020 | SCE | SCE | Gro | CZ14 | 4.572 | old
2020 | SCE | SCE | Gro | CZ14 | 1.925 | ex
2020 | SCE | SCE | Gro | CZ14 | 0.441 | rec
2020 | SCE | Any | Gro | CZ14 | 0.222 | new
2020 | SCE | SCE | Gro | CZ15 | 2.609 | old
2020 | SCE | SCE | Gro | CZ15 | 1.227 | ex
2020 | SCE | SCE | Gro | CZ15 | 0.281 | rec
2020 | SCE | Any | Gro | CZ15 | 0.141 | new
2020 | SCE | SCE | Gro | CZ16 | 1.837 | old
2020 | SCE | SCE | Gro | CZ16 | 0.759 | ex
2020 | SCE | SCE | Gro | CZ16 | 0.175 | rec
2020 | SCE | SCE | HGR | CZ05 | 0.137 | old
2020 | SCE | SCE | HGR | CZ05 | 0.021 | ex
2020 | SCE | SCE | HGR | CZ05 | 0.004 | rec
2020 | SCE | SCE | HGR | CZ06 | 16.006 | old
2020 | SCE | SCE | HGR | CZ06 | 2.464 | ex
2020 | SCE | SCE | HGR | CZ06 | 0.48 | rec
2020 | SCE | Any | HGR | CZ06 | 0.28 | new
2020 | SCE | SCE | HGR | CZ08 | 10.317 | old
2020 | SCE | SCE | HGR | CZ08 | 1.576 | ex
2020 | SCE | SCE | HGR | CZ08 | 0.303 | rec
2020 | SCE | Any | HGR | CZ08 | 0.195 | new
2020 | SCE | SCE | HGR | CZ09 | 7.431 | old
2020 | SCE | SCE | HGR | CZ09 | 1.299 | ex
2020 | SCE | SCE | HGR | CZ09 | 0.301 | rec
2020 | SCE | Any | HGR | CZ09 | 0.29 | new
2020 | SCE | SCE | HGR | CZ10 | 2.175 | old
2020 | SCE | SCE | HGR | CZ10 | 0.986 | ex
2020 | SCE | SCE | HGR | CZ10 | 0.215 | rec
2020 | SCE | Any | HGR | CZ10 | 0.145 | new
2020 | SCE | SCE | HGR | CZ13 | 0.474 | old
2020 | SCE | SCE | HGR | CZ13 | 0.113 | ex
2020 | SCE | SCE | HGR | CZ13 | 0.03 | rec
2020 | SCE | SCE | HGR | CZ14 | 1.137 | old
2020 | SCE | SCE | HGR | CZ14 | 0.405 | ex
2020 | SCE | SCE | HGR | CZ14 | 0.097 | rec
2020 | SCE | Any | HGR | CZ14 | 0.052 | new
2020 | SCE | SCE | HGR | CZ15 | 5.563 | old
2020 | SCE | SCE | HGR | CZ15 | 2.519 | ex
2020 | SCE | SCE | HGR | CZ15 | 0.549 | rec
2020 | SCE | Any | HGR | CZ15 | 0.278 | new
2020 | SCE | SCE | HGR | CZ16 | 1.653 | old
2020 | SCE | SCE | HGR | CZ16 | 0.422 | ex
2020 | SCE | SCE | HGR | CZ16 | 0.116 | rec
2020 | SCE | SCE | Hsp | CZ05 | 0.846 | old
2020 | SCE | SCE | Hsp | CZ05 | 0.152 | ex
2020 | SCE | SCE | Hsp | CZ05 | 0.025 | rec
2020 | SCE | SCE | Hsp | CZ06 | 12.571 | old
2020 | SCE | SCE | Hsp | CZ06 | 2.322 | ex
2020 | SCE | SCE | Hsp | CZ06 | 0.392 | rec
2020 | SCE | Any | Hsp | CZ06 | 0.214 | new
2020 | SCE | SCE | Hsp | CZ08 | 13.377 | old
2020 | SCE | SCE | Hsp | CZ08 | 2.496 | ex
2020 | SCE | SCE | Hsp | CZ08 | 0.425 | rec
2020 | SCE | Any | Hsp | CZ08 | 0.247 | new
2020 | SCE | SCE | Hsp | CZ09 | 6.611 | old
2020 | SCE | SCE | Hsp | CZ09 | 1.43 | ex
2020 | SCE | SCE | Hsp | CZ09 | 0.271 | rec
2020 | SCE | Any | Hsp | CZ09 | 0.255 | new
2020 | SCE | SCE | Hsp | CZ10 | 6.854 | old
2020 | SCE | SCE | Hsp | CZ10 | 1.862 | ex
2020 | SCE | SCE | Hsp | CZ10 | 0.463 | rec
2020 | SCE | Any | Hsp | CZ10 | 0.247 | new
2020 | SCE | SCE | Hsp | CZ13 | 1.371 | old
2020 | SCE | SCE | Hsp | CZ13 | 0.272 | ex
2020 | SCE | SCE | Hsp | CZ13 | 0.071 | rec
2020 | SCE | SCE | Hsp | CZ14 | 1.231 | old
2020 | SCE | SCE | Hsp | CZ14 | 0.317 | ex
2020 | SCE | SCE | Hsp | CZ14 | 0.075 | rec
2020 | SCE | Any | Hsp | CZ14 | 0.039 | new
2020 | SCE | SCE | Hsp | CZ15 | 1.419 | old
2020 | SCE | SCE | Hsp | CZ15 | 0.386 | ex
2020 | SCE | SCE | Hsp | CZ15 | 0.096 | rec
2020 | SCE | Any | Hsp | CZ15 | 0.048 | new
2020 | SCE | SCE | Hsp | CZ16 | 0.914 | old
2020 | SCE | SCE | Hsp | CZ16 | 0.231 | ex
2020 | SCE | SCE | Hsp | CZ16 | 0.057 | rec
2020 | SCE | SCE | Htl | CZ05 | 0.137 | old
2020 | SCE | SCE | Htl | CZ05 | 0.021 | ex
2020 | SCE | SCE | Htl | CZ05 | 0.004 | rec
2020 | SCE | SCE | Htl | CZ06 | 16.006 | old
2020 | SCE | SCE | Htl | CZ06 | 2.464 | ex
2020 | SCE | SCE | Htl | CZ06 | 0.48 | rec
2020 | SCE | Any | Htl | CZ06 | 0.28 | new
2020 | SCE | SCE | Htl | CZ08 | 10.317 | old
2020 | SCE | SCE | Htl | CZ08 | 1.576 | ex
2020 | SCE | SCE | Htl | CZ08 | 0.303 | rec
2020 | SCE | Any | Htl | CZ08 | 0.195 | new
2020 | SCE | SCE | Htl | CZ09 | 7.431 | old
2020 | SCE | SCE | Htl | CZ09 | 1.299 | ex
2020 | SCE | SCE | Htl | CZ09 | 0.301 | rec
2020 | SCE | Any | Htl | CZ09 | 0.29 | new
2020 | SCE | SCE | Htl | CZ10 | 2.175 | old
2020 | SCE | SCE | Htl | CZ10 | 0.986 | ex
2020 | SCE | SCE | Htl | CZ10 | 0.215 | rec
2020 | SCE | Any | Htl | CZ10 | 0.145 | new
2020 | SCE | SCE | Htl | CZ13 | 0.474 | old
2020 | SCE | SCE | Htl | CZ13 | 0.113 | ex
2020 | SCE | SCE | Htl | CZ13 | 0.03 | rec
2020 | SCE | SCE | Htl | CZ14 | 1.137 | old
2020 | SCE | SCE | Htl | CZ14 | 0.405 | ex
2020 | SCE | SCE | Htl | CZ14 | 0.097 | rec
2020 | SCE | Any | Htl | CZ14 | 0.052 | new
2020 | SCE | SCE | Htl | CZ15 | 5.563 | old
2020 | SCE | SCE | Htl | CZ15 | 2.519 | ex
2020 | SCE | SCE | Htl | CZ15 | 0.549 | rec
2020 | SCE | Any | Htl | CZ15 | 0.278 | new
2020 | SCE | SCE | Htl | CZ16 | 1.653 | old
2020 | SCE | SCE | Htl | CZ16 | 0.422 | ex
2020 | SCE | SCE | Htl | CZ16 | 0.116 | rec
2020 | SCE | SCE | MBT | CZ05 | 0.387 | old
2020 | SCE | SCE | MBT | CZ05 | 0.077 | ex
2020 | SCE | SCE | MBT | CZ05 | 0.017 | rec
2020 | SCE | SCE | MBT | CZ06 | 32.51 | old
2020 | SCE | SCE | MBT | CZ06 | 6.365 | ex
2020 | SCE | SCE | MBT | CZ06 | 1.467 | rec
2020 | SCE | Any | MBT | CZ06 | 0.781 | new
2020 | SCE | SCE | MBT | CZ08 | 47.444 | old
2020 | SCE | SCE | MBT | CZ08 | 9.289 | ex
2020 | SCE | SCE | MBT | CZ08 | 2.135 | rec
2020 | SCE | Any | MBT | CZ08 | 1.142 | new
2020 | SCE | SCE | MBT | CZ09 | 22.149 | old
2020 | SCE | SCE | MBT | CZ09 | 4.334 | ex
2020 | SCE | SCE | MBT | CZ09 | 0.967 | rec
2020 | SCE | Any | MBT | CZ09 | 0.74 | new
2020 | SCE | SCE | MBT | CZ10 | 18.966 | old
2020 | SCE | SCE | MBT | CZ10 | 13.368 | ex
2020 | SCE | SCE | MBT | CZ10 | 2.939 | rec
2020 | SCE | Any | MBT | CZ10 | 1.607 | new
2020 | SCE | SCE | MBT | CZ13 | 2.887 | old
2020 | SCE | SCE | MBT | CZ13 | 0.962 | ex
2020 | SCE | SCE | MBT | CZ13 | 0.223 | rec
2020 | SCE | SCE | MBT | CZ14 | 4.946 | old
2020 | SCE | SCE | MBT | CZ14 | 2.213 | ex
2020 | SCE | SCE | MBT | CZ14 | 0.486 | rec
2020 | SCE | Any | MBT | CZ14 | 0.248 | new
2020 | SCE | SCE | MBT | CZ15 | 6.866 | old
2020 | SCE | SCE | MBT | CZ15 | 4.84 | ex
2020 | SCE | SCE | MBT | CZ15 | 1.064 | rec
2020 | SCE | Any | MBT | CZ15 | 0.533 | new
2020 | SCE | SCE | MBT | CZ16 | 2.849 | old
2020 | SCE | SCE | MBT | CZ16 | 1.377 | ex
2020 | SCE | SCE | MBT | CZ16 | 0.307 | rec
2020 | SCE | SCE | MLI | CZ05 | 0.387 | old
2020 | SCE | SCE | MLI | CZ05 | 0.077 | ex
2020 | SCE | SCE | MLI | CZ05 | 0.017 | rec
2020 | SCE | SCE | MLI | CZ06 | 32.51 | old
2020 | SCE | SCE | MLI | CZ06 | 6.365 | ex
2020 | SCE | SCE | MLI | CZ06 | 1.467 | rec
2020 | SCE | Any | MLI | CZ06 | 0.781 | new
2020 | SCE | SCE | MLI | CZ08 | 47.444 | old
2020 | SCE | SCE | MLI | CZ08 | 9.289 | ex
2020 | SCE | SCE | MLI | CZ08 | 2.135 | rec
2020 | SCE | Any | MLI | CZ08 | 1.142 | new
2020 | SCE | SCE | MLI | CZ09 | 22.149 | old
2020 | SCE | SCE | MLI | CZ09 | 4.334 | ex
2020 | SCE | SCE | MLI | CZ09 | 0.967 | rec
2020 | SCE | Any | MLI | CZ09 | 0.74 | new
2020 | SCE | SCE | MLI | CZ10 | 18.966 | old
2020 | SCE | SCE | MLI | CZ10 | 13.368 | ex
2020 | SCE | SCE | MLI | CZ10 | 2.939 | rec
2020 | SCE | Any | MLI | CZ10 | 1.607 | new
2020 | SCE | SCE | MLI | CZ13 | 2.887 | old
2020 | SCE | SCE | MLI | CZ13 | 0.962 | ex
2020 | SCE | SCE | MLI | CZ13 | 0.223 | rec
2020 | SCE | SCE | MLI | CZ14 | 4.946 | old
2020 | SCE | SCE | MLI | CZ14 | 2.213 | ex
2020 | SCE | SCE | MLI | CZ14 | 0.486 | rec
2020 | SCE | Any | MLI | CZ14 | 0.248 | new
2020 | SCE | SCE | MLI | CZ15 | 6.866 | old
2020 | SCE | SCE | MLI | CZ15 | 4.84 | ex
2020 | SCE | SCE | MLI | CZ15 | 1.064 | rec
2020 | SCE | Any | MLI | CZ15 | 0.533 | new
2020 | SCE | SCE | MLI | CZ16 | 2.849 | old
2020 | SCE | SCE | MLI | CZ16 | 1.377 | ex
2020 | SCE | SCE | MLI | CZ16 | 0.307 | rec
2020 | SCE | SCE | Mtl | CZ05 | 0.137 | old
2020 | SCE | SCE | Mtl | CZ05 | 0.021 | ex
2020 | SCE | SCE | Mtl | CZ05 | 0.004 | rec
2020 | SCE | SCE | Mtl | CZ06 | 16.006 | old
2020 | SCE | SCE | Mtl | CZ06 | 2.464 | ex
2020 | SCE | SCE | Mtl | CZ06 | 0.48 | rec
2020 | SCE | Any | Mtl | CZ06 | 0.28 | new
2020 | SCE | SCE | Mtl | CZ08 | 10.317 | old
2020 | SCE | SCE | Mtl | CZ08 | 1.576 | ex
2020 | SCE | SCE | Mtl | CZ08 | 0.303 | rec
2020 | SCE | Any | Mtl | CZ08 | 0.195 | new
2020 | SCE | SCE | Mtl | CZ09 | 7.431 | old
2020 | SCE | SCE | Mtl | CZ09 | 1.299 | ex
2020 | SCE | SCE | Mtl | CZ09 | 0.301 | rec
2020 | SCE | Any | Mtl | CZ09 | 0.29 | new
2020 | SCE | SCE | Mtl | CZ10 | 2.175 | old
2020 | SCE | SCE | Mtl | CZ10 | 0.986 | ex
2020 | SCE | SCE | Mtl | CZ10 | 0.215 | rec
2020 | SCE | Any | Mtl | CZ10 | 0.145 | new
2020 | SCE | SCE | Mtl | CZ13 | 0.474 | old
2020 | SCE | SCE | Mtl | CZ13 | 0.113 | ex
2020 | SCE | SCE | Mtl | CZ13 | 0.03 | rec
2020 | SCE | SCE | Mtl | CZ14 | 1.137 | old
2020 | SCE | SCE | Mtl | CZ14 | 0.405 | ex
2020 | SCE | SCE | Mtl | CZ14 | 0.097 | rec
2020 | SCE | Any | Mtl | CZ14 | 0.052 | new
2020 | SCE | SCE | Mtl | CZ15 | 5.563 | old
2020 | SCE | SCE | Mtl | CZ15 | 2.519 | ex
2020 | SCE | SCE | Mtl | CZ15 | 0.549 | rec
2020 | SCE | Any | Mtl | CZ15 | 0.278 | new
2020 | SCE | SCE | Mtl | CZ16 | 1.653 | old
2020 | SCE | SCE | Mtl | CZ16 | 0.422 | ex
2020 | SCE | SCE | Mtl | CZ16 | 0.116 | rec
2020 | SCE | SCE | Nrs | CZ05 | 0.846 | old
2020 | SCE | SCE | Nrs | CZ05 | 0.152 | ex
2020 | SCE | SCE | Nrs | CZ05 | 0.025 | rec
2020 | SCE | SCE | Nrs | CZ06 | 12.571 | old
2020 | SCE | SCE | Nrs | CZ06 | 2.322 | ex
2020 | SCE | SCE | Nrs | CZ06 | 0.392 | rec
2020 | SCE | Any | Nrs | CZ06 | 0.214 | new
2020 | SCE | SCE | Nrs | CZ08 | 13.377 | old
2020 | SCE | SCE | Nrs | CZ08 | 2.496 | ex
2020 | SCE | SCE | Nrs | CZ08 | 0.425 | rec
2020 | SCE | Any | Nrs | CZ08 | 0.247 | new
2020 | SCE | SCE | Nrs | CZ09 | 6.611 | old
2020 | SCE | SCE | Nrs | CZ09 | 1.43 | ex
2020 | SCE | SCE | Nrs | CZ09 | 0.271 | rec
2020 | SCE | Any | Nrs | CZ09 | 0.255 | new
2020 | SCE | SCE | Nrs | CZ10 | 6.854 | old
2020 | SCE | SCE | Nrs | CZ10 | 1.862 | ex
2020 | SCE | SCE | Nrs | CZ10 | 0.463 | rec
2020 | SCE | Any | Nrs | CZ10 | 0.247 | new
2020 | SCE | SCE | Nrs | CZ13 | 1.371 | old
2020 | SCE | SCE | Nrs | CZ13 | 0.272 | ex
2020 | SCE | SCE | Nrs | CZ13 | 0.071 | rec
2020 | SCE | SCE | Nrs | CZ14 | 1.231 | old
2020 | SCE | SCE | Nrs | CZ14 | 0.317 | ex
2020 | SCE | SCE | Nrs | CZ14 | 0.075 | rec
2020 | SCE | Any | Nrs | CZ14 | 0.039 | new
2020 | SCE | SCE | Nrs | CZ15 | 1.419 | old
2020 | SCE | SCE | Nrs | CZ15 | 0.386 | ex
2020 | SCE | SCE | Nrs | CZ15 | 0.096 | rec
2020 | SCE | Any | Nrs | CZ15 | 0.048 | new
2020 | SCE | SCE | Nrs | CZ16 | 0.914 | old
2020 | SCE | SCE | Nrs | CZ16 | 0.231 | ex
2020 | SCE | SCE | Nrs | CZ16 | 0.057 | rec
2020 | SCE | SCE | OfL | CZ05 | 1.225 | old
2020 | SCE | SCE | OfL | CZ05 | 0.12 | ex
2020 | SCE | SCE | OfL | CZ05 | 0.021 | rec
2020 | SCE | SCE | OfL | CZ06 | 109.432 | old
2020 | SCE | SCE | OfL | CZ06 | 11.459 | ex
2020 | SCE | SCE | OfL | CZ06 | 2.16 | rec
2020 | SCE | Any | OfL | CZ06 | 1.273 | new
2020 | SCE | SCE | OfL | CZ08 | 132.939 | old
2020 | SCE | SCE | OfL | CZ08 | 14.09 | ex
2020 | SCE | SCE | OfL | CZ08 | 2.691 | rec
2020 | SCE | Any | OfL | CZ08 | 1.712 | new
2020 | SCE | SCE | OfL | CZ09 | 79.468 | old
2020 | SCE | SCE | OfL | CZ09 | 10.412 | ex
2020 | SCE | SCE | OfL | CZ09 | 2.389 | rec
2020 | SCE | Any | OfL | CZ09 | 2.078 | new
2020 | SCE | SCE | OfL | CZ10 | 25.533 | old
2020 | SCE | SCE | OfL | CZ10 | 10.408 | ex
2020 | SCE | SCE | OfL | CZ10 | 2.127 | rec
2020 | SCE | Any | OfL | CZ10 | 1.227 | new
2020 | SCE | SCE | OfL | CZ13 | 3.293 | old
2020 | SCE | SCE | OfL | CZ13 | 0.706 | ex
2020 | SCE | SCE | OfL | CZ13 | 0.196 | rec
2020 | SCE | SCE | OfL | CZ14 | 6.448 | old
2020 | SCE | SCE | OfL | CZ14 | 1.707 | ex
2020 | SCE | SCE | OfL | CZ14 | 0.381 | rec
2020 | SCE | Any | OfL | CZ14 | 0.194 | new
2020 | SCE | SCE | OfL | CZ15 | 6.977 | old
2020 | SCE | SCE | OfL | CZ15 | 2.844 | ex
2020 | SCE | SCE | OfL | CZ15 | 0.581 | rec
2020 | SCE | Any | OfL | CZ15 | 0.291 | new
2020 | SCE | SCE | OfL | CZ16 | 3.012 | old
2020 | SCE | SCE | OfL | CZ16 | 0.736 | ex
2020 | SCE | SCE | OfL | CZ16 | 0.172 | rec
2020 | SCE | SCE | OfS | CZ05 | 0.285 | old
2020 | SCE | SCE | OfS | CZ05 | 0.046 | ex
2020 | SCE | SCE | OfS | CZ05 | 0.012 | rec
2020 | SCE | SCE | OfS | CZ06 | 24.662 | old
2020 | SCE | SCE | OfS | CZ06 | 4.067 | ex
2020 | SCE | SCE | OfS | CZ06 | 1.039 | rec
2020 | SCE | Any | OfS | CZ06 | 0.553 | new
2020 | SCE | SCE | OfS | CZ08 | 29.77 | old
2020 | SCE | SCE | OfS | CZ08 | 4.921 | ex
2020 | SCE | SCE | OfS | CZ08 | 1.254 | rec
2020 | SCE | Any | OfS | CZ08 | 0.685 | new
2020 | SCE | SCE | OfS | CZ09 | 15.6 | old
2020 | SCE | SCE | OfS | CZ09 | 2.721 | ex
2020 | SCE | SCE | OfS | CZ09 | 0.656 | rec
2020 | SCE | Any | OfS | CZ09 | 0.526 | new
2020 | SCE | SCE | OfS | CZ10 | 20.244 | old
2020 | SCE | SCE | OfS | CZ10 | 7.388 | ex
2020 | SCE | SCE | OfS | CZ10 | 1.581 | rec
2020 | SCE | Any | OfS | CZ10 | 0.865 | new
2020 | SCE | SCE | OfS | CZ13 | 5.081 | old
2020 | SCE | SCE | OfS | CZ13 | 1.055 | ex
2020 | SCE | SCE | OfS | CZ13 | 0.237 | rec
2020 | SCE | SCE | OfS | CZ14 | 2.955 | old
2020 | SCE | SCE | OfS | CZ14 | 0.941 | ex
2020 | SCE | SCE | OfS | CZ14 | 0.203 | rec
2020 | SCE | Any | OfS | CZ14 | 0.104 | new
2020 | SCE | SCE | OfS | CZ15 | 5.532 | old
2020 | SCE | SCE | OfS | CZ15 | 2.019 | ex
2020 | SCE | SCE | OfS | CZ15 | 0.432 | rec
2020 | SCE | Any | OfS | CZ15 | 0.217 | new
2020 | SCE | SCE | OfS | CZ16 | 1.728 | old
2020 | SCE | SCE | OfS | CZ16 | 0.471 | ex
2020 | SCE | SCE | OfS | CZ16 | 0.103 | rec
2020 | SCE | SCE | RFF | CZ05 | 0.118 | old
2020 | SCE | SCE | RFF | CZ05 | 0.027 | ex
2020 | SCE | SCE | RFF | CZ05 | 0.007 | rec
2020 | SCE | SCE | RFF | CZ06 | 8.122 | old
2020 | SCE | SCE | RFF | CZ06 | 1.902 | ex
2020 | SCE | SCE | RFF | CZ06 | 0.489 | rec
2020 | SCE | Any | RFF | CZ06 | 0.258 | new
2020 | SCE | SCE | RFF | CZ08 | 9.333 | old
2020 | SCE | SCE | RFF | CZ08 | 2.182 | ex
2020 | SCE | SCE | RFF | CZ08 | 0.552 | rec
2020 | SCE | Any | RFF | CZ08 | 0.3 | new
2020 | SCE | SCE | RFF | CZ09 | 5.181 | old
2020 | SCE | SCE | RFF | CZ09 | 1.199 | ex
2020 | SCE | SCE | RFF | CZ09 | 0.276 | rec
2020 | SCE | Any | RFF | CZ09 | 0.207 | new
2020 | SCE | SCE | RFF | CZ10 | 6.563 | old
2020 | SCE | SCE | RFF | CZ10 | 3.66 | ex
2020 | SCE | SCE | RFF | CZ10 | 0.643 | rec
2020 | SCE | Any | RFF | CZ10 | 0.338 | new
2020 | SCE | SCE | RFF | CZ13 | 0.599 | old
2020 | SCE | SCE | RFF | CZ13 | 0.209 | ex
2020 | SCE | SCE | RFF | CZ13 | 0.044 | rec
2020 | SCE | SCE | RFF | CZ14 | 1.437 | old
2020 | SCE | SCE | RFF | CZ14 | 0.686 | ex
2020 | SCE | SCE | RFF | CZ14 | 0.123 | rec
2020 | SCE | Any | RFF | CZ14 | 0.063 | new
2020 | SCE | SCE | RFF | CZ15 | 1.284 | old
2020 | SCE | SCE | RFF | CZ15 | 0.716 | ex
2020 | SCE | SCE | RFF | CZ15 | 0.125 | rec
2020 | SCE | Any | RFF | CZ15 | 0.063 | new
2020 | SCE | SCE | RFF | CZ16 | 0.563 | old
2020 | SCE | SCE | RFF | CZ16 | 0.256 | ex
2020 | SCE | SCE | RFF | CZ16 | 0.047 | rec
2020 | SCE | SCE | RSD | CZ05 | 0.118 | old
2020 | SCE | SCE | RSD | CZ05 | 0.027 | ex
2020 | SCE | SCE | RSD | CZ05 | 0.007 | rec
2020 | SCE | SCE | RSD | CZ06 | 8.122 | old
2020 | SCE | SCE | RSD | CZ06 | 1.902 | ex
2020 | SCE | SCE | RSD | CZ06 | 0.489 | rec
2020 | SCE | Any | RSD | CZ06 | 0.258 | new
2020 | SCE | SCE | RSD | CZ08 | 9.333 | old
2020 | SCE | SCE | RSD | CZ08 | 2.182 | ex
2020 | SCE | SCE | RSD | CZ08 | 0.552 | rec
2020 | SCE | Any | RSD | CZ08 | 0.3 | new
2020 | SCE | SCE | RSD | CZ09 | 5.181 | old
2020 | SCE | SCE | RSD | CZ09 | 1.199 | ex
2020 | SCE | SCE | RSD | CZ09 | 0.276 | rec
2020 | SCE | Any | RSD | CZ09 | 0.207 | new
2020 | SCE | SCE | RSD | CZ10 | 6.563 | old
2020 | SCE | SCE | RSD | CZ10 | 3.66 | ex
2020 | SCE | SCE | RSD | CZ10 | 0.643 | rec
2020 | SCE | Any | RSD | CZ10 | 0.338 | new
2020 | SCE | SCE | RSD | CZ13 | 0.599 | old
2020 | SCE | SCE | RSD | CZ13 | 0.209 | ex
2020 | SCE | SCE | RSD | CZ13 | 0.044 | rec
2020 | SCE | SCE | RSD | CZ14 | 1.437 | old
2020 | SCE | SCE | RSD | CZ14 | 0.686 | ex
2020 | SCE | SCE | RSD | CZ14 | 0.123 | rec
2020 | SCE | Any | RSD | CZ14 | 0.063 | new
2020 | SCE | SCE | RSD | CZ15 | 1.284 | old
2020 | SCE | SCE | RSD | CZ15 | 0.716 | ex
2020 | SCE | SCE | RSD | CZ15 | 0.125 | rec
2020 | SCE | Any | RSD | CZ15 | 0.063 | new
2020 | SCE | SCE | RSD | CZ16 | 0.563 | old
2020 | SCE | SCE | RSD | CZ16 | 0.256 | ex
2020 | SCE | SCE | RSD | CZ16 | 0.047 | rec
2020 | SCE | SCE | Rt3 | CZ05 | 0.557 | old
2020 | SCE | SCE | Rt3 | CZ05 | 0.124 | ex
2020 | SCE | SCE | Rt3 | CZ05 | 0.029 | rec
2020 | SCE | SCE | Rt3 | CZ06 | 31.015 | old
2020 | SCE | SCE | Rt3 | CZ06 | 6.932 | ex
2020 | SCE | SCE | Rt3 | CZ06 | 1.611 | rec
2020 | SCE | Any | Rt3 | CZ06 | 0.861 | new
2020 | SCE | SCE | Rt3 | CZ08 | 35.172 | old
2020 | SCE | SCE | Rt3 | CZ08 | 7.981 | ex
2020 | SCE | SCE | Rt3 | CZ08 | 1.845 | rec
2020 | SCE | Any | Rt3 | CZ08 | 1.032 | new
2020 | SCE | SCE | Rt3 | CZ09 | 18.751 | old
2020 | SCE | SCE | Rt3 | CZ09 | 4.496 | ex
2020 | SCE | SCE | Rt3 | CZ09 | 1.021 | rec
2020 | SCE | Any | Rt3 | CZ09 | 0.845 | new
2020 | SCE | SCE | Rt3 | CZ10 | 22.941 | old
2020 | SCE | SCE | Rt3 | CZ10 | 12.825 | ex
2020 | SCE | SCE | Rt3 | CZ10 | 2.777 | rec
2020 | SCE | Any | Rt3 | CZ10 | 1.493 | new
2020 | SCE | SCE | Rt3 | CZ13 | 3.222 | old
2020 | SCE | SCE | Rt3 | CZ13 | 1.314 | ex
2020 | SCE | SCE | Rt3 | CZ13 | 0.305 | rec
2020 | SCE | SCE | Rt3 | CZ14 | 4.584 | old
2020 | SCE | SCE | Rt3 | CZ14 | 1.98 | ex
2020 | SCE | SCE | Rt3 | CZ14 | 0.432 | rec
2020 | SCE | Any | Rt3 | CZ14 | 0.217 | new
2020 | SCE | SCE | Rt3 | CZ15 | 3.204 | old
2020 | SCE | SCE | Rt3 | CZ15 | 1.791 | ex
2020 | SCE | SCE | Rt3 | CZ15 | 0.388 | rec
2020 | SCE | Any | Rt3 | CZ15 | 0.195 | new
2020 | SCE | SCE | Rt3 | CZ16 | 0.946 | old
2020 | SCE | SCE | Rt3 | CZ16 | 0.415 | ex
2020 | SCE | SCE | Rt3 | CZ16 | 0.093 | rec
2020 | SCE | SCE | RtL | CZ05 | 0.557 | old
2020 | SCE | SCE | RtL | CZ05 | 0.124 | ex
2020 | SCE | SCE | RtL | CZ05 | 0.029 | rec
2020 | SCE | SCE | RtL | CZ06 | 31.015 | old
2020 | SCE | SCE | RtL | CZ06 | 6.932 | ex
2020 | SCE | SCE | RtL | CZ06 | 1.611 | rec
2020 | SCE | Any | RtL | CZ06 | 0.861 | new
2020 | SCE | SCE | RtL | CZ08 | 35.172 | old
2020 | SCE | SCE | RtL | CZ08 | 7.981 | ex
2020 | SCE | SCE | RtL | CZ08 | 1.845 | rec
2020 | SCE | Any | RtL | CZ08 | 1.032 | new
2020 | SCE | SCE | RtL | CZ09 | 18.751 | old
2020 | SCE | SCE | RtL | CZ09 | 4.496 | ex
2020 | SCE | SCE | RtL | CZ09 | 1.021 | rec
2020 | SCE | Any | RtL | CZ09 | 0.845 | new
2020 | SCE | SCE | RtL | CZ10 | 22.941 | old
2020 | SCE | SCE | RtL | CZ10 | 12.825 | ex
2020 | SCE | SCE | RtL | CZ10 | 2.777 | rec
2020 | SCE | Any | RtL | CZ10 | 1.493 | new
2020 | SCE | SCE | RtL | CZ13 | 3.222 | old
2020 | SCE | SCE | RtL | CZ13 | 1.314 | ex
2020 | SCE | SCE | RtL | CZ13 | 0.305 | rec
2020 | SCE | SCE | RtL | CZ14 | 4.584 | old
2020 | SCE | SCE | RtL | CZ14 | 1.98 | ex
2020 | SCE | SCE | RtL | CZ14 | 0.432 | rec
2020 | SCE | Any | RtL | CZ14 | 0.217 | new
2020 | SCE | SCE | RtL | CZ15 | 3.204 | old
2020 | SCE | SCE | RtL | CZ15 | 1.791 | ex
2020 | SCE | SCE | RtL | CZ15 | 0.388 | rec
2020 | SCE | Any | RtL | CZ15 | 0.195 | new
2020 | SCE | SCE | RtL | CZ16 | 0.946 | old
2020 | SCE | SCE | RtL | CZ16 | 0.415 | ex
2020 | SCE | SCE | RtL | CZ16 | 0.093 | rec
2020 | SCE | SCE | RtS | CZ05 | 0.557 | old
2020 | SCE | SCE | RtS | CZ05 | 0.124 | ex
2020 | SCE | SCE | RtS | CZ05 | 0.029 | rec
2020 | SCE | SCE | RtS | CZ06 | 31.015 | old
2020 | SCE | SCE | RtS | CZ06 | 6.932 | ex
2020 | SCE | SCE | RtS | CZ06 | 1.611 | rec
2020 | SCE | Any | RtS | CZ06 | 0.861 | new
2020 | SCE | SCE | RtS | CZ08 | 35.172 | old
2020 | SCE | SCE | RtS | CZ08 | 7.981 | ex
2020 | SCE | SCE | RtS | CZ08 | 1.845 | rec
2020 | SCE | Any | RtS | CZ08 | 1.032 | new
2020 | SCE | SCE | RtS | CZ09 | 18.751 | old
2020 | SCE | SCE | RtS | CZ09 | 4.496 | ex
2020 | SCE | SCE | RtS | CZ09 | 1.021 | rec
2020 | SCE | Any | RtS | CZ09 | 0.845 | new
2020 | SCE | SCE | RtS | CZ10 | 22.941 | old
2020 | SCE | SCE | RtS | CZ10 | 12.825 | ex
2020 | SCE | SCE | RtS | CZ10 | 2.777 | rec
2020 | SCE | Any | RtS | CZ10 | 1.493 | new
2020 | SCE | SCE | RtS | CZ13 | 3.222 | old
2020 | SCE | SCE | RtS | CZ13 | 1.314 | ex
2020 | SCE | SCE | RtS | CZ13 | 0.305 | rec
2020 | SCE | SCE | RtS | CZ14 | 4.584 | old
2020 | SCE | SCE | RtS | CZ14 | 1.98 | ex
2020 | SCE | SCE | RtS | CZ14 | 0.432 | rec
2020 | SCE | Any | RtS | CZ14 | 0.217 | new
2020 | SCE | SCE | RtS | CZ15 | 3.204 | old
2020 | SCE | SCE | RtS | CZ15 | 1.791 | ex
2020 | SCE | SCE | RtS | CZ15 | 0.388 | rec
2020 | SCE | Any | RtS | CZ15 | 0.195 | new
2020 | SCE | SCE | RtS | CZ16 | 0.946 | old
2020 | SCE | SCE | RtS | CZ16 | 0.415 | ex
2020 | SCE | SCE | RtS | CZ16 | 0.093 | rec
2020 | SCE | SCE | SCn | CZ05 | 0.029 | old
2020 | SCE | SCE | SCn | CZ05 | 0.006 | ex
2020 | SCE | SCE | SCn | CZ05 | 0.002 | rec
2020 | SCE | SCE | SCn | CZ06 | 24.434 | old
2020 | SCE | SCE | SCn | CZ06 | 5.571 | ex
2020 | SCE | SCE | SCn | CZ06 | 1.155 | rec
2020 | SCE | Any | SCn | CZ06 | 0.645 | new
2020 | SCE | SCE | SCn | CZ08 | 74.094 | old
2020 | SCE | SCE | SCn | CZ08 | 16.496 | ex
2020 | SCE | SCE | SCn | CZ08 | 3.436 | rec
2020 | SCE | Any | SCn | CZ08 | 1.838 | new
2020 | SCE | SCE | SCn | CZ09 | 18.62 | old
2020 | SCE | SCE | SCn | CZ09 | 5.225 | ex
2020 | SCE | SCE | SCn | CZ09 | 1.043 | rec
2020 | SCE | Any | SCn | CZ09 | 0.959 | new
2020 | SCE | SCE | SCn | CZ10 | 39.963 | old
2020 | SCE | SCE | SCn | CZ10 | 47.364 | ex
2020 | SCE | SCE | SCn | CZ10 | 11.108 | rec
2020 | SCE | Any | SCn | CZ10 | 5.673 | new
2020 | SCE | SCE | SCn | CZ13 | 2.365 | old
2020 | SCE | SCE | SCn | CZ13 | 1.585 | ex
2020 | SCE | SCE | SCn | CZ13 | 0.376 | rec
2020 | SCE | SCE | SCn | CZ14 | 1.079 | old
2020 | SCE | SCE | SCn | CZ14 | 0.928 | ex
2020 | SCE | SCE | SCn | CZ14 | 0.215 | rec
2020 | SCE | Any | SCn | CZ14 | 0.109 | new
2020 | SCE | SCE | SCn | CZ15 | 0.735 | old
2020 | SCE | SCE | SCn | CZ15 | 0.87 | ex
2020 | SCE | SCE | SCn | CZ15 | 0.204 | rec
2020 | SCE | Any | SCn | CZ15 | 0.103 | new
2020 | SCE | SCE | SCn | CZ16 | 0.789 | old
2020 | SCE | SCE | SCn | CZ16 | 0.862 | ex
2020 | SCE | SCE | SCn | CZ16 | 0.203 | rec
2020 | SCE | SCE | SUn | CZ05 | 0.029 | old
2020 | SCE | SCE | SUn | CZ05 | 0.006 | ex
2020 | SCE | SCE | SUn | CZ05 | 0.002 | rec
2020 | SCE | SCE | SUn | CZ06 | 24.434 | old
2020 | SCE | SCE | SUn | CZ06 | 5.571 | ex
2020 | SCE | SCE | SUn | CZ06 | 1.155 | rec
2020 | SCE | Any | SUn | CZ06 | 0.645 | new
2020 | SCE | SCE | SUn | CZ08 | 74.094 | old
2020 | SCE | SCE | SUn | CZ08 | 16.496 | ex
2020 | SCE | SCE | SUn | CZ08 | 3.436 | rec
2020 | SCE | Any | SUn | CZ08 | 1.838 | new
2020 | SCE | SCE | SUn | CZ09 | 18.62 | old
2020 | SCE | SCE | SUn | CZ09 | 5.225 | ex
2020 | SCE | SCE | SUn | CZ09 | 1.043 | rec
2020 | SCE | Any | SUn | CZ09 | 0.959 | new
2020 | SCE | SCE | SUn | CZ10 | 39.963 | old
2020 | SCE | SCE | SUn | CZ10 | 47.364 | ex
2020 | SCE | SCE | SUn | CZ10 | 11.108 | rec
2020 | SCE | Any | SUn | CZ10 | 5.673 | new
2020 | SCE | SCE | SUn | CZ13 | 2.365 | old
2020 | SCE | SCE | SUn | CZ13 | 1.585 | ex
2020 | SCE | SCE | SUn | CZ13 | 0.376 | rec
2020 | SCE | SCE | SUn | CZ14 | 1.079 | old
2020 | SCE | SCE | SUn | CZ14 | 0.928 | ex
2020 | SCE | SCE | SUn | CZ14 | 0.215 | rec
2020 | SCE | Any | SUn | CZ14 | 0.109 | new
2020 | SCE | SCE | SUn | CZ15 | 0.735 | old
2020 | SCE | SCE | SUn | CZ15 | 0.87 | ex
2020 | SCE | SCE | SUn | CZ15 | 0.204 | rec
2020 | SCE | Any | SUn | CZ15 | 0.103 | new
2020 | SCE | SCE | SUn | CZ16 | 0.789 | old
2020 | SCE | SCE | SUn | CZ16 | 0.862 | ex
2020 | SCE | SCE | SUn | CZ16 | 0.203 | rec
2020 | SCE | SCE | WRf | CZ06 | 3.807 | old
2020 | SCE | SCE | WRf | CZ06 | 0.927 | ex
2020 | SCE | SCE | WRf | CZ06 | 0.213 | rec
2020 | SCE | Any | WRf | CZ06 | 0.112 | new
2020 | SCE | SCE | WRf | CZ08 | 5.069 | old
2020 | SCE | SCE | WRf | CZ08 | 1.244 | ex
2020 | SCE | SCE | WRf | CZ08 | 0.285 | rec
2020 | SCE | Any | WRf | CZ08 | 0.152 | new
2020 | SCE | SCE | WRf | CZ09 | 1.429 | old
2020 | SCE | SCE | WRf | CZ09 | 0.435 | ex
2020 | SCE | SCE | WRf | CZ09 | 0.092 | rec
2020 | SCE | Any | WRf | CZ09 | 0.082 | new
2020 | SCE | SCE | WRf | CZ10 | 2.826 | old
2020 | SCE | SCE | WRf | CZ10 | 0.836 | ex
2020 | SCE | SCE | WRf | CZ10 | 0.22 | rec
2020 | SCE | Any | WRf | CZ10 | 0.112 | new
2020 | SCE | SCE | WRf | CZ13 | 2.294 | old
2020 | SCE | SCE | WRf | CZ13 | 1.031 | ex
2020 | SCE | SCE | WRf | CZ13 | 0.299 | rec
2020 | SCE | SCE | WRf | CZ14 | 0.038 | old
2020 | SCE | SCE | WRf | CZ14 | 0.011 | ex
2020 | SCE | SCE | WRf | CZ14 | 0.003 | rec
2020 | SCE | Any | WRf | CZ14 | 0.002 | new
2020 | SCE | SCE | WRf | CZ15 | 0.184 | old
2020 | SCE | SCE | WRf | CZ15 | 0.054 | ex
2020 | SCE | SCE | WRf | CZ15 | 0.015 | rec
2020 | SCE | Any | WRf | CZ15 | 0.008 | new
2020 | SCE | SCE | WRf | CZ16 | 0.048 | old
2020 | SCE | SCE | WRf | CZ16 | 0.022 | ex
2020 | SCE | SCE | WRf | CZ16 | 0.007 | rec
2020 | SCG | SCG | Asm | CZ05 | 0.387 | old
2020 | SCG | SCG | Asm | CZ05 | 0.077 | ex
2020 | SCG | SCG | Asm | CZ05 | 0.017 | rec
2020 | SCG | SCG | Asm | CZ06 | 35.525 | old
2020 | SCG | SCG | Asm | CZ06 | 6.94 | ex
2020 | SCG | SCG | Asm | CZ06 | 1.597 | rec
2020 | SCG | SCG | Asm | CZ08 | 53.499 | old
2020 | SCG | SCG | Asm | CZ08 | 10.442 | ex
2020 | SCG | SCG | Asm | CZ08 | 2.397 | rec
2020 | SCG | SCG | Asm | CZ09 | 45.6 | old
2020 | SCG | SCG | Asm | CZ09 | 9.001 | ex
2020 | SCG | SCG | Asm | CZ09 | 1.991 | rec
2020 | SCG | SCG | Asm | CZ10 | 18.966 | old
2020 | SCG | SCG | Asm | CZ10 | 13.368 | ex
2020 | SCG | SCG | Asm | CZ10 | 2.939 | rec
2020 | SCG | SCG | Asm | CZ13 | 2.887 | old
2020 | SCG | SCG | Asm | CZ13 | 0.962 | ex
2020 | SCG | SCG | Asm | CZ13 | 0.223 | rec
2020 | SCG | SCG | Asm | CZ14 | 4.946 | old
2020 | SCG | SCG | Asm | CZ14 | 2.213 | ex
2020 | SCG | SCG | Asm | CZ14 | 0.486 | rec
2020 | SCG | SCG | Asm | CZ15 | 6.866 | old
2020 | SCG | SCG | Asm | CZ15 | 4.84 | ex
2020 | SCG | SCG | Asm | CZ15 | 1.064 | rec
2020 | SCG | SCG | Asm | CZ16 | 2.849 | old
2020 | SCG | SCG | Asm | CZ16 | 1.377 | ex
2020 | SCG | SCG | Asm | CZ16 | 0.307 | rec
2020 | SCG | SCG | ECC | CZ05 | 0.014 | old
2020 | SCG | SCG | ECC | CZ05 | 0.004 | ex
2020 | SCG | SCG | ECC | CZ05 | 0.002 | rec
2020 | SCG | SCG | ECC | CZ06 | 13.415 | old
2020 | SCG | SCG | ECC | CZ06 | 2.359 | ex
2020 | SCG | SCG | ECC | CZ06 | 0.471 | rec
2020 | SCG | SCG | ECC | CZ08 | 22.543 | old
2020 | SCG | SCG | ECC | CZ08 | 3.811 | ex
2020 | SCG | SCG | ECC | CZ08 | 0.761 | rec
2020 | SCG | SCG | ECC | CZ09 | 19.552 | old
2020 | SCG | SCG | ECC | CZ09 | 2.485 | ex
2020 | SCG | SCG | ECC | CZ09 | 0.475 | rec
2020 | SCG | SCG | ECC | CZ10 | 4.501 | old
2020 | SCG | SCG | ECC | CZ10 | 2.169 | ex
2020 | SCG | SCG | ECC | CZ10 | 0.421 | rec
2020 | SCG | SCG | ECC | CZ13 | 0.874 | old
2020 | SCG | SCG | ECC | CZ13 | 0.516 | ex
2020 | SCG | SCG | ECC | CZ13 | 0.112 | rec
2020 | SCG | SCG | ECC | CZ14 | 1.617 | old
2020 | SCG | SCG | ECC | CZ14 | 0.724 | ex
2020 | SCG | SCG | ECC | CZ14 | 0.141 | rec
2020 | SCG | SCG | ECC | CZ15 | 1.31 | old
2020 | SCG | SCG | ECC | CZ15 | 0.632 | ex
2020 | SCG | SCG | ECC | CZ15 | 0.123 | rec
2020 | SCG | SCG | ECC | CZ16 | 2.926 | old
2020 | SCG | SCG | ECC | CZ16 | 1.415 | ex
2020 | SCG | SCG | ECC | CZ16 | 0.277 | rec
2020 | SCG | SCG | EPr | CZ05 | 0.062 | old
2020 | SCG | SCG | EPr | CZ05 | 0.007 | ex
2020 | SCG | SCG | EPr | CZ05 | 0.002 | rec
2020 | SCG | SCG | EPr | CZ06 | 12.305 | old
2020 | SCG | SCG | EPr | CZ06 | 1.377 | ex
2020 | SCG | SCG | EPr | CZ06 | 0.225 | rec
2020 | SCG | SCG | EPr | CZ08 | 21.745 | old
2020 | SCG | SCG | EPr | CZ08 | 2.499 | ex
2020 | SCG | SCG | EPr | CZ08 | 0.404 | rec
2020 | SCG | SCG | EPr | CZ09 | 20.238 | old
2020 | SCG | SCG | EPr | CZ09 | 2.463 | ex
2020 | SCG | SCG | EPr | CZ09 | 0.356 | rec
2020 | SCG | SCG | EPr | CZ10 | 10.428 | old
2020 | SCG | SCG | EPr | CZ10 | 3.815 | ex
2020 | SCG | SCG | EPr | CZ10 | 0.569 | rec
2020 | SCG | SCG | EPr | CZ13 | 2.284 | old
2020 | SCG | SCG | EPr | CZ13 | 0.624 | ex
2020 | SCG | SCG | EPr | CZ13 | 0.125 | rec
2020 | SCG | SCG | EPr | CZ14 | 2.86 | old
2020 | SCG | SCG | EPr | CZ14 | 0.85 | ex
2020 | SCG | SCG | EPr | CZ14 | 0.129 | rec
2020 | SCG | SCG | EPr | CZ15 | 0.93 | old
2020 | SCG | SCG | EPr | CZ15 | 0.34 | ex
2020 | SCG | SCG | EPr | CZ15 | 0.051 | rec
2020 | SCG | SCG | EPr | CZ16 | 1.313 | old
2020 | SCG | SCG | EPr | CZ16 | 0.422 | ex
2020 | SCG | SCG | EPr | CZ16 | 0.067 | rec
2020 | SCG | SCG | ERC | CZ05 | 0.062 | old
2020 | SCG | SCG | ERC | CZ05 | 0.007 | ex
2020 | SCG | SCG | ERC | CZ05 | 0.002 | rec
2020 | SCG | SCG | ERC | CZ06 | 12.305 | old
2020 | SCG | SCG | ERC | CZ06 | 1.377 | ex
2020 | SCG | SCG | ERC | CZ06 | 0.225 | rec
2020 | SCG | SCG | ERC | CZ08 | 21.745 | old
2020 | SCG | SCG | ERC | CZ08 | 2.499 | ex
2020 | SCG | SCG | ERC | CZ08 | 0.404 | rec
2020 | SCG | SCG | ERC | CZ09 | 20.238 | old
2020 | SCG | SCG | ERC | CZ09 | 2.463 | ex
2020 | SCG | SCG | ERC | CZ09 | 0.356 | rec
2020 | SCG | SCG | ERC | CZ10 | 10.428 | old
2020 | SCG | SCG | ERC | CZ10 | 3.815 | ex
2020 | SCG | SCG | ERC | CZ10 | 0.569 | rec
2020 | SCG | SCG | ERC | CZ13 | 2.284 | old
2020 | SCG | SCG | ERC | CZ13 | 0.624 | ex
2020 | SCG | SCG | ERC | CZ13 | 0.125 | rec
2020 | SCG | SCG | ERC | CZ14 | 2.86 | old
2020 | SCG | SCG | ERC | CZ14 | 0.85 | ex
2020 | SCG | SCG | ERC | CZ14 | 0.129 | rec
2020 | SCG | SCG | ERC | CZ15 | 0.93 | old
2020 | SCG | SCG | ERC | CZ15 | 0.34 | ex
2020 | SCG | SCG | ERC | CZ15 | 0.051 | rec
2020 | SCG | SCG | ERC | CZ16 | 1.313 | old
2020 | SCG | SCG | ERC | CZ16 | 0.422 | ex
2020 | SCG | SCG | ERC | CZ16 | 0.067 | rec
2020 | SCG | SCG | ESe | CZ05 | 0.062 | old
2020 | SCG | SCG | ESe | CZ05 | 0.007 | ex
2020 | SCG | SCG | ESe | CZ05 | 0.002 | rec
2020 | SCG | SCG | ESe | CZ06 | 12.305 | old
2020 | SCG | SCG | ESe | CZ06 | 1.377 | ex
2020 | SCG | SCG | ESe | CZ06 | 0.225 | rec
2020 | SCG | SCG | ESe | CZ08 | 21.745 | old
2020 | SCG | SCG | ESe | CZ08 | 2.499 | ex
2020 | SCG | SCG | ESe | CZ08 | 0.404 | rec
2020 | SCG | SCG | ESe | CZ09 | 20.238 | old
2020 | SCG | SCG | ESe | CZ09 | 2.463 | ex
2020 | SCG | SCG | ESe | CZ09 | 0.356 | rec
2020 | SCG | SCG | ESe | CZ10 | 10.428 | old
2020 | SCG | SCG | ESe | CZ10 | 3.815 | ex
2020 | SCG | SCG | ESe | CZ10 | 0.569 | rec
2020 | SCG | SCG | ESe | CZ13 | 2.284 | old
2020 | SCG | SCG | ESe | CZ13 | 0.624 | ex
2020 | SCG | SCG | ESe | CZ13 | 0.125 | rec
2020 | SCG | SCG | ESe | CZ14 | 2.86 | old
2020 | SCG | SCG | ESe | CZ14 | 0.85 | ex
2020 | SCG | SCG | ESe | CZ14 | 0.129 | rec
2020 | SCG | SCG | ESe | CZ15 | 0.93 | old
2020 | SCG | SCG | ESe | CZ15 | 0.34 | ex
2020 | SCG | SCG | ESe | CZ15 | 0.051 | rec
2020 | SCG | SCG | ESe | CZ16 | 1.313 | old
2020 | SCG | SCG | ESe | CZ16 | 0.422 | ex
2020 | SCG | SCG | ESe | CZ16 | 0.067 | rec
2020 | SCG | SCG | EUD | CZ05 | 0.014 | old
2020 | SCG | SCG | EUD | CZ05 | 0.004 | ex
2020 | SCG | SCG | EUD | CZ05 | 0.002 | rec
2020 | SCG | SCG | EUD | CZ06 | 13.415 | old
2020 | SCG | SCG | EUD | CZ06 | 2.359 | ex
2020 | SCG | SCG | EUD | CZ06 | 0.471 | rec
2020 | SCG | SCG | EUD | CZ08 | 22.543 | old
2020 | SCG | SCG | EUD | CZ08 | 3.811 | ex
2020 | SCG | SCG | EUD | CZ08 | 0.761 | rec
2020 | SCG | SCG | EUD | CZ09 | 19.552 | old
2020 | SCG | SCG | EUD | CZ09 | 2.485 | ex
2020 | SCG | SCG | EUD | CZ09 | 0.475 | rec
2020 | SCG | SCG | EUD | CZ10 | 4.501 | old
2020 | SCG | SCG | EUD | CZ10 | 2.169 | ex
2020 | SCG | SCG | EUD | CZ10 | 0.421 | rec
2020 | SCG | SCG | EUD | CZ13 | 0.874 | old
2020 | SCG | SCG | EUD | CZ13 | 0.516 | ex
2020 | SCG | SCG | EUD | CZ13 | 0.112 | rec
2020 | SCG | SCG | EUD | CZ14 | 1.617 | old
2020 | SCG | SCG | EUD | CZ14 | 0.724 | ex
2020 | SCG | SCG | EUD | CZ14 | 0.141 | rec
2020 | SCG | SCG | EUD | CZ15 | 1.31 | old
2020 | SCG | SCG | EUD | CZ15 | 0.632 | ex
2020 | SCG | SCG | EUD | CZ15 | 0.123 | rec
2020 | SCG | SCG | EUD | CZ16 | 2.926 | old
2020 | SCG | SCG | EUD | CZ16 | 1.415 | ex
2020 | SCG | SCG | EUD | CZ16 | 0.277 | rec
2020 | SCG | SCG | EUn | CZ05 | 0.014 | old
2020 | SCG | SCG | EUn | CZ05 | 0.004 | ex
2020 | SCG | SCG | EUn | CZ05 | 0.002 | rec
2020 | SCG | SCG | EUn | CZ06 | 13.415 | old
2020 | SCG | SCG | EUn | CZ06 | 2.359 | ex
2020 | SCG | SCG | EUn | CZ06 | 0.471 | rec
2020 | SCG | SCG | EUn | CZ08 | 22.543 | old
2020 | SCG | SCG | EUn | CZ08 | 3.811 | ex
2020 | SCG | SCG | EUn | CZ08 | 0.761 | rec
2020 | SCG | SCG | EUn | CZ09 | 19.552 | old
2020 | SCG | SCG | EUn | CZ09 | 2.485 | ex
2020 | SCG | SCG | EUn | CZ09 | 0.475 | rec
2020 | SCG | SCG | EUn | CZ10 | 4.501 | old
2020 | SCG | SCG | EUn | CZ10 | 2.169 | ex
2020 | SCG | SCG | EUn | CZ10 | 0.421 | rec
2020 | SCG | SCG | EUn | CZ13 | 0.874 | old
2020 | SCG | SCG | EUn | CZ13 | 0.516 | ex
2020 | SCG | SCG | EUn | CZ13 | 0.112 | rec
2020 | SCG | SCG | EUn | CZ14 | 1.617 | old
2020 | SCG | SCG | EUn | CZ14 | 0.724 | ex
2020 | SCG | SCG | EUn | CZ14 | 0.141 | rec
2020 | SCG | SCG | EUn | CZ15 | 1.31 | old
2020 | SCG | SCG | EUn | CZ15 | 0.632 | ex
2020 | SCG | SCG | EUn | CZ15 | 0.123 | rec
2020 | SCG | SCG | EUn | CZ16 | 2.926 | old
2020 | SCG | SCG | EUn | CZ16 | 1.415 | ex
2020 | SCG | SCG | EUn | CZ16 | 0.277 | rec
2020 | SCG | SCG | Gro | CZ05 | 0.405 | old
2020 | SCG | SCG | Gro | CZ05 | 0.086 | ex
2020 | SCG | SCG | Gro | CZ05 | 0.02 | rec
2020 | SCG | SCG | Gro | CZ06 | 22.419 | old
2020 | SCG | SCG | Gro | CZ06 | 4.814 | ex
2020 | SCG | SCG | Gro | CZ06 | 1.12 | rec
2020 | SCG | SCG | Gro | CZ08 | 34.064 | old
2020 | SCG | SCG | Gro | CZ08 | 7.371 | ex
2020 | SCG | SCG | Gro | CZ08 | 1.713 | rec
2020 | SCG | SCG | Gro | CZ09 | 31.265 | old
2020 | SCG | SCG | Gro | CZ09 | 7.267 | ex
2020 | SCG | SCG | Gro | CZ09 | 1.66 | rec
2020 | SCG | SCG | Gro | CZ10 | 18.551 | old
2020 | SCG | SCG | Gro | CZ10 | 8.729 | ex
2020 | SCG | SCG | Gro | CZ10 | 2.001 | rec
2020 | SCG | SCG | Gro | CZ13 | 2.833 | old
2020 | SCG | SCG | Gro | CZ13 | 1.069 | ex
2020 | SCG | SCG | Gro | CZ13 | 0.25 | rec
2020 | SCG | SCG | Gro | CZ14 | 4.572 | old
2020 | SCG | SCG | Gro | CZ14 | 1.925 | ex
2020 | SCG | SCG | Gro | CZ14 | 0.441 | rec
2020 | SCG | SCG | Gro | CZ15 | 2.609 | old
2020 | SCG | SCG | Gro | CZ15 | 1.227 | ex
2020 | SCG | SCG | Gro | CZ15 | 0.281 | rec
2020 | SCG | SCG | Gro | CZ16 | 1.837 | old
2020 | SCG | SCG | Gro | CZ16 | 0.759 | ex
2020 | SCG | SCG | Gro | CZ16 | 0.175 | rec
2020 | SCG | SCG | HGR | CZ05 | 0.137 | old
2020 | SCG | SCG | HGR | CZ05 | 0.021 | ex
2020 | SCG | SCG | HGR | CZ05 | 0.004 | rec
2020 | SCG | SCG | HGR | CZ06 | 17.564 | old
2020 | SCG | SCG | HGR | CZ06 | 2.776 | ex
2020 | SCG | SCG | HGR | CZ06 | 0.564 | rec
2020 | SCG | SCG | HGR | CZ08 | 13.447 | old
2020 | SCG | SCG | HGR | CZ08 | 2.205 | ex
2020 | SCG | SCG | HGR | CZ08 | 0.473 | rec
2020 | SCG | SCG | HGR | CZ09 | 18.88 | old
2020 | SCG | SCG | HGR | CZ09 | 3.407 | ex
2020 | SCG | SCG | HGR | CZ09 | 0.861 | rec
2020 | SCG | SCG | HGR | CZ10 | 2.175 | old
2020 | SCG | SCG | HGR | CZ10 | 0.986 | ex
2020 | SCG | SCG | HGR | CZ10 | 0.215 | rec
2020 | SCG | SCG | HGR | CZ13 | 0.474 | old
2020 | SCG | SCG | HGR | CZ13 | 0.113 | ex
2020 | SCG | SCG | HGR | CZ13 | 0.03 | rec
2020 | SCG | SCG | HGR | CZ14 | 1.137 | old
2020 | SCG | SCG | HGR | CZ14 | 0.405 | ex
2020 | SCG | SCG | HGR | CZ14 | 0.097 | rec
2020 | SCG | SCG | HGR | CZ15 | 5.563 | old
2020 | SCG | SCG | HGR | CZ15 | 2.519 | ex
2020 | SCG | SCG | HGR | CZ15 | 0.549 | rec
2020 | SCG | SCG | HGR | CZ16 | 1.653 | old
2020 | SCG | SCG | HGR | CZ16 | 0.422 | ex
2020 | SCG | SCG | HGR | CZ16 | 0.116 | rec
2020 | SCG | SCG | Hsp | CZ05 | 0.846 | old
2020 | SCG | SCG | Hsp | CZ05 | 0.152 | ex
2020 | SCG | SCG | Hsp | CZ05 | 0.025 | rec
2020 | SCG | SCG | Hsp | CZ06 | 14.16 | old
2020 | SCG | SCG | Hsp | CZ06 | 2.618 | ex
2020 | SCG | SCG | Hsp | CZ06 | 0.452 | rec
2020 | SCG | SCG | Hsp | CZ08 | 16.571 | old
2020 | SCG | SCG | Hsp | CZ08 | 3.089 | ex
2020 | SCG | SCG | Hsp | CZ08 | 0.545 | rec
2020 | SCG | SCG | Hsp | CZ09 | 19.04 | old
2020 | SCG | SCG | Hsp | CZ09 | 3.945 | ex
2020 | SCG | SCG | Hsp | CZ09 | 0.746 | rec
2020 | SCG | SCG | Hsp | CZ10 | 6.854 | old
2020 | SCG | SCG | Hsp | CZ10 | 1.862 | ex
2020 | SCG | SCG | Hsp | CZ10 | 0.463 | rec
2020 | SCG | SCG | Hsp | CZ13 | 1.371 | old
2020 | SCG | SCG | Hsp | CZ13 | 0.272 | ex
2020 | SCG | SCG | Hsp | CZ13 | 0.071 | rec
2020 | SCG | SCG | Hsp | CZ14 | 1.231 | old
2020 | SCG | SCG | Hsp | CZ14 | 0.317 | ex
2020 | SCG | SCG | Hsp | CZ14 | 0.075 | rec
2020 | SCG | SCG | Hsp | CZ15 | 1.419 | old
2020 | SCG | SCG | Hsp | CZ15 | 0.386 | ex
2020 | SCG | SCG | Hsp | CZ15 | 0.096 | rec
2020 | SCG | SCG | Hsp | CZ16 | 0.914 | old
2020 | SCG | SCG | Hsp | CZ16 | 0.231 | ex
2020 | SCG | SCG | Hsp | CZ16 | 0.057 | rec
2020 | SCG | SCG | Htl | CZ05 | 0.137 | old
2020 | SCG | SCG | Htl | CZ05 | 0.021 | ex
2020 | SCG | SCG | Htl | CZ05 | 0.004 | rec
2020 | SCG | SCG | Htl | CZ06 | 17.564 | old
2020 | SCG | SCG | Htl | CZ06 | 2.776 | ex
2020 | SCG | SCG | Htl | CZ06 | 0.564 | rec
2020 | SCG | SCG | Htl | CZ08 | 13.447 | old
2020 | SCG | SCG | Htl | CZ08 | 2.205 | ex
2020 | SCG | SCG | Htl | CZ08 | 0.473 | rec
2020 | SCG | SCG | Htl | CZ09 | 18.88 | old
2020 | SCG | SCG | Htl | CZ09 | 3.407 | ex
2020 | SCG | SCG | Htl | CZ09 | 0.861 | rec
2020 | SCG | SCG | Htl | CZ10 | 2.175 | old
2020 | SCG | SCG | Htl | CZ10 | 0.986 | ex
2020 | SCG | SCG | Htl | CZ10 | 0.215 | rec
2020 | SCG | SCG | Htl | CZ13 | 0.474 | old
2020 | SCG | SCG | Htl | CZ13 | 0.113 | ex
2020 | SCG | SCG | Htl | CZ13 | 0.03 | rec
2020 | SCG | SCG | Htl | CZ14 | 1.137 | old
2020 | SCG | SCG | Htl | CZ14 | 0.405 | ex
2020 | SCG | SCG | Htl | CZ14 | 0.097 | rec
2020 | SCG | SCG | Htl | CZ15 | 5.563 | old
2020 | SCG | SCG | Htl | CZ15 | 2.519 | ex
2020 | SCG | SCG | Htl | CZ15 | 0.549 | rec
2020 | SCG | SCG | Htl | CZ16 | 1.653 | old
2020 | SCG | SCG | Htl | CZ16 | 0.422 | ex
2020 | SCG | SCG | Htl | CZ16 | 0.116 | rec
2020 | SCG | SCG | MBT | CZ05 | 0.387 | old
2020 | SCG | SCG | MBT | CZ05 | 0.077 | ex
2020 | SCG | SCG | MBT | CZ05 | 0.017 | rec
2020 | SCG | SCG | MBT | CZ06 | 35.525 | old
2020 | SCG | SCG | MBT | CZ06 | 6.94 | ex
2020 | SCG | SCG | MBT | CZ06 | 1.597 | rec
2020 | SCG | SCG | MBT | CZ08 | 53.499 | old
2020 | SCG | SCG | MBT | CZ08 | 10.442 | ex
2020 | SCG | SCG | MBT | CZ08 | 2.397 | rec
2020 | SCG | SCG | MBT | CZ09 | 45.6 | old
2020 | SCG | SCG | MBT | CZ09 | 9.001 | ex
2020 | SCG | SCG | MBT | CZ09 | 1.991 | rec
2020 | SCG | SCG | MBT | CZ10 | 18.966 | old
2020 | SCG | SCG | MBT | CZ10 | 13.368 | ex
2020 | SCG | SCG | MBT | CZ10 | 2.939 | rec
2020 | SCG | SCG | MBT | CZ13 | 2.887 | old
2020 | SCG | SCG | MBT | CZ13 | 0.962 | ex
2020 | SCG | SCG | MBT | CZ13 | 0.223 | rec
2020 | SCG | SCG | MBT | CZ14 | 4.946 | old
2020 | SCG | SCG | MBT | CZ14 | 2.213 | ex
2020 | SCG | SCG | MBT | CZ14 | 0.486 | rec
2020 | SCG | SCG | MBT | CZ15 | 6.866 | old
2020 | SCG | SCG | MBT | CZ15 | 4.84 | ex
2020 | SCG | SCG | MBT | CZ15 | 1.064 | rec
2020 | SCG | SCG | MBT | CZ16 | 2.849 | old
2020 | SCG | SCG | MBT | CZ16 | 1.377 | ex
2020 | SCG | SCG | MBT | CZ16 | 0.307 | rec
2020 | SCG | SCG | MLI | CZ05 | 0.387 | old
2020 | SCG | SCG | MLI | CZ05 | 0.077 | ex
2020 | SCG | SCG | MLI | CZ05 | 0.017 | rec
2020 | SCG | SCG | MLI | CZ06 | 35.525 | old
2020 | SCG | SCG | MLI | CZ06 | 6.94 | ex
2020 | SCG | SCG | MLI | CZ06 | 1.597 | rec
2020 | SCG | SCG | MLI | CZ08 | 53.499 | old
2020 | SCG | SCG | MLI | CZ08 | 10.442 | ex
2020 | SCG | SCG | MLI | CZ08 | 2.397 | rec
2020 | SCG | SCG | MLI | CZ09 | 45.6 | old
2020 | SCG | SCG | MLI | CZ09 | 9.001 | ex
2020 | SCG | SCG | MLI | CZ09 | 1.991 | rec
2020 | SCG | SCG | MLI | CZ10 | 18.966 | old
2020 | SCG | SCG | MLI | CZ10 | 13.368 | ex
2020 | SCG | SCG | MLI | CZ10 | 2.939 | rec
2020 | SCG | SCG | MLI | CZ13 | 2.887 | old
2020 | SCG | SCG | MLI | CZ13 | 0.962 | ex
2020 | SCG | SCG | MLI | CZ13 | 0.223 | rec
2020 | SCG | SCG | MLI | CZ14 | 4.946 | old
2020 | SCG | SCG | MLI | CZ14 | 2.213 | ex
2020 | SCG | SCG | MLI | CZ14 | 0.486 | rec
2020 | SCG | SCG | MLI | CZ15 | 6.866 | old
2020 | SCG | SCG | MLI | CZ15 | 4.84 | ex
2020 | SCG | SCG | MLI | CZ15 | 1.064 | rec
2020 | SCG | SCG | MLI | CZ16 | 2.849 | old
2020 | SCG | SCG | MLI | CZ16 | 1.377 | ex
2020 | SCG | SCG | MLI | CZ16 | 0.307 | rec
2020 | SCG | SCG | Mtl | CZ05 | 0.137 | old
2020 | SCG | SCG | Mtl | CZ05 | 0.021 | ex
2020 | SCG | SCG | Mtl | CZ05 | 0.004 | rec
2020 | SCG | SCG | Mtl | CZ06 | 17.564 | old
2020 | SCG | SCG | Mtl | CZ06 | 2.776 | ex
2020 | SCG | SCG | Mtl | CZ06 | 0.564 | rec
2020 | SCG | SCG | Mtl | CZ08 | 13.447 | old
2020 | SCG | SCG | Mtl | CZ08 | 2.205 | ex
2020 | SCG | SCG | Mtl | CZ08 | 0.473 | rec
2020 | SCG | SCG | Mtl | CZ09 | 18.88 | old
2020 | SCG | SCG | Mtl | CZ09 | 3.407 | ex
2020 | SCG | SCG | Mtl | CZ09 | 0.861 | rec
2020 | SCG | SCG | Mtl | CZ10 | 2.175 | old
2020 | SCG | SCG | Mtl | CZ10 | 0.986 | ex
2020 | SCG | SCG | Mtl | CZ10 | 0.215 | rec
2020 | SCG | SCG | Mtl | CZ13 | 0.474 | old
2020 | SCG | SCG | Mtl | CZ13 | 0.113 | ex
2020 | SCG | SCG | Mtl | CZ13 | 0.03 | rec
2020 | SCG | SCG | Mtl | CZ14 | 1.137 | old
2020 | SCG | SCG | Mtl | CZ14 | 0.405 | ex
2020 | SCG | SCG | Mtl | CZ14 | 0.097 | rec
2020 | SCG | SCG | Mtl | CZ15 | 5.563 | old
2020 | SCG | SCG | Mtl | CZ15 | 2.519 | ex
2020 | SCG | SCG | Mtl | CZ15 | 0.549 | rec
2020 | SCG | SCG | Mtl | CZ16 | 1.653 | old
2020 | SCG | SCG | Mtl | CZ16 | 0.422 | ex
2020 | SCG | SCG | Mtl | CZ16 | 0.116 | rec
2020 | SCG | SCG | Nrs | CZ05 | 0.846 | old
2020 | SCG | SCG | Nrs | CZ05 | 0.152 | ex
2020 | SCG | SCG | Nrs | CZ05 | 0.025 | rec
2020 | SCG | SCG | Nrs | CZ06 | 14.16 | old
2020 | SCG | SCG | Nrs | CZ06 | 2.618 | ex
2020 | SCG | SCG | Nrs | CZ06 | 0.452 | rec
2020 | SCG | SCG | Nrs | CZ08 | 16.571 | old
2020 | SCG | SCG | Nrs | CZ08 | 3.089 | ex
2020 | SCG | SCG | Nrs | CZ08 | 0.545 | rec
2020 | SCG | SCG | Nrs | CZ09 | 19.04 | old
2020 | SCG | SCG | Nrs | CZ09 | 3.945 | ex
2020 | SCG | SCG | Nrs | CZ09 | 0.746 | rec
2020 | SCG | SCG | Nrs | CZ10 | 6.854 | old
2020 | SCG | SCG | Nrs | CZ10 | 1.862 | ex
2020 | SCG | SCG | Nrs | CZ10 | 0.463 | rec
2020 | SCG | SCG | Nrs | CZ13 | 1.371 | old
2020 | SCG | SCG | Nrs | CZ13 | 0.272 | ex
2020 | SCG | SCG | Nrs | CZ13 | 0.071 | rec
2020 | SCG | SCG | Nrs | CZ14 | 1.231 | old
2020 | SCG | SCG | Nrs | CZ14 | 0.317 | ex
2020 | SCG | SCG | Nrs | CZ14 | 0.075 | rec
2020 | SCG | SCG | Nrs | CZ15 | 1.419 | old
2020 | SCG | SCG | Nrs | CZ15 | 0.386 | ex
2020 | SCG | SCG | Nrs | CZ15 | 0.096 | rec
2020 | SCG | SCG | Nrs | CZ16 | 0.914 | old
2020 | SCG | SCG | Nrs | CZ16 | 0.231 | ex
2020 | SCG | SCG | Nrs | CZ16 | 0.057 | rec
2020 | SCG | SCG | OfL | CZ05 | 1.225 | old
2020 | SCG | SCG | OfL | CZ05 | 0.12 | ex
2020 | SCG | SCG | OfL | CZ05 | 0.021 | rec
2020 | SCG | SCG | OfL | CZ06 | 128.389 | old
2020 | SCG | SCG | OfL | CZ06 | 14.066 | ex
2020 | SCG | SCG | OfL | CZ06 | 2.852 | rec
2020 | SCG | SCG | OfL | CZ08 | 171.014 | old
2020 | SCG | SCG | OfL | CZ08 | 19.328 | ex
2020 | SCG | SCG | OfL | CZ08 | 4.08 | rec
2020 | SCG | SCG | OfL | CZ09 | 223.114 | old
2020 | SCG | SCG | OfL | CZ09 | 25.367 | ex
2020 | SCG | SCG | OfL | CZ09 | 5.925 | rec
2020 | SCG | SCG | OfL | CZ10 | 25.533 | old
2020 | SCG | SCG | OfL | CZ10 | 10.408 | ex
2020 | SCG | SCG | OfL | CZ10 | 2.127 | rec
2020 | SCG | SCG | OfL | CZ13 | 3.293 | old
2020 | SCG | SCG | OfL | CZ13 | 0.706 | ex
2020 | SCG | SCG | OfL | CZ13 | 0.196 | rec
2020 | SCG | SCG | OfL | CZ14 | 6.448 | old
2020 | SCG | SCG | OfL | CZ14 | 1.707 | ex
2020 | SCG | SCG | OfL | CZ14 | 0.381 | rec
2020 | SCG | SCG | OfL | CZ15 | 6.977 | old
2020 | SCG | SCG | OfL | CZ15 | 2.844 | ex
2020 | SCG | SCG | OfL | CZ15 | 0.581 | rec
2020 | SCG | SCG | OfL | CZ16 | 3.012 | old
2020 | SCG | SCG | OfL | CZ16 | 0.736 | ex
2020 | SCG | SCG | OfL | CZ16 | 0.172 | rec
2020 | SCG | SCG | OfS | CZ05 | 0.285 | old
2020 | SCG | SCG | OfS | CZ05 | 0.046 | ex
2020 | SCG | SCG | OfS | CZ05 | 0.012 | rec
2020 | SCG | SCG | OfS | CZ06 | 27.741 | old
2020 | SCG | SCG | OfS | CZ06 | 4.47 | ex
2020 | SCG | SCG | OfS | CZ06 | 1.135 | rec
2020 | SCG | SCG | OfS | CZ08 | 35.954 | old
2020 | SCG | SCG | OfS | CZ08 | 5.733 | ex
2020 | SCG | SCG | OfS | CZ08 | 1.446 | rec
2020 | SCG | SCG | OfS | CZ09 | 39.072 | old
2020 | SCG | SCG | OfS | CZ09 | 6.224 | ex
2020 | SCG | SCG | OfS | CZ09 | 1.448 | rec
2020 | SCG | SCG | OfS | CZ10 | 20.244 | old
2020 | SCG | SCG | OfS | CZ10 | 7.388 | ex
2020 | SCG | SCG | OfS | CZ10 | 1.581 | rec
2020 | SCG | SCG | OfS | CZ13 | 5.081 | old
2020 | SCG | SCG | OfS | CZ13 | 1.055 | ex
2020 | SCG | SCG | OfS | CZ13 | 0.237 | rec
2020 | SCG | SCG | OfS | CZ14 | 2.955 | old
2020 | SCG | SCG | OfS | CZ14 | 0.941 | ex
2020 | SCG | SCG | OfS | CZ14 | 0.203 | rec
2020 | SCG | SCG | OfS | CZ15 | 5.532 | old
2020 | SCG | SCG | OfS | CZ15 | 2.019 | ex
2020 | SCG | SCG | OfS | CZ15 | 0.432 | rec
2020 | SCG | SCG | OfS | CZ16 | 1.728 | old
2020 | SCG | SCG | OfS | CZ16 | 0.471 | ex
2020 | SCG | SCG | OfS | CZ16 | 0.103 | rec
2020 | SCG | SCG | RFF | CZ05 | 0.118 | old
2020 | SCG | SCG | RFF | CZ05 | 0.027 | ex
2020 | SCG | SCG | RFF | CZ05 | 0.007 | rec
2020 | SCG | SCG | RFF | CZ06 | 9.05 | old
2020 | SCG | SCG | RFF | CZ06 | 2.089 | ex
2020 | SCG | SCG | RFF | CZ06 | 0.533 | rec
2020 | SCG | SCG | RFF | CZ08 | 11.199 | old
2020 | SCG | SCG | RFF | CZ08 | 2.557 | ex
2020 | SCG | SCG | RFF | CZ08 | 0.64 | rec
2020 | SCG | SCG | RFF | CZ09 | 12.477 | old
2020 | SCG | SCG | RFF | CZ09 | 2.569 | ex
2020 | SCG | SCG | RFF | CZ09 | 0.55 | rec
2020 | SCG | SCG | RFF | CZ10 | 6.563 | old
2020 | SCG | SCG | RFF | CZ10 | 3.66 | ex
2020 | SCG | SCG | RFF | CZ10 | 0.643 | rec
2020 | SCG | SCG | RFF | CZ13 | 0.599 | old
2020 | SCG | SCG | RFF | CZ13 | 0.209 | ex
2020 | SCG | SCG | RFF | CZ13 | 0.044 | rec
2020 | SCG | SCG | RFF | CZ14 | 1.437 | old
2020 | SCG | SCG | RFF | CZ14 | 0.686 | ex
2020 | SCG | SCG | RFF | CZ14 | 0.123 | rec
2020 | SCG | SCG | RFF | CZ15 | 1.284 | old
2020 | SCG | SCG | RFF | CZ15 | 0.716 | ex
2020 | SCG | SCG | RFF | CZ15 | 0.125 | rec
2020 | SCG | SCG | RFF | CZ16 | 0.563 | old
2020 | SCG | SCG | RFF | CZ16 | 0.256 | ex
2020 | SCG | SCG | RFF | CZ16 | 0.047 | rec
2020 | SCG | SCG | RSD | CZ05 | 0.118 | old
2020 | SCG | SCG | RSD | CZ05 | 0.027 | ex
2020 | SCG | SCG | RSD | CZ05 | 0.007 | rec
2020 | SCG | SCG | RSD | CZ06 | 9.05 | old
2020 | SCG | SCG | RSD | CZ06 | 2.089 | ex
2020 | SCG | SCG | RSD | CZ06 | 0.533 | rec
2020 | SCG | SCG | RSD | CZ08 | 11.199 | old
2020 | SCG | SCG | RSD | CZ08 | 2.557 | ex
2020 | SCG | SCG | RSD | CZ08 | 0.64 | rec
2020 | SCG | SCG | RSD | CZ09 | 12.477 | old
2020 | SCG | SCG | RSD | CZ09 | 2.569 | ex
2020 | SCG | SCG | RSD | CZ09 | 0.55 | rec
2020 | SCG | SCG | RSD | CZ10 | 6.563 | old
2020 | SCG | SCG | RSD | CZ10 | 3.66 | ex
2020 | SCG | SCG | RSD | CZ10 | 0.643 | rec
2020 | SCG | SCG | RSD | CZ13 | 0.599 | old
2020 | SCG | SCG | RSD | CZ13 | 0.209 | ex
2020 | SCG | SCG | RSD | CZ13 | 0.044 | rec
2020 | SCG | SCG | RSD | CZ14 | 1.437 | old
2020 | SCG | SCG | RSD | CZ14 | 0.686 | ex
2020 | SCG | SCG | RSD | CZ14 | 0.123 | rec
2020 | SCG | SCG | RSD | CZ15 | 1.284 | old
2020 | SCG | SCG | RSD | CZ15 | 0.716 | ex
2020 | SCG | SCG | RSD | CZ15 | 0.125 | rec
2020 | SCG | SCG | RSD | CZ16 | 0.563 | old
2020 | SCG | SCG | RSD | CZ16 | 0.256 | ex
2020 | SCG | SCG | RSD | CZ16 | 0.047 | rec
2020 | SCG | SCG | Rt3 | CZ05 | 0.557 | old
2020 | SCG | SCG | Rt3 | CZ05 | 0.124 | ex
2020 | SCG | SCG | Rt3 | CZ05 | 0.029 | rec
2020 | SCG | SCG | Rt3 | CZ06 | 33.99 | old
2020 | SCG | SCG | Rt3 | CZ06 | 7.629 | ex
2020 | SCG | SCG | Rt3 | CZ06 | 1.777 | rec
2020 | SCG | SCG | Rt3 | CZ08 | 41.147 | old
2020 | SCG | SCG | Rt3 | CZ08 | 9.384 | ex
2020 | SCG | SCG | Rt3 | CZ08 | 2.18 | rec
2020 | SCG | SCG | Rt3 | CZ09 | 42.444 | old
2020 | SCG | SCG | Rt3 | CZ09 | 10.427 | ex
2020 | SCG | SCG | Rt3 | CZ09 | 2.36 | rec
2020 | SCG | SCG | Rt3 | CZ10 | 22.941 | old
2020 | SCG | SCG | Rt3 | CZ10 | 12.825 | ex
2020 | SCG | SCG | Rt3 | CZ10 | 2.777 | rec
2020 | SCG | SCG | Rt3 | CZ13 | 3.222 | old
2020 | SCG | SCG | Rt3 | CZ13 | 1.314 | ex
2020 | SCG | SCG | Rt3 | CZ13 | 0.305 | rec
2020 | SCG | SCG | Rt3 | CZ14 | 4.584 | old
2020 | SCG | SCG | Rt3 | CZ14 | 1.98 | ex
2020 | SCG | SCG | Rt3 | CZ14 | 0.432 | rec
2020 | SCG | SCG | Rt3 | CZ15 | 3.204 | old
2020 | SCG | SCG | Rt3 | CZ15 | 1.791 | ex
2020 | SCG | SCG | Rt3 | CZ15 | 0.388 | rec
2020 | SCG | SCG | Rt3 | CZ16 | 0.946 | old
2020 | SCG | SCG | Rt3 | CZ16 | 0.415 | ex
2020 | SCG | SCG | Rt3 | CZ16 | 0.093 | rec
2020 | SCG | SCG | RtL | CZ05 | 0.557 | old
2020 | SCG | SCG | RtL | CZ05 | 0.124 | ex
2020 | SCG | SCG | RtL | CZ05 | 0.029 | rec
2020 | SCG | SCG | RtL | CZ06 | 33.99 | old
2020 | SCG | SCG | RtL | CZ06 | 7.629 | ex
2020 | SCG | SCG | RtL | CZ06 | 1.777 | rec
2020 | SCG | SCG | RtL | CZ08 | 41.147 | old
2020 | SCG | SCG | RtL | CZ08 | 9.384 | ex
2020 | SCG | SCG | RtL | CZ08 | 2.18 | rec
2020 | SCG | SCG | RtL | CZ09 | 42.444 | old
2020 | SCG | SCG | RtL | CZ09 | 10.427 | ex
2020 | SCG | SCG | RtL | CZ09 | 2.36 | rec
2020 | SCG | SCG | RtL | CZ10 | 22.941 | old
2020 | SCG | SCG | RtL | CZ10 | 12.825 | ex
2020 | SCG | SCG | RtL | CZ10 | 2.777 | rec
2020 | SCG | SCG | RtL | CZ13 | 3.222 | old
2020 | SCG | SCG | RtL | CZ13 | 1.314 | ex
2020 | SCG | SCG | RtL | CZ13 | 0.305 | rec
2020 | SCG | SCG | RtL | CZ14 | 4.584 | old
2020 | SCG | SCG | RtL | CZ14 | 1.98 | ex
2020 | SCG | SCG | RtL | CZ14 | 0.432 | rec
2020 | SCG | SCG | RtL | CZ15 | 3.204 | old
2020 | SCG | SCG | RtL | CZ15 | 1.791 | ex
2020 | SCG | SCG | RtL | CZ15 | 0.388 | rec
2020 | SCG | SCG | RtL | CZ16 | 0.946 | old
2020 | SCG | SCG | RtL | CZ16 | 0.415 | ex
2020 | SCG | SCG | RtL | CZ16 | 0.093 | rec
2020 | SCG | SCG | RtS | CZ05 | 0.557 | old
2020 | SCG | SCG | RtS | CZ05 | 0.124 | ex
2020 | SCG | SCG | RtS | CZ05 | 0.029 | rec
2020 | SCG | SCG | RtS | CZ06 | 33.99 | old
2020 | SCG | SCG | RtS | CZ06 | 7.629 | ex
2020 | SCG | SCG | RtS | CZ06 | 1.777 | rec
2020 | SCG | SCG | RtS | CZ08 | 41.147 | old
2020 | SCG | SCG | RtS | CZ08 | 9.384 | ex
2020 | SCG | SCG | RtS | CZ08 | 2.18 | rec
2020 | SCG | SCG | RtS | CZ09 | 42.444 | old
2020 | SCG | SCG | RtS | CZ09 | 10.427 | ex
2020 | SCG | SCG | RtS | CZ09 | 2.36 | rec
2020 | SCG | SCG | RtS | CZ10 | 22.941 | old
2020 | SCG | SCG | RtS | CZ10 | 12.825 | ex
2020 | SCG | SCG | RtS | CZ10 | 2.777 | rec
2020 | SCG | SCG | RtS | CZ13 | 3.222 | old
2020 | SCG | SCG | RtS | CZ13 | 1.314 | ex
2020 | SCG | SCG | RtS | CZ13 | 0.305 | rec
2020 | SCG | SCG | RtS | CZ14 | 4.584 | old
2020 | SCG | SCG | RtS | CZ14 | 1.98 | ex
2020 | SCG | SCG | RtS | CZ14 | 0.432 | rec
2020 | SCG | SCG | RtS | CZ15 | 3.204 | old
2020 | SCG | SCG | RtS | CZ15 | 1.791 | ex
2020 | SCG | SCG | RtS | CZ15 | 0.388 | rec
2020 | SCG | SCG | RtS | CZ16 | 0.946 | old
2020 | SCG | SCG | RtS | CZ16 | 0.415 | ex
2020 | SCG | SCG | RtS | CZ16 | 0.093 | rec
2020 | SCG | SCG | SCn | CZ05 | 0.029 | old
2020 | SCG | SCG | SCn | CZ05 | 0.006 | ex
2020 | SCG | SCG | SCn | CZ05 | 0.002 | rec
2020 | SCG | SCG | SCn | CZ06 | 28.832 | old
2020 | SCG | SCG | SCn | CZ06 | 6.659 | ex
2020 | SCG | SCG | SCn | CZ06 | 1.383 | rec
2020 | SCG | SCG | SCn | CZ08 | 82.929 | old
2020 | SCG | SCG | SCn | CZ08 | 18.683 | ex
2020 | SCG | SCG | SCn | CZ08 | 3.893 | rec
2020 | SCG | SCG | SCn | CZ09 | 52.22 | old
2020 | SCG | SCG | SCn | CZ09 | 14.236 | ex
2020 | SCG | SCG | SCn | CZ09 | 2.792 | rec
2020 | SCG | SCG | SCn | CZ10 | 39.963 | old
2020 | SCG | SCG | SCn | CZ10 | 47.364 | ex
2020 | SCG | SCG | SCn | CZ10 | 11.108 | rec
2020 | SCG | SCG | SCn | CZ13 | 2.365 | old
2020 | SCG | SCG | SCn | CZ13 | 1.585 | ex
2020 | SCG | SCG | SCn | CZ13 | 0.376 | rec
2020 | SCG | SCG | SCn | CZ14 | 1.079 | old
2020 | SCG | SCG | SCn | CZ14 | 0.928 | ex
2020 | SCG | SCG | SCn | CZ14 | 0.215 | rec
2020 | SCG | SCG | SCn | CZ15 | 0.735 | old
2020 | SCG | SCG | SCn | CZ15 | 0.87 | ex
2020 | SCG | SCG | SCn | CZ15 | 0.204 | rec
2020 | SCG | SCG | SCn | CZ16 | 0.789 | old
2020 | SCG | SCG | SCn | CZ16 | 0.862 | ex
2020 | SCG | SCG | SCn | CZ16 | 0.203 | rec
2020 | SCG | SCG | SUn | CZ05 | 0.029 | old
2020 | SCG | SCG | SUn | CZ05 | 0.006 | ex
2020 | SCG | SCG | SUn | CZ05 | 0.002 | rec
2020 | SCG | SCG | SUn | CZ06 | 28.832 | old
2020 | SCG | SCG | SUn | CZ06 | 6.659 | ex
2020 | SCG | SCG | SUn | CZ06 | 1.383 | rec
2020 | SCG | SCG | SUn | CZ08 | 82.929 | old
2020 | SCG | SCG | SUn | CZ08 | 18.683 | ex
2020 | SCG | SCG | SUn | CZ08 | 3.893 | rec
2020 | SCG | SCG | SUn | CZ09 | 52.22 | old
2020 | SCG | SCG | SUn | CZ09 | 14.236 | ex
2020 | SCG | SCG | SUn | CZ09 | 2.792 | rec
2020 | SCG | SCG | SUn | CZ10 | 39.963 | old
2020 | SCG | SCG | SUn | CZ10 | 47.364 | ex
2020 | SCG | SCG | SUn | CZ10 | 11.108 | rec
2020 | SCG | SCG | SUn | CZ13 | 2.365 | old
2020 | SCG | SCG | SUn | CZ13 | 1.585 | ex
2020 | SCG | SCG | SUn | CZ13 | 0.376 | rec
2020 | SCG | SCG | SUn | CZ14 | 1.079 | old
2020 | SCG | SCG | SUn | CZ14 | 0.928 | ex
2020 | SCG | SCG | SUn | CZ14 | 0.215 | rec
2020 | SCG | SCG | SUn | CZ15 | 0.735 | old
2020 | SCG | SCG | SUn | CZ15 | 0.87 | ex
2020 | SCG | SCG | SUn | CZ15 | 0.204 | rec
2020 | SCG | SCG | SUn | CZ16 | 0.789 | old
2020 | SCG | SCG | SUn | CZ16 | 0.862 | ex
2020 | SCG | SCG | SUn | CZ16 | 0.203 | rec
2020 | SCG | SCG | WRf | CZ06 | 4.145 | old
2020 | SCG | SCG | WRf | CZ06 | 1.019 | ex
2020 | SCG | SCG | WRf | CZ06 | 0.233 | rec
2020 | SCG | SCG | WRf | CZ08 | 5.748 | old
2020 | SCG | SCG | WRf | CZ08 | 1.428 | ex
2020 | SCG | SCG | WRf | CZ08 | 0.325 | rec
2020 | SCG | SCG | WRf | CZ09 | 3.889 | old
2020 | SCG | SCG | WRf | CZ09 | 1.126 | ex
2020 | SCG | SCG | WRf | CZ09 | 0.237 | rec
2020 | SCG | SCG | WRf | CZ10 | 2.826 | old
2020 | SCG | SCG | WRf | CZ10 | 0.836 | ex
2020 | SCG | SCG | WRf | CZ10 | 0.22 | rec
2020 | SCG | SCG | WRf | CZ13 | 2.294 | old
2020 | SCG | SCG | WRf | CZ13 | 1.031 | ex
2020 | SCG | SCG | WRf | CZ13 | 0.299 | rec
2020 | SCG | SCG | WRf | CZ14 | 0.038 | old
2020 | SCG | SCG | WRf | CZ14 | 0.011 | ex
2020 | SCG | SCG | WRf | CZ14 | 0.003 | rec
2020 | SCG | SCG | WRf | CZ15 | 0.184 | old
2020 | SCG | SCG | WRf | CZ15 | 0.054 | ex
2020 | SCG | SCG | WRf | CZ15 | 0.015 | rec
2020 | SCG | SCG | WRf | CZ16 | 0.048 | old
2020 | SCG | SCG | WRf | CZ16 | 0.022 | ex
2020 | SCG | SCG | WRf | CZ16 | 0.007 | rec
2020 | SDG | SDG | Asm | CZ06 | 0.709 | old
2020 | SDG | SDG | Asm | CZ06 | 0.262 | ex
2020 | SDG | SDG | Asm | CZ06 | 0.059 | rec
2020 | SDG | SDG | Asm | CZ07 | 13.736 | old
2020 | SDG | SDG | Asm | CZ07 | 5.075 | ex
2020 | SDG | SDG | Asm | CZ07 | 1.142 | rec
2020 | SDG | Any | Asm | CZ07 | 0.286 | new
2020 | SDG | SDG | Asm | CZ08 | 0.435 | old
2020 | SDG | SDG | Asm | CZ08 | 0.16 | ex
2020 | SDG | SDG | Asm | CZ08 | 0.036 | rec
2020 | SDG | SDG | Asm | CZ10 | 6.6 | old
2020 | SDG | SDG | Asm | CZ10 | 2.44 | ex
2020 | SDG | SDG | Asm | CZ10 | 0.549 | rec
2020 | SDG | SDG | Asm | CZ14 | 0.208 | old
2020 | SDG | SDG | Asm | CZ14 | 0.076 | ex
2020 | SDG | SDG | Asm | CZ14 | 0.017 | rec
2020 | SDG | SDG | Asm | CZ15 | 0.067 | old
2020 | SDG | SDG | Asm | CZ15 | 0.026 | ex
2020 | SDG | SDG | Asm | CZ15 | 0.005 | rec
2020 | SDG | SDG | ECC | CZ06 | 0.06 | old
2020 | SDG | SDG | ECC | CZ06 | 0.02 | ex
2020 | SDG | SDG | ECC | CZ06 | 0.004 | rec
2020 | SDG | SDG | ECC | CZ07 | 8.56 | old
2020 | SDG | SDG | ECC | CZ07 | 2.885 | ex
2020 | SDG | SDG | ECC | CZ07 | 0.473 | rec
2020 | SDG | Any | ECC | CZ07 | 0.118 | new
2020 | SDG | SDG | ECC | CZ08 | 0.102 | old
2020 | SDG | SDG | ECC | CZ08 | 0.035 | ex
2020 | SDG | SDG | ECC | CZ08 | 0.005 | rec
2020 | SDG | SDG | ECC | CZ10 | 2.698 | old
2020 | SDG | SDG | ECC | CZ10 | 0.909 | ex
2020 | SDG | SDG | ECC | CZ10 | 0.149 | rec
2020 | SDG | SDG | ECC | CZ14 | 0.06 | old
2020 | SDG | SDG | ECC | CZ14 | 0.02 | ex
2020 | SDG | SDG | ECC | CZ14 | 0.004 | rec
2020 | SDG | SDG | EPr | CZ06 | 0.595 | old
2020 | SDG | SDG | EPr | CZ06 | 0.123 | ex
2020 | SDG | SDG | EPr | CZ06 | 0.017 | rec
2020 | SDG | SDG | EPr | CZ07 | 6.829 | old
2020 | SDG | SDG | EPr | CZ07 | 1.407 | ex
2020 | SDG | SDG | EPr | CZ07 | 0.193 | rec
2020 | SDG | Any | EPr | CZ07 | 0.048 | new
2020 | SDG | SDG | EPr | CZ08 | 0.671 | old
2020 | SDG | SDG | EPr | CZ08 | 0.138 | ex
2020 | SDG | SDG | EPr | CZ08 | 0.019 | rec
2020 | SDG | SDG | EPr | CZ10 | 3.978 | old
2020 | SDG | SDG | EPr | CZ10 | 0.82 | ex
2020 | SDG | SDG | EPr | CZ10 | 0.113 | rec
2020 | SDG | SDG | EPr | CZ14 | 0.109 | old
2020 | SDG | SDG | EPr | CZ14 | 0.022 | ex
2020 | SDG | SDG | EPr | CZ14 | 0.003 | rec
2020 | SDG | SDG | EPr | CZ15 | 0.029 | old
2020 | SDG | SDG | EPr | CZ15 | 0.007 | ex
2020 | SDG | SDG | EPr | CZ15 | 0.002 | rec
2020 | SDG | SDG | ERC | CZ06 | 0.595 | old
2020 | SDG | SDG | ERC | CZ06 | 0.123 | ex
2020 | SDG | SDG | ERC | CZ06 | 0.017 | rec
2020 | SDG | SDG | ERC | CZ07 | 6.829 | old
2020 | SDG | SDG | ERC | CZ07 | 1.407 | ex
2020 | SDG | SDG | ERC | CZ07 | 0.193 | rec
2020 | SDG | Any | ERC | CZ07 | 0.048 | new
2020 | SDG | SDG | ERC | CZ08 | 0.671 | old
2020 | SDG | SDG | ERC | CZ08 | 0.138 | ex
2020 | SDG | SDG | ERC | CZ08 | 0.019 | rec
2020 | SDG | SDG | ERC | CZ10 | 3.978 | old
2020 | SDG | SDG | ERC | CZ10 | 0.82 | ex
2020 | SDG | SDG | ERC | CZ10 | 0.113 | rec
2020 | SDG | SDG | ERC | CZ14 | 0.109 | old
2020 | SDG | SDG | ERC | CZ14 | 0.022 | ex
2020 | SDG | SDG | ERC | CZ14 | 0.003 | rec
2020 | SDG | SDG | ERC | CZ15 | 0.029 | old
2020 | SDG | SDG | ERC | CZ15 | 0.007 | ex
2020 | SDG | SDG | ERC | CZ15 | 0.002 | rec
2020 | SDG | SDG | ESe | CZ06 | 0.595 | old
2020 | SDG | SDG | ESe | CZ06 | 0.123 | ex
2020 | SDG | SDG | ESe | CZ06 | 0.017 | rec
2020 | SDG | SDG | ESe | CZ07 | 6.829 | old
2020 | SDG | SDG | ESe | CZ07 | 1.407 | ex
2020 | SDG | SDG | ESe | CZ07 | 0.193 | rec
2020 | SDG | Any | ESe | CZ07 | 0.048 | new
2020 | SDG | SDG | ESe | CZ08 | 0.671 | old
2020 | SDG | SDG | ESe | CZ08 | 0.138 | ex
2020 | SDG | SDG | ESe | CZ08 | 0.019 | rec
2020 | SDG | SDG | ESe | CZ10 | 3.978 | old
2020 | SDG | SDG | ESe | CZ10 | 0.82 | ex
2020 | SDG | SDG | ESe | CZ10 | 0.113 | rec
2020 | SDG | SDG | ESe | CZ14 | 0.109 | old
2020 | SDG | SDG | ESe | CZ14 | 0.022 | ex
2020 | SDG | SDG | ESe | CZ14 | 0.003 | rec
2020 | SDG | SDG | ESe | CZ15 | 0.029 | old
2020 | SDG | SDG | ESe | CZ15 | 0.007 | ex
2020 | SDG | SDG | ESe | CZ15 | 0.002 | rec
2020 | SDG | SDG | EUD | CZ06 | 0.06 | old
2020 | SDG | SDG | EUD | CZ06 | 0.02 | ex
2020 | SDG | SDG | EUD | CZ06 | 0.004 | rec
2020 | SDG | SDG | EUD | CZ07 | 8.56 | old
2020 | SDG | SDG | EUD | CZ07 | 2.885 | ex
2020 | SDG | SDG | EUD | CZ07 | 0.473 | rec
2020 | SDG | Any | EUD | CZ07 | 0.118 | new
2020 | SDG | SDG | EUD | CZ08 | 0.102 | old
2020 | SDG | SDG | EUD | CZ08 | 0.035 | ex
2020 | SDG | SDG | EUD | CZ08 | 0.005 | rec
2020 | SDG | SDG | EUD | CZ10 | 2.698 | old
2020 | SDG | SDG | EUD | CZ10 | 0.909 | ex
2020 | SDG | SDG | EUD | CZ10 | 0.149 | rec
2020 | SDG | SDG | EUD | CZ14 | 0.06 | old
2020 | SDG | SDG | EUD | CZ14 | 0.02 | ex
2020 | SDG | SDG | EUD | CZ14 | 0.004 | rec
2020 | SDG | SDG | EUn | CZ06 | 0.06 | old
2020 | SDG | SDG | EUn | CZ06 | 0.02 | ex
2020 | SDG | SDG | EUn | CZ06 | 0.004 | rec
2020 | SDG | SDG | EUn | CZ07 | 8.56 | old
2020 | SDG | SDG | EUn | CZ07 | 2.885 | ex
2020 | SDG | SDG | EUn | CZ07 | 0.473 | rec
2020 | SDG | Any | EUn | CZ07 | 0.118 | new
2020 | SDG | SDG | EUn | CZ08 | 0.102 | old
2020 | SDG | SDG | EUn | CZ08 | 0.035 | ex
2020 | SDG | SDG | EUn | CZ08 | 0.005 | rec
2020 | SDG | SDG | EUn | CZ10 | 2.698 | old
2020 | SDG | SDG | EUn | CZ10 | 0.909 | ex
2020 | SDG | SDG | EUn | CZ10 | 0.149 | rec
2020 | SDG | SDG | EUn | CZ14 | 0.06 | old
2020 | SDG | SDG | EUn | CZ14 | 0.02 | ex
2020 | SDG | SDG | EUn | CZ14 | 0.004 | rec
2020 | SDG | SDG | Gro | CZ06 | 1.452 | old
2020 | SDG | SDG | Gro | CZ06 | 0.479 | ex
2020 | SDG | SDG | Gro | CZ06 | 0.107 | rec
2020 | SDG | SDG | Gro | CZ07 | 15.647 | old
2020 | SDG | SDG | Gro | CZ07 | 5.166 | ex
2020 | SDG | SDG | Gro | CZ07 | 1.153 | rec
2020 | SDG | Any | Gro | CZ07 | 0.288 | new
2020 | SDG | SDG | Gro | CZ08 | 0.601 | old
2020 | SDG | SDG | Gro | CZ08 | 0.198 | ex
2020 | SDG | SDG | Gro | CZ08 | 0.044 | rec
2020 | SDG | SDG | Gro | CZ10 | 6.618 | old
2020 | SDG | SDG | Gro | CZ10 | 2.186 | ex
2020 | SDG | SDG | Gro | CZ10 | 0.488 | rec
2020 | SDG | SDG | Gro | CZ14 | 0.093 | old
2020 | SDG | SDG | Gro | CZ14 | 0.031 | ex
2020 | SDG | SDG | Gro | CZ14 | 0.007 | rec
2020 | SDG | SDG | Gro | CZ15 | 0.027 | old
2020 | SDG | SDG | Gro | CZ15 | 0.009 | ex
2020 | SDG | SDG | Gro | CZ15 | 0.003 | rec
2020 | SDG | SDG | HGR | CZ06 | 0.76 | old
2020 | SDG | SDG | HGR | CZ06 | 0.341 | ex
2020 | SDG | SDG | HGR | CZ06 | 0.075 | rec
2020 | SDG | SDG | HGR | CZ07 | 13.165 | old
2020 | SDG | SDG | HGR | CZ07 | 5.897 | ex
2020 | SDG | SDG | HGR | CZ07 | 1.292 | rec
2020 | SDG | Any | HGR | CZ07 | 0.323 | new
2020 | SDG | SDG | HGR | CZ08 | 0.049 | old
2020 | SDG | SDG | HGR | CZ08 | 0.023 | ex
2020 | SDG | SDG | HGR | CZ08 | 0.005 | rec
2020 | SDG | SDG | HGR | CZ10 | 1.493 | old
2020 | SDG | SDG | HGR | CZ10 | 0.67 | ex
2020 | SDG | SDG | HGR | CZ10 | 0.147 | rec
2020 | SDG | SDG | HGR | CZ14 | 0.148 | old
2020 | SDG | SDG | HGR | CZ14 | 0.068 | ex
2020 | SDG | SDG | HGR | CZ14 | 0.015 | rec
2020 | SDG | SDG | HGR | CZ15 | 0.18 | old
2020 | SDG | SDG | HGR | CZ15 | 0.081 | ex
2020 | SDG | SDG | HGR | CZ15 | 0.017 | rec
2020 | SDG | SDG | Hsp | CZ06 | 0.334 | old
2020 | SDG | SDG | Hsp | CZ06 | 0.057 | ex
2020 | SDG | SDG | Hsp | CZ06 | 0.011 | rec
2020 | SDG | SDG | Hsp | CZ07 | 10.755 | old
2020 | SDG | SDG | Hsp | CZ07 | 1.846 | ex
2020 | SDG | SDG | Hsp | CZ07 | 0.333 | rec
2020 | SDG | Any | Hsp | CZ07 | 0.083 | new
2020 | SDG | SDG | Hsp | CZ08 | 0.604 | old
2020 | SDG | SDG | Hsp | CZ08 | 0.104 | ex
2020 | SDG | SDG | Hsp | CZ08 | 0.019 | rec
2020 | SDG | SDG | Hsp | CZ10 | 1.912 | old
2020 | SDG | SDG | Hsp | CZ10 | 0.328 | ex
2020 | SDG | SDG | Hsp | CZ10 | 0.06 | rec
2020 | SDG | SDG | Hsp | CZ14 | 0.009 | old
2020 | SDG | SDG | Hsp | CZ14 | 0.004 | ex
2020 | SDG | SDG | Hsp | CZ14 | 0.002 | rec
2020 | SDG | SDG | Htl | CZ06 | 0.76 | old
2020 | SDG | SDG | Htl | CZ06 | 0.341 | ex
2020 | SDG | SDG | Htl | CZ06 | 0.075 | rec
2020 | SDG | SDG | Htl | CZ07 | 13.165 | old
2020 | SDG | SDG | Htl | CZ07 | 5.897 | ex
2020 | SDG | SDG | Htl | CZ07 | 1.292 | rec
2020 | SDG | Any | Htl | CZ07 | 0.323 | new
2020 | SDG | SDG | Htl | CZ08 | 0.049 | old
2020 | SDG | SDG | Htl | CZ08 | 0.023 | ex
2020 | SDG | SDG | Htl | CZ08 | 0.005 | rec
2020 | SDG | SDG | Htl | CZ10 | 1.493 | old
2020 | SDG | SDG | Htl | CZ10 | 0.67 | ex
2020 | SDG | SDG | Htl | CZ10 | 0.147 | rec
2020 | SDG | SDG | Htl | CZ14 | 0.148 | old
2020 | SDG | SDG | Htl | CZ14 | 0.068 | ex
2020 | SDG | SDG | Htl | CZ14 | 0.015 | rec
2020 | SDG | SDG | Htl | CZ15 | 0.18 | old
2020 | SDG | SDG | Htl | CZ15 | 0.081 | ex
2020 | SDG | SDG | Htl | CZ15 | 0.017 | rec
2020 | SDG | SDG | MBT | CZ06 | 0.709 | old
2020 | SDG | SDG | MBT | CZ06 | 0.262 | ex
2020 | SDG | SDG | MBT | CZ06 | 0.059 | rec
2020 | SDG | SDG | MBT | CZ07 | 13.736 | old
2020 | SDG | SDG | MBT | CZ07 | 5.075 | ex
2020 | SDG | SDG | MBT | CZ07 | 1.142 | rec
2020 | SDG | Any | MBT | CZ07 | 0.286 | new
2020 | SDG | SDG | MBT | CZ08 | 0.435 | old
2020 | SDG | SDG | MBT | CZ08 | 0.16 | ex
2020 | SDG | SDG | MBT | CZ08 | 0.036 | rec
2020 | SDG | SDG | MBT | CZ10 | 6.6 | old
2020 | SDG | SDG | MBT | CZ10 | 2.44 | ex
2020 | SDG | SDG | MBT | CZ10 | 0.549 | rec
2020 | SDG | SDG | MBT | CZ14 | 0.208 | old
2020 | SDG | SDG | MBT | CZ14 | 0.076 | ex
2020 | SDG | SDG | MBT | CZ14 | 0.017 | rec
2020 | SDG | SDG | MBT | CZ15 | 0.067 | old
2020 | SDG | SDG | MBT | CZ15 | 0.026 | ex
2020 | SDG | SDG | MBT | CZ15 | 0.005 | rec
2020 | SDG | SDG | MLI | CZ06 | 0.709 | old
2020 | SDG | SDG | MLI | CZ06 | 0.262 | ex
2020 | SDG | SDG | MLI | CZ06 | 0.059 | rec
2020 | SDG | SDG | MLI | CZ07 | 13.736 | old
2020 | SDG | SDG | MLI | CZ07 | 5.075 | ex
2020 | SDG | SDG | MLI | CZ07 | 1.142 | rec
2020 | SDG | Any | MLI | CZ07 | 0.286 | new
2020 | SDG | SDG | MLI | CZ08 | 0.435 | old
2020 | SDG | SDG | MLI | CZ08 | 0.16 | ex
2020 | SDG | SDG | MLI | CZ08 | 0.036 | rec
2020 | SDG | SDG | MLI | CZ10 | 6.6 | old
2020 | SDG | SDG | MLI | CZ10 | 2.44 | ex
2020 | SDG | SDG | MLI | CZ10 | 0.549 | rec
2020 | SDG | SDG | MLI | CZ14 | 0.208 | old
2020 | SDG | SDG | MLI | CZ14 | 0.076 | ex
2020 | SDG | SDG | MLI | CZ14 | 0.017 | rec
2020 | SDG | SDG | MLI | CZ15 | 0.067 | old
2020 | SDG | SDG | MLI | CZ15 | 0.026 | ex
2020 | SDG | SDG | MLI | CZ15 | 0.005 | rec
2020 | SDG | SDG | Mtl | CZ06 | 0.76 | old
2020 | SDG | SDG | Mtl | CZ06 | 0.341 | ex
2020 | SDG | SDG | Mtl | CZ06 | 0.075 | rec
2020 | SDG | SDG | Mtl | CZ07 | 13.165 | old
2020 | SDG | SDG | Mtl | CZ07 | 5.897 | ex
2020 | SDG | SDG | Mtl | CZ07 | 1.292 | rec
2020 | SDG | Any | Mtl | CZ07 | 0.323 | new
2020 | SDG | SDG | Mtl | CZ08 | 0.049 | old
2020 | SDG | SDG | Mtl | CZ08 | 0.023 | ex
2020 | SDG | SDG | Mtl | CZ08 | 0.005 | rec
2020 | SDG | SDG | Mtl | CZ10 | 1.493 | old
2020 | SDG | SDG | Mtl | CZ10 | 0.67 | ex
2020 | SDG | SDG | Mtl | CZ10 | 0.147 | rec
2020 | SDG | SDG | Mtl | CZ14 | 0.148 | old
2020 | SDG | SDG | Mtl | CZ14 | 0.068 | ex
2020 | SDG | SDG | Mtl | CZ14 | 0.015 | rec
2020 | SDG | SDG | Mtl | CZ15 | 0.18 | old
2020 | SDG | SDG | Mtl | CZ15 | 0.081 | ex
2020 | SDG | SDG | Mtl | CZ15 | 0.017 | rec
2020 | SDG | SDG | Nrs | CZ06 | 0.334 | old
2020 | SDG | SDG | Nrs | CZ06 | 0.057 | ex
2020 | SDG | SDG | Nrs | CZ06 | 0.011 | rec
2020 | SDG | SDG | Nrs | CZ07 | 10.755 | old
2020 | SDG | SDG | Nrs | CZ07 | 1.846 | ex
2020 | SDG | SDG | Nrs | CZ07 | 0.333 | rec
2020 | SDG | Any | Nrs | CZ07 | 0.083 | new
2020 | SDG | SDG | Nrs | CZ08 | 0.604 | old
2020 | SDG | SDG | Nrs | CZ08 | 0.104 | ex
2020 | SDG | SDG | Nrs | CZ08 | 0.019 | rec
2020 | SDG | SDG | Nrs | CZ10 | 1.912 | old
2020 | SDG | SDG | Nrs | CZ10 | 0.328 | ex
2020 | SDG | SDG | Nrs | CZ10 | 0.06 | rec
2020 | SDG | SDG | Nrs | CZ14 | 0.009 | old
2020 | SDG | SDG | Nrs | CZ14 | 0.004 | ex
2020 | SDG | SDG | Nrs | CZ14 | 0.002 | rec
2020 | SDG | SDG | OfL | CZ06 | 1.864 | old
2020 | SDG | SDG | OfL | CZ06 | 0.428 | ex
2020 | SDG | SDG | OfL | CZ06 | 0.081 | rec
2020 | SDG | SDG | OfL | CZ07 | 66.908 | old
2020 | SDG | SDG | OfL | CZ07 | 15.353 | ex
2020 | SDG | SDG | OfL | CZ07 | 2.935 | rec
2020 | SDG | Any | OfL | CZ07 | 0.734 | new
2020 | SDG | SDG | OfL | CZ08 | 1.743 | old
2020 | SDG | SDG | OfL | CZ08 | 0.401 | ex
2020 | SDG | SDG | OfL | CZ08 | 0.076 | rec
2020 | SDG | SDG | OfL | CZ10 | 14.894 | old
2020 | SDG | SDG | OfL | CZ10 | 3.417 | ex
2020 | SDG | SDG | OfL | CZ10 | 0.653 | rec
2020 | SDG | SDG | OfL | CZ14 | 0.361 | old
2020 | SDG | SDG | OfL | CZ14 | 0.083 | ex
2020 | SDG | SDG | OfL | CZ14 | 0.016 | rec
2020 | SDG | SDG | OfL | CZ15 | 0.112 | old
2020 | SDG | SDG | OfL | CZ15 | 0.026 | ex
2020 | SDG | SDG | OfL | CZ15 | 0.005 | rec
2020 | SDG | SDG | OfS | CZ06 | 1.044 | old
2020 | SDG | SDG | OfS | CZ06 | 0.167 | ex
2020 | SDG | SDG | OfS | CZ06 | 0.037 | rec
2020 | SDG | SDG | OfS | CZ07 | 37.463 | old
2020 | SDG | SDG | OfS | CZ07 | 5.963 | ex
2020 | SDG | SDG | OfS | CZ07 | 1.345 | rec
2020 | SDG | Any | OfS | CZ07 | 0.336 | new
2020 | SDG | SDG | OfS | CZ08 | 0.976 | old
2020 | SDG | SDG | OfS | CZ08 | 0.155 | ex
2020 | SDG | SDG | OfS | CZ08 | 0.035 | rec
2020 | SDG | SDG | OfS | CZ10 | 8.339 | old
2020 | SDG | SDG | OfS | CZ10 | 1.327 | ex
2020 | SDG | SDG | OfS | CZ10 | 0.3 | rec
2020 | SDG | SDG | OfS | CZ14 | 0.202 | old
2020 | SDG | SDG | OfS | CZ14 | 0.032 | ex
2020 | SDG | SDG | OfS | CZ14 | 0.008 | rec
2020 | SDG | SDG | OfS | CZ15 | 0.062 | old
2020 | SDG | SDG | OfS | CZ15 | 0.01 | ex
2020 | SDG | SDG | OfS | CZ15 | 0.003 | rec
2020 | SDG | SDG | RFF | CZ06 | 0.307 | old
2020 | SDG | SDG | RFF | CZ06 | 0.055 | ex
2020 | SDG | SDG | RFF | CZ06 | 0.013 | rec
2020 | SDG | SDG | RFF | CZ07 | 4.717 | old
2020 | SDG | SDG | RFF | CZ07 | 0.849 | ex
2020 | SDG | SDG | RFF | CZ07 | 0.201 | rec
2020 | SDG | Any | RFF | CZ07 | 0.05 | new
2020 | SDG | SDG | RFF | CZ08 | 0.206 | old
2020 | SDG | SDG | RFF | CZ08 | 0.038 | ex
2020 | SDG | SDG | RFF | CZ08 | 0.009 | rec
2020 | SDG | SDG | RFF | CZ10 | 1.477 | old
2020 | SDG | SDG | RFF | CZ10 | 0.266 | ex
2020 | SDG | SDG | RFF | CZ10 | 0.063 | rec
2020 | SDG | SDG | RFF | CZ14 | 0.014 | old
2020 | SDG | SDG | RFF | CZ14 | 0.004 | ex
2020 | SDG | SDG | RFF | CZ14 | 0.002 | rec
2020 | SDG | SDG | RFF | CZ15 | 0.007 | old
2020 | SDG | SDG | RFF | CZ15 | 0.004 | ex
2020 | SDG | SDG | RFF | CZ15 | 0.002 | rec
2020 | SDG | SDG | RSD | CZ06 | 0.307 | old
2020 | SDG | SDG | RSD | CZ06 | 0.055 | ex
2020 | SDG | SDG | RSD | CZ06 | 0.013 | rec
2020 | SDG | SDG | RSD | CZ07 | 4.717 | old
2020 | SDG | SDG | RSD | CZ07 | 0.849 | ex
2020 | SDG | SDG | RSD | CZ07 | 0.201 | rec
2020 | SDG | Any | RSD | CZ07 | 0.05 | new
2020 | SDG | SDG | RSD | CZ08 | 0.206 | old
2020 | SDG | SDG | RSD | CZ08 | 0.038 | ex
2020 | SDG | SDG | RSD | CZ08 | 0.009 | rec
2020 | SDG | SDG | RSD | CZ10 | 1.477 | old
2020 | SDG | SDG | RSD | CZ10 | 0.266 | ex
2020 | SDG | SDG | RSD | CZ10 | 0.063 | rec
2020 | SDG | SDG | RSD | CZ14 | 0.014 | old
2020 | SDG | SDG | RSD | CZ14 | 0.004 | ex
2020 | SDG | SDG | RSD | CZ14 | 0.002 | rec
2020 | SDG | SDG | RSD | CZ15 | 0.007 | old
2020 | SDG | SDG | RSD | CZ15 | 0.004 | ex
2020 | SDG | SDG | RSD | CZ15 | 0.002 | rec
2020 | SDG | SDG | Rt3 | CZ06 | 0.949 | old
2020 | SDG | SDG | Rt3 | CZ06 | 0.259 | ex
2020 | SDG | SDG | Rt3 | CZ06 | 0.057 | rec
2020 | SDG | SDG | Rt3 | CZ07 | 18.511 | old
2020 | SDG | SDG | Rt3 | CZ07 | 5.042 | ex
2020 | SDG | SDG | Rt3 | CZ07 | 1.122 | rec
2020 | SDG | Any | Rt3 | CZ07 | 0.281 | new
2020 | SDG | SDG | Rt3 | CZ08 | 1.703 | old
2020 | SDG | SDG | Rt3 | CZ08 | 0.463 | ex
2020 | SDG | SDG | Rt3 | CZ08 | 0.103 | rec
2020 | SDG | SDG | Rt3 | CZ10 | 6.894 | old
2020 | SDG | SDG | Rt3 | CZ10 | 1.878 | ex
2020 | SDG | SDG | Rt3 | CZ10 | 0.418 | rec
2020 | SDG | SDG | Rt3 | CZ14 | 0.026 | old
2020 | SDG | SDG | Rt3 | CZ14 | 0.008 | ex
2020 | SDG | SDG | Rt3 | CZ14 | 0.002 | rec
2020 | SDG | SDG | Rt3 | CZ15 | 0.009 | old
2020 | SDG | SDG | Rt3 | CZ15 | 0.004 | ex
2020 | SDG | SDG | Rt3 | CZ15 | 0.002 | rec
2020 | SDG | SDG | RtL | CZ06 | 0.949 | old
2020 | SDG | SDG | RtL | CZ06 | 0.259 | ex
2020 | SDG | SDG | RtL | CZ06 | 0.057 | rec
2020 | SDG | SDG | RtL | CZ07 | 18.511 | old
2020 | SDG | SDG | RtL | CZ07 | 5.042 | ex
2020 | SDG | SDG | RtL | CZ07 | 1.122 | rec
2020 | SDG | Any | RtL | CZ07 | 0.281 | new
2020 | SDG | SDG | RtL | CZ08 | 1.703 | old
2020 | SDG | SDG | RtL | CZ08 | 0.463 | ex
2020 | SDG | SDG | RtL | CZ08 | 0.103 | rec
2020 | SDG | SDG | RtL | CZ10 | 6.894 | old
2020 | SDG | SDG | RtL | CZ10 | 1.878 | ex
2020 | SDG | SDG | RtL | CZ10 | 0.418 | rec
2020 | SDG | SDG | RtL | CZ14 | 0.026 | old
2020 | SDG | SDG | RtL | CZ14 | 0.008 | ex
2020 | SDG | SDG | RtL | CZ14 | 0.002 | rec
2020 | SDG | SDG | RtL | CZ15 | 0.009 | old
2020 | SDG | SDG | RtL | CZ15 | 0.004 | ex
2020 | SDG | SDG | RtL | CZ15 | 0.002 | rec
2020 | SDG | SDG | RtS | CZ06 | 0.949 | old
2020 | SDG | SDG | RtS | CZ06 | 0.259 | ex
2020 | SDG | SDG | RtS | CZ06 | 0.057 | rec
2020 | SDG | SDG | RtS | CZ07 | 18.511 | old
2020 | SDG | SDG | RtS | CZ07 | 5.042 | ex
2020 | SDG | SDG | RtS | CZ07 | 1.122 | rec
2020 | SDG | Any | RtS | CZ07 | 0.281 | new
2020 | SDG | SDG | RtS | CZ08 | 1.703 | old
2020 | SDG | SDG | RtS | CZ08 | 0.463 | ex
2020 | SDG | SDG | RtS | CZ08 | 0.103 | rec
2020 | SDG | SDG | RtS | CZ10 | 6.894 | old
2020 | SDG | SDG | RtS | CZ10 | 1.878 | ex
2020 | SDG | SDG | RtS | CZ10 | 0.418 | rec
2020 | SDG | SDG | RtS | CZ14 | 0.026 | old
2020 | SDG | SDG | RtS | CZ14 | 0.008 | ex
2020 | SDG | SDG | RtS | CZ14 | 0.002 | rec
2020 | SDG | SDG | RtS | CZ15 | 0.009 | old
2020 | SDG | SDG | RtS | CZ15 | 0.004 | ex
2020 | SDG | SDG | RtS | CZ15 | 0.002 | rec
2020 | SDG | SDG | SCn | CZ06 | 0.712 | old
2020 | SDG | SDG | SCn | CZ06 | 0.201 | ex
2020 | SDG | SDG | SCn | CZ06 | 0.04 | rec
2020 | SDG | SDG | SCn | CZ07 | 18.505 | old
2020 | SDG | SDG | SCn | CZ07 | 5.235 | ex
2020 | SDG | SDG | SCn | CZ07 | 1.04 | rec
2020 | SDG | Any | SCn | CZ07 | 0.26 | new
2020 | SDG | SDG | SCn | CZ08 | 0.433 | old
2020 | SDG | SDG | SCn | CZ08 | 0.122 | ex
2020 | SDG | SDG | SCn | CZ08 | 0.024 | rec
2020 | SDG | SDG | SCn | CZ10 | 8.45 | old
2020 | SDG | SDG | SCn | CZ10 | 2.391 | ex
2020 | SDG | SDG | SCn | CZ10 | 0.475 | rec
2020 | SDG | SDG | SCn | CZ14 | 0.082 | old
2020 | SDG | SDG | SCn | CZ14 | 0.025 | ex
2020 | SDG | SDG | SCn | CZ14 | 0.005 | rec
2020 | SDG | SDG | SCn | CZ15 | 0.039 | old
2020 | SDG | SDG | SCn | CZ15 | 0.011 | ex
2020 | SDG | SDG | SCn | CZ15 | 0.003 | rec
2020 | SDG | SDG | SUn | CZ06 | 0.712 | old
2020 | SDG | SDG | SUn | CZ06 | 0.201 | ex
2020 | SDG | SDG | SUn | CZ06 | 0.04 | rec
2020 | SDG | SDG | SUn | CZ07 | 18.505 | old
2020 | SDG | SDG | SUn | CZ07 | 5.235 | ex
2020 | SDG | SDG | SUn | CZ07 | 1.04 | rec
2020 | SDG | Any | SUn | CZ07 | 0.26 | new
2020 | SDG | SDG | SUn | CZ08 | 0.433 | old
2020 | SDG | SDG | SUn | CZ08 | 0.122 | ex
2020 | SDG | SDG | SUn | CZ08 | 0.024 | rec
2020 | SDG | SDG | SUn | CZ10 | 8.45 | old
2020 | SDG | SDG | SUn | CZ10 | 2.391 | ex
2020 | SDG | SDG | SUn | CZ10 | 0.475 | rec
2020 | SDG | SDG | SUn | CZ14 | 0.082 | old
2020 | SDG | SDG | SUn | CZ14 | 0.025 | ex
2020 | SDG | SDG | SUn | CZ14 | 0.005 | rec
2020 | SDG | SDG | SUn | CZ15 | 0.039 | old
2020 | SDG | SDG | SUn | CZ15 | 0.011 | ex
2020 | SDG | SDG | SUn | CZ15 | 0.003 | rec
2020 | SDG | SDG | WRf | CZ06 | 0.006 | old
2020 | SDG | SDG | WRf | CZ06 | 0.004 | ex
2020 | SDG | SDG | WRf | CZ06 | 0.002 | rec
2020 | SDG | SDG | WRf | CZ07 | 0.451 | old
2020 | SDG | SDG | WRf | CZ07 | 0.11 | ex
2020 | SDG | SDG | WRf | CZ07 | 0.03 | rec
2020 | SDG | Any | WRf | CZ07 | 0.008 | new
2020 | SDG | SDG | WRf | CZ10 | 0.129 | old
2020 | SDG | SDG | WRf | CZ10 | 0.032 | ex
2020 | SDG | SDG | WRf | CZ10 | 0.008 | rec
[7 empty] | #REF! | #REF!
[7 empty] | #REF! | #REF!
[7 empty] | #REF! | #REF!
[7 empty] | #REF! | #REF!

## PA and CZ combos (hidden)
Selected PA for each CZ based on available data and most preferred PA source
| BldgLoc | PA1 | PA2 | PA3 | Column1
| CZ01 | PGE
| CZ02 | PGE |  |  |  |  | Example lookup:
| CZ03 | PGE |  |  |  |  | CZ | PA
| CZ04 | PGE |  |  |  |  | CZ15 | SCE
| CZ05 | SCE | PGE
| CZ06 | SCE | SDG
| CZ07 | SDG | [7 empty] | Where Building Loaction is in multiple PAs 1. Verified that AStdWBkWh column matches to within 5%. 2. The oder for PAs is SCE, PGE and SDG
| CZ08 | SCE | SDG
| CZ09 | SCE
| CZ10 | SCE | SDG
| CZ11 | PGE
| CZ12 | PGE
| CZ13 | SCE | PGE
| CZ14 | SCE | SDG
| CZ15 | SCE | PGE | SDG
| CZ16 | SCE | PGE
Comparison
|  | Values | PA
|  | Count of Original index |  |  | Sum of AStdWBkWh
| BldgLoc | PGE | SCE | SDG | PGE | SCE | SDG |  | PGE | SCE | SDG
| CZ05 | 40 | 40 |  | 2828.8 | 2841.6 |  |  | 99.55% | 100% | 0%
| CZ06 |  | 40 | 40 |  | 4394.6 | 4395 |  | 0% | 100% | 100%
| CZ08 |  | 40 | 40 |  | 4850.2 | 4855.2 |  | 0% | 100% | 100.1%
| CZ10 |  | 40 | 40 |  | 4990.6 | 5013.6 |  | 0% | 100% | 100.5%
| CZ13 | 40 | 40 |  | 5186.4 | 5156 |  |  | 100.6% | 100% | 0%
| CZ14 |  | 40 | 40 |  | 4936.6 | 4920.8 |  | 0% | 100% | 99.68%
| CZ15 |  | 40 | 24 |  | 7624 | 4530 |  | 0% | 100% | 59.42%
| CZ16 | 40 | 40 |  | 3183.6 | 3156.8 |  |  | 100.8% | 100% | 0%
Detailed comparison
|  |  | Values | PA
|  |  | Count of Original index |  |  | Sum of AStdWBkWh
BldgLoc | MeasureID | BldgType | PGE | SCE | SDG | PGE | SCE | SDG |  | PGE | SCE | SDG | % differnce
CZ01 |  |  | 40 |  |  | 1009.2
CZ02 |  |  | 40 |  |  | 3361
CZ03 |  |  | 40 |  |  | 2548.8
CZ04 |  |  | 40 |  |  | 3802.6
CZ05 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC | 1 | 1 |  | 48.4 | 48.4 |  |  | 100% | 100% |  | 0%
|  | ESe | 1 | 1 |  | 41.3 | 41.3 |  |  | 100% | 100% |  | 0%
|  | EUn | 1 | 1 |  | 40.9 | 40.7 |  |  | 100.5% | 100% |  | -0.4914%
|  | Hsp | 1 | 1 |  | 23.4 | 23.5 |  |  | 99.57% | 100% |  | 0.4255%
|  | Htl | 1 | 1 |  | 84.1 | 84.7 |  |  | 99.29% | 100% |  | 0.7084%
|  | MBT | 1 | 1 |  | 49.9 | 49.7 |  |  | 100.4% | 100% |  | -0.4024%
|  | Nrs | 1 | 1 |  | 54.9 | 57 |  |  | 96.32% | 100% |  | 3.684%
|  | OfL | 1 | 1 |  | 47.9 | 48 |  |  | 99.79% | 100% |  | 0.2083%
|  | OfS | 1 | 1 |  | 55.6 | 55.5 |  |  | 100.2% | 100% |  | -0.1802%
|  | Rt3 | 1 | 1 |  | 52.6 | 52.4 |  |  | 100.4% | 100% |  | -0.3817%
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC | 1 | 1 |  | 88.8 | 88.8 |  |  | 100% | 100% |  | 0%
|  | ESe | 1 | 1 |  | 75.8 | 75.7 |  |  | 100.1% | 100% |  | -0.1321%
|  | EUn | 1 | 1 |  | 75 | 74.6 |  |  | 100.5% | 100% |  | -0.5362%
|  | Hsp | 1 | 1 |  | 42.9 | 43 |  |  | 99.77% | 100% |  | 0.2326%
|  | Htl | 1 | 1 |  | 154 | 155 |  |  | 99.35% | 100% |  | 0.6452%
|  | MBT | 1 | 1 |  | 91.5 | 91.3 |  |  | 100.2% | 100% |  | -0.2191%
|  | Nrs | 1 | 1 |  | 101 | 105 |  |  | 96.19% | 100% |  | 3.81%
|  | OfL | 1 | 1 |  | 87.9 | 88 |  |  | 99.89% | 100% |  | 0.1136%
|  | OfS | 1 | 1 |  | 102 | 102 |  |  | 100% | 100% |  | 0%
|  | Rt3 | 1 | 1 |  | 96.5 | 96.2 |  |  | 100.3% | 100% |  | -0.3119%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC | 1 | 1 |  | 48.4 | 48.4 |  |  | 100% | 100% |  | 0%
|  | ESe | 1 | 1 |  | 41.3 | 41.3 |  |  | 100% | 100% |  | 0%
|  | EUn | 1 | 1 |  | 40.9 | 40.7 |  |  | 100.5% | 100% |  | -0.4914%
|  | Hsp | 1 | 1 |  | 23.4 | 23.5 |  |  | 99.57% | 100% |  | 0.4255%
|  | Htl | 1 | 1 |  | 84.1 | 84.7 |  |  | 99.29% | 100% |  | 0.7084%
|  | MBT | 1 | 1 |  | 49.9 | 49.7 |  |  | 100.4% | 100% |  | -0.4024%
|  | Nrs | 1 | 1 |  | 54.9 | 57 |  |  | 96.32% | 100% |  | 3.684%
|  | OfL | 1 | 1 |  | 47.9 | 48 |  |  | 99.79% | 100% |  | 0.2083%
|  | OfS | 1 | 1 |  | 55.6 | 55.5 |  |  | 100.2% | 100% |  | -0.1802%
|  | Rt3 | 1 | 1 |  | 52.6 | 52.4 |  |  | 100.4% | 100% |  | -0.3817%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC | 1 | 1 |  | 88.8 | 88.8 |  |  | 100% | 100% |  | 0%
|  | ESe | 1 | 1 |  | 75.8 | 75.7 |  |  | 100.1% | 100% |  | -0.1321%
|  | EUn | 1 | 1 |  | 75 | 74.6 |  |  | 100.5% | 100% |  | -0.5362%
|  | Hsp | 1 | 1 |  | 42.9 | 43 |  |  | 99.77% | 100% |  | 0.2326%
|  | Htl | 1 | 1 |  | 154 | 155 |  |  | 99.35% | 100% |  | 0.6452%
|  | MBT | 1 | 1 |  | 91.5 | 91.3 |  |  | 100.2% | 100% |  | -0.2191%
|  | Nrs | 1 | 1 |  | 101 | 105 |  |  | 96.19% | 100% |  | 3.81%
|  | OfL | 1 | 1 |  | 87.9 | 88 |  |  | 99.89% | 100% |  | 0.1136%
|  | OfS | 1 | 1 |  | 102 | 102 |  |  | 100% | 100% |  | 0%
|  | Rt3 | 1 | 1 |  | 96.5 | 96.2 |  |  | 100.3% | 100% |  | -0.3119%
CZ06 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC |  | 1 | 1 |  | 76 | 76.1 |  |  | 100% | 100.1% | -0.1316%
|  | ESe |  | 1 | 1 |  | 56.8 | 57.2 |  |  | 100% | 100.7% | -0.7042%
|  | EUn |  | 1 | 1 |  | 62.8 | 62.8 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 50.3 | 50.3 |  |  | 100% | 100% | 0%
|  | Htl |  | 1 | 1 |  | 108 | 108 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 77.2 | 77.3 |  |  | 100% | 100.1% | -0.1295%
|  | Nrs |  | 1 | 1 |  | 96.1 | 95.5 |  |  | 100% | 99.38% | 0.6243%
|  | OfL |  | 1 | 1 |  | 78 | 78 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 81.6 | 81.9 |  |  | 100% | 100.4% | -0.3676%
|  | Rt3 |  | 1 | 1 |  | 88.1 | 88.2 |  |  | 100% | 100.1% | -0.1135%
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC |  | 1 | 1 |  | 139 | 140 |  |  | 100% | 100.7% | -0.7194%
|  | ESe |  | 1 | 1 |  | 104 | 105 |  |  | 100% | 101% | -0.9615%
|  | EUn |  | 1 | 1 |  | 115 | 115 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 92.4 | 92.2 |  |  | 100% | 99.78% | 0.2165%
|  | Htl |  | 1 | 1 |  | 199 | 198 |  |  | 100% | 99.5% | 0.5025%
|  | MBT |  | 1 | 1 |  | 142 | 142 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 176 | 175 |  |  | 100% | 99.43% | 0.5682%
|  | OfL |  | 1 | 1 |  | 143 | 143 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 150 | 150 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 162 | 162 |  |  | 100% | 100% | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC |  | 1 | 1 |  | 76 | 76.1 |  |  | 100% | 100.1% | -0.1316%
|  | ESe |  | 1 | 1 |  | 56.8 | 57.2 |  |  | 100% | 100.7% | -0.7042%
|  | EUn |  | 1 | 1 |  | 62.8 | 62.8 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 50.3 | 50.3 |  |  | 100% | 100% | 0%
|  | Htl |  | 1 | 1 |  | 108 | 108 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 77.2 | 77.3 |  |  | 100% | 100.1% | -0.1295%
|  | Nrs |  | 1 | 1 |  | 96.1 | 95.5 |  |  | 100% | 99.38% | 0.6243%
|  | OfL |  | 1 | 1 |  | 78 | 78 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 81.6 | 81.9 |  |  | 100% | 100.4% | -0.3676%
|  | Rt3 |  | 1 | 1 |  | 88.1 | 88.2 |  |  | 100% | 100.1% | -0.1135%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC |  | 1 | 1 |  | 139 | 140 |  |  | 100% | 100.7% | -0.7194%
|  | ESe |  | 1 | 1 |  | 104 | 105 |  |  | 100% | 101% | -0.9615%
|  | EUn |  | 1 | 1 |  | 115 | 115 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 92.4 | 92.2 |  |  | 100% | 99.78% | 0.2165%
|  | Htl |  | 1 | 1 |  | 199 | 198 |  |  | 100% | 99.5% | 0.5025%
|  | MBT |  | 1 | 1 |  | 142 | 142 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 176 | 175 |  |  | 100% | 99.43% | 0.5682%
|  | OfL |  | 1 | 1 |  | 143 | 143 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 150 | 150 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 162 | 162 |  |  | 100% | 100% | 0%
CZ07 |  |  |  |  | 40 |  |  | 4287.8
CZ08 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC |  | 1 | 1 |  | 83 | 83.1 |  |  | 100% | 100.1% | -0.1205%
|  | ESe |  | 1 | 1 |  | 66 | 66.6 |  |  | 100% | 100.9% | -0.9091%
|  | EUn |  | 1 | 1 |  | 69.6 | 69.8 |  |  | 100% | 100.3% | -0.2874%
|  | Hsp |  | 1 | 1 |  | 56.3 | 56.3 |  |  | 100% | 100% | 0%
|  | Htl |  | 1 | 1 |  | 119 | 119 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 81.5 | 81.6 |  |  | 100% | 100.1% | -0.1227%
|  | Nrs |  | 1 | 1 |  | 111 | 111 |  |  | 100% | 100% | 0%
|  | OfL |  | 1 | 1 |  | 79.6 | 79.6 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 89.6 | 89.9 |  |  | 100% | 100.3% | -0.3348%
|  | Rt3 |  | 1 | 1 |  | 99.5 | 99.7 |  |  | 100% | 100.2% | -0.201%
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC |  | 1 | 1 |  | 152 | 153 |  |  | 100% | 100.7% | -0.6579%
|  | ESe |  | 1 | 1 |  | 121 | 122 |  |  | 100% | 100.8% | -0.8264%
|  | EUn |  | 1 | 1 |  | 128 | 128 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 103 | 103 |  |  | 100% | 100% | 0%
|  | Htl |  | 1 | 1 |  | 219 | 218 |  |  | 100% | 99.54% | 0.4566%
|  | MBT |  | 1 | 1 |  | 150 | 150 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 204 | 203 |  |  | 100% | 99.51% | 0.4902%
|  | OfL |  | 1 | 1 |  | 146 | 146 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 164 | 165 |  |  | 100% | 100.6% | -0.6098%
|  | Rt3 |  | 1 | 1 |  | 183 | 183 |  |  | 100% | 100% | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC |  | 1 | 1 |  | 83 | 83.1 |  |  | 100% | 100.1% | -0.1205%
|  | ESe |  | 1 | 1 |  | 66 | 66.6 |  |  | 100% | 100.9% | -0.9091%
|  | EUn |  | 1 | 1 |  | 69.6 | 69.8 |  |  | 100% | 100.3% | -0.2874%
|  | Hsp |  | 1 | 1 |  | 56.3 | 56.3 |  |  | 100% | 100% | 0%
|  | Htl |  | 1 | 1 |  | 119 | 119 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 81.5 | 81.6 |  |  | 100% | 100.1% | -0.1227%
|  | Nrs |  | 1 | 1 |  | 111 | 111 |  |  | 100% | 100% | 0%
|  | OfL |  | 1 | 1 |  | 79.6 | 79.6 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 89.6 | 89.9 |  |  | 100% | 100.3% | -0.3348%
|  | Rt3 |  | 1 | 1 |  | 99.5 | 99.7 |  |  | 100% | 100.2% | -0.201%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC |  | 1 | 1 |  | 152 | 153 |  |  | 100% | 100.7% | -0.6579%
|  | ESe |  | 1 | 1 |  | 121 | 122 |  |  | 100% | 100.8% | -0.8264%
|  | EUn |  | 1 | 1 |  | 128 | 128 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 103 | 103 |  |  | 100% | 100% | 0%
|  | Htl |  | 1 | 1 |  | 219 | 218 |  |  | 100% | 99.54% | 0.4566%
|  | MBT |  | 1 | 1 |  | 150 | 150 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 204 | 203 |  |  | 100% | 99.51% | 0.4902%
|  | OfL |  | 1 | 1 |  | 146 | 146 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 164 | 165 |  |  | 100% | 100.6% | -0.6098%
|  | Rt3 |  | 1 | 1 |  | 183 | 183 |  |  | 100% | 100% | 0%
CZ09 |  |  |  | 40 |  |  | 4485.4 |  |  |  | 100%
CZ10 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC |  | 1 | 1 |  | 87.7 | 87.8 |  |  | 100% | 100.1% | -0.114%
|  | ESe |  | 1 | 1 |  | 66.5 | 66.7 |  |  | 100% | 100.3% | -0.3008%
|  | EUn |  | 1 | 1 |  | 76.3 | 76.3 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 57.8 | 57.9 |  |  | 100% | 100.2% | -0.173%
|  | Htl |  | 1 | 1 |  | 118 | 118 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 83 | 83 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 114 | 118 |  |  | 100% | 103.5% | -3.509%
|  | OfL |  | 1 | 1 |  | 83.9 | 84 |  |  | 100% | 100.1% | -0.1192%
|  | OfS |  | 1 | 1 |  | 91.1 | 91.1 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 102 | 102 |  |  | 100% | 100% | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC |  | 1 | 1 |  | 161 | 161 |  |  | 100% | 100% | 0%
|  | ESe |  | 1 | 1 |  | 122 | 122 |  |  | 100% | 100% | 0%
|  | EUn |  | 1 | 1 |  | 140 | 140 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 106 | 106 |  |  | 100% | 100% | 0%
|  | Htl |  | 1 | 1 |  | 217 | 217 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 152 | 152 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 209 | 216 |  |  | 100% | 103.3% | -3.349%
|  | OfL |  | 1 | 1 |  | 154 | 154 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 167 | 167 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 187 | 187 |  |  | 100% | 100% | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC |  | 1 | 1 |  | 87.7 | 87.8 |  |  | 100% | 100.1% | -0.114%
|  | ESe |  | 1 | 1 |  | 66.5 | 66.7 |  |  | 100% | 100.3% | -0.3008%
|  | EUn |  | 1 | 1 |  | 76.3 | 76.3 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 57.8 | 57.9 |  |  | 100% | 100.2% | -0.173%
|  | Htl |  | 1 | 1 |  | 118 | 118 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 83 | 83 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 114 | 118 |  |  | 100% | 103.5% | -3.509%
|  | OfL |  | 1 | 1 |  | 83.9 | 84 |  |  | 100% | 100.1% | -0.1192%
|  | OfS |  | 1 | 1 |  | 91.1 | 91.1 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 102 | 102 |  |  | 100% | 100% | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC |  | 1 | 1 |  | 161 | 161 |  |  | 100% | 100% | 0%
|  | ESe |  | 1 | 1 |  | 122 | 122 |  |  | 100% | 100% | 0%
|  | EUn |  | 1 | 1 |  | 140 | 140 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 106 | 106 |  |  | 100% | 100% | 0%
|  | Htl |  | 1 | 1 |  | 217 | 217 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 152 | 152 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 209 | 216 |  |  | 100% | 103.3% | -3.349%
|  | OfL |  | 1 | 1 |  | 154 | 154 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 167 | 167 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 187 | 187 |  |  | 100% | 100% | 0%
CZ11 |  |  | 40 |  |  | 5098.4
CZ12 |  |  | 40 |  |  | 4253.4
CZ13 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC | 1 | 1 |  | 92.9 | 92.8 |  |  | 100.1% | 100% |  | -0.1078%
|  | ESe | 1 | 1 |  | 66.9 | 66.8 |  |  | 100.1% | 100% |  | -0.1497%
|  | EUn | 1 | 1 |  | 84.8 | 84.7 |  |  | 100.1% | 100% |  | -0.1181%
|  | Hsp | 1 | 1 |  | 64.4 | 63.9 |  |  | 100.8% | 100% |  | -0.7825%
|  | Htl | 1 | 1 |  | 127 | 126 |  |  | 100.8% | 100% |  | -0.7937%
|  | MBT | 1 | 1 |  | 80.9 | 80.9 |  |  | 100% | 100% |  | 0%
|  | Nrs | 1 | 1 |  | 128 | 125 |  |  | 102.4% | 100% |  | -2.4%
|  | OfL | 1 | 1 |  | 83 | 82.7 |  |  | 100.4% | 100% |  | -0.3628%
|  | OfS | 1 | 1 |  | 89.6 | 89.5 |  |  | 100.1% | 100% |  | -0.1117%
|  | Rt3 | 1 | 1 |  | 97.7 | 97.7 |  |  | 100% | 100% |  | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC | 1 | 1 |  | 171 | 170 |  |  | 100.6% | 100% |  | -0.5882%
|  | ESe | 1 | 1 |  | 123 | 123 |  |  | 100% | 100% |  | 0%
|  | EUn | 1 | 1 |  | 156 | 155 |  |  | 100.6% | 100% |  | -0.6452%
|  | Hsp | 1 | 1 |  | 118 | 117 |  |  | 100.9% | 100% |  | -0.8547%
|  | Htl | 1 | 1 |  | 232 | 231 |  |  | 100.4% | 100% |  | -0.4329%
|  | MBT | 1 | 1 |  | 148 | 148 |  |  | 100% | 100% |  | 0%
|  | Nrs | 1 | 1 |  | 235 | 229 |  |  | 102.6% | 100% |  | -2.62%
|  | OfL | 1 | 1 |  | 152 | 152 |  |  | 100% | 100% |  | 0%
|  | OfS | 1 | 1 |  | 164 | 164 |  |  | 100% | 100% |  | 0%
|  | Rt3 | 1 | 1 |  | 179 | 179 |  |  | 100% | 100% |  | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC | 1 | 1 |  | 92.9 | 92.8 |  |  | 100.1% | 100% |  | -0.1078%
|  | ESe | 1 | 1 |  | 66.9 | 66.8 |  |  | 100.1% | 100% |  | -0.1497%
|  | EUn | 1 | 1 |  | 84.8 | 84.7 |  |  | 100.1% | 100% |  | -0.1181%
|  | Hsp | 1 | 1 |  | 64.4 | 63.9 |  |  | 100.8% | 100% |  | -0.7825%
|  | Htl | 1 | 1 |  | 127 | 126 |  |  | 100.8% | 100% |  | -0.7937%
|  | MBT | 1 | 1 |  | 80.9 | 80.9 |  |  | 100% | 100% |  | 0%
|  | Nrs | 1 | 1 |  | 128 | 125 |  |  | 102.4% | 100% |  | -2.4%
|  | OfL | 1 | 1 |  | 83 | 82.7 |  |  | 100.4% | 100% |  | -0.3628%
|  | OfS | 1 | 1 |  | 89.6 | 89.5 |  |  | 100.1% | 100% |  | -0.1117%
|  | Rt3 | 1 | 1 |  | 97.7 | 97.7 |  |  | 100% | 100% |  | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC | 1 | 1 |  | 171 | 170 |  |  | 100.6% | 100% |  | -0.5882%
|  | ESe | 1 | 1 |  | 123 | 123 |  |  | 100% | 100% |  | 0%
|  | EUn | 1 | 1 |  | 156 | 155 |  |  | 100.6% | 100% |  | -0.6452%
|  | Hsp | 1 | 1 |  | 118 | 117 |  |  | 100.9% | 100% |  | -0.8547%
|  | Htl | 1 | 1 |  | 232 | 231 |  |  | 100.4% | 100% |  | -0.4329%
|  | MBT | 1 | 1 |  | 148 | 148 |  |  | 100% | 100% |  | 0%
|  | Nrs | 1 | 1 |  | 235 | 229 |  |  | 102.6% | 100% |  | -2.62%
|  | OfL | 1 | 1 |  | 152 | 152 |  |  | 100% | 100% |  | 0%
|  | OfS | 1 | 1 |  | 164 | 164 |  |  | 100% | 100% |  | 0%
|  | Rt3 | 1 | 1 |  | 179 | 179 |  |  | 100% | 100% |  | 0%
CZ14 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC |  | 1 | 1 |  | 85.2 | 85.3 |  |  | 100% | 100.1% | -0.1174%
|  | ESe |  | 1 | 1 |  | 62.4 | 62.8 |  |  | 100% | 100.6% | -0.641%
|  | EUn |  | 1 | 1 |  | 78 | 77.9 |  |  | 100% | 99.87% | 0.1282%
|  | Hsp |  | 1 | 1 |  | 59.4 | 58.9 |  |  | 100% | 99.16% | 0.8418%
|  | Htl |  | 1 | 1 |  | 117 | 117 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 79.2 | 79.2 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 125 | 123 |  |  | 100% | 98.4% | 1.6%
|  | OfL |  | 1 | 1 |  | 82 | 82.3 |  |  | 100% | 100.4% | -0.3659%
|  | OfS |  | 1 | 1 |  | 87.9 | 87.7 |  |  | 100% | 99.77% | 0.2275%
|  | Rt3 |  | 1 | 1 |  | 94.2 | 94.3 |  |  | 100% | 100.1% | -0.1062%
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC |  | 1 | 1 |  | 156 | 156 |  |  | 100% | 100% | 0%
|  | ESe |  | 1 | 1 |  | 115 | 115 |  |  | 100% | 100% | 0%
|  | EUn |  | 1 | 1 |  | 143 | 143 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 109 | 108 |  |  | 100% | 99.08% | 0.9174%
|  | Htl |  | 1 | 1 |  | 215 | 215 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 145 | 145 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 230 | 225 |  |  | 100% | 97.83% | 2.174%
|  | OfL |  | 1 | 1 |  | 151 | 151 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 161 | 161 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 173 | 173 |  |  | 100% | 100% | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC |  | 1 | 1 |  | 85.2 | 85.3 |  |  | 100% | 100.1% | -0.1174%
|  | ESe |  | 1 | 1 |  | 62.4 | 62.8 |  |  | 100% | 100.6% | -0.641%
|  | EUn |  | 1 | 1 |  | 78 | 77.9 |  |  | 100% | 99.87% | 0.1282%
|  | Hsp |  | 1 | 1 |  | 59.4 | 58.9 |  |  | 100% | 99.16% | 0.8418%
|  | Htl |  | 1 | 1 |  | 117 | 117 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 79.2 | 79.2 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 125 | 123 |  |  | 100% | 98.4% | 1.6%
|  | OfL |  | 1 | 1 |  | 82 | 82.3 |  |  | 100% | 100.4% | -0.3659%
|  | OfS |  | 1 | 1 |  | 87.9 | 87.7 |  |  | 100% | 99.77% | 0.2275%
|  | Rt3 |  | 1 | 1 |  | 94.2 | 94.3 |  |  | 100% | 100.1% | -0.1062%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC |  | 1 | 1 |  | 156 | 156 |  |  | 100% | 100% | 0%
|  | ESe |  | 1 | 1 |  | 115 | 115 |  |  | 100% | 100% | 0%
|  | EUn |  | 1 | 1 |  | 143 | 143 |  |  | 100% | 100% | 0%
|  | Hsp |  | 1 | 1 |  | 109 | 108 |  |  | 100% | 99.08% | 0.9174%
|  | Htl |  | 1 | 1 |  | 215 | 215 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 145 | 145 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 | 1 |  | 230 | 225 |  |  | 100% | 97.83% | 2.174%
|  | OfL |  | 1 | 1 |  | 151 | 151 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 161 | 161 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 173 | 173 |  |  | 100% | 100% | 0%
CZ15 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC |  | 1 |  |  | 133 |  |  |  | 100%
|  | ESe |  | 1 | 1 |  | 102 | 102 |  |  | 100% | 100% | 0%
|  | EUn |  | 1 |  |  | 120 |  |  |  | 100%
|  | Hsp |  | 1 |  |  | 102 |  |  |  | 100%
|  | Htl |  | 1 | 1 |  | 172 | 172 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 123 | 123 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 |  |  | 190 |  |  |  | 100%
|  | OfL |  | 1 | 1 |  | 121 | 121 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 136 | 136 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 146 | 146 |  |  | 100% | 100% | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC |  | 1 |  |  | 244 |  |  |  | 100%
|  | ESe |  | 1 | 1 |  | 187 | 186 |  |  | 100% | 99.47% | 0.5348%
|  | EUn |  | 1 |  |  | 219 |  |  |  | 100%
|  | Hsp |  | 1 |  |  | 187 |  |  |  | 100%
|  | Htl |  | 1 | 1 |  | 315 | 315 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 226 | 226 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 |  |  | 349 |  |  |  | 100%
|  | OfL |  | 1 | 1 |  | 222 | 222 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 249 | 249 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 269 | 267 |  |  | 100% | 99.26% | 0.7435%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC |  | 1 |  |  | 133 |  |  |  | 100%
|  | ESe |  | 1 | 1 |  | 102 | 102 |  |  | 100% | 100% | 0%
|  | EUn |  | 1 |  |  | 120 |  |  |  | 100%
|  | Hsp |  | 1 |  |  | 102 |  |  |  | 100%
|  | Htl |  | 1 | 1 |  | 172 | 172 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 123 | 123 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 |  |  | 190 |  |  |  | 100%
|  | OfL |  | 1 | 1 |  | 121 | 121 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 136 | 136 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 146 | 146 |  |  | 100% | 100% | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC |  | 1 |  |  | 244 |  |  |  | 100%
|  | ESe |  | 1 | 1 |  | 187 | 186 |  |  | 100% | 99.47% | 0.5348%
|  | EUn |  | 1 |  |  | 219 |  |  |  | 100%
|  | Hsp |  | 1 |  |  | 187 |  |  |  | 100%
|  | Htl |  | 1 | 1 |  | 315 | 315 |  |  | 100% | 100% | 0%
|  | MBT |  | 1 | 1 |  | 226 | 226 |  |  | 100% | 100% | 0%
|  | Nrs |  | 1 |  |  | 349 |  |  |  | 100%
|  | OfL |  | 1 | 1 |  | 222 | 222 |  |  | 100% | 100% | 0%
|  | OfS |  | 1 | 1 |  | 249 | 249 |  |  | 100% | 100% | 0%
|  | Rt3 |  | 1 | 1 |  | 269 | 267 |  |  | 100% | 99.26% | 0.7435%
CZ16 | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | ECC | 1 | 1 |  | 56.1 | 56.1 |  |  | 100% | 100% |  | 0%
|  | ESe | 1 | 1 |  | 38.4 | 38.6 |  |  | 99.48% | 100% |  | 0.5181%
|  | EUn | 1 | 1 |  | 52.2 | 52.3 |  |  | 99.81% | 100% |  | 0.1912%
|  | Hsp | 1 | 1 |  | 34.8 | 34.5 |  |  | 100.9% | 100% |  | -0.8696%
|  | Htl | 1 | 1 |  | 98.8 | 97.3 |  |  | 101.5% | 100% |  | -1.542%
|  | MBT | 1 | 1 |  | 46.8 | 46.8 |  |  | 100% | 100% |  | 0%
|  | Nrs | 1 | 1 |  | 73.2 | 70.1 |  |  | 104.4% | 100% |  | -4.422%
|  | OfL | 1 | 1 |  | 50.2 | 49.9 |  |  | 100.6% | 100% |  | -0.6012%
|  | OfS | 1 | 1 |  | 56.3 | 56.2 |  |  | 100.2% | 100% |  | -0.1779%
|  | Rt3 | 1 | 1 |  | 55.1 | 55.1 |  |  | 100% | 100% |  | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | ECC | 1 | 1 |  | 103 | 103 |  |  | 100% | 100% |  | 0%
|  | ESe | 1 | 1 |  | 70.4 | 70.8 |  |  | 99.44% | 100% |  | 0.565%
|  | EUn | 1 | 1 |  | 95.8 | 95.9 |  |  | 99.9% | 100% |  | 0.1043%
|  | Hsp | 1 | 1 |  | 63.8 | 63.3 |  |  | 100.8% | 100% |  | -0.7899%
|  | Htl | 1 | 1 |  | 181 | 178 |  |  | 101.7% | 100% |  | -1.685%
|  | MBT | 1 | 1 |  | 85.9 | 85.9 |  |  | 100% | 100% |  | 0%
|  | Nrs | 1 | 1 |  | 134 | 129 |  |  | 103.9% | 100% |  | -3.876%
|  | OfL | 1 | 1 |  | 92 | 91.6 |  |  | 100.4% | 100% |  | -0.4367%
|  | OfS | 1 | 1 |  | 103 | 103 |  |  | 100% | 100% |  | 0%
|  | Rt3 | 1 | 1 |  | 101 | 101 |  |  | 100% | 100% |  | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | ECC | 1 | 1 |  | 56.1 | 56.1 |  |  | 100% | 100% |  | 0%
|  | ESe | 1 | 1 |  | 38.4 | 38.6 |  |  | 99.48% | 100% |  | 0.5181%
|  | EUn | 1 | 1 |  | 52.2 | 52.3 |  |  | 99.81% | 100% |  | 0.1912%
|  | Hsp | 1 | 1 |  | 34.8 | 34.5 |  |  | 100.9% | 100% |  | -0.8696%
|  | Htl | 1 | 1 |  | 98.8 | 97.3 |  |  | 101.5% | 100% |  | -1.542%
|  | MBT | 1 | 1 |  | 46.8 | 46.8 |  |  | 100% | 100% |  | 0%
|  | Nrs | 1 | 1 |  | 73.2 | 70.1 |  |  | 104.4% | 100% |  | -4.422%
|  | OfL | 1 | 1 |  | 50.2 | 49.9 |  |  | 100.6% | 100% |  | -0.6012%
|  | OfS | 1 | 1 |  | 56.3 | 56.2 |  |  | 100.2% | 100% |  | -0.1779%
|  | Rt3 | 1 | 1 |  | 55.1 | 55.1 |  |  | 100% | 100% |  | 0%
| NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | ECC | 1 | 1 |  | 103 | 103 |  |  | 100% | 100% |  | 0%
|  | ESe | 1 | 1 |  | 70.4 | 70.8 |  |  | 99.44% | 100% |  | 0.565%
|  | EUn | 1 | 1 |  | 95.8 | 95.9 |  |  | 99.9% | 100% |  | 0.1043%
|  | Hsp | 1 | 1 |  | 63.8 | 63.3 |  |  | 100.8% | 100% |  | -0.7899%
|  | Htl | 1 | 1 |  | 181 | 178 |  |  | 101.7% | 100% |  | -1.685%
|  | MBT | 1 | 1 |  | 85.9 | 85.9 |  |  | 100% | 100% |  | 0%
|  | Nrs | 1 | 1 |  | 134 | 129 |  |  | 103.9% | 100% |  | -3.876%
|  | OfL | 1 | 1 |  | 92 | 91.6 |  |  | 100.4% | 100% |  | -0.4367%
|  | OfS | 1 | 1 |  | 103 | 103 |  |  | 100% | 100% |  | 0%
|  | Rt3 | 1 | 1 |  | 101 | 101 |  |  | 100% | 100% |  | 0%
[8 empty] | min |  | 96.19% |  | 97.83% | -4.422%
[8 empty] | max |  | 104.4% |  | 103.5% | 3.81%
[8 empty] | count below 95% |  | 0 |  | 0
[8 empty] | count above 95% |  | 0 |  | 0
Note on E34: Nicholas Fette: For this measure, SDG doesn't cover all building types. See below.
Note on K45: Nicholas Fette: This column checks the ratio between PGE and SCE values. If difference is less than 5%, we take the SCE data for this CZ/MeasureID combination.
Note on K378: Nicholas Fette: No values differ by more than 5%. So we are taking SCE data for all cases where there is overlap between PA.

## Tier Def
| EER | IPLV |  | EER | IPLV
>=150 tons | 10.1 | 14 | <150 tons | 10.1 | 13.7
Tier 1 | 11.1 | 15.4 | Tier 1 | 11.1 | 15.1
| 9.901% | 10% |  | 9.901% | 10.22%
Tier 2 | 12.1 | 16.9 | Tier 2 | 12.1 | 16.6
| 19.8% | 20.71% |  | 19.8% | 21.17%

## Compare w step10.3
[5 empty] | Step 10.5 - Ex=(Old+Ex), No Rec, New is New |  |  | Step 10.3 - No Old, No Rec, Only Ex and New |  |  | % higher for Step 10.5
EnergyImpactID | BldgType | BldgVint | BldgHVAC | BldgLoc | AStdWBkWh | AStdWBkW | AStdWBtherm | AStdWBkWh | AStdWBkW | AStdWBtherm | AStdWBkWh | AStdWBkW
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ01 | 15.56 | 0.02 | 0 | 19.42 | 0.02 | 0 | -19.88% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ02 | 65.39 | 0.06 | 0 | 58.97 | 0.05 | 0 | 10.89% | 20%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ03 | 45.07 | 0.04 | 0 | 45.34 | 0.03 | 0 | -0.5955% | 33.33%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ04 | 71.98 | 0.05 | 0 | 66.21 | 0.04 | 0 | 8.715% | 25%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ05 | 54.14 | 0.03 | 0 | 51.18 | 0.03 | 0 | 5.784% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ06 | 84.38 | 0.04 | 0 | 79.79 | 0.04 | 0 | 5.753% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ07 | 80.17 | 0.03 | 0 | 77.93 | 0.03 | 0 | 2.874% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ08 | 90.57 | 0.04 | 0 | 84.56 | 0.04 | 0 | 7.107% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ09 | 86.75 | 0.05 | 0 | 79.5 | 0.05 | 0 | 9.119% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ10 | 95.37 | 0.06 | 0 | 88.04 | 0.05 | 0 | 8.326% | 20%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ11 | 97.57 | 0.06 | 0 | 87.64 | 0.06 | 0 | 11.33% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ12 | 80.07 | 0.06 | 0 | 72.42 | 0.05 | 0 | 10.56% | 20%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ13 | 98.78 | 0.06 | 0 | 88.75 | 0.05 | 0 | 11.3% | 20%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ14 | 92.92 | 0.05 | 0 | 84.76 | 0.05 | 0 | 9.627% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ15 | 150.47 | 0.05 | 0 | 135.34 | 0.05 | 0 | 11.18% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | Ex | Any | CZ16 | 60.79 | 0.05 | 0 | 54.75 | 0.05 | 0 | 11.03% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ01 | 28.52 | 0.04 | 0 | 35.61 | 0.04 | 0 | -19.91% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ02 | 120.09 | 0.1 | 0 | 108.34 | 0.09 | 0 | 10.85% | 11.11%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ03 | 82.7 | 0.07 | 0 | 83.21 | 0.06 | 0 | -0.6129% | 16.67%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ04 | 131.85 | 0.09 | 0 | 121.63 | 0.08 | 0 | 8.403% | 12.5%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ05 | 99.35 | 0.06 | 0 | 93.88 | 0.05 | 0 | 5.827% | 20%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ06 | 154.75 | 0.08 | 0 | 146.49 | 0.07 | 0 | 5.639% | 14.29%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ07 | 147.24 | 0.06 | 0 | 143.23 | 0.06 | 0 | 2.8% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ08 | 166.28 | 0.07 | 0 | 155.27 | 0.07 | 0 | 7.091% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ09 | 159.05 | 0.09 | 0 | 145.58 | 0.09 | 0 | 9.253% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ10 | 175 | 0.1 | 0 | 161.43 | 0.09 | 0 | 8.406% | 11.11%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ11 | 178.96 | 0.12 | 0 | 160.75 | 0.11 | 0 | 11.33% | 9.091%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ12 | 147.08 | 0.11 | 0 | 132.72 | 0.1 | 0 | 10.82% | 10%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ13 | 181.17 | 0.1 | 0 | 162.67 | 0.09 | 0 | 11.37% | 11.11%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ14 | 170.52 | 0.09 | 0 | 155.59 | 0.09 | 0 | 9.596% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ15 | 275.99 | 0.1 | 0 | 248.34 | 0.09 | 0 | 11.13% | 11.11%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | Ex | Any | CZ16 | 111.57 | 0.09 | 0 | 100.41 | 0.08 | 0 | 11.11% | 12.5%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ01 | 15.56 | 0.02 | 0 | 19.42 | 0.02 | 0 | -19.88% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ02 | 65.39 | 0.06 | 0 | 58.97 | 0.05 | 0 | 10.89% | 20%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ03 | 45.07 | 0.04 | 0 | 45.34 | 0.03 | 0 | -0.5955% | 33.33%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ04 | 71.98 | 0.05 | 0 | 66.21 | 0.04 | 0 | 8.715% | 25%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ05 | 54.14 | 0.03 | 0 | 51.18 | 0.03 | 0 | 5.784% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ06 | 84.38 | 0.04 | 0 | 79.79 | 0.04 | 0 | 5.753% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ07 | 80.17 | 0.03 | 0 | 77.93 | 0.03 | 0 | 2.874% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ08 | 90.57 | 0.04 | 0 | 84.56 | 0.04 | 0 | 7.107% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ09 | 86.75 | 0.05 | 0 | 79.5 | 0.05 | 0 | 9.119% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ10 | 95.37 | 0.06 | 0 | 88.04 | 0.05 | 0 | 8.326% | 20%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ11 | 97.57 | 0.06 | 0 | 87.64 | 0.06 | 0 | 11.33% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ12 | 80.07 | 0.06 | 0 | 72.42 | 0.05 | 0 | 10.56% | 20%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ13 | 98.78 | 0.06 | 0 | 88.75 | 0.05 | 0 | 11.3% | 20%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ14 | 92.92 | 0.05 | 0 | 84.76 | 0.05 | 0 | 9.627% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ15 | 150.47 | 0.05 | 0 | 135.34 | 0.05 | 0 | 11.18% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | Ex | Any | CZ16 | 60.79 | 0.05 | 0 | 54.75 | 0.05 | 0 | 11.03% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ01 | 28.52 | 0.04 | 0 | 35.61 | 0.04 | 0 | -19.91% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ02 | 120.09 | 0.1 | 0 | 108.34 | 0.09 | 0 | 10.85% | 11.11%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ03 | 82.7 | 0.07 | 0 | 83.21 | 0.06 | 0 | -0.6129% | 16.67%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ04 | 131.85 | 0.09 | 0 | 121.63 | 0.08 | 0 | 8.403% | 12.5%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ05 | 99.35 | 0.06 | 0 | 93.88 | 0.05 | 0 | 5.827% | 20%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ06 | 154.75 | 0.08 | 0 | 146.49 | 0.07 | 0 | 5.639% | 14.29%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ07 | 147.24 | 0.06 | 0 | 143.23 | 0.06 | 0 | 2.8% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ08 | 166.28 | 0.07 | 0 | 155.27 | 0.07 | 0 | 7.091% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ09 | 159.05 | 0.09 | 0 | 145.58 | 0.09 | 0 | 9.253% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ10 | 175 | 0.1 | 0 | 161.43 | 0.09 | 0 | 8.406% | 11.11%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ11 | 178.96 | 0.12 | 0 | 160.75 | 0.11 | 0 | 11.33% | 9.091%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ12 | 147.08 | 0.11 | 0 | 132.72 | 0.1 | 0 | 10.82% | 10%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ13 | 181.17 | 0.1 | 0 | 162.67 | 0.09 | 0 | 11.37% | 11.11%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ14 | 170.52 | 0.09 | 0 | 155.59 | 0.09 | 0 | 9.596% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ15 | 275.99 | 0.1 | 0 | 248.34 | 0.09 | 0 | 11.13% | 11.11%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | Ex | Any | CZ16 | 111.57 | 0.09 | 0 | 100.41 | 0.08 | 0 | 11.11% | 12.5%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ01 | 16.48 | 0.02 | 0 | 16.48 | 0.02 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ02 | 54.01 | 0.05 | 0 | 54.01 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ03 | 40.97 | 0.03 | 0 | 40.97 | 0.03 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ04 | 60.91 | 0.04 | 0 | 60.91 | 0.04 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ05 | 46.6 | 0.03 | 0 | 46.6 | 0.03 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ06 | 73.32 | 0.04 | 0 | 73.32 | 0.04 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ07 | 72.02 | 0.03 | 0 | 72.02 | 0.03 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ08 | 78.69 | 0.03 | 0 | 78.69 | 0.03 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ09 | 73.12 | 0.04 | 0 | 73.12 | 0.04 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ10 | 84.33 | 0.05 | 0 | 84.33 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ11 | 83 | 0.06 | 0 | 83 | 0.06 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ12 | 68.39 | 0.05 | 0 | 68.39 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ13 | 84.26 | 0.05 | 0 | 84.26 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ14 | 81.5 | 0.05 | 0 | 81.5 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ15 | 130.6 | 0.05 | 0 | 130.6 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | Com | New | Any | CZ16 | 52.09 | 0.04 | 0 | 52.09 | 0.04 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ01 | 30.24 | 0.04 | 0 | 30.24 | 0.04 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ02 | 99.11 | 0.09 | 0 | 99.11 | 0.09 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ03 | 75.12 | 0.05 | 0 | 75.12 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ04 | 111.75 | 0.07 | 0 | 111.75 | 0.07 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ05 | 85.48 | 0.05 | 0 | 85.48 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ06 | 134.25 | 0.07 | 0 | 134.25 | 0.07 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ07 | 132.19 | 0.06 | 0 | 132.19 | 0.06 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ08 | 144.4 | 0.06 | 0 | 144.4 | 0.06 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ09 | 134.08 | 0.08 | 0 | 134.08 | 0.08 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ10 | 154.94 | 0.09 | 0 | 154.94 | 0.09 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ11 | 152.34 | 0.1 | 0 | 152.34 | 0.1 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ12 | 125.39 | 0.09 | 0 | 125.39 | 0.09 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ13 | 154.52 | 0.09 | 0 | 154.52 | 0.09 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ14 | 149.62 | 0.08 | 0 | 149.62 | 0.08 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ15 | 239.6 | 0.09 | 0 | 239.6 | 0.09 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | Com | New | Any | CZ16 | 95.5 | 0.08 | 0 | 95.5 | 0.08 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ01 | 16.48 | 0.02 | 0 | 16.48 | 0.02 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ02 | 54.01 | 0.05 | 0 | 54.01 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ03 | 40.97 | 0.03 | 0 | 40.97 | 0.03 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ04 | 60.91 | 0.04 | 0 | 60.91 | 0.04 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ05 | 46.6 | 0.03 | 0 | 46.6 | 0.03 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ06 | 73.32 | 0.04 | 0 | 73.32 | 0.04 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ07 | 72.02 | 0.03 | 0 | 72.02 | 0.03 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ08 | 78.69 | 0.03 | 0 | 78.69 | 0.03 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ09 | 73.12 | 0.04 | 0 | 73.12 | 0.04 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ10 | 84.33 | 0.05 | 0 | 84.33 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ11 | 83 | 0.06 | 0 | 83 | 0.06 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ12 | 68.39 | 0.05 | 0 | 68.39 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ13 | 84.26 | 0.05 | 0 | 84.26 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ14 | 81.5 | 0.05 | 0 | 81.5 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ15 | 130.6 | 0.05 | 0 | 130.6 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | Com | New | Any | CZ16 | 52.09 | 0.04 | 0 | 52.09 | 0.04 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ01 | 30.24 | 0.04 | 0 | 30.24 | 0.04 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ02 | 99.11 | 0.09 | 0 | 99.11 | 0.09 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ03 | 75.12 | 0.05 | 0 | 75.12 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ04 | 111.75 | 0.07 | 0 | 111.75 | 0.07 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ05 | 85.48 | 0.05 | 0 | 85.48 | 0.05 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ06 | 134.25 | 0.07 | 0 | 134.25 | 0.07 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ07 | 132.19 | 0.06 | 0 | 132.19 | 0.06 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ08 | 144.4 | 0.06 | 0 | 144.4 | 0.06 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ09 | 134.08 | 0.08 | 0 | 134.08 | 0.08 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ10 | 154.94 | 0.09 | 0 | 154.94 | 0.09 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ11 | 152.34 | 0.1 | 0 | 152.34 | 0.1 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ12 | 125.39 | 0.09 | 0 | 125.39 | 0.09 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ13 | 154.52 | 0.09 | 0 | 154.52 | 0.09 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ14 | 149.62 | 0.08 | 0 | 149.62 | 0.08 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ15 | 239.6 | 0.09 | 0 | 239.6 | 0.09 | 0 | 0% | 0%
NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | Com | New | Any | CZ16 | 95.5 | 0.08 | 0 | 95.5 | 0.08 | 0 | 0% | 0%

## Pivots (hidden)
Sum of Fraction | Column Labels
Row Labels | ex | new | old | rec | Grand Total
CZ01 | 391% | 18.83% | 2017% | 73.63% | 25
SUn | 25.72% | 1.026% | 69.15% | 4.104% | 1
Asm | 15.28% | 0.8234% | 80.7% | 3.202% | 1
ECC | 7.182% | 0.4386% | 90.62% | 1.754% | 1
EPr | 13.35% | 0.5563% | 83.73% | 2.364% | 1
ERC | 13.35% | 0.5563% | 83.73% | 2.364% | 1
ESe | 13.35% | 0.5563% | 83.73% | 2.364% | 1
EUD | 7.182% | 0.4386% | 90.62% | 1.754% | 1
EUn | 7.182% | 0.4386% | 90.62% | 1.754% | 1
Gro | 12.9% | 0.7538% | 83.42% | 2.931% | 1
HGR | 22.9% | 1.022% | 72.09% | 3.988% | 1
Hsp | 17.98% | 0.7653% | 78.32% | 2.934% | 1
Htl | 22.9% | 1.022% | 72.09% | 3.988% | 1
MBT | 15.28% | 0.8234% | 80.7% | 3.202% | 1
MLI | 15.28% | 0.8234% | 80.7% | 3.202% | 1
Mtl | 22.9% | 1.022% | 72.09% | 3.988% | 1
Nrs | 17.98% | 0.7653% | 78.32% | 2.934% | 1
OfL | 20.35% | 0.6916% | 76.2% | 2.767% | 1
OfS | 14.06% | 0.7785% | 82.09% | 3.071% | 1
RFF | 6.667% | 0.5128% | 91.03% | 1.795% | 1
RSD | 6.667% | 0.5128% | 91.03% | 1.795% | 1
Rt3 | 12.92% | 0.7342% | 83.41% | 2.937% | 1
RtL | 12.92% | 0.7342% | 83.41% | 2.937% | 1
RtS | 12.92% | 0.7342% | 83.41% | 2.937% | 1
SCn | 25.72% | 1.026% | 69.15% | 4.104% | 1
WRf | 28.03% | 1.274% | 66.24% | 4.459% | 1
CZ02 | 366.1% | 18.64% | 2041% | 74.39% | 25
SUn | 16.26% | 0.8104% | 79.69% | 3.233% | 1
Asm | 12.85% | 0.6438% | 83.92% | 2.585% | 1
ECC | 16.28% | 0.7714% | 79.88% | 3.065% | 1
EPr | 11.81% | 0.4935% | 85.71% | 1.993% | 1
ERC | 11.81% | 0.4935% | 85.71% | 1.993% | 1
ESe | 11.81% | 0.4935% | 85.71% | 1.993% | 1
EUD | 16.28% | 0.7714% | 79.88% | 3.065% | 1
EUn | 16.28% | 0.7714% | 79.88% | 3.065% | 1
Gro | 14.08% | 0.7797% | 82.02% | 3.119% | 1
HGR | 18.22% | 0.9286% | 77.14% | 3.714% | 1
Hsp | 15.5% | 0.8062% | 80.45% | 3.24% | 1
Htl | 18.22% | 0.9286% | 77.14% | 3.714% | 1
MBT | 12.85% | 0.6438% | 83.92% | 2.585% | 1
MLI | 12.85% | 0.6438% | 83.92% | 2.585% | 1
Mtl | 18.22% | 0.9286% | 77.14% | 3.714% | 1
Nrs | 15.5% | 0.8062% | 80.45% | 3.24% | 1
OfL | 18.64% | 0.8655% | 77.04% | 3.457% | 1
OfS | 14.94% | 0.8821% | 80.66% | 3.511% | 1
RFF | 9.127% | 0.5599% | 88.13% | 2.184% | 1
RSD | 9.127% | 0.5599% | 88.13% | 2.184% | 1
Rt3 | 13.99% | 0.7737% | 82.13% | 3.106% | 1
RtL | 13.99% | 0.7737% | 82.13% | 3.106% | 1
RtS | 13.99% | 0.7737% | 82.13% | 3.106% | 1
SCn | 16.26% | 0.8104% | 79.69% | 3.233% | 1
WRf | 17.27% | 0.925% | 78.21% | 3.597% | 1
CZ03 | 296.5% | 15.47% | 2126% | 61.94% | 25
SUn | 11.88% | 0.7994% | 84.12% | 3.198% | 1
Asm | 11.42% | 0.5047% | 86.05% | 2.021% | 1
ECC | 13.26% | 0.5889% | 83.79% | 2.36% | 1
EPr | 9.098% | 0.3901% | 88.95% | 1.566% | 1
ERC | 9.098% | 0.3901% | 88.95% | 1.566% | 1
ESe | 9.098% | 0.3901% | 88.95% | 1.566% | 1
EUD | 13.26% | 0.5889% | 83.79% | 2.36% | 1
EUn | 13.26% | 0.5889% | 83.79% | 2.36% | 1
Gro | 12.44% | 0.719% | 83.96% | 2.879% | 1
HGR | 12.45% | 0.4612% | 85.24% | 1.848% | 1
Hsp | 11.2% | 0.7506% | 85.05% | 2.997% | 1
Htl | 12.45% | 0.4612% | 85.24% | 1.848% | 1
MBT | 11.42% | 0.5047% | 86.05% | 2.021% | 1
MLI | 11.42% | 0.5047% | 86.05% | 2.021% | 1
Mtl | 12.45% | 0.4612% | 85.24% | 1.848% | 1
Nrs | 11.2% | 0.7506% | 85.05% | 2.997% | 1
OfL | 15.9% | 0.7468% | 80.36% | 2.987% | 1
OfS | 14.19% | 0.8902% | 81.36% | 3.564% | 1
RFF | 9.437% | 0.5852% | 87.64% | 2.341% | 1
RSD | 9.437% | 0.5852% | 87.64% | 2.341% | 1
Rt3 | 12.38% | 0.7179% | 84.03% | 2.872% | 1
RtL | 12.38% | 0.7179% | 84.03% | 2.872% | 1
RtS | 12.38% | 0.7179% | 84.03% | 2.872% | 1
SCn | 11.88% | 0.7994% | 84.12% | 3.198% | 1
WRf | 13.09% | 0.86% | 82.61% | 3.44% | 1
CZ04 | 379.1% | 19.35% | 2024% | 77.31% | 25
SUn | 16.08% | 0.7932% | 79.95% | 3.173% | 1
Asm | 13.3% | 0.7051% | 83.18% | 2.821% | 1
ECC | 17.7% | 0.8297% | 78.17% | 3.302% | 1
EPr | 12.62% | 0.5143% | 84.8% | 2.057% | 1
ERC | 12.62% | 0.5143% | 84.8% | 2.057% | 1
ESe | 12.62% | 0.5143% | 84.8% | 2.057% | 1
EUD | 17.7% | 0.8297% | 78.17% | 3.302% | 1
EUn | 17.7% | 0.8297% | 78.17% | 3.302% | 1
Gro | 14.73% | 0.808% | 81.24% | 3.225% | 1
HGR | 18.03% | 0.9735% | 77.11% | 3.894% | 1
Hsp | 16.23% | 0.8408% | 79.59% | 3.341% | 1
Htl | 18.03% | 0.9735% | 77.11% | 3.894% | 1
MBT | 13.3% | 0.7051% | 83.18% | 2.821% | 1
MLI | 13.3% | 0.7051% | 83.18% | 2.821% | 1
Mtl | 18.03% | 0.9735% | 77.11% | 3.894% | 1
Nrs | 16.23% | 0.8408% | 79.59% | 3.341% | 1
OfL | 20.67% | 0.97% | 74.49% | 3.878% | 1
OfS | 15.59% | 0.9177% | 79.82% | 3.667% | 1
RFF | 9.565% | 0.5298% | 87.76% | 2.147% | 1
RSD | 9.565% | 0.5298% | 87.76% | 2.147% | 1
Rt3 | 14.67% | 0.8013% | 81.31% | 3.211% | 1
RtL | 14.67% | 0.8013% | 81.31% | 3.211% | 1
RtS | 14.67% | 0.8013% | 81.31% | 3.211% | 1
SCn | 16.08% | 0.7932% | 79.95% | 3.173% | 1
WRf | 15.35% | 0.853% | 80.43% | 3.362% | 1
CZ05 | 381.2% | 20.01% | 2020% | 78.58% | 25
SUn | 16.24% | 0.8792% | 79.6% | 3.283% | 1
Asm | 13.87% | 0.7375% | 82.42% | 2.973% | 1
ECC | 17.69% | 0.8534% | 78.11% | 3.35% | 1
EPr | 12.36% | 0.5736% | 84.96% | 2.103% | 1
ERC | 12.36% | 0.5736% | 84.96% | 2.103% | 1
ESe | 12.36% | 0.5736% | 84.96% | 2.103% | 1
EUD | 17.69% | 0.8534% | 78.11% | 3.35% | 1
EUn | 17.69% | 0.8534% | 78.11% | 3.35% | 1
Gro | 15.23% | 0.8501% | 80.52% | 3.401% | 1
HGR | 17.68% | 0.95% | 77.57% | 3.8% | 1
Hsp | 15.34% | 0.6735% | 81.2% | 2.782% | 1
Htl | 17.68% | 0.95% | 77.57% | 3.8% | 1
MBT | 13.87% | 0.7375% | 82.42% | 2.973% | 1
MLI | 13.87% | 0.7375% | 82.42% | 2.973% | 1
Mtl | 17.68% | 0.95% | 77.57% | 3.8% | 1
Nrs | 15.34% | 0.6735% | 81.2% | 2.782% | 1
OfL | 17.17% | 0.7976% | 78.84% | 3.19% | 1
OfS | 14.95% | 0.9002% | 80.55% | 3.601% | 1
RFF | 11.96% | 0.7905% | 84.39% | 2.866% | 1
RSD | 11.96% | 0.7905% | 84.39% | 2.866% | 1
Rt3 | 15.55% | 0.8589% | 80.12% | 3.479% | 1
RtL | 15.55% | 0.8589% | 80.12% | 3.479% | 1
RtS | 15.55% | 0.8589% | 80.12% | 3.479% | 1
SCn | 16.24% | 0.8792% | 79.6% | 3.283% | 1
WRf | 15.36% | 0.8532% | 80.38% | 3.413% | 1
CZ06 | 375% | 20.04% | 2025% | 80.16% | 25
SUn | 17.85% | 0.9263% | 77.52% | 3.702% | 1
Asm | 15.74% | 0.9059% | 79.74% | 3.622% | 1
ECC | 14.91% | 0.7465% | 81.36% | 2.98% | 1
EPr | 10.11% | 0.4096% | 87.83% | 1.646% | 1
ERC | 10.11% | 0.4096% | 87.83% | 1.646% | 1
ESe | 10.11% | 0.4096% | 87.83% | 1.646% | 1
EUD | 14.91% | 0.7465% | 81.36% | 2.98% | 1
EUn | 14.91% | 0.7465% | 81.36% | 2.98% | 1
Gro | 17.03% | 0.9875% | 78.04% | 3.948% | 1
HGR | 13.51% | 0.6778% | 83.1% | 2.709% | 1
Hsp | 15.08% | 0.6459% | 81.69% | 2.581% | 1
Htl | 13.51% | 0.6778% | 83.1% | 2.709% | 1
MBT | 15.74% | 0.9059% | 79.74% | 3.622% | 1
MLI | 15.74% | 0.9059% | 79.74% | 3.622% | 1
Mtl | 13.51% | 0.6778% | 83.1% | 2.709% | 1
Nrs | 15.08% | 0.6459% | 81.69% | 2.581% | 1
OfL | 9.541% | 0.468% | 88.12% | 1.872% | 1
OfS | 13.41% | 0.8519% | 82.33% | 3.406% | 1
RFF | 17.73% | 1.131% | 76.6% | 4.536% | 1
RSD | 17.73% | 1.131% | 76.6% | 4.536% | 1
Rt3 | 17.42% | 1.012% | 77.52% | 4.049% | 1
RtL | 17.42% | 1.012% | 77.52% | 4.049% | 1
RtS | 17.42% | 1.012% | 77.52% | 4.049% | 1
SCn | 17.85% | 0.9263% | 77.52% | 3.702% | 1
WRf | 18.63% | 1.07% | 76.02% | 4.28% | 1
CZ07 | 515.1% | 26.24% | 1854% | 104.7% | 25
SUn | 20.91% | 1.038% | 73.9% | 4.153% | 1
Asm | 25.08% | 1.413% | 67.87% | 5.643% | 1
ECC | 23.97% | 0.9804% | 71.12% | 3.93% | 1
EPr | 16.6% | 0.5662% | 80.56% | 2.277% | 1
ERC | 16.6% | 0.5662% | 80.56% | 2.277% | 1
ESe | 16.6% | 0.5662% | 80.56% | 2.277% | 1
EUD | 23.97% | 0.9804% | 71.12% | 3.93% | 1
EUn | 23.97% | 0.9804% | 71.12% | 3.93% | 1
Gro | 23.21% | 1.294% | 70.31% | 5.181% | 1
HGR | 28.52% | 1.562% | 63.67% | 6.248% | 1
Hsp | 14.18% | 0.6376% | 82.62% | 2.558% | 1
Htl | 28.52% | 1.562% | 63.67% | 6.248% | 1
MBT | 25.08% | 1.413% | 67.87% | 5.643% | 1
MLI | 25.08% | 1.413% | 67.87% | 5.643% | 1
Mtl | 28.52% | 1.562% | 63.67% | 6.248% | 1
Nrs | 14.18% | 0.6376% | 82.62% | 2.558% | 1
OfL | 17.87% | 0.8542% | 77.86% | 3.416% | 1
OfS | 13.22% | 0.7449% | 83.05% | 2.982% | 1
RFF | 14.6% | 0.8595% | 81.09% | 3.455% | 1
RSD | 14.6% | 0.8595% | 81.09% | 3.455% | 1
Rt3 | 20.2% | 1.126% | 74.17% | 4.496% | 1
RtL | 20.2% | 1.126% | 74.17% | 4.496% | 1
RtS | 20.2% | 1.126% | 74.17% | 4.496% | 1
SCn | 20.91% | 1.038% | 73.9% | 4.153% | 1
WRf | 18.36% | 1.336% | 75.29% | 5.008% | 1
CZ08 | 373.8% | 19.98% | 2026% | 79.95% | 25
SUn | 17.48% | 0.9101% | 77.97% | 3.641% | 1
Asm | 15.66% | 0.8994% | 79.84% | 3.597% | 1
ECC | 14.51% | 0.7232% | 81.87% | 2.899% | 1
EPr | 10.31% | 0.4174% | 87.6% | 1.666% | 1
ERC | 10.31% | 0.4174% | 87.6% | 1.666% | 1
ESe | 10.31% | 0.4174% | 87.6% | 1.666% | 1
EUD | 14.51% | 0.7232% | 81.87% | 2.899% | 1
EUn | 14.51% | 0.7232% | 81.87% | 2.899% | 1
Gro | 16.96% | 0.9826% | 78.12% | 3.933% | 1
HGR | 13.3% | 0.682% | 83.28% | 2.731% | 1
Hsp | 15.18% | 0.6591% | 81.52% | 2.639% | 1
Htl | 13.3% | 0.682% | 83.28% | 2.731% | 1
MBT | 15.66% | 0.8994% | 79.84% | 3.597% | 1
MLI | 15.66% | 0.8994% | 79.84% | 3.597% | 1
Mtl | 13.3% | 0.682% | 83.28% | 2.731% | 1
Nrs | 15.18% | 0.6591% | 81.52% | 2.639% | 1
OfL | 9.716% | 0.4918% | 87.83% | 1.967% | 1
OfS | 13.36% | 0.8464% | 82.42% | 3.38% | 1
RFF | 17.68% | 1.11% | 76.76% | 4.446% | 1
RSD | 17.68% | 1.11% | 76.76% | 4.446% | 1
Rt3 | 17.65% | 1.022% | 77.24% | 4.087% | 1
RtL | 17.65% | 1.022% | 77.24% | 4.087% | 1
RtS | 17.65% | 1.022% | 77.24% | 4.087% | 1
SCn | 17.48% | 0.9101% | 77.97% | 3.641% | 1
WRf | 18.75% | 1.067% | 75.9% | 4.28% | 1
CZ09 | 386.4% | 20.4% | 2012% | 81.59% | 25
SUn | 20.46% | 1.008% | 74.49% | 4.033% | 1
Asm | 15.73% | 0.8728% | 79.91% | 3.489% | 1
ECC | 12.2% | 0.5883% | 84.86% | 2.35% | 1
EPr | 10.9% | 0.4051% | 87.07% | 1.621% | 1
ERC | 10.9% | 0.4051% | 87.07% | 1.621% | 1
ESe | 10.9% | 0.4051% | 87.07% | 1.621% | 1
EUD | 12.2% | 0.5883% | 84.86% | 2.35% | 1
EUn | 12.2% | 0.5883% | 84.86% | 2.35% | 1
Gro | 17.75% | 1.015% | 77.17% | 4.059% | 1
HGR | 14.49% | 0.8932% | 81.03% | 3.579% | 1
Hsp | 16.64% | 0.7895% | 79.42% | 3.149% | 1
Htl | 14.49% | 0.8932% | 81.03% | 3.579% | 1
MBT | 15.73% | 0.8728% | 79.91% | 3.489% | 1
MLI | 15.73% | 0.8728% | 79.91% | 3.489% | 1
Mtl | 14.49% | 0.8932% | 81.03% | 3.579% | 1
Nrs | 16.64% | 0.7895% | 79.42% | 3.149% | 1
OfL | 10.26% | 0.5958% | 86.76% | 2.384% | 1
OfS | 13.5% | 0.794% | 82.53% | 3.176% | 1
RFF | 16.78% | 0.9217% | 78.62% | 3.678% | 1
RSD | 16.78% | 0.9217% | 78.62% | 3.678% | 1
Rt3 | 18.57% | 1.052% | 76.17% | 4.208% | 1
RtL | 18.57% | 1.052% | 76.17% | 4.208% | 1
RtS | 18.57% | 1.052% | 76.17% | 4.208% | 1
SCn | 20.46% | 1.008% | 74.49% | 4.033% | 1
WRf | 21.41% | 1.125% | 72.95% | 4.513% | 1
CZ10 | 737.8% | 38.53% | 1570% | 154% | 25
SUn | 45.41% | 2.653% | 41.32% | 10.61% | 1
Asm | 35.69% | 1.966% | 54.48% | 7.863% | 1
ECC | 28.85% | 1.358% | 64.34% | 5.45% | 1
EPr | 24.25% | 0.8953% | 71.27% | 3.59% | 1
ERC | 24.25% | 0.8953% | 71.27% | 3.59% | 1
ESe | 24.25% | 0.8953% | 71.27% | 3.59% | 1
EUD | 28.85% | 1.358% | 64.34% | 5.45% | 1
EUn | 28.85% | 1.358% | 64.34% | 5.45% | 1
Gro | 28.48% | 1.627% | 63.38% | 6.51% | 1
HGR | 28.7% | 1.575% | 63.46% | 6.267% | 1
Hsp | 19.38% | 1.182% | 74.72% | 4.717% | 1
Htl | 28.7% | 1.575% | 63.46% | 6.267% | 1
MBT | 35.69% | 1.966% | 54.48% | 7.863% | 1
MLI | 35.69% | 1.966% | 54.48% | 7.863% | 1
Mtl | 28.7% | 1.575% | 63.46% | 6.267% | 1
Nrs | 19.38% | 1.182% | 74.72% | 4.717% | 1
OfL | 25.16% | 1.274% | 68.48% | 5.094% | 1
OfS | 23.25% | 1.249% | 70.5% | 4.999% | 1
RFF | 31.77% | 1.416% | 61.16% | 5.65% | 1
RSD | 31.77% | 1.416% | 61.16% | 5.65% | 1
Rt3 | 31.36% | 1.701% | 60.13% | 6.804% | 1
RtL | 31.36% | 1.701% | 60.13% | 6.804% | 1
RtS | 31.36% | 1.701% | 60.13% | 6.804% | 1
SCn | 45.41% | 2.653% | 41.32% | 10.61% | 1
WRf | 21.18% | 1.392% | 71.86% | 5.569% | 1
CZ11 | 503.2% | 26.21% | 1866% | 104.9% | 25
SUn | 30.83% | 1.546% | 61.44% | 6.184% | 1
Asm | 18.63% | 1.024% | 76.25% | 4.098% | 1
ECC | 19.54% | 0.9466% | 75.71% | 3.803% | 1
EPr | 20.08% | 0.9388% | 75.25% | 3.734% | 1
ERC | 20.08% | 0.9388% | 75.25% | 3.734% | 1
ESe | 20.08% | 0.9388% | 75.25% | 3.734% | 1
EUD | 19.54% | 0.9466% | 75.71% | 3.803% | 1
EUn | 19.54% | 0.9466% | 75.71% | 3.803% | 1
Gro | 20.68% | 1.143% | 73.59% | 4.584% | 1
HGR | 19.78% | 1.051% | 74.92% | 4.245% | 1
Hsp | 19.99% | 0.98% | 75.11% | 3.92% | 1
Htl | 19.78% | 1.051% | 74.92% | 4.245% | 1
MBT | 18.63% | 1.024% | 76.25% | 4.098% | 1
MLI | 18.63% | 1.024% | 76.25% | 4.098% | 1
Mtl | 19.78% | 1.051% | 74.92% | 4.245% | 1
Nrs | 19.99% | 0.98% | 75.11% | 3.92% | 1
OfL | 23.7% | 1.256% | 70.04% | 5.012% | 1
OfS | 16.82% | 0.8961% | 78.7% | 3.584% | 1
RFF | 11.22% | 0.6234% | 85.66% | 2.494% | 1
RSD | 11.22% | 0.6234% | 85.66% | 2.494% | 1
Rt3 | 19.38% | 1.065% | 75.28% | 4.274% | 1
RtL | 19.38% | 1.065% | 75.28% | 4.274% | 1
RtS | 19.38% | 1.065% | 75.28% | 4.274% | 1
SCn | 30.83% | 1.546% | 61.44% | 6.184% | 1
WRf | 25.73% | 1.533% | 66.67% | 6.067% | 1
CZ12 | 491% | 25.47% | 1882% | 101.8% | 25
SUn | 27.74% | 1.469% | 64.91% | 5.877% | 1
Asm | 16.28% | 0.8587% | 79.43% | 3.435% | 1
ECC | 19.27% | 0.921% | 76.13% | 3.673% | 1
EPr | 19.05% | 0.8226% | 76.84% | 3.284% | 1
ERC | 19.05% | 0.8226% | 76.84% | 3.284% | 1
ESe | 19.05% | 0.8226% | 76.84% | 3.284% | 1
EUD | 19.27% | 0.921% | 76.13% | 3.673% | 1
EUn | 19.27% | 0.921% | 76.13% | 3.673% | 1
Gro | 20.12% | 1.02% | 74.78% | 4.08% | 1
HGR | 21.56% | 1.183% | 72.51% | 4.743% | 1
Hsp | 17.78% | 0.9814% | 77.31% | 3.932% | 1
Htl | 21.56% | 1.183% | 72.51% | 4.743% | 1
MBT | 16.28% | 0.8587% | 79.43% | 3.435% | 1
MLI | 16.28% | 0.8587% | 79.43% | 3.435% | 1
Mtl | 21.56% | 1.183% | 72.51% | 4.743% | 1
Nrs | 17.78% | 0.9814% | 77.31% | 3.932% | 1
OfL | 25.27% | 1.215% | 68.65% | 4.86% | 1
OfS | 17.11% | 0.9451% | 78.16% | 3.78% | 1
RFF | 11.87% | 0.6306% | 84.99% | 2.505% | 1
RSD | 11.87% | 0.6306% | 84.99% | 2.505% | 1
Rt3 | 19.25% | 0.9748% | 75.87% | 3.899% | 1
RtL | 19.25% | 0.9748% | 75.87% | 3.899% | 1
RtS | 19.25% | 0.9748% | 75.87% | 3.899% | 1
SCn | 27.74% | 1.469% | 64.91% | 5.877% | 1
WRf | 27.47% | 1.845% | 63.31% | 7.38% | 1
CZ13 | 517.7% | 28.37% | 1841% | 113.3% | 25
SUn | 31.21% | 1.612% | 60.73% | 6.449% | 1
Asm | 18.94% | 1.096% | 75.59% | 4.372% | 1
ECC | 22.99% | 1.166% | 71.18% | 4.662% | 1
EPr | 18.44% | 0.8991% | 77.04% | 3.612% | 1
ERC | 18.44% | 0.8991% | 77.04% | 3.612% | 1
ESe | 18.44% | 0.8991% | 77.04% | 3.612% | 1
EUD | 22.99% | 1.166% | 71.18% | 4.662% | 1
EUn | 22.99% | 1.166% | 71.18% | 4.662% | 1
Gro | 21.41% | 1.266% | 72.28% | 5.048% | 1
HGR | 18.67% | 1.081% | 75.99% | 4.252% | 1
Hsp | 19.36% | 1.005% | 75.63% | 4% | 1
Htl | 18.67% | 1.081% | 75.99% | 4.252% | 1
MBT | 18.94% | 1.096% | 75.59% | 4.372% | 1
MLI | 18.94% | 1.096% | 75.59% | 4.372% | 1
Mtl | 18.67% | 1.081% | 75.99% | 4.252% | 1
Nrs | 19.36% | 1.005% | 75.63% | 4% | 1
OfL | 19.85% | 1.201% | 74.14% | 4.807% | 1
OfS | 16.95% | 0.913% | 78.48% | 3.659% | 1
RFF | 15.2% | 0.82% | 80.7% | 3.28% | 1
RSD | 15.2% | 0.82% | 80.7% | 3.28% | 1
Rt3 | 21.54% | 1.242% | 72.24% | 4.977% | 1
RtL | 21.54% | 1.242% | 72.24% | 4.977% | 1
RtS | 21.54% | 1.242% | 72.24% | 4.977% | 1
SCn | 31.21% | 1.612% | 60.73% | 6.449% | 1
WRf | 26.14% | 1.669% | 65.52% | 6.671% | 1
CZ14 | 664% | 35.83% | 1659% | 141.1% | 25
SUn | 40.32% | 2.337% | 48.02% | 9.325% | 1
Asm | 28.42% | 1.566% | 63.77% | 6.244% | 1
ECC | 28.68% | 1.387% | 64.35% | 5.587% | 1
EPr | 21.86% | 0.8252% | 74% | 3.313% | 1
ERC | 21.86% | 0.8252% | 74% | 3.313% | 1
ESe | 21.86% | 0.8252% | 74% | 3.313% | 1
EUD | 28.68% | 1.387% | 64.35% | 5.587% | 1
EUn | 28.68% | 1.387% | 64.35% | 5.587% | 1
Gro | 27.28% | 1.56% | 64.92% | 6.248% | 1
HGR | 24.66% | 1.46% | 68.01% | 5.869% | 1
Hsp | 19.33% | 1.182% | 74.88% | 4.606% | 1
Htl | 24.66% | 1.46% | 68.01% | 5.869% | 1
MBT | 28.42% | 1.566% | 63.77% | 6.244% | 1
MLI | 28.42% | 1.566% | 63.77% | 6.244% | 1
Mtl | 24.66% | 1.46% | 68.01% | 5.869% | 1
Nrs | 19.33% | 1.182% | 74.88% | 4.606% | 1
OfL | 19.73% | 1.094% | 74.79% | 4.389% | 1
OfS | 22.4% | 1.217% | 71.54% | 4.846% | 1
RFF | 30.08% | 1.377% | 63.13% | 5.421% | 1
RSD | 30.08% | 1.377% | 63.13% | 5.421% | 1
Rt3 | 27.86% | 1.523% | 64.54% | 6.079% | 1
RtL | 27.86% | 1.523% | 64.54% | 6.079% | 1
RtS | 27.86% | 1.523% | 64.54% | 6.079% | 1
SCn | 40.32% | 2.337% | 48.02% | 9.325% | 1
WRf | 20.75% | 1.887% | 71.7% | 5.66% | 1
CZ15 | 763.4% | 40.35% | 1536% | 160.4% | 25
SUn | 46.4% | 2.729% | 39.98% | 10.89% | 1
Asm | 37.09% | 2.037% | 52.73% | 8.15% | 1
ECC | 30.15% | 1.479% | 62.5% | 5.868% | 1
EPr | 25.38% | 0.9974% | 69.78% | 3.842% | 1
ERC | 25.38% | 0.9974% | 69.78% | 3.842% | 1
ESe | 25.38% | 0.9974% | 69.78% | 3.842% | 1
EUD | 30.15% | 1.479% | 62.5% | 5.868% | 1
EUn | 30.15% | 1.479% | 62.5% | 5.868% | 1
Gro | 29.27% | 1.676% | 62.34% | 6.715% | 1
HGR | 28.73% | 1.56% | 63.45% | 6.258% | 1
Hsp | 20.05% | 1.247% | 73.71% | 4.987% | 1
Htl | 28.73% | 1.56% | 63.45% | 6.258% | 1
MBT | 37.09% | 2.037% | 52.73% | 8.15% | 1
MLI | 37.09% | 2.037% | 52.73% | 8.15% | 1
Mtl | 28.73% | 1.56% | 63.45% | 6.258% | 1
Nrs | 20.05% | 1.247% | 73.71% | 4.987% | 1
OfL | 26.9% | 1.37% | 66.23% | 5.495% | 1
OfS | 24.9% | 1.335% | 68.43% | 5.333% | 1
RFF | 33.19% | 1.456% | 59.52% | 5.825% | 1
RSD | 33.19% | 1.456% | 59.52% | 5.825% | 1
Rt3 | 32.67% | 1.777% | 58.46% | 7.088% | 1
RtL | 32.67% | 1.777% | 58.46% | 7.088% | 1
RtS | 32.67% | 1.777% | 58.46% | 7.088% | 1
SCn | 46.4% | 2.729% | 39.98% | 10.89% | 1
WRf | 21.01% | 1.556% | 71.6% | 5.837% | 1
CZ16 | 642.3% | 35.83% | 1681% | 140.9% | 25
SUn | 41.03% | 2.35% | 47.27% | 9.343% | 1
Asm | 27.81% | 1.546% | 64.47% | 6.174% | 1
ECC | 29.86% | 1.454% | 62.83% | 5.847% | 1
EPr | 22.43% | 0.9202% | 73.02% | 3.635% | 1
ERC | 22.43% | 0.9202% | 73.02% | 3.635% | 1
ESe | 22.43% | 0.9202% | 73.02% | 3.635% | 1
EUD | 29.86% | 1.454% | 62.83% | 5.847% | 1
EUn | 29.86% | 1.454% | 62.83% | 5.847% | 1
Gro | 25.38% | 1.453% | 67.37% | 5.799% | 1
HGR | 19.6% | 1.252% | 74.14% | 5.008% | 1
Hsp | 19.04% | 1.114% | 75.28% | 4.566% | 1
Htl | 19.6% | 1.252% | 74.14% | 5.008% | 1
MBT | 27.81% | 1.546% | 64.47% | 6.174% | 1
MLI | 27.81% | 1.546% | 64.47% | 6.174% | 1
Mtl | 19.6% | 1.252% | 74.14% | 5.008% | 1
Nrs | 19.04% | 1.114% | 75.28% | 4.566% | 1
OfL | 18.98% | 1.073% | 75.66% | 4.282% | 1
OfS | 19.18% | 1.049% | 75.59% | 4.18% | 1
RFF | 26.11% | 1.25% | 67.79% | 4.856% | 1
RSD | 26.11% | 1.25% | 67.79% | 4.856% | 1
Rt3 | 26.59% | 1.479% | 65.96% | 5.975% | 1
RtL | 26.59% | 1.479% | 65.96% | 5.975% | 1
RtS | 26.59% | 1.479% | 65.96% | 5.975% | 1
SCn | 41.03% | 2.35% | 47.27% | 9.343% | 1
WRf | 27.59% | 2.874% | 60.34% | 9.195% | 1
Grand Total | 77.838 | 4.0955 | 301.7793 | 16.2872 | 400