## MeasureExAnte
PA | MeasureID | Qualifier | SourceDesc | Sector | EnergyImpactID | MeasCostID | StdCostID | EUL_ID | RUL_ID | Version | VersionSource | LastMod | Description | MeasDesc | MeasTechID | MeasImpactType | MeasImpactCalcType | UseCategory | UseSubCategory | TechGroup | TechType | Status | Comment | PreDesc | PreMultiTech | PreTechID | PreTechGroup | PreTechType | StdDesc | StdMultiTech | StdTechID | StdTechGroup | StdTechType | ScaleBasis | TechBased | ApplyIE | IETableName | ImpWeighting | WeightGroupID | LegacyID | StdScaleVal | PreScaleVal | DEER Measure ID | DEER Scale
Any | SWHC020A | None | SWHC020-02 | Com | SWHC020A | SWHC020_02_M001 | SWHC020_02_B001 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | AirCldScrewChlr-gte150tons-10.1EER-14IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [5 empty] | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | weighted
Any | SWHC020B | None | SWHC020-02 | Com | SWHC020B | SWHC020_02_M002 | SWHC020_02_B001 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | AirCldScrewChlr-gte150tons-10.1EER-14IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [5 empty] | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | weighted
Any | SWHC020C | None | SWHC020-02 | Com | SWHC020C | SWHC020_02_M003 | SWHC020_02_B002 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | AirCldScrewChlr-lt150tons-10.1EER-13.7IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [5 empty] | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | weighted
Any | SWHC020D | None | SWHC020-02 | Com | SWHC020D | SWHC020_02_M004 | SWHC020_02_B002 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | AirCldScrewChlr-lt150tons-10.1EER-13.7IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [5 empty] | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | weighted
Any | SWHC020A | None | SWHC020-02 | Ind | SWHC020A | SWHC020_02_M001 | SWHC020_02_B001 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | AirCldScrewChlr-gte150tons-10.1EER-14IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [5 empty] | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-11.1EER-15.4IPLV | weighted
Any | SWHC020B | None | SWHC020-02 | Ind | SWHC020B | SWHC020_02_M002 | SWHC020_02_B001 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | AirCldScrewChlr-gte150tons-10.1EER-14IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [5 empty] | NE-HVAC-Chlr-AirCldScrewChlr-gte150tons-12.1EER-16.9IPLV | weighted
Any | SWHC020C | None | SWHC020-02 | Ind | SWHC020C | SWHC020_02_M003 | SWHC020_02_B002 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | AirCldScrewChlr-lt150tons-10.1EER-13.7IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [5 empty] | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-11.1EER-15.1IPLV | weighted
Any | SWHC020D | None | SWHC020-02 | Ind | SWHC020D | SWHC020_02_M004 | SWHC020_02_B002 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | AirCldScrewChlr-lt150tons-10.1EER-13.7IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [5 empty] | NE-HVAC-Chlr-AirCldScrewChlr-lt150tons-12.1EER-16.6IPLV | weighted

## ImplementationExAnte
PA | ImplementationID | StartDate | ExpiryDate | SourceDesc | MeasAppType | DeliveryType | MeasureID | MeasQualifier | Sector | GSIA_ID | NTG_ID | CostQualifier | MeasCostID | StdCostID | Version | VersionSource | LastMod | Description | ImplementerID | MeasImpactType | Status | Comment
SCE | AC-20094ComAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyFiSDrI
SCE | AC-21113ComAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyFiSDwSD
SCE | AC-20095ComAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyMdSMdS
SCE | AC-21114ComAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyFiSDrI
SCE | AC-20096ComAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyFiSDwSD
SCE | AC-21115ComAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyMdSMdS
SCE | AC-20097ComAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyFiSDrI
SCE | AC-21116ComAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyFiSDwSD
SCE | AC-20094ComAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyMdSMdS
SCE | AC-21113ComAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyFiSDrI
SCE | AC-20095ComAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyFiSDwSD
SCE | AC-21114ComAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyMdSMdS
SCE | AC-20096ComAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyFiSDrI
SCE | AC-21115ComAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyFiSDwSD
SCE | AC-20097ComAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyMdSMdS
SCE | AC-21116ComAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyFiSDrI
SCE | AC-20094ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyFiSDwSD
SCE | AC-21113ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyMdSMdS
SCE | AC-20095ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyFiSDrI
SCE | AC-21114ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyFiSDwSD
SCE | AC-20096ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyMdSMdS
SCE | AC-21115ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyFiSDrI
SCE | AC-20097ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyFiSDwSD
SCE | AC-21116ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyMdSMdS
SCE | AC-20094IndAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyFiSDrI
SCE | AC-21113IndAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyFiSDwSD
SCE | AC-20095IndAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyMdSMdS
SCE | AC-21114IndAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyFiSDrI
SCE | AC-20096IndAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyFiSDwSD
SCE | AC-21115IndAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) | AC-20094ComAnyMdSMdS
SCE | AC-20097IndAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyFiSDrI
SCE | AC-21116IndAnyUpSUSI | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyFiSDwSD
SCE | AC-20094IndAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyMdSMdS
SCE | AC-21113IndAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyFiSDrI
SCE | AC-20095IndAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyFiSDwSD
SCE | AC-21114IndAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) | AC-20095ComAnyMdSMdS
SCE | AC-20096IndAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyFiSDrI
SCE | AC-21115IndAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyFiSDwSD
SCE | AC-20097IndAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyMdSMdS
SCE | AC-21116IndAnyFiSDwSD | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyFiSDrI
SCE | AC-20094ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyFiSDwSD
SCE | AC-21113IndAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) | AC-20096ComAnyMdSMdS
SCE | AC-20095ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyFiSDrI
SCE | AC-21114IndAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyFiSDwSD
SCE | AC-20096ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyMdSMdS
SCE | AC-21115IndAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyFiSDrI
SCE | AC-20097ComAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyFiSDwSD
SCE | AC-21116IndAnyFiSDrI | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed |  | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) | AC-20097ComAnyMdSMdS
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV378 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV379 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV380 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
PGE | HV381 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467168 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467167 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467170 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467169 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467172 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467171 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467174 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467173 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467175 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467176 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467179 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467180 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467183 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467184 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467187 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467188 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467177 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467178 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467181 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467182 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467185 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467186 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467189 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467190 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467168 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467167 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467170 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467169 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467172 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467171 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467174 | 2022-01-01 |  | SWHC020-02 | NR | UpDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467173 | 2022-01-01 |  | SWHC020-02 | NC | UpDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467175 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467176 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467179 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467180 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467183 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467184 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467187 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467188 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemed | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467177 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467178 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M001 | SWHC020_02_B001 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 11.1 EER, 15.4 IPLV) |  | Deem-WP | Proposed
SDG | 467181 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467182 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M002 | SWHC020_02_B002 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (>= 150 tons, 12.1 EER, 16.9 IPLV) |  | Deem-WP | Proposed
SDG | 467185 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467186 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M003 | SWHC020_02_B003 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 11.1 EER, 15.1 IPLV) |  | Deem-WP | Proposed
SDG | 467189 | 2022-01-01 |  | SWHC020-02 | NR | DnDeemDI | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed
SDG | 467190 | 2022-01-01 |  | SWHC020-02 | NC | DnDeemDI | SWHC020D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC020_02_M004 | SWHC020_02_B004 | ExAnte2022 | IOU workpaper | 2020-11-19 | Air Cooled Constant Speed Screw Chiller (< 150 tons, 12.1 EER, 16.6 IPLV) |  | Deem-WP | Proposed

## EnergyImpactExAnte
PA | EnergyImpactID | BldgType | BldgVint | BldgLoc | BldgHVAC | SourceDesc | Version | VersionSource | LastMod | NormUnit | NumUnit | MeasArea | ScaleBasis | APreWBkWh | APreWBkW | APreWBtherm | AStdWBkWh | AStdWBkW | AStdWBtherm | APreEUkWh | APreEUkW | APreEUtherm | AStdEUkWh | AStdEUkW | AStdEUtherm | ElecImpactProfile | GasImpactProfile | Flag
Any | SWHC020A | Com | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 15.56 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.39 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45.07 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.98 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.14 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.38 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 80.17 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.57 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.75 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.37 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 97.57 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 80.07 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 98.78 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 92.92 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 150.47 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.79 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 9.28 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 62.29 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 41.26 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.83 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 46.61 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.69 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.12 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.58 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.62 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 94.92 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.91 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.58 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 99.93 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.36 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143.79 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.31 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 7.98 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.51 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 32.52 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.4 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.08 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.29 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 58.23 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.52 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.17 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.78 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.8 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.21 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.46 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 70.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 113.01 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 44.8 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 15.55 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.16 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.69 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.78 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45.71 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 70.77 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 63.56 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.29 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.2 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.9 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.89 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 80.18 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.51 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87.63 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 132.82 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 57.56 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 6.45 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.14 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 29.7 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 50.79 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 28.52 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 61.78 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.44 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 67.94 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 66.32 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.74 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.71 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.61 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.89 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.47 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120.08 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.11 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.73 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 103.62 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.08 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 108.72 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 99.46 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.99 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 121.98 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.26 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.47 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.12 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.82 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.1 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 141.42 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 135.27 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 191.27 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111.88 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 11.33 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.71 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 39.57 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.42 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 46.46 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.44 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.86 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.42 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.95 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.23 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.38 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 69.83 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.26 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.9 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.23 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 49.02 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 19.98 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.44 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.23 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.88 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.5 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 107.83 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 108.77 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 123.65 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115.51 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.12 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.43 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 110.69 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 142.18 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.89 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 211.23 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.5 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 11.22 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 61.83 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.26 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 69.08 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.33 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.51 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.5 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.46 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.58 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.29 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.74 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.73 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.19 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 92.59 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136.65 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 53.72 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 13.34 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.53 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 49.61 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.9 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 58.88 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.82 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.87 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.1 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.5 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 102.74 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 104.67 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87.87 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 104.71 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.73 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 159.49 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 62.97 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 11.53 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 69.1 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45.37 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.78 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 50.9 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 88.1 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.63 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 103.98 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.42 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 104.01 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 97.37 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.85 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100.28 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.95 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149.85 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.83 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 16.48 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.01 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.97 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.91 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 46.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.32 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.02 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.69 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.12 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.33 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.39 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.26 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.5 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Com | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.09 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 15 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 56.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.7 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 63.9 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 48.8 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.1 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.9 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 80.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.7 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.3 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.7 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.9 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.1 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ECC | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 9.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 38.2 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 27.1 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.8 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 34.9 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 44.3 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 53 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 50.5 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.4 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.9 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.5 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.4 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.8 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.9 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | ESe | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 34.2 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 12.4 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 49.9 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 34.9 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 39.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 63 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.2 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.5 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.8 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.2 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.8 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | EUn | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 48.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 4.7 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 30 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 22.9 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 36.1 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 20.4 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 43.2 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.2 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 47.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 47.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 43.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 56.7 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 88.8 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Hsp | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 30.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 67.8 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87.6 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 105 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 112 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 113 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 122 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 117 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Htl | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.1 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 17.9 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 53.5 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 61.2 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 48.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.4 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.8 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.5 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | MBT | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 46 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 5.7 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.5 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 31.3 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 30.4 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 67.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 62.3 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.7 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.2 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 97.9 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.4 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 110 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 177 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Nrs | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 14.1 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.1 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.7 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 58.3 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45.3 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.1 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.5 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.3 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.4 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.4 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.9 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 116 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfL | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 47 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 16.2 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.3 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 43.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.8 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.2 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.7 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.9 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.4 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.4 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.1 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.7 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.1 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | OfS | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 15.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.2 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 44.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.4 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 46.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.2 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 97.4 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.1 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.7 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.5 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 141 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020A | Rt3 | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 28.52 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120.09 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.7 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.85 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 99.35 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.75 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 147.24 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166.28 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 159.05 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 178.96 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 147.08 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 181.17 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170.52 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 275.99 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111.57 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 17.07 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 114.48 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.69 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126.15 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.54 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 146.55 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139.5 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166.32 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 153.05 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 174.31 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 186.31 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 156.97 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183.32 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 167.75 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 263.56 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109.13 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 14.68 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 94.61 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.72 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.47 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.46 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 108.48 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 106.49 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.82 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 117.95 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 138.85 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.58 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.82 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 144.09 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 129.69 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 206.84 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.12 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 28.42 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 110.04 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.67 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120.49 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.81 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.1 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 116.72 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 145.68 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139.76 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 157.51 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.67 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 146.76 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.19 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 160.99 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 243.96 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 105.54 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 11.75 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.29 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.52 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.26 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.29 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 113.17 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 110.65 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124.92 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 121.73 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.6 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.48 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109.14 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143.19 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.24 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 220.8 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.31 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111.36 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 189.89 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 163.69 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 199.13 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 182.44 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 219.58 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 224.58 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 239.79 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 218.54 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 238.77 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 253.48 | 0.16 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 218.67 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 260.06 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 248.62 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 350.82 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 205.53 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 20.77 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111.41 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.62 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 125.45 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.31 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 141.98 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.19 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 156.04 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.18 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.64 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 128.47 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.38 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 153.97 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 240.7 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.96 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 36.67 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.67 | 0.16 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 108.51 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 172.27 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118.4 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 197.95 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 199.04 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 227.6 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 211.55 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 238.19 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 252.27 | 0.17 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 203.83 | 0.17 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 260.88 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 259.38 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 387.52 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.86 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 20.49 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 113.86 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.56 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126.39 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 94.26 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151.13 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 133.44 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.63 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.91 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 171.14 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 164.93 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.43 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170.82 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 169.96 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 250.46 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 98.3 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 24.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134.87 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.99 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 142.73 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 107.88 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 168.85 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155.94 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 186.32 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 171.84 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 188.68 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 192.01 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 160.97 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 191.93 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 186.27 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 292.31 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115.89 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 21.15 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 127 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.22 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.85 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.43 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 161.98 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149.5 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 190.32 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 165.84 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 191.02 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 178.98 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.19 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183.55 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.79 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 275.42 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100.27 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 30.24 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 99.11 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.12 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111.75 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.48 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134.25 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 132.19 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 144.4 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134.08 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.94 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 152.34 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 125.39 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.52 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149.62 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 239.6 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Com | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.5 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 27.6 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 103 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 117 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.5 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 148 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 156 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 165 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ECC | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 18 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 70 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 49.8 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.5 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.1 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.6 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 97.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 92.6 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 110 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 94.5 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 167 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | ESe | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 62.8 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 22.8 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.5 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.9 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 102 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 116 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 211 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | EUn | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.3 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 8.6 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.1 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 66.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 37.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.3 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.4 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87.7 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 96.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.2 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 104 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.8 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 163 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Hsp | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 56.5 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 152 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 161 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 193 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 206 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 208 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 217 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 184 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 225 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 215 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 312 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Htl | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 167 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 32.8 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 98.1 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.6 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 112 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 141 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 141 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 216 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | MBT | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.4 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 10.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 57.3 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 114 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 150 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 180 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 201 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 211 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 201 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 325 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Nrs | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 25.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.8 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 107 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 125 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 146 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 147 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 144 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 214 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfL | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 29.8 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 80.1 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.9 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 132 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 142 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 160 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 152 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 240 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | OfS | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.5 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 28.4 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.1 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.8 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 142 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 167 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 179 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 171 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 144 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 174 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 168 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 258 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020B | Rt3 | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 15.56 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.39 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45.07 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.98 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.14 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.38 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 80.17 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.57 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.75 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.37 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 97.57 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 80.07 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 98.78 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 92.92 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 150.47 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.79 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 9.28 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 62.29 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 41.26 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.83 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 46.61 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.69 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.12 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.58 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.62 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 94.92 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.91 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.58 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 99.93 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.36 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143.79 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.31 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 7.98 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.51 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 32.52 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.4 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.08 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.29 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 58.23 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.52 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.17 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.78 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.8 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.21 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.46 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 70.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 113.01 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 44.8 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 15.55 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.16 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.69 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.78 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45.71 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 70.77 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 63.56 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.29 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.2 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.9 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.89 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 80.18 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.51 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87.63 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 132.82 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 57.56 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 6.45 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.14 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 29.7 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 50.79 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 28.52 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 61.78 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.44 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 67.94 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 66.32 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.74 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.71 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.61 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.89 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.47 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120.08 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.11 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.73 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 103.62 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.08 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 108.72 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 99.46 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.99 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 121.98 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.26 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.47 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.12 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.82 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.1 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 141.42 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 135.27 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 191.27 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111.88 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 11.33 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.71 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 39.57 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.42 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 46.46 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.44 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.86 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.42 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.95 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.23 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.38 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 69.83 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.26 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.9 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.23 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 49.02 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 19.98 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.44 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.23 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.88 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.5 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 107.83 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 108.77 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 123.65 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115.51 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.12 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.43 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 110.69 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 142.18 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.89 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 211.23 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.5 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 11.22 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 61.83 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.26 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 69.08 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.33 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.51 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.5 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.46 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.58 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.29 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.74 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.73 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.19 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 92.59 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136.65 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 53.72 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 13.34 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.53 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 49.61 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.9 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 58.88 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.82 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.87 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.1 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.5 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 102.74 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 104.67 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87.87 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 104.71 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.73 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 159.49 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 62.97 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 11.53 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 69.1 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45.37 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.78 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 50.9 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 88.1 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.63 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 103.98 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.42 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 104.01 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 97.37 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.85 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100.28 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.95 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149.85 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.83 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 16.48 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.01 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.97 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.91 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 46.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.32 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.02 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.69 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.12 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.33 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.39 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.26 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.5 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Com | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.09 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 15 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 56.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.7 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 63.9 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 48.8 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.1 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.9 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 80.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.7 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.3 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.7 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.9 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.1 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ECC | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 9.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 38.2 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 27.1 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.8 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 34.9 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 44.3 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 53 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 50.5 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.4 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.9 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.5 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.4 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.8 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.9 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | ESe | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 34.2 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 12.4 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 49.9 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 34.9 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 39.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 63 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.2 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.5 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.8 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.2 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.8 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | EUn | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 48.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 4.7 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 30 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 22.9 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 36.1 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 20.4 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 43.2 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42.2 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 47.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 47.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 43.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 56.7 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 88.8 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Hsp | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 30.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 67.8 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87.6 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 105 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 112 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 113 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 122 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 117 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Htl | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.1 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 17.9 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 53.5 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 61.2 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 48.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.4 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.8 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.5 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | MBT | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 46 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 5.7 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.5 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 31.3 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 30.4 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 67.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 62.3 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.7 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.2 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 97.9 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.4 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 110 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 177 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Nrs | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 14.1 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.1 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.7 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 58.3 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 45.3 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.1 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.5 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.3 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 76.4 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.4 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.9 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 116 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfL | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 47 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 16.2 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.3 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 43.6 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.8 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.2 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.7 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.9 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.4 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.4 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.1 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.7 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.1 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | OfS | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 15.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.2 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 44.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.4 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 46.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.2 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 97.4 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.1 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.7 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.5 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 141 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020C | Rt3 | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 28.52 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120.09 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.7 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.85 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 99.35 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.75 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 147.24 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166.28 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 159.05 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 178.96 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 147.08 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 181.17 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170.52 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 275.99 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111.57 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 17.07 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 114.48 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.69 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126.15 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.54 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 146.55 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139.5 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166.32 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 153.05 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 174.31 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 186.31 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 156.97 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183.32 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 167.75 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 263.56 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109.13 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 14.68 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 94.61 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 59.72 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.47 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.46 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 108.48 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 106.49 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.82 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 117.95 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 138.85 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.58 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.82 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 144.09 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 129.69 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 206.84 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.12 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 28.42 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 110.04 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.67 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120.49 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.81 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.1 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 116.72 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 145.68 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139.76 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 157.51 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.67 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 146.76 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.19 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 160.99 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 243.96 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 105.54 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 11.75 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.29 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.52 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.26 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.29 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 113.17 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 110.65 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124.92 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 121.73 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.6 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.48 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109.14 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143.19 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.24 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 220.8 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.31 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111.36 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 189.89 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 163.69 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 199.13 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 182.44 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 219.58 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 224.58 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 239.79 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 218.54 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 238.77 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 253.48 | 0.16 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 218.67 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 260.06 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 248.62 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 350.82 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 205.53 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 20.77 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111.41 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.62 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 125.45 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.31 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 141.98 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.19 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 156.04 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.18 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.64 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 128.47 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.38 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 153.97 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 240.7 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.96 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 36.67 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.67 | 0.16 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 108.51 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 172.27 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118.4 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 197.95 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 199.04 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 227.6 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 211.55 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 238.19 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 252.27 | 0.17 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 203.83 | 0.17 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 260.88 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 259.38 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 387.52 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.86 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 20.49 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 113.86 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.56 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126.39 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 94.26 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151.13 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 133.44 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.63 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.91 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 171.14 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 164.93 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.43 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170.82 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 169.96 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 250.46 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 98.3 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 24.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134.87 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 90.99 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 142.73 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 107.88 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 168.85 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155.94 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 186.32 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 171.84 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 188.68 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 192.01 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 160.97 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 191.93 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 186.27 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 292.31 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115.89 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 21.15 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 127 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.22 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.85 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.43 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 161.98 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149.5 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 190.32 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 165.84 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 191.02 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 178.98 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.19 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183.55 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.79 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 275.42 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | Ex | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100.27 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 30.24 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 99.11 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 75.12 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111.75 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.48 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134.25 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 132.19 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 144.4 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134.08 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.94 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 152.34 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 125.39 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 154.52 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149.62 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 239.6 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Com | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.5 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 27.6 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 103 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 117 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.5 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 148 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 156 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 165 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ECC | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 18 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 70 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 49.8 | 0.01 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 78.5 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64.1 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.6 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 97.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 92.6 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 110 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 94.5 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 111 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 167 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | ESe | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 62.8 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 22.8 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 91.5 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 64 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 71.9 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 102 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 116 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 211 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | EUn | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.3 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 8.6 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.1 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 42 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 66.3 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 37.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.3 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.4 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87.7 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 87.2 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 96.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.2 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 104 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.8 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 163 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Hsp | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 56.5 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 73.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 152 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 161 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 193 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 206 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 208 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 217 | 0.14 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 184 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 225 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 215 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 312 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Htl | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 167 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 32.8 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 98.1 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.6 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 112 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 89.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 141 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 141 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 216 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | MBT | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.4 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 10.5 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 57.3 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.7 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 114 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 150 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 180 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 201 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151 | 0.15 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 211 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 201 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 325 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Nrs | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 25.8 | 0.02 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.8 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.6 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 107 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.2 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 125 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 146 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 147 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 144 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 214 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfL | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 86.3 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 29.8 | 0.03 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109 | 0.08 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 80.1 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.9 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 132 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155 | 0.04 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 142 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 160 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 152 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 240 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | OfS | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.5 | 0.07 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ01 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 28.4 | 0.05 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ02 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ03 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.1 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ04 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ05 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.8 | 0.06 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ06 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ07 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 142 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ08 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 167 | 0.09 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ09 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 151 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ10 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 179 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ11 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 171 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ12 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 144 | 0.13 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ13 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 174 | 0.12 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ14 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 168 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ15 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 258 | 0.11 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC020D | Rt3 | New | CZ16 | cWtd | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 100 | 0.1 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual

## CostExAnte
PA | MeasCostID | CostQualifier | BldgType | BldgVint | BldgLoc | DeliveryType | SourceDesc | Version | VersionSource | LastMod | NormUnit | CostType | GenCost | LaborCost | MatlCost | Description | Sector | UseCategory | UseSubCategory | TechGroup | TechType | TechID | MeasAppType | InstallHours | LaborRate | LocCostAdj | Status | Comment | MeasLaborID | StdLaborRateID
Any | SWHC020_02_B001 | Any | Any | Any | Any | Any | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | Full |  | 0 | 644.5 | Air-Cooled Chiller, Standard Efficiency, >= 150 tons | Com | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed
Any | SWHC020_02_B002 | Any | Any | Any | Any | Any | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | Full |  | 0 | 827 | Air-Cooled Chiller, Standard Efficiency, < 150 tons | Com | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed
Any | SWHC020_02_M001 | Any | Any | Any | Any | Any | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | Full |  | 0 | 747 | Air-Cooled Chiller, >= 150 tons, 11.1 EER, 15.4 IPLV | Com | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed
Any | SWHC020_02_M002 | Any | Any | Any | Any | Any | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | Full |  | 0 | 795 | Air-Cooled Chiller, >= 150 tons, 12.1 EER, 16.9 IPLV | Com | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed
Any | SWHC020_02_M003 | Any | Any | Any | Any | Any | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | Full |  | 0 | 927 | Air-Cooled Chiller, < 150 tons, 11.1 EER, 15.1 IPLV | Com | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed
Any | SWHC020_02_M004 | Any | Any | Any | Any | Any | SWHC020-02 | ExAnte2022 | IOU workpaper | 2020-11-19 | Cap-Tons | Full |  | 0 | 1120 | Air-Cooled Chiller, < 150 tons, 12.1 EER, 16.6 IPLV | Com | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed

## CostExAnte (2) (hidden)
4
PA | MeasCostID | CostQualifier | BldgType | BldgVint | BldgLoc | DeliveryType | SourceDesc | Version | VersionSource | LastMod | NormUnit | CostType | GenCost | LaborCost | MatlCost | Description | Sector | UseCategory | UseSubCategory | TechGroup | TechType | TechID | MeasAppType | InstallHours | LaborRate | LocCostAdj | Status | Comment | MeasLaborID | StdLaborRateID
#REF! | Measure | Any | #REF! | #REF! | #REF! | #REF! | #REF! | ExAnte2020 | IOU workpaper | 2020-11-29 | #REF! | Full |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  | #REF! | Proposed
PGE | Measure | Any | Com | Ex | CZ01 | UpDeemed | SWHC020-01 | ExAnte2020 | IOU workpaper | 2019-04-24 | Cap-Tons | Full |  | 0 | 803.66 | Air-Cooled Chiller, < 150 tons, 12.1 EER, 16.6 IPLV, CZ01 | Com | HVAC | SpaceCool | Chiller | Screw |  | NC |  |  | None | Proposed
PGE | Measure | Any | Com | Ex | CZ01 | UpDeemed | SWHC020-01 | ExAnte2020 | IOU workpaper | 2019-04-24 | Cap-Tons | Full |  | 0 | 589.32 | Air-Cooled Chiller, â‰¥ 150 tons, 11.1 EER, 15.4 IPLV, CZ01 | Com | HVAC | SpaceCool | Chiller | Screw |  | NC |  |  | None | Proposed
PGE | Measure | Any | Com | Ex | CZ01 | UpDeemed | SWHC020-01 | ExAnte2020 | IOU workpaper | 2019-04-24 | Cap-Tons | Full |  | 0 | 639.15 | Air-Cooled Chiller, â‰¥ 150 tons, 12.1 EER, 16.9 IPLV, CZ01 | Com | HVAC | SpaceCool | Chiller | Screw |  | NC |  |  | None | Proposed