## Intro
eQuest Outputs
Introduction
This workbook contains the eQuest outputs that were further refined using the Ex and Com weightings to create the final list of measure impacts. There were 7,040 eQuest models, 3,520 "base case" models and 3,520 "measure case" models.
The "eQuest Outputs" tab contains 3,520 rows, with a side by side comparison of the base- and measure-cases. The total building energy consumption and peak demand is shown, as well as the cooling tons.

## eQuest Outputs
No. | Model Name | CZ | BT | Vint | Size | EER Rating | IEER Rating | Tons | Measure kWh/ton | Measure kW/ton | Base kWh/Ton | Base kW/Ton | Savings kWh/Ton | Savings kW/Ton
1 | MCLU-65to135-Asm-CZ01-2003-19IEER | CZ01 | Asm | 2003 | 65to135 | 12 | 19 | 295.9943 | 1920.7551 | 0.38158 | 2061.8919 | 0.42558 | 141.1368 | 0.044001
2 | MCLU-65to135-Asm-CZ01-2007-19IEER | CZ01 | Asm | 2007 | 65to135 | 12 | 19 | 294.1249 | 1932.2556 | 0.38394 | 2073.277 | 0.42804 | 141.0214 | 0.044098
3 | MCLU-65to135-Asm-CZ01-2011-19IEER | CZ01 | Asm | 2011 | 65to135 | 12 | 19 | 293.13 | 1934.76 | 0.37332 | 2080.3056 | 0.42987 | 145.5455 | 0.056555
4 | MCLU-65to135-Asm-CZ01-2015-19IEER | CZ01 | Asm | 2015 | 65to135 | 12 | 19 | 284.2061 | 1975.7008 | 0.37852 | 2120.3682 | 0.43452 | 144.6674 | 0.056005
5 | MCLU-65to135-Asm-CZ01-2020-19IEER | CZ01 | Asm | 2020 | 65to135 | 12 | 19 | 277.5676 | 1835.5096 | 0.35897 | 1975.6035 | 0.40265 | 140.0939 | 0.043679
6 | MCLU-65to135-ECC-CZ01-2003-19IEER | CZ01 | ECC | 2003 | 65to135 | 12 | 19 | 740.9278 | 2357.7983 | 0.53442 | 2457.6704 | 0.57102 | 99.8721 | 0.036598
7 | MCLU-65to135-ECC-CZ01-2007-19IEER | CZ01 | ECC | 2007 | 65to135 | 12 | 19 | 740.6437 | 2358.8713 | 0.53464 | 2458.6354 | 0.57126 | 99.7641 | 0.03662
8 | MCLU-65to135-ECC-CZ01-2011-19IEER | CZ01 | ECC | 2011 | 65to135 | 12 | 19 | 740.3345 | 2349.7911 | 0.51516 | 2458.6847 | 0.5709 | 108.8936 | 0.055741
9 | MCLU-65to135-ECC-CZ01-2015-19IEER | CZ01 | ECC | 2015 | 65to135 | 12 | 19 | 694.5188 | 2485.6346 | 0.54191 | 2595.9768 | 0.60014 | 110.3422 | 0.058226
10 | MCLU-65to135-ECC-CZ01-2020-19IEER | CZ01 | ECC | 2020 | 65to135 | 12 | 19 | 651.8481 | 2206.4885 | 0.51339 | 2313.5057 | 0.55344 | 107.0172 | 0.040044
11 | MCLU-65to135-EPr-CZ01-2003-19IEER | CZ01 | EPr | 2003 | 65to135 | 12 | 19 | 109.9912 | 1733.8239 | 0.28859 | 1809.7561 | 0.31075 | 75.9322 | 0.022154
12 | MCLU-65to135-EPr-CZ01-2007-19IEER | CZ01 | EPr | 2007 | 65to135 | 12 | 19 | 109.794 | 1737.0471 | 0.28917 | 1812.7911 | 0.31131 | 75.744 | 0.022147
13 | MCLU-65to135-EPr-CZ01-2011-19IEER | CZ01 | EPr | 2011 | 65to135 | 12 | 19 | 109.794 | 1732.7359 | 0.28205 | 1812.7911 | 0.31131 | 80.0552 | 0.029267
14 | MCLU-65to135-EPr-CZ01-2015-19IEER | CZ01 | EPr | 2015 | 65to135 | 12 | 19 | 102.321 | 1831.5978 | 0.29508 | 1912.6591 | 0.3246 | 81.0613 | 0.029514
15 | MCLU-65to135-EPr-CZ01-2020-19IEER | CZ01 | EPr | 2020 | 65to135 | 12 | 19 | 98.3843 | 1599.3101 | 0.25943 | 1678.4479 | 0.28265 | 79.1378 | 0.023225
16 | MCLU-65to135-ERC-CZ01-2003-19IEER | CZ01 | ERC | 2003 | 65to135 | 12 | 19 | 4.7598 | 1433.9244 | 0.20876 | 1502.8351 | 0.21117 | 68.9107 | 0.002409
17 | MCLU-65to135-ERC-CZ01-2007-19IEER | CZ01 | ERC | 2007 | 65to135 | 12 | 19 | 4.758 | 1434.6478 | 0.20883 | 1503.5351 | 0.21124 | 68.8873 | 0.0024097
18 | MCLU-65to135-ERC-CZ01-2011-19IEER | CZ01 | ERC | 2011 | 65to135 | 12 | 19 | 4.758 | 1429.7318 | 0.20762 | 1503.5351 | 0.21124 | 73.8033 | 0.0036215
19 | MCLU-65to135-ERC-CZ01-2015-19IEER | CZ01 | ERC | 2015 | 65to135 | 12 | 19 | 4.5682 | 1479.8543 | 0.21383 | 1557.0289 | 0.21595 | 77.1745 | 0.0021257
20 | MCLU-65to135-ERC-CZ01-2020-19IEER | CZ01 | ERC | 2020 | 65to135 | 12 | 19 | 4.355 | 1294.0824 | 0.18675 | 1371.2945 | 0.1879 | 77.2122 | 0.0011509
21 | MCLU-65to135-ESe-CZ01-2003-19IEER | CZ01 | ESe | 2003 | 65to135 | 12 | 19 | 351.3603 | 1801.2991 | 0.24498 | 1881.7121 | 0.26446 | 80.4129 | 0.019479
22 | MCLU-65to135-ESe-CZ01-2007-19IEER | CZ01 | ESe | 2007 | 65to135 | 12 | 19 | 350.6739 | 1804.8343 | 0.24544 | 1885.1205 | 0.26494 | 80.2862 | 0.019503
23 | MCLU-65to135-ESe-CZ01-2011-19IEER | CZ01 | ESe | 2011 | 65to135 | 12 | 19 | 349.7968 | 1804.1239 | 0.23769 | 1889.1661 | 0.26539 | 85.0422 | 0.027701
24 | MCLU-65to135-ESe-CZ01-2015-19IEER | CZ01 | ESe | 2015 | 65to135 | 12 | 19 | 334.2018 | 1873.8038 | 0.24375 | 1960.0284 | 0.27155 | 86.2246 | 0.0278
25 | MCLU-65to135-ESe-CZ01-2020-19IEER | CZ01 | ESe | 2020 | 65to135 | 12 | 19 | 314.2719 | 1649.5351 | 0.23408 | 1734.7447 | 0.25526 | 85.2096 | 0.021181
26 | MCLU-65to135-EUn-CZ01-2003-19IEER | CZ01 | EUn | 2003 | 65to135 | 12 | 19 | 2308.4602 | 2468.8819 | 0.62954 | 2567.1196 | 0.6584 | 98.2376 | 0.028863
27 | MCLU-65to135-EUn-CZ01-2007-19IEER | CZ01 | EUn | 2007 | 65to135 | 12 | 19 | 2305.7252 | 2459.0285 | 0.62704 | 2557.1669 | 0.65582 | 98.1384 | 0.028785
28 | MCLU-65to135-EUn-CZ01-2011-19IEER | CZ01 | EUn | 2011 | 65to135 | 12 | 19 | 2296.3044 | 2444.8783 | 0.61256 | 2553.4398 | 0.6598 | 108.5615 | 0.047238
29 | MCLU-65to135-EUn-CZ01-2015-19IEER | CZ01 | EUn | 2015 | 65to135 | 12 | 19 | 2072.2287 | 2670.7932 | 0.66001 | 2782.0009 | 0.71014 | 111.2077 | 0.050125
30 | MCLU-65to135-EUn-CZ01-2020-19IEER | CZ01 | EUn | 2020 | 65to135 | 12 | 19 | 1975.0166 | 2439.4017 | 0.62272 | 2543.6859 | 0.65362 | 104.2842 | 0.030906
31 | MCLU-65to135-Gro-CZ01-2003-19IEER | CZ01 | Gro | 2003 | 65to135 | 12 | 19 | 68.6603 | 23048.9925 | 2.9813 | 23474.3541 | 3.0559 | 425.3617 | 0.074576
32 | MCLU-65to135-Gro-CZ01-2007-19IEER | CZ01 | Gro | 2007 | 65to135 | 12 | 19 | 68.1557 | 20797.6295 | 2.7938 | 21118.503 | 2.8604 | 320.8735 | 0.066636
33 | MCLU-65to135-Gro-CZ01-2011-19IEER | CZ01 | Gro | 2011 | 65to135 | 12 | 19 | 67.5742 | 20978.4516 | 2.8173 | 21296.8595 | 2.8834 | 318.4079 | 0.06611
34 | MCLU-65to135-Gro-CZ01-2015-19IEER | CZ01 | Gro | 2015 | 65to135 | 12 | 19 | 63.3947 | 21435.6614 | 2.8618 | 21730.0994 | 2.9204 | 294.438 | 0.058668
35 | MCLU-65to135-Gro-CZ01-2020-19IEER | CZ01 | Gro | 2020 | 65to135 | 12 | 19 | 60.9963 | 21611.7444 | 2.8726 | 21878.202 | 2.9272 | 266.4576 | 0.054532
36 | MCLU-65to135-Hsp-CZ01-2003-19IEER | CZ01 | Hsp | 2003 | 65to135 | 12 | 19 | 680.4571 | 3834.6931 | 0.57549 | 4131.878 | 0.60111 | 297.185 | 0.025618
37 | MCLU-65to135-Hsp-CZ01-2007-19IEER | CZ01 | Hsp | 2007 | 65to135 | 12 | 19 | 680.4571 | 3834.7413 | 0.57549 | 4131.8823 | 0.60112 | 297.1409 | 0.025622
38 | MCLU-65to135-Hsp-CZ01-2011-19IEER | CZ01 | Hsp | 2011 | 65to135 | 12 | 19 | 680.4571 | 3829.2914 | 0.56373 | 4131.8748 | 0.6005 | 302.5833 | 0.036773
39 | MCLU-65to135-Hsp-CZ01-2015-19IEER | CZ01 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 3808.205 | 0.55929 | 4112.5461 | 0.59584 | 304.3411 | 0.036547
40 | MCLU-65to135-Hsp-CZ01-2020-19IEER | CZ01 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3331.0878 | 0.50078 | 3641.5156 | 0.52795 | 310.4278 | 0.027172
41 | MCLU-65to135-Htl-CZ01-2003-19IEER | CZ01 | Htl | 2003 | 65to135 | 12 | 19 | 255.2555 | 2955.8676 | 0.43243 | 3014.769 | 0.44163 | 58.9014 | 0.0092012
42 | MCLU-65to135-Htl-CZ01-2007-19IEER | CZ01 | Htl | 2007 | 65to135 | 12 | 19 | 255.2349 | 2877.1012 | 0.41599 | 2936.3892 | 0.42527 | 59.288 | 0.0092818
43 | MCLU-65to135-Htl-CZ01-2011-19IEER | CZ01 | Htl | 2011 | 65to135 | 12 | 19 | 251.3978 | 2849.5785 | 0.42119 | 2910.784 | 0.43303 | 61.2055 | 0.01184
44 | MCLU-65to135-Htl-CZ01-2015-19IEER | CZ01 | Htl | 2015 | 65to135 | 12 | 19 | 219.6688 | 3010.3727 | 0.44132 | 3074.9274 | 0.45363 | 64.5547 | 0.012302
45 | MCLU-65to135-Htl-CZ01-2020-19IEER | CZ01 | Htl | 2020 | 65to135 | 12 | 19 | 218.2138 | 2906.265 | 0.43102 | 2968.8319 | 0.44063 | 62.5669 | 0.00961
46 | MCLU-65to135-MBT-CZ01-2003-19IEER | CZ01 | MBT | 2003 | 65to135 | 12 | 19 | 316.7266 | 4240.1094 | 0.48425 | 4315.1288 | 0.51231 | 75.0194 | 0.028061
47 | MCLU-65to135-MBT-CZ01-2007-19IEER | CZ01 | MBT | 2007 | 65to135 | 12 | 19 | 313.8924 | 4283.8263 | 0.48929 | 4355.8065 | 0.51735 | 71.9802 | 0.028065
48 | MCLU-65to135-MBT-CZ01-2011-19IEER | CZ01 | MBT | 2011 | 65to135 | 12 | 19 | 309.5782 | 4259.0365 | 0.47762 | 4352.3842 | 0.51657 | 93.3477 | 0.038942
49 | MCLU-65to135-MBT-CZ01-2015-19IEER | CZ01 | MBT | 2015 | 65to135 | 12 | 19 | 302.3217 | 4325.3253 | 0.48342 | 4417.9748 | 0.52227 | 92.6495 | 0.038853
50 | MCLU-65to135-MBT-CZ01-2020-19IEER | CZ01 | MBT | 2020 | 65to135 | 12 | 19 | 278.4527 | 4229.615 | 0.47954 | 4295.4062 | 0.50746 | 65.7912 | 0.027924
51 | MCLU-65to135-MLI-CZ01-2003-19IEER | CZ01 | MLI | 2003 | 65to135 | 12 | 19 | 178.48 | 3416.3218 | 0.36816 | 3548.2352 | 0.38936 | 131.9134 | 0.021201
52 | MCLU-65to135-MLI-CZ01-2007-19IEER | CZ01 | MLI | 2007 | 65to135 | 12 | 19 | 176.2673 | 3458.103 | 0.37287 | 3589.4879 | 0.39384 | 131.3849 | 0.02097
53 | MCLU-65to135-MLI-CZ01-2011-19IEER | CZ01 | MLI | 2011 | 65to135 | 12 | 19 | 168.3722 | 3613.225 | 0.38424 | 3745.882 | 0.4104 | 132.657 | 0.026158
54 | MCLU-65to135-MLI-CZ01-2015-19IEER | CZ01 | MLI | 2015 | 65to135 | 12 | 19 | 167.1292 | 3615.9701 | 0.38409 | 3749.8499 | 0.41021 | 133.8798 | 0.026121
55 | MCLU-65to135-MLI-CZ01-2020-19IEER | CZ01 | MLI | 2020 | 65to135 | 12 | 19 | 163.1496 | 3099.4515 | 0.33082 | 3234.9381 | 0.3525 | 135.4865 | 0.021684
56 | MCLU-65to135-Mtl-CZ01-2003-19IEER | CZ01 | Mtl | 2003 | 65to135 | 12 | 19 | 47.6959 | 2829.7792 | 0.32592 | 2890.4444 | 0.33151 | 60.6652 | 0.00559
57 | MCLU-65to135-Mtl-CZ01-2007-19IEER | CZ01 | Mtl | 2007 | 65to135 | 12 | 19 | 47.6959 | 2754.4193 | 0.31492 | 2814.8768 | 0.32066 | 60.4575 | 0.0057488
58 | MCLU-65to135-Mtl-CZ01-2011-19IEER | CZ01 | Mtl | 2011 | 65to135 | 12 | 19 | 47.5164 | 2725.3182 | 0.314 | 2788.3291 | 0.32186 | 63.0109 | 0.0078621
59 | MCLU-65to135-Mtl-CZ01-2015-19IEER | CZ01 | Mtl | 2015 | 65to135 | 12 | 19 | 40.7854 | 2805.7462 | 0.35779 | 2871.9352 | 0.36598 | 66.189 | 0.0081892
60 | MCLU-65to135-Mtl-CZ01-2020-19IEER | CZ01 | Mtl | 2020 | 65to135 | 12 | 19 | 40.6265 | 2739.1743 | 0.35058 | 2802.2478 | 0.35617 | 63.0735 | 0.0055917
61 | MCLU-65to135-Nrs-CZ01-2003-19IEER | CZ01 | Nrs | 2003 | 65to135 | 12 | 19 | 181.7396 | 3905.2074 | 0.61434 | 4043.0597 | 0.63138 | 137.8523 | 0.017033
62 | MCLU-65to135-Nrs-CZ01-2007-19IEER | CZ01 | Nrs | 2007 | 65to135 | 12 | 19 | 181.7385 | 3862.4092 | 0.60186 | 4000.8585 | 0.61888 | 138.4493 | 0.017024
63 | MCLU-65to135-Nrs-CZ01-2011-19IEER | CZ01 | Nrs | 2011 | 65to135 | 12 | 19 | 181.7385 | 3858.7175 | 0.59687 | 4000.8585 | 0.61888 | 142.141 | 0.022009
64 | MCLU-65to135-Nrs-CZ01-2015-19IEER | CZ01 | Nrs | 2015 | 65to135 | 12 | 19 | 181.607 | 3807.7431 | 0.5791 | 3950.2103 | 0.6007 | 142.4672 | 0.021603
65 | MCLU-65to135-Nrs-CZ01-2020-19IEER | CZ01 | Nrs | 2020 | 65to135 | 12 | 19 | 181.607 | 3457.4157 | 0.53136 | 3601.8355 | 0.54866 | 144.4199 | 0.0173
66 | MCLU-65to135-OfL-CZ01-2003-19IEER | CZ01 | OfL | 2003 | 65to135 | 12 | 19 | 463.2832 | 3033.3073 | 0.44062 | 3108.7837 | 0.45315 | 75.4764 | 0.012534
67 | MCLU-65to135-OfL-CZ01-2007-19IEER | CZ01 | OfL | 2007 | 65to135 | 12 | 19 | 462.9621 | 3035.5685 | 0.44094 | 3110.9054 | 0.45348 | 75.3369 | 0.012536
68 | MCLU-65to135-OfL-CZ01-2011-19IEER | CZ01 | OfL | 2011 | 65to135 | 12 | 19 | 459.851 | 2999.5022 | 0.42927 | 3088.9837 | 0.45123 | 89.4815 | 0.021966
69 | MCLU-65to135-OfL-CZ01-2015-19IEER | CZ01 | OfL | 2015 | 65to135 | 12 | 19 | 450.0077 | 3020.3302 | 0.42999 | 3115.7173 | 0.45041 | 95.387 | 0.02042
70 | MCLU-65to135-OfL-CZ01-2020-19IEER | CZ01 | OfL | 2020 | 65to135 | 12 | 19 | 434.6976 | 2900.5226 | 0.42372 | 2983.5584 | 0.43522 | 83.0358 | 0.0115
71 | MCLU-65to135-OfS-CZ01-2003-19IEER | CZ01 | OfS | 2003 | 65to135 | 12 | 19 | 29.1655 | 2346.3093 | 0.31931 | 2443.1534 | 0.33278 | 96.8441 | 0.013464
72 | MCLU-65to135-OfS-CZ01-2007-19IEER | CZ01 | OfS | 2007 | 65to135 | 12 | 19 | 29.1607 | 2346.95 | 0.3194 | 2443.684 | 0.33287 | 96.734 | 0.01347
73 | MCLU-65to135-OfS-CZ01-2011-19IEER | CZ01 | OfS | 2011 | 65to135 | 12 | 19 | 29.0522 | 2316.4491 | 0.30865 | 2425.0696 | 0.3302 | 108.6205 | 0.02155
74 | MCLU-65to135-OfS-CZ01-2015-19IEER | CZ01 | OfS | 2015 | 65to135 | 12 | 19 | 25.6222 | 2587.7055 | 0.34023 | 2695.2821 | 0.36101 | 107.5767 | 0.020773
75 | MCLU-65to135-OfS-CZ01-2020-19IEER | CZ01 | OfS | 2020 | 65to135 | 12 | 19 | 24.8438 | 2447.3635 | 0.32716 | 2546.1462 | 0.33965 | 98.7827 | 0.012488
76 | MCLU-65to135-RFF-CZ01-2003-19IEER | CZ01 | RFF | 2003 | 65to135 | 12 | 19 | 6.5758 | 5465.5769 | 0.91644 | 5657.6382 | 0.96385 | 192.0613 | 0.047411
77 | MCLU-65to135-RFF-CZ01-2007-19IEER | CZ01 | RFF | 2007 | 65to135 | 12 | 19 | 6.51 | 5520.0118 | 0.92626 | 5713.4747 | 0.97508 | 193.463 | 0.048824
78 | MCLU-65to135-RFF-CZ01-2011-19IEER | CZ01 | RFF | 2011 | 65to135 | 12 | 19 | 6.4485 | 5564.9237 | 0.91682 | 5768.7839 | 0.98426 | 203.8602 | 0.067444
79 | MCLU-65to135-RFF-CZ01-2015-19IEER | CZ01 | RFF | 2015 | 65to135 | 12 | 19 | 6.2657 | 5472.6184 | 0.89415 | 5676.5414 | 0.96097 | 203.923 | 0.06682
80 | MCLU-65to135-RFF-CZ01-2020-19IEER | CZ01 | RFF | 2020 | 65to135 | 12 | 19 | 5.7437 | 5195.2501 | 0.86215 | 5391.2089 | 0.91206 | 195.9588 | 0.049902
81 | MCLU-65to135-RSD-CZ01-2003-19IEER | CZ01 | RSD | 2003 | 65to135 | 12 | 19 | 11.7575 | 5548.8205 | 0.96314 | 5699.3803 | 1.0178 | 150.5598 | 0.054661
82 | MCLU-65to135-RSD-CZ01-2007-19IEER | CZ01 | RSD | 2007 | 65to135 | 12 | 19 | 11.6172 | 5615.5363 | 0.97609 | 5766.5815 | 1.0312 | 151.0452 | 0.055103
83 | MCLU-65to135-RSD-CZ01-2011-19IEER | CZ01 | RSD | 2011 | 65to135 | 12 | 19 | 11.6172 | 5605.5543 | 0.95963 | 5766.5815 | 1.0312 | 161.0272 | 0.071565
84 | MCLU-65to135-RSD-CZ01-2015-19IEER | CZ01 | RSD | 2015 | 65to135 | 12 | 19 | 11.1578 | 5574.1751 | 0.94273 | 5729.092 | 1.0096 | 154.9169 | 0.066831
85 | MCLU-65to135-RSD-CZ01-2020-19IEER | CZ01 | RSD | 2020 | 65to135 | 12 | 19 | 9.9638 | 5245.1121 | 0.88479 | 5387.6669 | 0.92956 | 142.5548 | 0.044765
86 | MCLU-65to135-Rt3-CZ01-2003-19IEER | CZ01 | Rt3 | 2003 | 65to135 | 12 | 19 | 204.7912 | 6032.7061 | 1.0522 | 6117.9369 | 1.0782 | 85.2308 | 0.026049
87 | MCLU-65to135-Rt3-CZ01-2007-19IEER | CZ01 | Rt3 | 2007 | 65to135 | 12 | 19 | 204.7502 | 6034.568 | 1.0525 | 6119.4417 | 1.0786 | 84.8737 | 0.026066
88 | MCLU-65to135-Rt3-CZ01-2011-19IEER | CZ01 | Rt3 | 2011 | 65to135 | 12 | 19 | 202.1919 | 6097.6317 | 1.0408 | 6206.3625 | 1.0942 | 108.7308 | 0.053374
89 | MCLU-65to135-Rt3-CZ01-2015-19IEER | CZ01 | Rt3 | 2015 | 65to135 | 12 | 19 | 190.2373 | 5810.5727 | 0.99452 | 5934.5962 | 1.0473 | 124.0235 | 0.052753
90 | MCLU-65to135-Rt3-CZ01-2020-19IEER | CZ01 | Rt3 | 2020 | 65to135 | 12 | 19 | 180.7228 | 5404.778 | 0.94808 | 5519.9053 | 0.97731 | 115.1274 | 0.029224
91 | MCLU-65to135-RtL-CZ01-2003-19IEER | CZ01 | RtL | 2003 | 65to135 | 12 | 19 | 176.7263 | 6697.9194 | 1.1583 | 6841.8812 | 1.2034 | 143.9619 | 0.045106
92 | MCLU-65to135-RtL-CZ01-2007-19IEER | CZ01 | RtL | 2007 | 65to135 | 12 | 19 | 175.7196 | 6742.7765 | 1.1667 | 6884.7529 | 1.2124 | 141.9765 | 0.045715
93 | MCLU-65to135-RtL-CZ01-2011-19IEER | CZ01 | RtL | 2011 | 65to135 | 12 | 19 | 174.7127 | 6749.66 | 1.149 | 6934.8327 | 1.2223 | 185.1727 | 0.073223
94 | MCLU-65to135-RtL-CZ01-2015-19IEER | CZ01 | RtL | 2015 | 65to135 | 12 | 19 | 166.6902 | 6561.5772 | 1.1338 | 6767.7425 | 1.2099 | 206.1653 | 0.076068
95 | MCLU-65to135-RtL-CZ01-2020-19IEER | CZ01 | RtL | 2020 | 65to135 | 12 | 19 | 155.5826 | 6372.9299 | 1.1517 | 6555.3134 | 1.2064 | 182.3835 | 0.054624
96 | MCLU-65to135-RtS-CZ01-2003-19IEER | CZ01 | RtS | 2003 | 65to135 | 12 | 19 | 12.6362 | 3999.3057 | 0.6664 | 4135.7049 | 0.69297 | 136.3993 | 0.026575
97 | MCLU-65to135-RtS-CZ01-2007-19IEER | CZ01 | RtS | 2007 | 65to135 | 12 | 19 | 12.6287 | 4002.0315 | 0.66685 | 4138.0622 | 0.69342 | 136.0307 | 0.026577
98 | MCLU-65to135-RtS-CZ01-2011-19IEER | CZ01 | RtS | 2011 | 65to135 | 12 | 19 | 12.5801 | 4006.7278 | 0.65423 | 4155.474 | 0.6964 | 148.7462 | 0.042165
99 | MCLU-65to135-RtS-CZ01-2015-19IEER | CZ01 | RtS | 2015 | 65to135 | 12 | 19 | 12.1753 | 3789.7671 | 0.61257 | 3949.5149 | 0.6539 | 159.7477 | 0.041335
100 | MCLU-65to135-RtS-CZ01-2020-19IEER | CZ01 | RtS | 2020 | 65to135 | 12 | 19 | 11.8506 | 3514.8196 | 0.58129 | 3668.2928 | 0.60984 | 153.4732 | 0.028556
101 | MCLU-65to135-SCn-CZ01-2003-19IEER | CZ01 | SCn | 2003 | 65to135 | 12 | 19 | 323.1694 | 2191.4342 | 0.17678 | 2368.4435 | 0.19539 | 177.0093 | 0.018603
102 | MCLU-65to135-SCn-CZ01-2007-19IEER | CZ01 | SCn | 2007 | 65to135 | 12 | 19 | 321.3788 | 2201.746 | 0.17774 | 2373.9359 | 0.1964 | 172.1899 | 0.018657
103 | MCLU-65to135-SCn-CZ01-2011-19IEER | CZ01 | SCn | 2011 | 65to135 | 12 | 19 | 314.2012 | 2250.2165 | 0.18082 | 2426.6645 | 0.20032 | 176.4481 | 0.019506
104 | MCLU-65to135-SCn-CZ01-2015-19IEER | CZ01 | SCn | 2015 | 65to135 | 12 | 19 | 314.0361 | 2250.9231 | 0.18087 | 2426.3087 | 0.20037 | 175.3856 | 0.019495
105 | MCLU-65to135-SCn-CZ01-2020-19IEER | CZ01 | SCn | 2020 | 65to135 | 12 | 19 | 310.3607 | 1975.4303 | 0.15735 | 2157.0482 | 0.17585 | 181.6179 | 0.018495
106 | MCLU-65to135-WRf-CZ01-2003-19IEER | CZ01 | WRf | 2003 | 65to135 | 12 | 19 | 9.6437 | 370537.3896 | 45.131 | 370736.3464 | 45.1745 | 198.9568 | 0.043471
107 | MCLU-65to135-WRf-CZ01-2007-19IEER | CZ01 | WRf | 2007 | 65to135 | 12 | 19 | 9.493 | 370223.0212 | 44.8656 | 370425.6121 | 44.9088 | 202.591 | 0.043131
108 | MCLU-65to135-WRf-CZ01-2011-19IEER | CZ01 | WRf | 2011 | 65to135 | 12 | 19 | 9.3503 | 372667.9802 | 45.0997 | 372875.9602 | 45.1433 | 207.98 | 0.043647
109 | MCLU-65to135-WRf-CZ01-2015-19IEER | CZ01 | WRf | 2015 | 65to135 | 12 | 19 | 9.0281 | 385963.669 | 46.7047 | 386173.1157 | 46.7486 | 209.4468 | 0.043894
110 | MCLU-65to135-WRf-CZ01-2020-19IEER | CZ01 | WRf | 2020 | 65to135 | 12 | 19 | 8.1541 | 398608.7359 | 47.9691 | 398825.0377 | 48.0146 | 216.3018 | 0.045505
111 | MCLU-65to135-Asm-CZ02-2003-19IEER | CZ02 | Asm | 2003 | 65to135 | 12 | 19 | 297.1638 | 2316.0936 | 0.88841 | 2556.4656 | 1.0078 | 240.372 | 0.1194
112 | MCLU-65to135-Asm-CZ02-2007-19IEER | CZ02 | Asm | 2007 | 65to135 | 12 | 19 | 294.2872 | 2421.9409 | 0.90228 | 2637.3567 | 1.0194 | 215.4158 | 0.11709
113 | MCLU-65to135-Asm-CZ02-2011-19IEER | CZ02 | Asm | 2011 | 65to135 | 12 | 19 | 291.4026 | 2481.5646 | 0.87619 | 2735.9158 | 1.0318 | 254.3512 | 0.15565
114 | MCLU-65to135-Asm-CZ02-2015-19IEER | CZ02 | Asm | 2015 | 65to135 | 12 | 19 | 281.5065 | 2525.2843 | 0.87838 | 2777.2492 | 1.0355 | 251.965 | 0.15712
115 | MCLU-65to135-Asm-CZ02-2020-19IEER | CZ02 | Asm | 2020 | 65to135 | 12 | 19 | 272.1375 | 2465.0469 | 0.89543 | 2648.4132 | 1.011 | 183.3663 | 0.11562
116 | MCLU-65to135-ECC-CZ02-2003-19IEER | CZ02 | ECC | 2003 | 65to135 | 12 | 19 | 723.6116 | 2726.7914 | 0.51907 | 2894.5531 | 0.61362 | 167.7617 | 0.094545
117 | MCLU-65to135-ECC-CZ02-2007-19IEER | CZ02 | ECC | 2007 | 65to135 | 12 | 19 | 722.0554 | 2731.9854 | 0.5189 | 2899.8205 | 0.61332 | 167.8351 | 0.094426
118 | MCLU-65to135-ECC-CZ02-2011-19IEER | CZ02 | ECC | 2011 | 65to135 | 12 | 19 | 720.1639 | 2675.2063 | 0.47797 | 2904.2246 | 0.61292 | 229.0183 | 0.13495
119 | MCLU-65to135-ECC-CZ02-2015-19IEER | CZ02 | ECC | 2015 | 65to135 | 12 | 19 | 688.217 | 2761.1031 | 0.47206 | 2988.482 | 0.60712 | 227.3789 | 0.13506
120 | MCLU-65to135-ECC-CZ02-2020-19IEER | CZ02 | ECC | 2020 | 65to135 | 12 | 19 | 656.1552 | 2482.3067 | 0.4855 | 2653.5562 | 0.57797 | 171.2496 | 0.092471
121 | MCLU-65to135-EPr-CZ02-2003-19IEER | CZ02 | EPr | 2003 | 65to135 | 12 | 19 | 113.8126 | 1880.5749 | 0.056319 | 1995.6446 | 0.064794 | 115.0697 | 0.0084755
122 | MCLU-65to135-EPr-CZ02-2007-19IEER | CZ02 | EPr | 2007 | 65to135 | 12 | 19 | 112.4806 | 1900.307 | 0.055076 | 2015.9075 | 0.063092 | 115.6005 | 0.0080154
123 | MCLU-65to135-EPr-CZ02-2011-19IEER | CZ02 | EPr | 2011 | 65to135 | 12 | 19 | 109.7668 | 1909.6079 | 0.049132 | 2062.4523 | 0.061191 | 152.8444 | 0.012059
124 | MCLU-65to135-EPr-CZ02-2015-19IEER | CZ02 | EPr | 2015 | 65to135 | 12 | 19 | 102.966 | 1988.6946 | 0.034774 | 2141.0242 | 0.037368 | 152.3297 | 0.0025937
125 | MCLU-65to135-EPr-CZ02-2020-19IEER | CZ02 | EPr | 2020 | 65to135 | 12 | 19 | 97.196 | 1807.7117 | 0.024765 | 1926.6411 | 0.025924 | 118.9294 | 0.0011587
126 | MCLU-65to135-ERC-CZ02-2003-19IEER | CZ02 | ERC | 2003 | 65to135 | 12 | 19 | 5.2739 | 1476.6454 | 0.1066 | 1570.6304 | 0.13166 | 93.985 | 0.025063
127 | MCLU-65to135-ERC-CZ02-2007-19IEER | CZ02 | ERC | 2007 | 65to135 | 12 | 19 | 5.2523 | 1482.0447 | 0.10585 | 1576.4043 | 0.13064 | 94.3596 | 0.024799
128 | MCLU-65to135-ERC-CZ02-2011-19IEER | CZ02 | ERC | 2011 | 65to135 | 12 | 19 | 5.1322 | 1478.3524 | 0.082261 | 1604.261 | 0.11765 | 125.9085 | 0.035389
129 | MCLU-65to135-ERC-CZ02-2015-19IEER | CZ02 | ERC | 2015 | 65to135 | 12 | 19 | 4.9937 | 1498.5353 | 0.065287 | 1622.7109 | 0.089718 | 124.1756 | 0.024432
130 | MCLU-65to135-ERC-CZ02-2020-19IEER | CZ02 | ERC | 2020 | 65to135 | 12 | 19 | 4.8156 | 1333.3091 | 0.059725 | 1431.0323 | 0.074019 | 97.7232 | 0.014293
131 | MCLU-65to135-ESe-CZ02-2003-19IEER | CZ02 | ESe | 2003 | 65to135 | 12 | 19 | 357.5064 | 1972.5788 | 0.15117 | 2095.592 | 0.1785 | 123.0132 | 0.027326
132 | MCLU-65to135-ESe-CZ02-2007-19IEER | CZ02 | ESe | 2007 | 65to135 | 12 | 19 | 355.9703 | 1980.3378 | 0.15099 | 2103.4074 | 0.17814 | 123.0695 | 0.027149
133 | MCLU-65to135-ESe-CZ02-2011-19IEER | CZ02 | ESe | 2011 | 65to135 | 12 | 19 | 354.3347 | 1949.6072 | 0.13506 | 2110.7422 | 0.17723 | 161.135 | 0.042166
134 | MCLU-65to135-ESe-CZ02-2015-19IEER | CZ02 | ESe | 2015 | 65to135 | 12 | 19 | 343.7403 | 1982.1681 | 0.12273 | 2141.2863 | 0.15445 | 159.1182 | 0.031723
135 | MCLU-65to135-ESe-CZ02-2020-19IEER | CZ02 | ESe | 2020 | 65to135 | 12 | 19 | 327.4148 | 1774.1841 | 0.10874 | 1897.0829 | 0.1263 | 122.8988 | 0.017562
136 | MCLU-65to135-EUn-CZ02-2003-19IEER | CZ02 | EUn | 2003 | 65to135 | 12 | 19 | 2168.0137 | 2959.6804 | 0.76875 | 3130.2712 | 0.86806 | 170.5908 | 0.099302
137 | MCLU-65to135-EUn-CZ02-2007-19IEER | CZ02 | EUn | 2007 | 65to135 | 12 | 19 | 2155.7623 | 2957.1809 | 0.76174 | 3127.666 | 0.86075 | 170.4851 | 0.09901
138 | MCLU-65to135-EUn-CZ02-2011-19IEER | CZ02 | EUn | 2011 | 65to135 | 12 | 19 | 2130.871 | 2914.6463 | 0.7227 | 3147.2131 | 0.86507 | 232.5668 | 0.14238
139 | MCLU-65to135-EUn-CZ02-2015-19IEER | CZ02 | EUn | 2015 | 65to135 | 12 | 19 | 2005.1643 | 3022.3433 | 0.72426 | 3255.484 | 0.86807 | 233.1407 | 0.14381
140 | MCLU-65to135-EUn-CZ02-2020-19IEER | CZ02 | EUn | 2020 | 65to135 | 12 | 19 | 1912.8833 | 2819.5919 | 0.74616 | 2993.3701 | 0.84391 | 173.7781 | 0.097742
141 | MCLU-65to135-Gro-CZ02-2003-19IEER | CZ02 | Gro | 2003 | 65to135 | 12 | 19 | 119.1571 | 13648.9714 | 2.1032 | 13997.6898 | 2.2585 | 348.7184 | 0.15531
142 | MCLU-65to135-Gro-CZ02-2007-19IEER | CZ02 | Gro | 2007 | 65to135 | 12 | 19 | 117.331 | 12505.0891 | 1.9934 | 12828.6933 | 2.1591 | 323.6042 | 0.16573
143 | MCLU-65to135-Gro-CZ02-2011-19IEER | CZ02 | Gro | 2011 | 65to135 | 12 | 19 | 115.5259 | 12696.0964 | 2.0194 | 13017.1858 | 2.1846 | 321.0894 | 0.16519
144 | MCLU-65to135-Gro-CZ02-2015-19IEER | CZ02 | Gro | 2015 | 65to135 | 12 | 19 | 111.2313 | 12628.2057 | 2.0051 | 12939.378 | 2.1648 | 311.1723 | 0.15968
145 | MCLU-65to135-Gro-CZ02-2020-19IEER | CZ02 | Gro | 2020 | 65to135 | 12 | 19 | 107.6956 | 12634.9948 | 1.9993 | 12939.5251 | 2.1574 | 304.5302 | 0.15817
146 | MCLU-65to135-Hsp-CZ02-2003-19IEER | CZ02 | Hsp | 2003 | 65to135 | 12 | 19 | 680.4571 | 4095.5813 | 0.77464 | 4437.1189 | 0.89465 | 341.5376 | 0.12
147 | MCLU-65to135-Hsp-CZ02-2007-19IEER | CZ02 | Hsp | 2007 | 65to135 | 12 | 19 | 680.4571 | 4095.221 | 0.7739 | 4436.6216 | 0.89363 | 341.4006 | 0.11972
148 | MCLU-65to135-Hsp-CZ02-2011-19IEER | CZ02 | Hsp | 2011 | 65to135 | 12 | 19 | 680.4571 | 4040.1289 | 0.72711 | 4436.112 | 0.8926 | 395.9832 | 0.16549
149 | MCLU-65to135-Hsp-CZ02-2015-19IEER | CZ02 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 4012.4561 | 0.71603 | 4407.3005 | 0.881 | 394.8444 | 0.16497
150 | MCLU-65to135-Hsp-CZ02-2020-19IEER | CZ02 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3558.5274 | 0.68455 | 3904.9289 | 0.80234 | 346.4014 | 0.11779
151 | MCLU-65to135-Htl-CZ02-2003-19IEER | CZ02 | Htl | 2003 | 65to135 | 12 | 19 | 233.2466 | 3590.6133 | 0.98224 | 3663.9061 | 1.0111 | 73.2928 | 0.028821
152 | MCLU-65to135-Htl-CZ02-2007-19IEER | CZ02 | Htl | 2007 | 65to135 | 12 | 19 | 232.9358 | 3470.7506 | 0.91942 | 3544.0904 | 0.9482 | 73.3398 | 0.028784
153 | MCLU-65to135-Htl-CZ02-2011-19IEER | CZ02 | Htl | 2011 | 65to135 | 12 | 19 | 226.7807 | 3480.6484 | 0.91689 | 3572.8262 | 0.95752 | 92.1778 | 0.040631
154 | MCLU-65to135-Htl-CZ02-2015-19IEER | CZ02 | Htl | 2015 | 65to135 | 12 | 19 | 201.9628 | 3640.453 | 0.92416 | 3736.0567 | 0.96651 | 95.6037 | 0.042358
155 | MCLU-65to135-Htl-CZ02-2020-19IEER | CZ02 | Htl | 2020 | 65to135 | 12 | 19 | 200.1921 | 3550.1465 | 0.92285 | 3626.6947 | 0.95256 | 76.5482 | 0.029713
156 | MCLU-65to135-MBT-CZ02-2003-19IEER | CZ02 | MBT | 2003 | 65to135 | 12 | 19 | 327.3748 | 4394.2979 | 0.69427 | 4534.5839 | 0.78923 | 140.286 | 0.094962
157 | MCLU-65to135-MBT-CZ02-2007-19IEER | CZ02 | MBT | 2007 | 65to135 | 12 | 19 | 321.6115 | 4473.8498 | 0.70237 | 4612.7478 | 0.79677 | 138.898 | 0.094397
158 | MCLU-65to135-MBT-CZ02-2011-19IEER | CZ02 | MBT | 2011 | 65to135 | 12 | 19 | 304.5354 | 4597.0651 | 0.68175 | 4797.5415 | 0.81398 | 200.4765 | 0.13223
159 | MCLU-65to135-MBT-CZ02-2015-19IEER | CZ02 | MBT | 2015 | 65to135 | 12 | 19 | 296.0389 | 4682.889 | 0.68886 | 4882.3006 | 0.8212 | 199.4116 | 0.13234
160 | MCLU-65to135-MBT-CZ02-2020-19IEER | CZ02 | MBT | 2020 | 65to135 | 12 | 19 | 273.8718 | 4591.5738 | 0.71331 | 4725.3923 | 0.80712 | 133.8185 | 0.093812
161 | MCLU-65to135-MLI-CZ02-2003-19IEER | CZ02 | MLI | 2003 | 65to135 | 12 | 19 | 200.5957 | 3244.4182 | 0.52883 | 3404.7946 | 0.59676 | 160.3764 | 0.067931
162 | MCLU-65to135-MLI-CZ02-2007-19IEER | CZ02 | MLI | 2007 | 65to135 | 12 | 19 | 195.8969 | 3316.6713 | 0.53671 | 3476.4465 | 0.60469 | 159.7751 | 0.06798
163 | MCLU-65to135-MLI-CZ02-2011-19IEER | CZ02 | MLI | 2011 | 65to135 | 12 | 19 | 191.258 | 3355.416 | 0.51457 | 3550.703 | 0.61278 | 195.287 | 0.098209
164 | MCLU-65to135-MLI-CZ02-2015-19IEER | CZ02 | MLI | 2015 | 65to135 | 12 | 19 | 189.1115 | 3369.6063 | 0.51589 | 3564.6796 | 0.61425 | 195.0734 | 0.09836
165 | MCLU-65to135-MLI-CZ02-2020-19IEER | CZ02 | MLI | 2020 | 65to135 | 12 | 19 | 174.8454 | 3079.835 | 0.51365 | 3240.1146 | 0.58117 | 160.2796 | 0.067521
166 | MCLU-65to135-Mtl-CZ02-2003-19IEER | CZ02 | Mtl | 2003 | 65to135 | 12 | 19 | 42.7448 | 3531.7295 | 0.90012 | 3591.8661 | 0.92002 | 60.1366 | 0.019903
167 | MCLU-65to135-Mtl-CZ02-2007-19IEER | CZ02 | Mtl | 2007 | 65to135 | 12 | 19 | 42.7448 | 3403.8582 | 0.83525 | 3463.9703 | 0.85514 | 60.1121 | 0.019892
168 | MCLU-65to135-Mtl-CZ02-2011-19IEER | CZ02 | Mtl | 2011 | 65to135 | 12 | 19 | 41.6068 | 3403.597 | 0.83061 | 3476.5378 | 0.85855 | 72.9408 | 0.027939
169 | MCLU-65to135-Mtl-CZ02-2015-19IEER | CZ02 | Mtl | 2015 | 65to135 | 12 | 19 | 35.1616 | 3621.0479 | 0.85191 | 3697.8721 | 0.88156 | 76.8242 | 0.029647
170 | MCLU-65to135-Mtl-CZ02-2020-19IEER | CZ02 | Mtl | 2020 | 65to135 | 12 | 19 | 35.0228 | 3551.5485 | 0.84956 | 3612.9043 | 0.87014 | 61.3558 | 0.02058
171 | MCLU-65to135-Nrs-CZ02-2003-19IEER | CZ02 | Nrs | 2003 | 65to135 | 12 | 19 | 182.346 | 4270.3002 | 0.90266 | 4437.4746 | 0.96157 | 167.1744 | 0.05891
172 | MCLU-65to135-Nrs-CZ02-2007-19IEER | CZ02 | Nrs | 2007 | 65to135 | 12 | 19 | 182.3427 | 4198.8568 | 0.86954 | 4366.2723 | 0.92819 | 167.4155 | 0.058646
173 | MCLU-65to135-Nrs-CZ02-2011-19IEER | CZ02 | Nrs | 2011 | 65to135 | 12 | 19 | 182.1468 | 4196.2356 | 0.83857 | 4390.8379 | 0.92063 | 194.6022 | 0.082065
174 | MCLU-65to135-Nrs-CZ02-2015-19IEER | CZ02 | Nrs | 2015 | 65to135 | 12 | 19 | 181.6558 | 4110.0389 | 0.78932 | 4302.2992 | 0.87046 | 192.2603 | 0.081133
175 | MCLU-65to135-Nrs-CZ02-2020-19IEER | CZ02 | Nrs | 2020 | 65to135 | 12 | 19 | 181.607 | 3766.1295 | 0.75182 | 3933.6171 | 0.80883 | 167.4877 | 0.057003
176 | MCLU-65to135-OfL-CZ02-2003-19IEER | CZ02 | OfL | 2003 | 65to135 | 12 | 19 | 418.608 | 3678.8335 | 0.6268 | 3823.504 | 0.67823 | 144.6706 | 0.051431
177 | MCLU-65to135-OfL-CZ02-2007-19IEER | CZ02 | OfL | 2007 | 65to135 | 12 | 19 | 418.1919 | 3682.3328 | 0.62708 | 3826.9701 | 0.67849 | 144.6373 | 0.051412
178 | MCLU-65to135-OfL-CZ02-2011-19IEER | CZ02 | OfL | 2011 | 65to135 | 12 | 19 | 403.2723 | 3706.3731 | 0.61128 | 3915.9806 | 0.68268 | 209.6076 | 0.071409
179 | MCLU-65to135-OfL-CZ02-2015-19IEER | CZ02 | OfL | 2015 | 65to135 | 12 | 19 | 398.5592 | 3685.1737 | 0.6111 | 3892.6293 | 0.68236 | 207.4557 | 0.071258
180 | MCLU-65to135-OfL-CZ02-2020-19IEER | CZ02 | OfL | 2020 | 65to135 | 12 | 19 | 386.3437 | 3578.0396 | 0.61423 | 3722.2839 | 0.6639 | 144.2443 | 0.049671
181 | MCLU-65to135-OfS-CZ02-2003-19IEER | CZ02 | OfS | 2003 | 65to135 | 12 | 19 | 28.2143 | 2719.3001 | 0.47952 | 2873.0528 | 0.53093 | 153.7528 | 0.051405
182 | MCLU-65to135-OfS-CZ02-2007-19IEER | CZ02 | OfS | 2007 | 65to135 | 12 | 19 | 28.1402 | 2725.985 | 0.4798 | 2879.6344 | 0.53111 | 153.6494 | 0.051314
183 | MCLU-65to135-OfS-CZ02-2011-19IEER | CZ02 | OfS | 2011 | 65to135 | 12 | 19 | 27.6492 | 2687.0335 | 0.45705 | 2898.734 | 0.53053 | 211.7005 | 0.073485
184 | MCLU-65to135-OfS-CZ02-2015-19IEER | CZ02 | OfS | 2015 | 65to135 | 12 | 19 | 24.6717 | 2937.8687 | 0.48339 | 3145.5258 | 0.55414 | 207.6571 | 0.07075
185 | MCLU-65to135-OfS-CZ02-2020-19IEER | CZ02 | OfS | 2020 | 65to135 | 12 | 19 | 23.9167 | 2834.1829 | 0.48288 | 2985.2324 | 0.53223 | 151.0495 | 0.049349
186 | MCLU-65to135-RFF-CZ02-2003-19IEER | CZ02 | RFF | 2003 | 65to135 | 12 | 19 | 6.4577 | 6115.9698 | 1.4924 | 6418.3743 | 1.6112 | 302.4046 | 0.11877
187 | MCLU-65to135-RFF-CZ02-2007-19IEER | CZ02 | RFF | 2007 | 65to135 | 12 | 19 | 6.3787 | 6187.1449 | 1.5057 | 6490.3617 | 1.6243 | 303.2168 | 0.11856
188 | MCLU-65to135-RFF-CZ02-2011-19IEER | CZ02 | RFF | 2011 | 65to135 | 12 | 19 | 6.3031 | 6167.5528 | 1.481 | 6560.884 | 1.6364 | 393.3312 | 0.15542
189 | MCLU-65to135-RFF-CZ02-2015-19IEER | CZ02 | RFF | 2015 | 65to135 | 12 | 19 | 6.2385 | 5936.0397 | 1.4326 | 6320.5436 | 1.5924 | 384.5038 | 0.15973
190 | MCLU-65to135-RFF-CZ02-2020-19IEER | CZ02 | RFF | 2020 | 65to135 | 12 | 19 | 5.9058 | 5545.0691 | 1.4058 | 5849.8636 | 1.5264 | 304.7945 | 0.1206
191 | MCLU-65to135-RSD-CZ02-2003-19IEER | CZ02 | RSD | 2003 | 65to135 | 12 | 19 | 12.1318 | 5898.9105 | 1.4342 | 6168.5461 | 1.5573 | 269.6357 | 0.12316
192 | MCLU-65to135-RSD-CZ02-2007-19IEER | CZ02 | RSD | 2007 | 65to135 | 12 | 19 | 11.9859 | 5968.0477 | 1.4465 | 6239.238 | 1.57 | 271.1903 | 0.12348
193 | MCLU-65to135-RSD-CZ02-2011-19IEER | CZ02 | RSD | 2011 | 65to135 | 12 | 19 | 11.7453 | 5987.2055 | 1.4196 | 6359.9643 | 1.5899 | 372.7588 | 0.17032
194 | MCLU-65to135-RSD-CZ02-2015-19IEER | CZ02 | RSD | 2015 | 65to135 | 12 | 19 | 11.5106 | 5824.4874 | 1.3903 | 6182.9179 | 1.5616 | 358.4305 | 0.1713
195 | MCLU-65to135-RSD-CZ02-2020-19IEER | CZ02 | RSD | 2020 | 65to135 | 12 | 19 | 10.6829 | 5352.2973 | 1.354 | 5614.2897 | 1.4758 | 261.9924 | 0.12175
196 | MCLU-65to135-Rt3-CZ02-2003-19IEER | CZ02 | Rt3 | 2003 | 65to135 | 12 | 19 | 234.6579 | 5761.3038 | 1.3091 | 5957.5638 | 1.4386 | 196.26 | 0.12949
197 | MCLU-65to135-Rt3-CZ02-2007-19IEER | CZ02 | Rt3 | 2007 | 65to135 | 12 | 19 | 233.9396 | 5778.3637 | 1.3109 | 5974.4238 | 1.4403 | 196.0601 | 0.12938
198 | MCLU-65to135-Rt3-CZ02-2011-19IEER | CZ02 | Rt3 | 2011 | 65to135 | 12 | 19 | 233.1917 | 5698.5448 | 1.2595 | 5992.1354 | 1.442 | 293.5906 | 0.1825
199 | MCLU-65to135-Rt3-CZ02-2015-19IEER | CZ02 | Rt3 | 2015 | 65to135 | 12 | 19 | 223.9643 | 5346.2563 | 1.2052 | 5640.7435 | 1.389 | 294.4872 | 0.18375
200 | MCLU-65to135-Rt3-CZ02-2020-19IEER | CZ02 | Rt3 | 2020 | 65to135 | 12 | 19 | 213.9657 | 5041.951 | 1.2004 | 5248.0864 | 1.3304 | 206.1355 | 0.13
201 | MCLU-65to135-RtL-CZ02-2003-19IEER | CZ02 | RtL | 2003 | 65to135 | 12 | 19 | 206.6262 | 6234.0133 | 1.3824 | 6442.308 | 1.5129 | 208.2947 | 0.1305
202 | MCLU-65to135-RtL-CZ02-2007-19IEER | CZ02 | RtL | 2007 | 65to135 | 12 | 19 | 203.6703 | 6323.314 | 1.3967 | 6530.894 | 1.5269 | 207.58 | 0.13028
203 | MCLU-65to135-RtL-CZ02-2011-19IEER | CZ02 | RtL | 2011 | 65to135 | 12 | 19 | 200.6513 | 6311.7791 | 1.3618 | 6624.5048 | 1.5417 | 312.7257 | 0.17988
204 | MCLU-65to135-RtL-CZ02-2015-19IEER | CZ02 | RtL | 2015 | 65to135 | 12 | 19 | 193.2287 | 6099.4772 | 1.3466 | 6421.044 | 1.5277 | 321.5668 | 0.18102
205 | MCLU-65to135-RtL-CZ02-2020-19IEER | CZ02 | RtL | 2020 | 65to135 | 12 | 19 | 181.1492 | 5977.1789 | 1.3946 | 6205.6005 | 1.5257 | 228.4216 | 0.13111
206 | MCLU-65to135-RtS-CZ02-2003-19IEER | CZ02 | RtS | 2003 | 65to135 | 12 | 19 | 15.0644 | 3798.777 | 0.93705 | 4013.3113 | 1.0529 | 214.5343 | 0.11585
207 | MCLU-65to135-RtS-CZ02-2007-19IEER | CZ02 | RtS | 2007 | 65to135 | 12 | 19 | 14.7799 | 3867.3696 | 0.94936 | 4080.8152 | 1.0648 | 213.4456 | 0.11547
208 | MCLU-65to135-RtS-CZ02-2011-19IEER | CZ02 | RtS | 2011 | 65to135 | 12 | 19 | 14.5012 | 3856.5742 | 0.91669 | 4149.6025 | 1.0771 | 293.0282 | 0.16045
209 | MCLU-65to135-RtS-CZ02-2015-19IEER | CZ02 | RtS | 2015 | 65to135 | 12 | 19 | 14.1826 | 3611.4588 | 0.8679 | 3903.6212 | 1.0316 | 292.1624 | 0.16375
210 | MCLU-65to135-RtS-CZ02-2020-19IEER | CZ02 | RtS | 2020 | 65to135 | 12 | 19 | 13.5385 | 3493.0303 | 0.89 | 3712.6788 | 1.0079 | 219.6485 | 0.11791
211 | MCLU-65to135-SCn-CZ02-2003-19IEER | CZ02 | SCn | 2003 | 65to135 | 12 | 19 | 244.6731 | 2969.7041 | 0.45647 | 3172.122 | 0.52833 | 202.4179 | 0.071858
212 | MCLU-65to135-SCn-CZ02-2007-19IEER | CZ02 | SCn | 2007 | 65to135 | 12 | 19 | 233.5572 | 3099.0794 | 0.46983 | 3300.1963 | 0.53963 | 201.1168 | 0.069801
213 | MCLU-65to135-SCn-CZ02-2011-19IEER | CZ02 | SCn | 2011 | 65to135 | 12 | 19 | 222.3069 | 3218.5241 | 0.45537 | 3436.4356 | 0.55141 | 217.9115 | 0.096042
214 | MCLU-65to135-SCn-CZ02-2015-19IEER | CZ02 | SCn | 2015 | 65to135 | 12 | 19 | 218.7582 | 3267.2578 | 0.46182 | 3485.0594 | 0.55708 | 217.8016 | 0.095265
215 | MCLU-65to135-SCn-CZ02-2020-19IEER | CZ02 | SCn | 2020 | 65to135 | 12 | 19 | 197.6813 | 3146.45 | 0.48114 | 3344.0339 | 0.54562 | 197.5839 | 0.064475
216 | MCLU-65to135-WRf-CZ02-2003-19IEER | CZ02 | WRf | 2003 | 65to135 | 12 | 19 | 13.7731 | 270766.0312 | 37.6859 | 271074.8399 | 37.8001 | 308.8087 | 0.11413
217 | MCLU-65to135-WRf-CZ02-2007-19IEER | CZ02 | WRf | 2007 | 65to135 | 12 | 19 | 13.6211 | 264445.7894 | 35.4472 | 264755.3017 | 35.5602 | 309.5122 | 0.11305
218 | MCLU-65to135-WRf-CZ02-2011-19IEER | CZ02 | WRf | 2011 | 65to135 | 12 | 19 | 12.5737 | 278440.5591 | 35.7762 | 278765.8222 | 35.8793 | 325.2631 | 0.10301
219 | MCLU-65to135-WRf-CZ02-2015-19IEER | CZ02 | WRf | 2015 | 65to135 | 12 | 19 | 12.1856 | 287288.0544 | 36.9023 | 287612.129 | 37.0025 | 324.0746 | 0.10019
220 | MCLU-65to135-WRf-CZ02-2020-19IEER | CZ02 | WRf | 2020 | 65to135 | 12 | 19 | 11.5629 | 285660.2199 | 36.6013 | 285975.0472 | 36.6961 | 314.8273 | 0.0948
221 | MCLU-65to135-Asm-CZ03-2003-19IEER | CZ03 | Asm | 2003 | 65to135 | 12 | 19 | 353.1677 | 1786.9844 | 0.49598 | 1961.5096 | 0.58459 | 174.5251 | 0.088604
222 | MCLU-65to135-Asm-CZ03-2007-19IEER | CZ03 | Asm | 2007 | 65to135 | 12 | 19 | 350.7268 | 1798.3113 | 0.49848 | 1972.9597 | 0.58708 | 174.6484 | 0.088598
223 | MCLU-65to135-Asm-CZ03-2011-19IEER | CZ03 | Asm | 2011 | 65to135 | 12 | 19 | 348.3356 | 1768.9624 | 0.46106 | 1981.4891 | 0.58963 | 212.5266 | 0.12857
224 | MCLU-65to135-Asm-CZ03-2015-19IEER | CZ03 | Asm | 2015 | 65to135 | 12 | 19 | 303.1609 | 1957.8244 | 0.49783 | 2162.56 | 0.62672 | 204.7356 | 0.12889
225 | MCLU-65to135-Asm-CZ03-2020-19IEER | CZ03 | Asm | 2020 | 65to135 | 12 | 19 | 293.4321 | 1860.0799 | 0.5124 | 2033.7215 | 0.60045 | 173.6416 | 0.088055
226 | MCLU-65to135-ECC-CZ03-2003-19IEER | CZ03 | ECC | 2003 | 65to135 | 12 | 19 | 854.286 | 2185.6613 | 0.32637 | 2291.1666 | 0.38988 | 105.5052 | 0.063518
227 | MCLU-65to135-ECC-CZ03-2007-19IEER | CZ03 | ECC | 2007 | 65to135 | 12 | 19 | 853.9062 | 2186.6241 | 0.32601 | 2292.04 | 0.38934 | 105.4159 | 0.063335
228 | MCLU-65to135-ECC-CZ03-2011-19IEER | CZ03 | ECC | 2011 | 65to135 | 12 | 19 | 853.4898 | 2153.3127 | 0.30041 | 2291.2864 | 0.38858 | 137.9737 | 0.088165
229 | MCLU-65to135-ECC-CZ03-2015-19IEER | CZ03 | ECC | 2015 | 65to135 | 12 | 19 | 755.8112 | 2401.5985 | 0.32183 | 2542.9607 | 0.41066 | 141.3622 | 0.088828
230 | MCLU-65to135-ECC-CZ03-2020-19IEER | CZ03 | ECC | 2020 | 65to135 | 12 | 19 | 714.0795 | 2145.2157 | 0.31887 | 2259.5266 | 0.38257 | 114.3109 | 0.063695
231 | MCLU-65to135-EPr-CZ03-2003-19IEER | CZ03 | EPr | 2003 | 65to135 | 12 | 19 | 130.5716 | 1550.1556 | 0.026618 | 1629.6558 | 0.027043 | 79.5002 | 0.00042473
232 | MCLU-65to135-EPr-CZ03-2007-19IEER | CZ03 | EPr | 2007 | 65to135 | 12 | 19 | 130.2547 | 1553.8194 | 0.026662 | 1633.129 | 0.027082 | 79.3097 | 0.0004198
233 | MCLU-65to135-EPr-CZ03-2011-19IEER | CZ03 | EPr | 2011 | 65to135 | 12 | 19 | 129.9263 | 1538.2404 | 0.026293 | 1636.7741 | 0.027121 | 98.5338 | 0.00082751
234 | MCLU-65to135-EPr-CZ03-2015-19IEER | CZ03 | EPr | 2015 | 65to135 | 12 | 19 | 113.9842 | 1714.1596 | 0.028106 | 1819.5425 | 0.02854 | 105.3828 | 0.00043435
235 | MCLU-65to135-EPr-CZ03-2020-19IEER | CZ03 | EPr | 2020 | 65to135 | 12 | 19 | 108.642 | 1525.1116 | 0.01887 | 1613.6242 | 0.019056 | 88.5126 | 0.00018543
236 | MCLU-65to135-ERC-CZ03-2003-19IEER | CZ03 | ERC | 2003 | 65to135 | 12 | 19 | 5.7111 | 1299.382 | 0.029828 | 1361.044 | 0.031093 | 61.662 | 0.0012657
237 | MCLU-65to135-ERC-CZ03-2007-19IEER | CZ03 | ERC | 2007 | 65to135 | 12 | 19 | 5.7079 | 1300.1805 | 0.029787 | 1361.8095 | 0.031041 | 61.629 | 0.0012544
238 | MCLU-65to135-ERC-CZ03-2011-19IEER | CZ03 | ERC | 2011 | 65to135 | 12 | 19 | 5.7046 | 1279.1569 | 0.028713 | 1362.6732 | 0.030996 | 83.5162 | 0.0022834
239 | MCLU-65to135-ERC-CZ03-2015-19IEER | CZ03 | ERC | 2015 | 65to135 | 12 | 19 | 5.3051 | 1346.9175 | 0.026166 | 1434.4817 | 0.026166 | 87.5642 | 0
240 | MCLU-65to135-ERC-CZ03-2020-19IEER | CZ03 | ERC | 2020 | 65to135 | 12 | 19 | 5.091 | 1190.0149 | 0.017477 | 1262.629 | 0.017477 | 72.6142 | 0
241 | MCLU-65to135-ESe-CZ03-2003-19IEER | CZ03 | ESe | 2003 | 65to135 | 12 | 19 | 433.0058 | 1576.6132 | 0.082262 | 1658.9872 | 0.088401 | 82.374 | 0.0061389
242 | MCLU-65to135-ESe-CZ03-2007-19IEER | CZ03 | ESe | 2007 | 65to135 | 12 | 19 | 432.0537 | 1579.9492 | 0.082361 | 1662.2245 | 0.08848 | 82.2753 | 0.0061184
243 | MCLU-65to135-ESe-CZ03-2011-19IEER | CZ03 | ESe | 2011 | 65to135 | 12 | 19 | 431.0502 | 1558.8998 | 0.077942 | 1664.7878 | 0.088504 | 105.888 | 0.010562
244 | MCLU-65to135-ESe-CZ03-2015-19IEER | CZ03 | ESe | 2015 | 65to135 | 12 | 19 | 368.3566 | 1774.61 | 0.074474 | 1881.3383 | 0.078419 | 106.7283 | 0.0039455
245 | MCLU-65to135-ESe-CZ03-2020-19IEER | CZ03 | ESe | 2020 | 65to135 | 12 | 19 | 349.8195 | 1566.7409 | 0.05729 | 1656.4914 | 0.058815 | 89.7505 | 0.0015249
246 | MCLU-65to135-EUn-CZ03-2003-19IEER | CZ03 | EUn | 2003 | 65to135 | 12 | 19 | 2543.674 | 2336.3844 | 0.48697 | 2451.3991 | 0.55703 | 115.0147 | 0.070059
247 | MCLU-65to135-EUn-CZ03-2007-19IEER | CZ03 | EUn | 2007 | 65to135 | 12 | 19 | 2538.4642 | 2330.5049 | 0.48237 | 2445.3133 | 0.55229 | 114.8084 | 0.069923
248 | MCLU-65to135-EUn-CZ03-2011-19IEER | CZ03 | EUn | 2011 | 65to135 | 12 | 19 | 2518.1219 | 2304.4935 | 0.45469 | 2452.8498 | 0.55432 | 148.3563 | 0.099631
249 | MCLU-65to135-EUn-CZ03-2015-19IEER | CZ03 | EUn | 2015 | 65to135 | 12 | 19 | 2204.105 | 2580.5871 | 0.48661 | 2728.2996 | 0.58766 | 147.7125 | 0.10105
250 | MCLU-65to135-EUn-CZ03-2020-19IEER | CZ03 | EUn | 2020 | 65to135 | 12 | 19 | 2105.618 | 2371.5503 | 0.48743 | 2487.5566 | 0.55709 | 116.0063 | 0.06966
251 | MCLU-65to135-Gro-CZ03-2003-19IEER | CZ03 | Gro | 2003 | 65to135 | 12 | 19 | 90.3586 | 17800.2148 | 2.4453 | 18201.9707 | 2.553 | 401.7559 | 0.10772
252 | MCLU-65to135-Gro-CZ03-2007-19IEER | CZ03 | Gro | 2007 | 65to135 | 12 | 19 | 89.4314 | 16221.5776 | 2.3257 | 16551.4242 | 2.448 | 329.8466 | 0.12223
253 | MCLU-65to135-Gro-CZ03-2011-19IEER | CZ03 | Gro | 2011 | 65to135 | 12 | 19 | 88.4926 | 16393.9031 | 2.3485 | 16722.1346 | 2.4701 | 328.2314 | 0.12159
254 | MCLU-65to135-Gro-CZ03-2015-19IEER | CZ03 | Gro | 2015 | 65to135 | 12 | 19 | 82.8602 | 16758.4395 | 2.3895 | 17076.256 | 2.5005 | 317.8165 | 0.111
255 | MCLU-65to135-Gro-CZ03-2020-19IEER | CZ03 | Gro | 2020 | 65to135 | 12 | 19 | 80.5727 | 16701.2142 | 2.3746 | 17013.0228 | 2.479 | 311.8086 | 0.10443
256 | MCLU-65to135-Hsp-CZ03-2003-19IEER | CZ03 | Hsp | 2003 | 65to135 | 12 | 19 | 680.9668 | 3975.378 | 0.67758 | 4250.5491 | 0.7582 | 275.1711 | 0.080622
257 | MCLU-65to135-Hsp-CZ03-2007-19IEER | CZ03 | Hsp | 2007 | 65to135 | 12 | 19 | 680.9668 | 3975.3247 | 0.67719 | 4250.4523 | 0.75774 | 275.1276 | 0.080548
258 | MCLU-65to135-Hsp-CZ03-2011-19IEER | CZ03 | Hsp | 2011 | 65to135 | 12 | 19 | 680.9668 | 3943.1158 | 0.64508 | 4250.3551 | 0.75725 | 307.2393 | 0.11217
259 | MCLU-65to135-Hsp-CZ03-2015-19IEER | CZ03 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 3906.1442 | 0.63214 | 4213.2087 | 0.74293 | 307.0645 | 0.11079
260 | MCLU-65to135-Hsp-CZ03-2020-19IEER | CZ03 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3430.9068 | 0.59085 | 3722.1315 | 0.66823 | 291.2247 | 0.077379
261 | MCLU-65to135-Htl-CZ03-2003-19IEER | CZ03 | Htl | 2003 | 65to135 | 12 | 19 | 269.0709 | 2739.6819 | 0.61506 | 2800.8957 | 0.63674 | 61.2138 | 0.021684
262 | MCLU-65to135-Htl-CZ03-2007-19IEER | CZ03 | Htl | 2007 | 65to135 | 12 | 19 | 269.0457 | 2657.3289 | 0.58072 | 2718.8398 | 0.60231 | 61.5109 | 0.021595
263 | MCLU-65to135-Htl-CZ03-2011-19IEER | CZ03 | Htl | 2011 | 65to135 | 12 | 19 | 262.7993 | 2668.2933 | 0.57816 | 2737.8395 | 0.60918 | 69.5462 | 0.031016
264 | MCLU-65to135-Htl-CZ03-2015-19IEER | CZ03 | Htl | 2015 | 65to135 | 12 | 19 | 227.8842 | 2853.1679 | 0.58859 | 2925.2946 | 0.6211 | 72.1266 | 0.032504
265 | MCLU-65to135-Htl-CZ03-2020-19IEER | CZ03 | Htl | 2020 | 65to135 | 12 | 19 | 226.5437 | 2757.3145 | 0.58411 | 2821.189 | 0.60632 | 63.8746 | 0.022209
266 | MCLU-65to135-MBT-CZ03-2003-19IEER | CZ03 | MBT | 2003 | 65to135 | 12 | 19 | 348.9057 | 4002.4276 | 0.53124 | 4105.325 | 0.59633 | 102.8975 | 0.065095
267 | MCLU-65to135-MBT-CZ03-2007-19IEER | CZ03 | MBT | 2007 | 65to135 | 12 | 19 | 345.4439 | 4046.8052 | 0.53514 | 4148.1236 | 0.59988 | 101.3184 | 0.064746
268 | MCLU-65to135-MBT-CZ03-2011-19IEER | CZ03 | MBT | 2011 | 65to135 | 12 | 19 | 335.333 | 4073.7697 | 0.51474 | 4218.7624 | 0.60565 | 144.9927 | 0.090908
269 | MCLU-65to135-MBT-CZ03-2015-19IEER | CZ03 | MBT | 2015 | 65to135 | 12 | 19 | 311.1328 | 4335.3467 | 0.53823 | 4480.0659 | 0.62815 | 144.7192 | 0.08992
270 | MCLU-65to135-MBT-CZ03-2020-19IEER | CZ03 | MBT | 2020 | 65to135 | 12 | 19 | 290.9587 | 4187.8556 | 0.54051 | 4286.0857 | 0.60325 | 98.2301 | 0.062746
271 | MCLU-65to135-MLI-CZ03-2003-19IEER | CZ03 | MLI | 2003 | 65to135 | 12 | 19 | 198.3329 | 3143.3867 | 0.40718 | 3275.7305 | 0.45173 | 132.3438 | 0.044552
272 | MCLU-65to135-MLI-CZ03-2007-19IEER | CZ03 | MLI | 2007 | 65to135 | 12 | 19 | 194.7941 | 3199.1979 | 0.41272 | 3331.121 | 0.45701 | 131.9231 | 0.044284
273 | MCLU-65to135-MLI-CZ03-2011-19IEER | CZ03 | MLI | 2011 | 65to135 | 12 | 19 | 191.1994 | 3242.4142 | 0.39998 | 3389.7028 | 0.46317 | 147.2885 | 0.063191
274 | MCLU-65to135-MLI-CZ03-2015-19IEER | CZ03 | MLI | 2015 | 65to135 | 12 | 19 | 188.0371 | 3272.5798 | 0.40244 | 3420.3413 | 0.46528 | 147.7615 | 0.062841
275 | MCLU-65to135-MLI-CZ03-2020-19IEER | CZ03 | MLI | 2020 | 65to135 | 12 | 19 | 181.9707 | 2834.3114 | 0.36655 | 2968.7874 | 0.4092 | 134.476 | 0.042653
276 | MCLU-65to135-Mtl-CZ03-2003-19IEER | CZ03 | Mtl | 2003 | 65to135 | 12 | 19 | 51.122 | 2545.7209 | 0.52504 | 2601.3182 | 0.54058 | 55.5973 | 0.015539
277 | MCLU-65to135-Mtl-CZ03-2007-19IEER | CZ03 | Mtl | 2007 | 65to135 | 12 | 19 | 51.122 | 2468.1919 | 0.4931 | 2523.8102 | 0.50864 | 55.6183 | 0.015538
278 | MCLU-65to135-Mtl-CZ03-2011-19IEER | CZ03 | Mtl | 2011 | 65to135 | 12 | 19 | 49.9903 | 2465.6116 | 0.49005 | 2527.6849 | 0.51211 | 62.0733 | 0.022057
279 | MCLU-65to135-Mtl-CZ03-2015-19IEER | CZ03 | Mtl | 2015 | 65to135 | 12 | 19 | 42.4967 | 2667.2625 | 0.50697 | 2732.2511 | 0.53108 | 64.9886 | 0.024111
280 | MCLU-65to135-Mtl-CZ03-2020-19IEER | CZ03 | Mtl | 2020 | 65to135 | 12 | 19 | 42.1198 | 2602.8962 | 0.50229 | 2659.6942 | 0.51879 | 56.798 | 0.016499
281 | MCLU-65to135-Nrs-CZ03-2003-19IEER | CZ03 | Nrs | 2003 | 65to135 | 12 | 19 | 185.6788 | 4128.6841 | 0.75939 | 4268.5901 | 0.79889 | 139.906 | 0.039496
282 | MCLU-65to135-Nrs-CZ03-2007-19IEER | CZ03 | Nrs | 2007 | 65to135 | 12 | 19 | 185.6743 | 4060.0222 | 0.73552 | 4200.2533 | 0.77486 | 140.231 | 0.039345
283 | MCLU-65to135-Nrs-CZ03-2011-19IEER | CZ03 | Nrs | 2011 | 65to135 | 12 | 19 | 185.6697 | 4045.9637 | 0.71902 | 4202.2505 | 0.77418 | 156.2869 | 0.055159
284 | MCLU-65to135-Nrs-CZ03-2015-19IEER | CZ03 | Nrs | 2015 | 65to135 | 12 | 19 | 181.6163 | 3970.4505 | 0.66985 | 4121.802 | 0.72127 | 151.3515 | 0.051425
285 | MCLU-65to135-Nrs-CZ03-2020-19IEER | CZ03 | Nrs | 2020 | 65to135 | 12 | 19 | 181.607 | 3616.806 | 0.62724 | 3759.2862 | 0.66306 | 142.4802 | 0.035819
286 | MCLU-65to135-OfL-CZ03-2003-19IEER | CZ03 | OfL | 2003 | 65to135 | 12 | 19 | 516.4556 | 2869.953 | 0.44459 | 2965.4862 | 0.48254 | 95.5332 | 0.037952
287 | MCLU-65to135-OfL-CZ03-2007-19IEER | CZ03 | OfL | 2007 | 65to135 | 12 | 19 | 516.0348 | 2872.3324 | 0.44483 | 2967.7895 | 0.48275 | 95.4571 | 0.037922
288 | MCLU-65to135-OfL-CZ03-2011-19IEER | CZ03 | OfL | 2011 | 65to135 | 12 | 19 | 507.5031 | 2848.1353 | 0.4276 | 2979.859 | 0.4824 | 131.7237 | 0.054798
289 | MCLU-65to135-OfL-CZ03-2015-19IEER | CZ03 | OfL | 2015 | 65to135 | 12 | 19 | 471.8428 | 3009.329 | 0.44706 | 3139.4579 | 0.5003 | 130.129 | 0.053242
290 | MCLU-65to135-OfL-CZ03-2020-19IEER | CZ03 | OfL | 2020 | 65to135 | 12 | 19 | 457.2089 | 2902.8889 | 0.44773 | 2997.0764 | 0.48418 | 94.1875 | 0.036452
291 | MCLU-65to135-OfS-CZ03-2003-19IEER | CZ03 | OfS | 2003 | 65to135 | 12 | 19 | 34.0542 | 2144.8105 | 0.32947 | 2254.6488 | 0.36654 | 109.8383 | 0.03707
292 | MCLU-65to135-OfS-CZ03-2007-19IEER | CZ03 | OfS | 2007 | 65to135 | 12 | 19 | 34.0474 | 2145.3142 | 0.32925 | 2255.0832 | 0.36624 | 109.769 | 0.036991
293 | MCLU-65to135-OfS-CZ03-2011-19IEER | CZ03 | OfS | 2011 | 65to135 | 12 | 19 | 33.9326 | 2096.6755 | 0.31069 | 2237.9757 | 0.36359 | 141.3001 | 0.052902
294 | MCLU-65to135-OfS-CZ03-2015-19IEER | CZ03 | OfS | 2015 | 65to135 | 12 | 19 | 27.5212 | 2524.6022 | 0.35954 | 2665.0573 | 0.41203 | 140.4551 | 0.052496
295 | MCLU-65to135-OfS-CZ03-2020-19IEER | CZ03 | OfS | 2020 | 65to135 | 12 | 19 | 26.7497 | 2407.2843 | 0.35526 | 2515.568 | 0.39118 | 108.2837 | 0.035928
296 | MCLU-65to135-RFF-CZ03-2003-19IEER | CZ03 | RFF | 2003 | 65to135 | 12 | 19 | 7.73 | 4881.8738 | 0.98085 | 5084.4256 | 1.0699 | 202.5518 | 0.089047
297 | MCLU-65to135-RFF-CZ03-2007-19IEER | CZ03 | RFF | 2007 | 65to135 | 12 | 19 | 7.6687 | 4920.5327 | 0.98664 | 5124.8534 | 1.0761 | 204.3206 | 0.08945
298 | MCLU-65to135-RFF-CZ03-2011-19IEER | CZ03 | RFF | 2011 | 65to135 | 12 | 19 | 7.6189 | 4906.3147 | 0.94334 | 5158.2718 | 1.0806 | 251.9571 | 0.13731
299 | MCLU-65to135-RFF-CZ03-2015-19IEER | CZ03 | RFF | 2015 | 65to135 | 12 | 19 | 7.1608 | 4958.0603 | 0.94688 | 5213.9158 | 1.0858 | 255.8556 | 0.13895
300 | MCLU-65to135-RFF-CZ03-2020-19IEER | CZ03 | RFF | 2020 | 65to135 | 12 | 19 | 6.7224 | 4625.2505 | 0.93527 | 4851.103 | 1.0302 | 225.8525 | 0.09491
301 | MCLU-65to135-RSD-CZ03-2003-19IEER | CZ03 | RSD | 2003 | 65to135 | 12 | 19 | 13.4723 | 5113.0618 | 1.0493 | 5318.9017 | 1.1499 | 205.8399 | 0.10058
302 | MCLU-65to135-RSD-CZ03-2007-19IEER | CZ03 | RSD | 2007 | 65to135 | 12 | 19 | 13.3366 | 5165.9343 | 1.0582 | 5372.8072 | 1.1594 | 206.8729 | 0.1012
303 | MCLU-65to135-RSD-CZ03-2011-19IEER | CZ03 | RSD | 2011 | 65to135 | 12 | 19 | 13.2001 | 5166.2785 | 1.0204 | 5428.3632 | 1.1685 | 262.0846 | 0.14807
304 | MCLU-65to135-RSD-CZ03-2015-19IEER | CZ03 | RSD | 2015 | 65to135 | 12 | 19 | 12.0371 | 5353.0256 | 1.0448 | 5600.4011 | 1.1908 | 247.3755 | 0.14598
305 | MCLU-65to135-RSD-CZ03-2020-19IEER | CZ03 | RSD | 2020 | 65to135 | 12 | 19 | 10.986 | 4935.7342 | 1.0083 | 5131.6257 | 1.1055 | 195.8916 | 0.09715
306 | MCLU-65to135-Rt3-CZ03-2003-19IEER | CZ03 | Rt3 | 2003 | 65to135 | 12 | 19 | 215.9562 | 6021.1773 | 1.1877 | 6137.2621 | 1.2785 | 116.0847 | 0.090844
307 | MCLU-65to135-Rt3-CZ03-2007-19IEER | CZ03 | Rt3 | 2007 | 65to135 | 12 | 19 | 215.9062 | 6022.9507 | 1.1869 | 6138.7675 | 1.2778 | 115.8168 | 0.090847
308 | MCLU-65to135-Rt3-CZ03-2011-19IEER | CZ03 | Rt3 | 2011 | 65to135 | 12 | 19 | 215.8551 | 5951.2638 | 1.1394 | 6140.2958 | 1.2768 | 189.032 | 0.13739
309 | MCLU-65to135-Rt3-CZ03-2015-19IEER | CZ03 | Rt3 | 2015 | 65to135 | 12 | 19 | 203.2051 | 5674.703 | 1.0987 | 5868.4326 | 1.2356 | 193.7296 | 0.13687
310 | MCLU-65to135-Rt3-CZ03-2020-19IEER | CZ03 | Rt3 | 2020 | 65to135 | 12 | 19 | 193.3872 | 5317.9306 | 1.0805 | 5454.9959 | 1.1701 | 137.0654 | 0.089587
311 | MCLU-65to135-RtL-CZ03-2003-19IEER | CZ03 | RtL | 2003 | 65to135 | 12 | 19 | 184.0477 | 6745.9332 | 1.2972 | 6932.5848 | 1.3896 | 186.6516 | 0.092437
312 | MCLU-65to135-RtL-CZ03-2007-19IEER | CZ03 | RtL | 2007 | 65to135 | 12 | 19 | 182.9165 | 6792.7641 | 1.3042 | 6978.8247 | 1.3959 | 186.0605 | 0.091795
313 | MCLU-65to135-RtL-CZ03-2011-19IEER | CZ03 | RtL | 2011 | 65to135 | 12 | 19 | 181.7653 | 6756.403 | 1.2683 | 7027.2514 | 1.4029 | 270.8484 | 0.13452
314 | MCLU-65to135-RtL-CZ03-2015-19IEER | CZ03 | RtL | 2015 | 65to135 | 12 | 19 | 172.5745 | 6607.2357 | 1.2612 | 6892.9474 | 1.3978 | 285.7118 | 0.1366
315 | MCLU-65to135-RtL-CZ03-2020-19IEER | CZ03 | RtL | 2020 | 65to135 | 12 | 19 | 161.7677 | 6434.444 | 1.2925 | 6655.6508 | 1.3869 | 221.2068 | 0.094414
316 | MCLU-65to135-RtS-CZ03-2003-19IEER | CZ03 | RtS | 2003 | 65to135 | 12 | 19 | 14.1786 | 3786.2677 | 0.76973 | 3934.6576 | 0.85148 | 148.3899 | 0.081758
317 | MCLU-65to135-RtS-CZ03-2007-19IEER | CZ03 | RtS | 2007 | 65to135 | 12 | 19 | 14.1703 | 3787.9809 | 0.76789 | 3936.0459 | 0.84943 | 148.065 | 0.081547
318 | MCLU-65to135-RtS-CZ03-2011-19IEER | CZ03 | RtS | 2011 | 65to135 | 12 | 19 | 14.1616 | 3743.2124 | 0.72754 | 3937.6657 | 0.84735 | 194.4533 | 0.11982
319 | MCLU-65to135-RtS-CZ03-2015-19IEER | CZ03 | RtS | 2015 | 65to135 | 12 | 19 | 13.0958 | 3692.9509 | 0.71441 | 3889.4627 | 0.83167 | 196.5118 | 0.11726
320 | MCLU-65to135-RtS-CZ03-2020-19IEER | CZ03 | RtS | 2020 | 65to135 | 12 | 19 | 12.7283 | 3464.2026 | 0.71 | 3621.7794 | 0.78822 | 157.5767 | 0.078216
321 | MCLU-65to135-SCn-CZ03-2003-19IEER | CZ03 | SCn | 2003 | 65to135 | 12 | 19 | 323.173 | 2198.0854 | 0.21499 | 2374.1758 | 0.24381 | 176.0904 | 0.028821
322 | MCLU-65to135-SCn-CZ03-2007-19IEER | CZ03 | SCn | 2007 | 65to135 | 12 | 19 | 321.3844 | 2206.6834 | 0.2133 | 2379.1677 | 0.24149 | 172.4844 | 0.028187
323 | MCLU-65to135-SCn-CZ03-2011-19IEER | CZ03 | SCn | 2011 | 65to135 | 12 | 19 | 319.702 | 2213.1149 | 0.2044 | 2387.1026 | 0.23893 | 173.9877 | 0.034532
324 | MCLU-65to135-SCn-CZ03-2015-19IEER | CZ03 | SCn | 2015 | 65to135 | 12 | 19 | 319.2675 | 2213.9573 | 0.20304 | 2396.3141 | 0.23697 | 182.3568 | 0.03393
325 | MCLU-65to135-SCn-CZ03-2020-19IEER | CZ03 | SCn | 2020 | 65to135 | 12 | 19 | 317.1341 | 1938.8579 | 0.17368 | 2115.6562 | 0.19952 | 176.7983 | 0.025838
326 | MCLU-65to135-WRf-CZ03-2003-19IEER | CZ03 | WRf | 2003 | 65to135 | 12 | 19 | 12.4547 | 300218.8776 | 38.988 | 300479.2252 | 39.0685 | 260.3476 | 0.080438
327 | MCLU-65to135-WRf-CZ03-2007-19IEER | CZ03 | WRf | 2007 | 65to135 | 12 | 19 | 11.5841 | 313070.2499 | 39.5643 | 313344.6677 | 39.6436 | 274.4178 | 0.07928
328 | MCLU-65to135-WRf-CZ03-2011-19IEER | CZ03 | WRf | 2011 | 65to135 | 12 | 19 | 11.6524 | 304258.3471 | 37.9452 | 304542.9236 | 38.0243 | 284.5765 | 0.079154
329 | MCLU-65to135-WRf-CZ03-2015-19IEER | CZ03 | WRf | 2015 | 65to135 | 12 | 19 | 11.0155 | 321829.6071 | 40.1237 | 322118.5759 | 40.1988 | 288.9688 | 0.075091
330 | MCLU-65to135-WRf-CZ03-2020-19IEER | CZ03 | WRf | 2020 | 65to135 | 12 | 19 | 9.7379 | 344237.9654 | 42.7762 | 344531.1485 | 42.8483 | 293.183 | 0.072067
331 | MCLU-65to135-Asm-CZ04-2003-19IEER | CZ04 | Asm | 2003 | 65to135 | 12 | 19 | 313.9286 | 2270.0942 | 0.78619 | 2520.7196 | 0.90276 | 250.6254 | 0.11657
332 | MCLU-65to135-Asm-CZ04-2007-19IEER | CZ04 | Asm | 2007 | 65to135 | 12 | 19 | 311.6412 | 2283.5773 | 0.79078 | 2534.186 | 0.90721 | 250.6087 | 0.11643
333 | MCLU-65to135-Asm-CZ04-2011-19IEER | CZ04 | Asm | 2011 | 65to135 | 12 | 19 | 309.3472 | 2322.6429 | 0.76105 | 2623.9696 | 0.92032 | 301.3267 | 0.15928
334 | MCLU-65to135-Asm-CZ04-2015-19IEER | CZ04 | Asm | 2015 | 65to135 | 12 | 19 | 279.3925 | 2556.3158 | 0.80233 | 2824.5588 | 0.96105 | 268.2431 | 0.15872
335 | MCLU-65to135-Asm-CZ04-2020-19IEER | CZ04 | Asm | 2020 | 65to135 | 12 | 19 | 271.4942 | 2507.5457 | 0.82244 | 2694.4485 | 0.93468 | 186.9028 | 0.11225
336 | MCLU-65to135-ECC-CZ04-2003-19IEER | CZ04 | ECC | 2003 | 65to135 | 12 | 19 | 756.2831 | 2658.1991 | 0.84737 | 2825.4708 | 0.97052 | 167.2717 | 0.12315
337 | MCLU-65to135-ECC-CZ04-2007-19IEER | CZ04 | ECC | 2007 | 65to135 | 12 | 19 | 754.9936 | 2662.127 | 0.84767 | 2829.4292 | 0.97068 | 167.3023 | 0.12301
338 | MCLU-65to135-ECC-CZ04-2011-19IEER | CZ04 | ECC | 2011 | 65to135 | 12 | 19 | 753.5454 | 2597.4331 | 0.79751 | 2831.8918 | 0.97055 | 234.4586 | 0.17304
339 | MCLU-65to135-ECC-CZ04-2015-19IEER | CZ04 | ECC | 2015 | 65to135 | 12 | 19 | 696.1272 | 2762.4153 | 0.83098 | 2998.2288 | 1.0051 | 235.8135 | 0.17415
340 | MCLU-65to135-ECC-CZ04-2020-19IEER | CZ04 | ECC | 2020 | 65to135 | 12 | 19 | 665.3979 | 2485.7389 | 0.83132 | 2658.0087 | 0.95469 | 172.2698 | 0.12337
341 | MCLU-65to135-EPr-CZ04-2003-19IEER | CZ04 | EPr | 2003 | 65to135 | 12 | 19 | 122.125 | 1787.501 | 0.44051 | 1901.1455 | 0.5054 | 113.6445 | 0.064885
342 | MCLU-65to135-EPr-CZ04-2007-19IEER | CZ04 | EPr | 2007 | 65to135 | 12 | 19 | 121.1162 | 1800.8354 | 0.4426 | 1914.9314 | 0.50731 | 114.096 | 0.064711
343 | MCLU-65to135-EPr-CZ04-2011-19IEER | CZ04 | EPr | 2011 | 65to135 | 12 | 19 | 117.9048 | 1809.627 | 0.42166 | 1965.7026 | 0.51506 | 156.0756 | 0.093396
344 | MCLU-65to135-EPr-CZ04-2015-19IEER | CZ04 | EPr | 2015 | 65to135 | 12 | 19 | 106.1381 | 1956.8891 | 0.44488 | 2115.4188 | 0.53789 | 158.5297 | 0.093013
345 | MCLU-65to135-EPr-CZ04-2020-19IEER | CZ04 | EPr | 2020 | 65to135 | 12 | 19 | 100.9245 | 1772.2502 | 0.43889 | 1892.5065 | 0.50081 | 120.2563 | 0.061922
346 | MCLU-65to135-ERC-CZ04-2003-19IEER | CZ04 | ERC | 2003 | 65to135 | 12 | 19 | 5.7519 | 1405.1465 | 0.26614 | 1492.1299 | 0.29357 | 86.9834 | 0.027429
347 | MCLU-65to135-ERC-CZ04-2007-19IEER | CZ04 | ERC | 2007 | 65to135 | 12 | 19 | 5.7379 | 1408.0888 | 0.26612 | 1495.2138 | 0.29349 | 87.125 | 0.027373
348 | MCLU-65to135-ERC-CZ04-2011-19IEER | CZ04 | ERC | 2011 | 65to135 | 12 | 19 | 5.5367 | 1413.5361 | 0.24794 | 1539.7386 | 0.29273 | 126.2025 | 0.044793
349 | MCLU-65to135-ERC-CZ04-2015-19IEER | CZ04 | ERC | 2015 | 65to135 | 12 | 19 | 5.217 | 1459.2669 | 0.2457 | 1584.4607 | 0.28554 | 125.1938 | 0.03984
350 | MCLU-65to135-ERC-CZ04-2020-19IEER | CZ04 | ERC | 2020 | 65to135 | 12 | 19 | 5.0504 | 1300.3101 | 0.22821 | 1394.5096 | 0.25225 | 94.1995 | 0.02404
351 | MCLU-65to135-ESe-CZ04-2003-19IEER | CZ04 | ESe | 2003 | 65to135 | 12 | 19 | 390.6631 | 1889.6598 | 0.40488 | 2010.5828 | 0.47014 | 120.923 | 0.065269
352 | MCLU-65to135-ESe-CZ04-2007-19IEER | CZ04 | ESe | 2007 | 65to135 | 12 | 19 | 389.4632 | 1894.9193 | 0.40549 | 2015.9492 | 0.47052 | 121.0299 | 0.065034
353 | MCLU-65to135-ESe-CZ04-2011-19IEER | CZ04 | ESe | 2011 | 65to135 | 12 | 19 | 388.1488 | 1852.7042 | 0.37674 | 2020.8774 | 0.47105 | 168.1732 | 0.094313
354 | MCLU-65to135-ESe-CZ04-2015-19IEER | CZ04 | ESe | 2015 | 65to135 | 12 | 19 | 350.9667 | 1968.4761 | 0.37625 | 2131.9661 | 0.47089 | 163.49 | 0.094646
355 | MCLU-65to135-ESe-CZ04-2020-19IEER | CZ04 | ESe | 2020 | 65to135 | 12 | 19 | 335.4967 | 1760.8914 | 0.39276 | 1884.2025 | 0.45615 | 123.3112 | 0.063389
356 | MCLU-65to135-EUn-CZ04-2003-19IEER | CZ04 | EUn | 2003 | 65to135 | 12 | 19 | 2282.8716 | 2848.3831 | 1.0039 | 3021.3483 | 1.1099 | 172.9653 | 0.10599
357 | MCLU-65to135-EUn-CZ04-2007-19IEER | CZ04 | EUn | 2007 | 65to135 | 12 | 19 | 2272.8094 | 2843.0228 | 0.99788 | 3015.9697 | 1.1036 | 172.9469 | 0.10573
358 | MCLU-65to135-EUn-CZ04-2011-19IEER | CZ04 | EUn | 2011 | 65to135 | 12 | 19 | 2244.1496 | 2796.6767 | 0.96152 | 3037.1479 | 1.1122 | 240.4712 | 0.15066
359 | MCLU-65to135-EUn-CZ04-2015-19IEER | CZ04 | EUn | 2015 | 65to135 | 12 | 19 | 2035.9825 | 2994.674 | 1.0113 | 3235.7732 | 1.1624 | 241.0992 | 0.15106
360 | MCLU-65to135-EUn-CZ04-2020-19IEER | CZ04 | EUn | 2020 | 65to135 | 12 | 19 | 1945.9037 | 2793.7574 | 1.0037 | 2969.2941 | 1.1091 | 175.5368 | 0.10536
361 | MCLU-65to135-Gro-CZ04-2003-19IEER | CZ04 | Gro | 2003 | 65to135 | 12 | 19 | 111.9605 | 14606.0655 | 2.1818 | 14972.8886 | 2.3245 | 366.8231 | 0.14266
362 | MCLU-65to135-Gro-CZ04-2007-19IEER | CZ04 | Gro | 2007 | 65to135 | 12 | 19 | 109.7901 | 13493.8799 | 2.0839 | 13832.7096 | 2.2428 | 338.8297 | 0.15896
363 | MCLU-65to135-Gro-CZ04-2011-19IEER | CZ04 | Gro | 2011 | 65to135 | 12 | 19 | 108.1941 | 13689.2364 | 2.1117 | 14025.1188 | 2.2702 | 335.8824 | 0.15854
364 | MCLU-65to135-Gro-CZ04-2015-19IEER | CZ04 | Gro | 2015 | 65to135 | 12 | 19 | 102.1632 | 13875.4113 | 2.1341 | 14200.3269 | 2.2872 | 324.9157 | 0.15308
365 | MCLU-65to135-Gro-CZ04-2020-19IEER | CZ04 | Gro | 2020 | 65to135 | 12 | 19 | 99.3298 | 13828.8489 | 2.1219 | 14146.0931 | 2.2729 | 317.2442 | 0.151
366 | MCLU-65to135-Hsp-CZ04-2003-19IEER | CZ04 | Hsp | 2003 | 65to135 | 12 | 19 | 682.6035 | 4147.826 | 0.76012 | 4481.7725 | 0.87312 | 333.9466 | 0.11299
367 | MCLU-65to135-Hsp-CZ04-2007-19IEER | CZ04 | Hsp | 2007 | 65to135 | 12 | 19 | 682.6032 | 4147.4299 | 0.75962 | 4481.2463 | 0.87246 | 333.8164 | 0.11284
368 | MCLU-65to135-Hsp-CZ04-2011-19IEER | CZ04 | Hsp | 2011 | 65to135 | 12 | 19 | 682.6028 | 4081.6314 | 0.71591 | 4480.7102 | 0.8718 | 399.0788 | 0.15589
369 | MCLU-65to135-Hsp-CZ04-2015-19IEER | CZ04 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 4046.2442 | 0.69761 | 4442.3484 | 0.85259 | 396.1042 | 0.15498
370 | MCLU-65to135-Hsp-CZ04-2020-19IEER | CZ04 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3592.9778 | 0.66489 | 3934.4832 | 0.77518 | 341.5054 | 0.1103
371 | MCLU-65to135-Htl-CZ04-2003-19IEER | CZ04 | Htl | 2003 | 65to135 | 12 | 19 | 240.442 | 3530.1651 | 0.88307 | 3605.8992 | 0.91097 | 75.7341 | 0.0279
372 | MCLU-65to135-Htl-CZ04-2007-19IEER | CZ04 | Htl | 2007 | 65to135 | 12 | 19 | 240.0918 | 3408.0693 | 0.82872 | 3483.8194 | 0.85657 | 75.7501 | 0.027847
373 | MCLU-65to135-Htl-CZ04-2011-19IEER | CZ04 | Htl | 2011 | 65to135 | 12 | 19 | 230.9529 | 3448.7632 | 0.8318 | 3546.6634 | 0.87259 | 97.9002 | 0.040791
374 | MCLU-65to135-Htl-CZ04-2015-19IEER | CZ04 | Htl | 2015 | 65to135 | 12 | 19 | 204.0197 | 3598.7993 | 0.83556 | 3698.6051 | 0.87707 | 99.8058 | 0.041511
375 | MCLU-65to135-Htl-CZ04-2020-19IEER | CZ04 | Htl | 2020 | 65to135 | 12 | 19 | 202.2324 | 3510.0936 | 0.83512 | 3588.5633 | 0.86348 | 78.4698 | 0.028363
376 | MCLU-65to135-MBT-CZ04-2003-19IEER | CZ04 | MBT | 2003 | 65to135 | 12 | 19 | 338.4282 | 4314.2781 | 0.63905 | 4461.1046 | 0.72539 | 146.8266 | 0.086332
377 | MCLU-65to135-MBT-CZ04-2007-19IEER | CZ04 | MBT | 2007 | 65to135 | 12 | 19 | 333.0365 | 4385.9125 | 0.64727 | 4532.1725 | 0.73327 | 146.26 | 0.086006
378 | MCLU-65to135-MBT-CZ04-2011-19IEER | CZ04 | MBT | 2011 | 65to135 | 12 | 19 | 314.7394 | 4509.6357 | 0.63218 | 4727.5489 | 0.75364 | 217.9132 | 0.12146
379 | MCLU-65to135-MBT-CZ04-2015-19IEER | CZ04 | MBT | 2015 | 65to135 | 12 | 19 | 291.9786 | 4788.6256 | 0.6597 | 5004.7111 | 0.78136 | 216.0855 | 0.12166
380 | MCLU-65to135-MBT-CZ04-2020-19IEER | CZ04 | MBT | 2020 | 65to135 | 12 | 19 | 270.5792 | 4694.8282 | 0.68033 | 4836.6615 | 0.76578 | 141.8333 | 0.085456
381 | MCLU-65to135-MLI-CZ04-2003-19IEER | CZ04 | MLI | 2003 | 65to135 | 12 | 19 | 202.5522 | 3225.5376 | 0.48018 | 3384.5993 | 0.54362 | 159.0617 | 0.063443
382 | MCLU-65to135-MLI-CZ04-2007-19IEER | CZ04 | MLI | 2007 | 65to135 | 12 | 19 | 198.0562 | 3294.4896 | 0.48852 | 3453.0564 | 0.55196 | 158.5668 | 0.063445
383 | MCLU-65to135-MLI-CZ04-2011-19IEER | CZ04 | MLI | 2011 | 65to135 | 12 | 19 | 193.5228 | 3327.7096 | 0.46844 | 3525.5636 | 0.56076 | 197.854 | 0.092319
384 | MCLU-65to135-MLI-CZ04-2015-19IEER | CZ04 | MLI | 2015 | 65to135 | 12 | 19 | 190.2307 | 3359.2339 | 0.4715 | 3556.6415 | 0.56385 | 197.4077 | 0.092353
385 | MCLU-65to135-MLI-CZ04-2020-19IEER | CZ04 | MLI | 2020 | 65to135 | 12 | 19 | 176.6995 | 3059.2717 | 0.46616 | 3218.0636 | 0.52892 | 158.7919 | 0.062763
386 | MCLU-65to135-Mtl-CZ04-2003-19IEER | CZ04 | Mtl | 2003 | 65to135 | 12 | 19 | 44.2581 | 3410.1679 | 0.80365 | 3470.7538 | 0.82291 | 60.586 | 0.019259
387 | MCLU-65to135-Mtl-CZ04-2007-19IEER | CZ04 | Mtl | 2007 | 65to135 | 12 | 19 | 44.2581 | 3282.5319 | 0.74727 | 3343.1074 | 0.76651 | 60.5755 | 0.01924
388 | MCLU-65to135-Mtl-CZ04-2011-19IEER | CZ04 | Mtl | 2011 | 65to135 | 12 | 19 | 42.2722 | 3314.8651 | 0.75066 | 3390.9543 | 0.77811 | 76.0892 | 0.027457
389 | MCLU-65to135-Mtl-CZ04-2015-19IEER | CZ04 | Mtl | 2015 | 65to135 | 12 | 19 | 35.7752 | 3541.3758 | 0.76453 | 3621.7259 | 0.79355 | 80.3501 | 0.029013
390 | MCLU-65to135-Mtl-CZ04-2020-19IEER | CZ04 | Mtl | 2020 | 65to135 | 12 | 19 | 35.6439 | 3475.1801 | 0.76252 | 3537.3414 | 0.78226 | 62.1613 | 0.01974
391 | MCLU-65to135-Nrs-CZ04-2003-19IEER | CZ04 | Nrs | 2003 | 65to135 | 12 | 19 | 187.2632 | 4337.7564 | 0.87907 | 4508.9354 | 0.93611 | 171.179 | 0.057042
392 | MCLU-65to135-Nrs-CZ04-2007-19IEER | CZ04 | Nrs | 2007 | 65to135 | 12 | 19 | 187.1991 | 4253.767 | 0.84688 | 4425.1299 | 0.90375 | 171.3628 | 0.056866
393 | MCLU-65to135-Nrs-CZ04-2011-19IEER | CZ04 | Nrs | 2011 | 65to135 | 12 | 19 | 186.2543 | 4265.3868 | 0.82092 | 4468.9291 | 0.90019 | 203.5423 | 0.079271
394 | MCLU-65to135-Nrs-CZ04-2015-19IEER | CZ04 | Nrs | 2015 | 65to135 | 12 | 19 | 181.638 | 4161.7272 | 0.75741 | 4355.372 | 0.83351 | 193.6448 | 0.076093
395 | MCLU-65to135-Nrs-CZ04-2020-19IEER | CZ04 | Nrs | 2020 | 65to135 | 12 | 19 | 181.607 | 3816.9301 | 0.71978 | 3983.147 | 0.77292 | 166.2169 | 0.053133
396 | MCLU-65to135-OfL-CZ04-2003-19IEER | CZ04 | OfL | 2003 | 65to135 | 12 | 19 | 445.8637 | 3506.0879 | 0.57191 | 3656.3466 | 0.61792 | 150.2586 | 0.046012
397 | MCLU-65to135-OfL-CZ04-2007-19IEER | CZ04 | OfL | 2007 | 65to135 | 12 | 19 | 445.4138 | 3509.4558 | 0.57233 | 3659.7224 | 0.6183 | 150.2666 | 0.045979
398 | MCLU-65to135-OfL-CZ04-2011-19IEER | CZ04 | OfL | 2011 | 65to135 | 12 | 19 | 428.1528 | 3536.3425 | 0.5603 | 3757.4991 | 0.62556 | 221.1566 | 0.065259
399 | MCLU-65to135-OfL-CZ04-2015-19IEER | CZ04 | OfL | 2015 | 65to135 | 12 | 19 | 401.9344 | 3691.9269 | 0.57973 | 3908.6666 | 0.64396 | 216.7398 | 0.064228
400 | MCLU-65to135-OfL-CZ04-2020-19IEER | CZ04 | OfL | 2020 | 65to135 | 12 | 19 | 389.6167 | 3591.6236 | 0.58143 | 3737.6143 | 0.62597 | 145.9907 | 0.044543
401 | MCLU-65to135-OfS-CZ04-2003-19IEER | CZ04 | OfS | 2003 | 65to135 | 12 | 19 | 30.9292 | 2533.5457 | 0.42115 | 2690.1331 | 0.46712 | 156.5875 | 0.045964
402 | MCLU-65to135-OfS-CZ04-2007-19IEER | CZ04 | OfS | 2007 | 65to135 | 12 | 19 | 30.8541 | 2539.301 | 0.42167 | 2695.8077 | 0.46761 | 156.5067 | 0.045935
403 | MCLU-65to135-OfS-CZ04-2011-19IEER | CZ04 | OfS | 2011 | 65to135 | 12 | 19 | 30.187 | 2507.5483 | 0.40299 | 2725.9068 | 0.46894 | 218.3585 | 0.06595
404 | MCLU-65to135-OfS-CZ04-2015-19IEER | CZ04 | OfS | 2015 | 65to135 | 12 | 19 | 25.06 | 2924.6122 | 0.44938 | 3137.99 | 0.51354 | 213.3778 | 0.064157
405 | MCLU-65to135-OfS-CZ04-2020-19IEER | CZ04 | OfS | 2020 | 65to135 | 12 | 19 | 24.3189 | 2825.3972 | 0.44759 | 2975.7387 | 0.49168 | 150.3414 | 0.044095
406 | MCLU-65to135-RFF-CZ04-2003-19IEER | CZ04 | RFF | 2003 | 65to135 | 12 | 19 | 6.7901 | 5915.722 | 1.3535 | 6222.7591 | 1.4713 | 307.0372 | 0.11771
407 | MCLU-65to135-RFF-CZ04-2007-19IEER | CZ04 | RFF | 2007 | 65to135 | 12 | 19 | 6.7324 | 5963.4315 | 1.3622 | 6271.3494 | 1.4797 | 307.9179 | 0.1175
408 | MCLU-65to135-RFF-CZ04-2011-19IEER | CZ04 | RFF | 2011 | 65to135 | 12 | 19 | 6.6698 | 5913.9379 | 1.3267 | 6325.4563 | 1.4894 | 411.5184 | 0.16271
409 | MCLU-65to135-RFF-CZ04-2015-19IEER | CZ04 | RFF | 2015 | 65to135 | 12 | 19 | 6.365 | 5879.1639 | 1.3219 | 6286.6448 | 1.487 | 407.4809 | 0.16508
410 | MCLU-65to135-RFF-CZ04-2020-19IEER | CZ04 | RFF | 2020 | 65to135 | 12 | 19 | 6.0374 | 5496.0358 | 1.3015 | 5811.8575 | 1.4198 | 315.8217 | 0.11831
411 | MCLU-65to135-RSD-CZ04-2003-19IEER | CZ04 | RSD | 2003 | 65to135 | 12 | 19 | 12.6888 | 5764.1077 | 1.3313 | 6038.6786 | 1.4516 | 274.5709 | 0.12031
412 | MCLU-65to135-RSD-CZ04-2007-19IEER | CZ04 | RSD | 2007 | 65to135 | 12 | 19 | 12.5757 | 5814.6719 | 1.3405 | 6090.6978 | 1.4608 | 276.0259 | 0.12023
413 | MCLU-65to135-RSD-CZ04-2011-19IEER | CZ04 | RSD | 2011 | 65to135 | 12 | 19 | 12.2777 | 5836.6928 | 1.3178 | 6234.3868 | 1.4869 | 397.694 | 0.16908
414 | MCLU-65to135-RSD-CZ04-2015-19IEER | CZ04 | RSD | 2015 | 65to135 | 12 | 19 | 11.4382 | 5906.0335 | 1.3284 | 6296.0182 | 1.4999 | 389.9846 | 0.17147
415 | MCLU-65to135-RSD-CZ04-2020-19IEER | CZ04 | RSD | 2020 | 65to135 | 12 | 19 | 10.6393 | 5422.8835 | 1.2892 | 5701.7957 | 1.4075 | 278.9122 | 0.11837
416 | MCLU-65to135-Rt3-CZ04-2003-19IEER | CZ04 | Rt3 | 2003 | 65to135 | 12 | 19 | 237.4197 | 5766.5671 | 1.2475 | 5963.4245 | 1.3713 | 196.8575 | 0.12376
417 | MCLU-65to135-Rt3-CZ04-2007-19IEER | CZ04 | Rt3 | 2007 | 65to135 | 12 | 19 | 236.6416 | 5784.9108 | 1.2503 | 5981.681 | 1.3739 | 196.7702 | 0.12363
418 | MCLU-65to135-Rt3-CZ04-2011-19IEER | CZ04 | Rt3 | 2011 | 65to135 | 12 | 19 | 235.8368 | 5695.7883 | 1.1992 | 6000.7706 | 1.3768 | 304.9823 | 0.17756
419 | MCLU-65to135-Rt3-CZ04-2015-19IEER | CZ04 | Rt3 | 2015 | 65to135 | 12 | 19 | 225.3377 | 5367.5795 | 1.1484 | 5671.9906 | 1.327 | 304.4111 | 0.17864
420 | MCLU-65to135-Rt3-CZ04-2020-19IEER | CZ04 | Rt3 | 2020 | 65to135 | 12 | 19 | 215.5258 | 5066.05 | 1.1432 | 5271.9114 | 1.2675 | 205.8615 | 0.12435
421 | MCLU-65to135-RtL-CZ04-2003-19IEER | CZ04 | RtL | 2003 | 65to135 | 12 | 19 | 203.0217 | 6430.5667 | 1.3457 | 6650.2367 | 1.4679 | 219.67 | 0.12227
422 | MCLU-65to135-RtL-CZ04-2007-19IEER | CZ04 | RtL | 2007 | 65to135 | 12 | 19 | 200.3757 | 6515.2304 | 1.3606 | 6735.0659 | 1.4828 | 219.8355 | 0.12211
423 | MCLU-65to135-RtL-CZ04-2011-19IEER | CZ04 | RtL | 2011 | 65to135 | 12 | 19 | 197.6818 | 6484.0285 | 1.3256 | 6824.3546 | 1.4984 | 340.3261 | 0.17275
424 | MCLU-65to135-RtL-CZ04-2015-19IEER | CZ04 | RtL | 2015 | 65to135 | 12 | 19 | 189.5252 | 6290.8804 | 1.3128 | 6638.4959 | 1.4869 | 347.6155 | 0.1741
425 | MCLU-65to135-RtL-CZ04-2020-19IEER | CZ04 | RtL | 2020 | 65to135 | 12 | 19 | 178.0412 | 6165.7903 | 1.3589 | 6405.9517 | 1.4821 | 240.1614 | 0.12317
426 | MCLU-65to135-RtS-CZ04-2003-19IEER | CZ04 | RtS | 2003 | 65to135 | 12 | 19 | 15.793 | 3678.2011 | 0.83183 | 3893.808 | 0.94154 | 215.6069 | 0.10971
427 | MCLU-65to135-RtS-CZ04-2007-19IEER | CZ04 | RtS | 2007 | 65to135 | 12 | 19 | 15.5893 | 3722.7784 | 0.83949 | 3937.6667 | 0.94915 | 214.8883 | 0.10967
428 | MCLU-65to135-RtS-CZ04-2011-19IEER | CZ04 | RtS | 2011 | 65to135 | 12 | 19 | 15.3423 | 3692.982 | 0.803 | 3993.138 | 0.95944 | 300.1559 | 0.15643
429 | MCLU-65to135-RtS-CZ04-2015-19IEER | CZ04 | RtS | 2015 | 65to135 | 12 | 19 | 14.4685 | 3574.8965 | 0.78203 | 3873.2556 | 0.93971 | 298.3591 | 0.15768
430 | MCLU-65to135-RtS-CZ04-2020-19IEER | CZ04 | RtS | 2020 | 65to135 | 12 | 19 | 13.8401 | 3459.7379 | 0.80471 | 3679.3599 | 0.91485 | 219.6219 | 0.11014
431 | MCLU-65to135-SCn-CZ04-2003-19IEER | CZ04 | SCn | 2003 | 65to135 | 12 | 19 | 235.1149 | 3095.5981 | 0.41306 | 3302.1253 | 0.4776 | 206.5272 | 0.064539
432 | MCLU-65to135-SCn-CZ04-2007-19IEER | CZ04 | SCn | 2007 | 65to135 | 12 | 19 | 226.1074 | 3207.6497 | 0.42427 | 3413.1843 | 0.48748 | 205.5346 | 0.063209
433 | MCLU-65to135-SCn-CZ04-2011-19IEER | CZ04 | SCn | 2011 | 65to135 | 12 | 19 | 217.1937 | 3301.1405 | 0.40808 | 3531.9318 | 0.49842 | 230.7913 | 0.090341
434 | MCLU-65to135-SCn-CZ04-2015-19IEER | CZ04 | SCn | 2015 | 65to135 | 12 | 19 | 213.7836 | 3348.3682 | 0.4112 | 3578.2485 | 0.50155 | 229.8803 | 0.090353
435 | MCLU-65to135-SCn-CZ04-2020-19IEER | CZ04 | SCn | 2020 | 65to135 | 12 | 19 | 195.5427 | 3188.2404 | 0.42118 | 3389.4136 | 0.48311 | 201.1732 | 0.061935
436 | MCLU-65to135-WRf-CZ04-2003-19IEER | CZ04 | WRf | 2003 | 65to135 | 12 | 19 | 13.8498 | 274390.4648 | 37.1909 | 274722.7965 | 37.2868 | 332.3317 | 0.095829
437 | MCLU-65to135-WRf-CZ04-2007-19IEER | CZ04 | WRf | 2007 | 65to135 | 12 | 19 | 13.5695 | 269776.2272 | 35.4518 | 270111.1538 | 35.5455 | 334.9266 | 0.093707
438 | MCLU-65to135-WRf-CZ04-2011-19IEER | CZ04 | WRf | 2011 | 65to135 | 12 | 19 | 12.6227 | 281064.213 | 36.0386 | 281416.1925 | 36.128 | 351.9796 | 0.089394
439 | MCLU-65to135-WRf-CZ04-2015-19IEER | CZ04 | WRf | 2015 | 65to135 | 12 | 19 | 11.9123 | 297787.9041 | 38.1685 | 298140.1441 | 38.2567 | 352.2401 | 0.088177
440 | MCLU-65to135-WRf-CZ04-2020-19IEER | CZ04 | WRf | 2020 | 65to135 | 12 | 19 | 11.1944 | 299381.2607 | 38.3141 | 299726.0396 | 38.3963 | 344.7789 | 0.082129
441 | MCLU-65to135-Asm-CZ05-2003-19IEER | CZ05 | Asm | 2003 | 65to135 | 12 | 19 | 344.7074 | 1823.4002 | 0.40645 | 2002.4237 | 0.47241 | 179.0235 | 0.065962
442 | MCLU-65to135-Asm-CZ05-2007-19IEER | CZ05 | Asm | 2007 | 65to135 | 12 | 19 | 341.3424 | 1839.0232 | 0.40997 | 2018.0796 | 0.47622 | 179.0564 | 0.06625
443 | MCLU-65to135-Asm-CZ05-2011-19IEER | CZ05 | Asm | 2011 | 65to135 | 12 | 19 | 341.3424 | 1804.0378 | 0.38478 | 2018.0796 | 0.47622 | 214.0418 | 0.091444
444 | MCLU-65to135-Asm-CZ05-2015-19IEER | CZ05 | Asm | 2015 | 65to135 | 12 | 19 | 297.8855 | 1990.4637 | 0.41929 | 2194.4528 | 0.50988 | 203.9891 | 0.090591
445 | MCLU-65to135-Asm-CZ05-2020-19IEER | CZ05 | Asm | 2020 | 65to135 | 12 | 19 | 286.4738 | 2015.6333 | 0.44358 | 2155.5002 | 0.5029 | 139.8669 | 0.059322
446 | MCLU-65to135-ECC-CZ05-2003-19IEER | CZ05 | ECC | 2003 | 65to135 | 12 | 19 | 832.2933 | 2250.8805 | 0.5337 | 2354.8094 | 0.59467 | 103.929 | 0.060974
447 | MCLU-65to135-ECC-CZ05-2007-19IEER | CZ05 | ECC | 2007 | 65to135 | 12 | 19 | 831.9151 | 2252.0235 | 0.53376 | 2355.9109 | 0.59473 | 103.8874 | 0.060967
448 | MCLU-65to135-ECC-CZ05-2011-19IEER | CZ05 | ECC | 2011 | 65to135 | 12 | 19 | 831.8822 | 2216.493 | 0.50488 | 2354.2294 | 0.59437 | 137.7364 | 0.089482
449 | MCLU-65to135-ECC-CZ05-2015-19IEER | CZ05 | ECC | 2015 | 65to135 | 12 | 19 | 735.9524 | 2473.0069 | 0.55953 | 2615.1773 | 0.65196 | 142.1704 | 0.092428
450 | MCLU-65to135-ECC-CZ05-2020-19IEER | CZ05 | ECC | 2020 | 65to135 | 12 | 19 | 693.6637 | 2214.3533 | 0.54439 | 2326.289 | 0.60749 | 111.9357 | 0.063105
451 | MCLU-65to135-EPr-CZ05-2003-19IEER | CZ05 | EPr | 2003 | 65to135 | 12 | 19 | 125.9756 | 1635.6382 | 0.296 | 1711.4713 | 0.32933 | 75.8332 | 0.033331
452 | MCLU-65to135-EPr-CZ05-2007-19IEER | CZ05 | EPr | 2007 | 65to135 | 12 | 19 | 125.6637 | 1639.5763 | 0.29653 | 1715.3323 | 0.32979 | 75.756 | 0.033264
453 | MCLU-65to135-EPr-CZ05-2011-19IEER | CZ05 | EPr | 2011 | 65to135 | 12 | 19 | 125.6637 | 1617.9795 | 0.28269 | 1715.3323 | 0.32979 | 97.3527 | 0.047102
454 | MCLU-65to135-EPr-CZ05-2015-19IEER | CZ05 | EPr | 2015 | 65to135 | 12 | 19 | 110.2832 | 1801.7477 | 0.30974 | 1906.708 | 0.35809 | 104.9603 | 0.048344
455 | MCLU-65to135-EPr-CZ05-2020-19IEER | CZ05 | EPr | 2020 | 65to135 | 12 | 19 | 105.3569 | 1621.764 | 0.2888 | 1701.3987 | 0.32174 | 79.6347 | 0.032943
456 | MCLU-65to135-ERC-CZ05-2003-19IEER | CZ05 | ERC | 2003 | 65to135 | 12 | 19 | 5.3785 | 1409.7321 | 0.20171 | 1485.0876 | 0.20865 | 75.3556 | 0.0069403
457 | MCLU-65to135-ERC-CZ05-2007-19IEER | CZ05 | ERC | 2007 | 65to135 | 12 | 19 | 5.3776 | 1410.1613 | 0.20168 | 1485.5522 | 0.2086 | 75.3909 | 0.0069234
458 | MCLU-65to135-ERC-CZ05-2011-19IEER | CZ05 | ERC | 2011 | 65to135 | 12 | 19 | 5.3776 | 1382.4974 | 0.1974 | 1485.5522 | 0.2086 | 103.0548 | 0.011195
459 | MCLU-65to135-ERC-CZ05-2015-19IEER | CZ05 | ERC | 2015 | 65to135 | 12 | 19 | 4.9713 | 1461.3879 | 0.20562 | 1568.2435 | 0.21367 | 106.8555 | 0.0080522
460 | MCLU-65to135-ERC-CZ05-2020-19IEER | CZ05 | ERC | 2020 | 65to135 | 12 | 19 | 4.763 | 1299.3578 | 0.17886 | 1385.6284 | 0.1829 | 86.2705 | 0.0040374
461 | MCLU-65to135-ESe-CZ05-2003-19IEER | CZ05 | ESe | 2003 | 65to135 | 12 | 19 | 419.6943 | 1642.5027 | 0.256 | 1726.0085 | 0.29314 | 83.5059 | 0.03714
462 | MCLU-65to135-ESe-CZ05-2007-19IEER | CZ05 | ESe | 2007 | 65to135 | 12 | 19 | 418.8856 | 1645.7428 | 0.25639 | 1729.1656 | 0.29353 | 83.4228 | 0.037145
463 | MCLU-65to135-ESe-CZ05-2011-19IEER | CZ05 | ESe | 2011 | 65to135 | 12 | 19 | 418.8543 | 1618.4121 | 0.24004 | 1728.34 | 0.29349 | 109.9278 | 0.053445
464 | MCLU-65to135-ESe-CZ05-2015-19IEER | CZ05 | ESe | 2015 | 65to135 | 12 | 19 | 356.566 | 1845.6819 | 0.26078 | 1957.0608 | 0.31295 | 111.3789 | 0.052167
465 | MCLU-65to135-ESe-CZ05-2020-19IEER | CZ05 | ESe | 2020 | 65to135 | 12 | 19 | 336.0159 | 1643.954 | 0.26076 | 1735.0995 | 0.29774 | 91.1455 | 0.036983
466 | MCLU-65to135-EUn-CZ05-2003-19IEER | CZ05 | EUn | 2003 | 65to135 | 12 | 19 | 2479.6955 | 2424.3131 | 0.64495 | 2535.5496 | 0.69908 | 111.2364 | 0.054129
467 | MCLU-65to135-EUn-CZ05-2007-19IEER | CZ05 | EUn | 2007 | 65to135 | 12 | 19 | 2476.5423 | 2416.3332 | 0.64184 | 2527.3823 | 0.69595 | 111.0491 | 0.054103
468 | MCLU-65to135-EUn-CZ05-2011-19IEER | CZ05 | EUn | 2011 | 65to135 | 12 | 19 | 2461.7711 | 2382.6714 | 0.61883 | 2528.5459 | 0.69962 | 145.8745 | 0.08079
469 | MCLU-65to135-EUn-CZ05-2015-19IEER | CZ05 | EUn | 2015 | 65to135 | 12 | 19 | 2156.9373 | 2664.1039 | 0.6879 | 2809.8657 | 0.77087 | 145.7619 | 0.082971
470 | MCLU-65to135-EUn-CZ05-2020-19IEER | CZ05 | EUn | 2020 | 65to135 | 12 | 19 | 2058.1843 | 2458.3049 | 0.664 | 2568.4068 | 0.71792 | 110.1019 | 0.053925
471 | MCLU-65to135-Gro-CZ05-2003-19IEER | CZ05 | Gro | 2003 | 65to135 | 12 | 19 | 81.6448 | 19637.237 | 2.5138 | 20055.3117 | 2.5906 | 418.0747 | 0.076855
472 | MCLU-65to135-Gro-CZ05-2007-19IEER | CZ05 | Gro | 2007 | 65to135 | 12 | 19 | 80.7578 | 17893.0569 | 2.3811 | 18229.6759 | 2.4541 | 336.619 | 0.072958
473 | MCLU-65to135-Gro-CZ05-2011-19IEER | CZ05 | Gro | 2011 | 65to135 | 12 | 19 | 80.7578 | 17893.0569 | 2.3811 | 18229.6759 | 2.4541 | 336.619 | 0.072958
474 | MCLU-65to135-Gro-CZ05-2015-19IEER | CZ05 | Gro | 2015 | 65to135 | 12 | 19 | 75.4438 | 18332.2523 | 2.4195 | 18658.9617 | 2.4845 | 326.7094 | 0.064979
475 | MCLU-65to135-Gro-CZ05-2020-19IEER | CZ05 | Gro | 2020 | 65to135 | 12 | 19 | 72.6112 | 18465.8607 | 2.4232 | 18772.0085 | 2.4819 | 306.1478 | 0.058754
476 | MCLU-65to135-Hsp-CZ05-2003-19IEER | CZ05 | Hsp | 2003 | 65to135 | 12 | 19 | 681.4533 | 3979.979 | 0.6239 | 4252.1293 | 0.67542 | 272.1503 | 0.05152
477 | MCLU-65to135-Hsp-CZ05-2007-19IEER | CZ05 | Hsp | 2007 | 65to135 | 12 | 19 | 681.4533 | 3980.041 | 0.62381 | 4252.1429 | 0.6753 | 272.102 | 0.051488
478 | MCLU-65to135-Hsp-CZ05-2011-19IEER | CZ05 | Hsp | 2011 | 65to135 | 12 | 19 | 681.4533 | 3948.9445 | 0.60298 | 4252.1429 | 0.6753 | 303.1985 | 0.072317
479 | MCLU-65to135-Hsp-CZ05-2015-19IEER | CZ05 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4567 | 3913.8359 | 0.59438 | 4216.4553 | 0.66474 | 302.6194 | 0.070357
480 | MCLU-65to135-Hsp-CZ05-2020-19IEER | CZ05 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4567 | 3438.6973 | 0.54379 | 3724.1127 | 0.59267 | 285.4154 | 0.048883
481 | MCLU-65to135-Htl-CZ05-2003-19IEER | CZ05 | Htl | 2003 | 65to135 | 12 | 19 | 266.3085 | 2859.4258 | 0.48594 | 2912.651 | 0.49885 | 53.2253 | 0.012907
482 | MCLU-65to135-Htl-CZ05-2007-19IEER | CZ05 | Htl | 2007 | 65to135 | 12 | 19 | 266.2807 | 2773.7037 | 0.46455 | 2827.2056 | 0.47745 | 53.5019 | 0.012893
483 | MCLU-65to135-Htl-CZ05-2011-19IEER | CZ05 | Htl | 2011 | 65to135 | 12 | 19 | 260.1129 | 2778.2167 | 0.46863 | 2839.2883 | 0.48716 | 61.0716 | 0.018528
484 | MCLU-65to135-Htl-CZ05-2015-19IEER | CZ05 | Htl | 2015 | 65to135 | 12 | 19 | 225.6472 | 2962.8598 | 0.49032 | 3024.9661 | 0.5094 | 62.1063 | 0.01908
485 | MCLU-65to135-Htl-CZ05-2020-19IEER | CZ05 | Htl | 2020 | 65to135 | 12 | 19 | 224.2519 | 2865.4798 | 0.48263 | 2919.0939 | 0.4954 | 53.6141 | 0.012768
486 | MCLU-65to135-MBT-CZ05-2003-19IEER | CZ05 | MBT | 2003 | 65to135 | 12 | 19 | 347.8698 | 4048.3711 | 0.49332 | 4149.7364 | 0.53921 | 101.3653 | 0.045882
487 | MCLU-65to135-MBT-CZ05-2007-19IEER | CZ05 | MBT | 2007 | 65to135 | 12 | 19 | 344.3195 | 4094.4213 | 0.49868 | 4194.6005 | 0.54475 | 100.1793 | 0.046066
488 | MCLU-65to135-MBT-CZ05-2011-19IEER | CZ05 | MBT | 2011 | 65to135 | 12 | 19 | 336.5007 | 4090.875 | 0.48463 | 4237.1472 | 0.55021 | 146.2721 | 0.065579
489 | MCLU-65to135-MBT-CZ05-2015-19IEER | CZ05 | MBT | 2015 | 65to135 | 12 | 19 | 311.5379 | 4361.548 | 0.50977 | 4507.5542 | 0.57475 | 146.0062 | 0.064983
490 | MCLU-65to135-MBT-CZ05-2020-19IEER | CZ05 | MBT | 2020 | 65to135 | 12 | 19 | 287.3222 | 4280.8511 | 0.51373 | 4376.9769 | 0.55898 | 96.1257 | 0.045249
491 | MCLU-65to135-MLI-CZ05-2003-19IEER | CZ05 | MLI | 2003 | 65to135 | 12 | 19 | 196.0479 | 3182.893 | 0.36585 | 3316.3597 | 0.39785 | 133.4667 | 0.032
492 | MCLU-65to135-MLI-CZ05-2007-19IEER | CZ05 | MLI | 2007 | 65to135 | 12 | 19 | 192.3889 | 3241.9188 | 0.37231 | 3374.7108 | 0.40428 | 132.792 | 0.031976
493 | MCLU-65to135-MLI-CZ05-2011-19IEER | CZ05 | MLI | 2011 | 65to135 | 12 | 19 | 192.3889 | 3226.0463 | 0.36164 | 3374.7108 | 0.40428 | 148.6645 | 0.042646
494 | MCLU-65to135-MLI-CZ05-2015-19IEER | CZ05 | MLI | 2015 | 65to135 | 12 | 19 | 189.064 | 3258.1823 | 0.36437 | 3407.2713 | 0.40675 | 149.089 | 0.042381
495 | MCLU-65to135-MLI-CZ05-2020-19IEER | CZ05 | MLI | 2020 | 65to135 | 12 | 19 | 179.1405 | 2880.1211 | 0.33073 | 3015.3879 | 0.36149 | 135.2668 | 0.030752
496 | MCLU-65to135-Mtl-CZ05-2003-19IEER | CZ05 | Mtl | 2003 | 65to135 | 12 | 19 | 50.6889 | 2619.492 | 0.38425 | 2676.4935 | 0.39358 | 57.0016 | 0.0093276
497 | MCLU-65to135-Mtl-CZ05-2007-19IEER | CZ05 | Mtl | 2007 | 65to135 | 12 | 19 | 50.6889 | 2539.6653 | 0.36645 | 2596.6234 | 0.37584 | 56.9581 | 0.0093892
498 | MCLU-65to135-Mtl-CZ05-2011-19IEER | CZ05 | Mtl | 2011 | 65to135 | 12 | 19 | 49.493 | 2529.1505 | 0.36942 | 2592.5375 | 0.3828 | 63.387 | 0.013388
499 | MCLU-65to135-Mtl-CZ05-2015-19IEER | CZ05 | Mtl | 2015 | 65to135 | 12 | 19 | 42.1269 | 2713.3435 | 0.40504 | 2779.2793 | 0.41948 | 65.9357 | 0.014441
500 | MCLU-65to135-Mtl-CZ05-2020-19IEER | CZ05 | Mtl | 2020 | 65to135 | 12 | 19 | 41.6832 | 2648.8927 | 0.40143 | 2706.2898 | 0.41104 | 57.397 | 0.009611
501 | MCLU-65to135-Nrs-CZ05-2003-19IEER | CZ05 | Nrs | 2003 | 65to135 | 12 | 19 | 185.4875 | 4180.7859 | 0.67654 | 4305.8154 | 0.70176 | 125.0295 | 0.025213
502 | MCLU-65to135-Nrs-CZ05-2007-19IEER | CZ05 | Nrs | 2007 | 65to135 | 12 | 19 | 185.482 | 4112.7298 | 0.65942 | 4238.1411 | 0.68458 | 125.4113 | 0.025153
503 | MCLU-65to135-Nrs-CZ05-2011-19IEER | CZ05 | Nrs | 2011 | 65to135 | 12 | 19 | 185.482 | 4095.9939 | 0.64946 | 4238.1411 | 0.68458 | 142.1472 | 0.035112
504 | MCLU-65to135-Nrs-CZ05-2015-19IEER | CZ05 | Nrs | 2015 | 65to135 | 12 | 19 | 181.607 | 4008.5442 | 0.61679 | 4144.7322 | 0.64941 | 136.188 | 0.032623
505 | MCLU-65to135-Nrs-CZ05-2020-19IEER | CZ05 | Nrs | 2020 | 65to135 | 12 | 19 | 181.607 | 3657.164 | 0.57177 | 3783.5308 | 0.59524 | 126.3668 | 0.023462
506 | MCLU-65to135-OfL-CZ05-2003-19IEER | CZ05 | OfL | 2003 | 65to135 | 12 | 19 | 513.2354 | 2910.022 | 0.4267 | 3010.9242 | 0.45755 | 100.9022 | 0.030844
507 | MCLU-65to135-OfL-CZ05-2007-19IEER | CZ05 | OfL | 2007 | 65to135 | 12 | 19 | 512.7488 | 2912.8849 | 0.42708 | 3013.733 | 0.45791 | 100.8481 | 0.030837
508 | MCLU-65to135-OfL-CZ05-2011-19IEER | CZ05 | OfL | 2011 | 65to135 | 12 | 19 | 503.0415 | 2898.3173 | 0.41555 | 3039.5984 | 0.46088 | 141.2811 | 0.045336
509 | MCLU-65to135-OfL-CZ05-2015-19IEER | CZ05 | OfL | 2015 | 65to135 | 12 | 19 | 467.3063 | 3062.4503 | 0.43721 | 3201.7909 | 0.48204 | 139.3406 | 0.044827
510 | MCLU-65to135-OfL-CZ05-2020-19IEER | CZ05 | OfL | 2020 | 65to135 | 12 | 19 | 451.6801 | 2965.1577 | 0.4369 | 3063.2253 | 0.46728 | 98.0676 | 0.030375
511 | MCLU-65to135-OfS-CZ05-2003-19IEER | CZ05 | OfS | 2003 | 65to135 | 12 | 19 | 33.6426 | 2190.6044 | 0.3079 | 2303.3658 | 0.33676 | 112.7613 | 0.028854
512 | MCLU-65to135-OfS-CZ05-2007-19IEER | CZ05 | OfS | 2007 | 65to135 | 12 | 19 | 33.6345 | 2191.3403 | 0.30793 | 2304.0699 | 0.33678 | 112.7296 | 0.028846
513 | MCLU-65to135-OfS-CZ05-2011-19IEER | CZ05 | OfS | 2011 | 65to135 | 12 | 19 | 33.5276 | 2138.532 | 0.29253 | 2286.0893 | 0.33441 | 147.5573 | 0.041883
514 | MCLU-65to135-OfS-CZ05-2015-19IEER | CZ05 | OfS | 2015 | 65to135 | 12 | 19 | 27.1739 | 2572.281 | 0.34519 | 2719.3983 | 0.38765 | 147.1174 | 0.042463
515 | MCLU-65to135-OfS-CZ05-2020-19IEER | CZ05 | OfS | 2020 | 65to135 | 12 | 19 | 26.3969 | 2456.515 | 0.33844 | 2567.8781 | 0.36709 | 111.3631 | 0.028652
516 | MCLU-65to135-RFF-CZ05-2003-19IEER | CZ05 | RFF | 2003 | 65to135 | 12 | 19 | 7.35 | 5107.897 | 0.90585 | 5318.5053 | 0.97111 | 210.6083 | 0.065256
517 | MCLU-65to135-RFF-CZ05-2007-19IEER | CZ05 | RFF | 2007 | 65to135 | 12 | 19 | 7.2746 | 5160.1881 | 0.91478 | 5373.2118 | 0.98093 | 213.0237 | 0.06615
518 | MCLU-65to135-RFF-CZ05-2011-19IEER | CZ05 | RFF | 2011 | 65to135 | 12 | 19 | 7.2746 | 5115.7384 | 0.88359 | 5373.2118 | 0.98093 | 257.4734 | 0.097337
519 | MCLU-65to135-RFF-CZ05-2015-19IEER | CZ05 | RFF | 2015 | 65to135 | 12 | 19 | 6.8121 | 5185.94 | 0.89396 | 5447.0149 | 0.99261 | 261.0749 | 0.098655
520 | MCLU-65to135-RFF-CZ05-2020-19IEER | CZ05 | RFF | 2020 | 65to135 | 12 | 19 | 6.2777 | 4916.8529 | 0.87779 | 5150.5879 | 0.95012 | 233.735 | 0.072324
521 | MCLU-65to135-RSD-CZ05-2003-19IEER | CZ05 | RSD | 2003 | 65to135 | 12 | 19 | 13.2701 | 5179.2356 | 0.94662 | 5388.1969 | 1.0223 | 208.9613 | 0.075643
522 | MCLU-65to135-RSD-CZ05-2007-19IEER | CZ05 | RSD | 2007 | 65to135 | 12 | 19 | 13.1028 | 5246.1146 | 0.95864 | 5456.3108 | 1.0347 | 210.1962 | 0.07608
523 | MCLU-65to135-RSD-CZ05-2011-19IEER | CZ05 | RSD | 2011 | 65to135 | 12 | 19 | 13.1028 | 5193.4422 | 0.92739 | 5456.3108 | 1.0347 | 262.8686 | 0.10733
524 | MCLU-65to135-RSD-CZ05-2015-19IEER | CZ05 | RSD | 2015 | 65to135 | 12 | 19 | 11.96 | 5370.6157 | 0.95246 | 5613.2882 | 1.0562 | 242.6725 | 0.1037
525 | MCLU-65to135-RSD-CZ05-2020-19IEER | CZ05 | RSD | 2020 | 65to135 | 12 | 19 | 10.7033 | 5038.6547 | 0.91489 | 5229.8525 | 0.9863 | 191.1978 | 0.071411
526 | MCLU-65to135-Rt3-CZ05-2003-19IEER | CZ05 | Rt3 | 2003 | 65to135 | 12 | 19 | 215.625 | 6038.3016 | 1.0735 | 6154.043 | 1.1293 | 115.7415 | 0.055875
527 | MCLU-65to135-Rt3-CZ05-2007-19IEER | CZ05 | Rt3 | 2007 | 65to135 | 12 | 19 | 215.5723 | 6040.4324 | 1.0736 | 6155.988 | 1.1294 | 115.5556 | 0.055859
528 | MCLU-65to135-Rt3-CZ05-2011-19IEER | CZ05 | Rt3 | 2011 | 65to135 | 12 | 19 | 215.5723 | 5964.4799 | 1.037 | 6155.988 | 1.1294 | 191.5081 | 0.092442
529 | MCLU-65to135-Rt3-CZ05-2015-19IEER | CZ05 | Rt3 | 2015 | 65to135 | 12 | 19 | 202.6599 | 5692.3243 | 0.99605 | 5886.6164 | 1.0879 | 194.2921 | 0.091826
530 | MCLU-65to135-Rt3-CZ05-2020-19IEER | CZ05 | Rt3 | 2020 | 65to135 | 12 | 19 | 192.8107 | 5334.8184 | 0.96658 | 5469.2139 | 1.0226 | 134.3955 | 0.056043
531 | MCLU-65to135-RtL-CZ05-2003-19IEER | CZ05 | RtL | 2003 | 65to135 | 12 | 19 | 183.5405 | 6764.1434 | 1.1723 | 6954.8271 | 1.2373 | 190.6837 | 0.065066
532 | MCLU-65to135-RtL-CZ05-2007-19IEER | CZ05 | RtL | 2007 | 65to135 | 12 | 19 | 182.3887 | 6812.1318 | 1.1805 | 7002.4751 | 1.2458 | 190.3433 | 0.065277
533 | MCLU-65to135-RtL-CZ05-2011-19IEER | CZ05 | RtL | 2011 | 65to135 | 12 | 19 | 182.3887 | 6727.2193 | 1.1461 | 7002.4751 | 1.2458 | 275.2558 | 0.099679
534 | MCLU-65to135-RtL-CZ05-2015-19IEER | CZ05 | RtL | 2015 | 65to135 | 12 | 19 | 172.9526 | 6585.2972 | 1.1391 | 6875.7279 | 1.2421 | 290.4308 | 0.10307
535 | MCLU-65to135-RtL-CZ05-2020-19IEER | CZ05 | RtL | 2020 | 65to135 | 12 | 19 | 161.0049 | 6461.5451 | 1.171 | 6687.2583 | 1.2423 | 225.7133 | 0.071295
536 | MCLU-65to135-RtS-CZ05-2003-19IEER | CZ05 | RtS | 2003 | 65to135 | 12 | 19 | 13.9897 | 3838.8734 | 0.67111 | 3983.5132 | 0.7242 | 144.6397 | 0.053087
537 | MCLU-65to135-RtS-CZ05-2007-19IEER | CZ05 | RtS | 2007 | 65to135 | 12 | 19 | 13.981 | 3841.0031 | 0.67139 | 3985.3559 | 0.72435 | 144.3529 | 0.052964
538 | MCLU-65to135-RtS-CZ05-2011-19IEER | CZ05 | RtS | 2011 | 65to135 | 12 | 19 | 13.981 | 3792.9572 | 0.6449 | 3985.3559 | 0.72435 | 192.3987 | 0.079451
539 | MCLU-65to135-RtS-CZ05-2015-19IEER | CZ05 | RtS | 2015 | 65to135 | 12 | 19 | 12.9214 | 3741.8198 | 0.63577 | 3935.225 | 0.71367 | 193.4053 | 0.077901
540 | MCLU-65to135-RtS-CZ05-2020-19IEER | CZ05 | RtS | 2020 | 65to135 | 12 | 19 | 12.5377 | 3513.6584 | 0.62093 | 3667.8866 | 0.67315 | 154.2282 | 0.052218
541 | MCLU-65to135-SCn-CZ05-2003-19IEER | CZ05 | SCn | 2003 | 65to135 | 12 | 19 | 318.6954 | 2230.144 | 0.18607 | 2398.7296 | 0.20935 | 168.5856 | 0.023287
542 | MCLU-65to135-SCn-CZ05-2007-19IEER | CZ05 | SCn | 2007 | 65to135 | 12 | 19 | 317.0804 | 2236.6737 | 0.18635 | 2404.2311 | 0.20916 | 167.5574 | 0.022811
543 | MCLU-65to135-SCn-CZ05-2011-19IEER | CZ05 | SCn | 2011 | 65to135 | 12 | 19 | 317.0804 | 2231.3837 | 0.18443 | 2404.2311 | 0.20916 | 172.8475 | 0.024732
544 | MCLU-65to135-SCn-CZ05-2015-19IEER | CZ05 | SCn | 2015 | 65to135 | 12 | 19 | 316.6379 | 2234.2083 | 0.18407 | 2407.4186 | 0.20833 | 173.2103 | 0.024258
545 | MCLU-65to135-SCn-CZ05-2020-19IEER | CZ05 | SCn | 2020 | 65to135 | 12 | 19 | 313.1035 | 1952.0167 | 0.15438 | 2077.4494 | 0.16257 | 125.4327 | 0.0081902
546 | MCLU-65to135-WRf-CZ05-2003-19IEER | CZ05 | WRf | 2003 | 65to135 | 12 | 19 | 11.2517 | 330764.0437 | 40.1991 | 331055.7324 | 40.2667 | 291.6887 | 0.067516
547 | MCLU-65to135-WRf-CZ05-2007-19IEER | CZ05 | WRf | 2007 | 65to135 | 12 | 19 | 11.0687 | 325708.4971 | 39.0884 | 326004.2814 | 39.1579 | 295.7843 | 0.06948
548 | MCLU-65to135-WRf-CZ05-2011-19IEER | CZ05 | WRf | 2011 | 65to135 | 12 | 19 | 10.5368 | 335268.5026 | 40.0645 | 335588.5594 | 40.1348 | 320.0568 | 0.070288
549 | MCLU-65to135-WRf-CZ05-2015-19IEER | CZ05 | WRf | 2015 | 65to135 | 12 | 19 | 9.8995 | 356830.4655 | 42.6327 | 357153.7865 | 42.7037 | 323.321 | 0.071053
550 | MCLU-65to135-WRf-CZ05-2020-19IEER | CZ05 | WRf | 2020 | 65to135 | 12 | 19 | 9.1013 | 364187.5579 | 43.5719 | 364506.7648 | 43.6418 | 319.2069 | 0.069838
551 | MCLU-65to135-Asm-CZ06-2003-19IEER | CZ06 | Asm | 2003 | 65to135 | 12 | 19 | 383.6746 | 1891.5509 | 0.56643 | 2137.5847 | 0.67599 | 246.0338 | 0.10956
552 | MCLU-65to135-Asm-CZ06-2007-19IEER | CZ06 | Asm | 2007 | 65to135 | 12 | 19 | 383.6746 | 1891.5509 | 0.56643 | 2137.5847 | 0.67599 | 246.0338 | 0.10956
553 | MCLU-65to135-Asm-CZ06-2011-19IEER | CZ06 | Asm | 2011 | 65to135 | 12 | 19 | 383.6746 | 1813.5645 | 0.51846 | 2137.5847 | 0.67599 | 324.0202 | 0.15753
554 | MCLU-65to135-Asm-CZ06-2015-19IEER | CZ06 | Asm | 2015 | 65to135 | 12 | 19 | 334.4524 | 1974.6937 | 0.57105 | 2294.9354 | 0.73055 | 320.2417 | 0.1595
555 | MCLU-65to135-Asm-CZ06-2020-19IEER | CZ06 | Asm | 2020 | 65to135 | 12 | 19 | 317.3357 | 1960.9674 | 0.61341 | 2206.0972 | 0.7242 | 245.1298 | 0.11079
556 | MCLU-65to135-ECC-CZ06-2003-19IEER | CZ06 | ECC | 2003 | 65to135 | 12 | 19 | 907.8948 | 2265.3052 | 0.65507 | 2424.1333 | 0.76823 | 158.8281 | 0.11317
557 | MCLU-65to135-ECC-CZ06-2007-19IEER | CZ06 | ECC | 2007 | 65to135 | 12 | 19 | 907.8948 | 2265.3052 | 0.65507 | 2424.1333 | 0.76823 | 158.8281 | 0.11317
558 | MCLU-65to135-ECC-CZ06-2011-19IEER | CZ06 | ECC | 2011 | 65to135 | 12 | 19 | 907.7816 | 2193.8402 | 0.60651 | 2422.6883 | 0.76791 | 228.8481 | 0.1614
559 | MCLU-65to135-ECC-CZ06-2015-19IEER | CZ06 | ECC | 2015 | 65to135 | 12 | 19 | 805.3526 | 2435.6523 | 0.66791 | 2669.4077 | 0.83246 | 233.7555 | 0.16456
560 | MCLU-65to135-ECC-CZ06-2020-19IEER | CZ06 | ECC | 2020 | 65to135 | 12 | 19 | 761.638 | 2228.5248 | 0.67907 | 2392.6581 | 0.7939 | 164.1333 | 0.11483
561 | MCLU-65to135-EPr-CZ06-2003-19IEER | CZ06 | EPr | 2003 | 65to135 | 12 | 19 | 143.1527 | 1563.0406 | 0.35136 | 1661.4466 | 0.41281 | 98.406 | 0.061447
562 | MCLU-65to135-EPr-CZ06-2007-19IEER | CZ06 | EPr | 2007 | 65to135 | 12 | 19 | 143.1527 | 1563.0406 | 0.35136 | 1661.4466 | 0.41281 | 98.406 | 0.061447
563 | MCLU-65to135-EPr-CZ06-2011-19IEER | CZ06 | EPr | 2011 | 65to135 | 12 | 19 | 143.1527 | 1522.1476 | 0.3264 | 1661.4466 | 0.41281 | 139.299 | 0.086404
564 | MCLU-65to135-EPr-CZ06-2015-19IEER | CZ06 | EPr | 2015 | 65to135 | 12 | 19 | 126.2407 | 1680.7318 | 0.35545 | 1826.0246 | 0.44201 | 145.2928 | 0.08656
565 | MCLU-65to135-EPr-CZ06-2020-19IEER | CZ06 | EPr | 2020 | 65to135 | 12 | 19 | 119.6304 | 1534.8128 | 0.34931 | 1639.3484 | 0.40969 | 104.5356 | 0.060373
566 | MCLU-65to135-ERC-CZ06-2003-19IEER | CZ06 | ERC | 2003 | 65to135 | 12 | 19 | 6.1951 | 1348.3556 | 0.22758 | 1430.5267 | 0.24508 | 82.1711 | 0.017496
567 | MCLU-65to135-ERC-CZ06-2007-19IEER | CZ06 | ERC | 2007 | 65to135 | 12 | 19 | 6.1955 | 1348.2366 | 0.22755 | 1430.4291 | 0.24503 | 82.1925 | 0.017487
568 | MCLU-65to135-ERC-CZ06-2011-19IEER | CZ06 | ERC | 2011 | 65to135 | 12 | 19 | 6.1955 | 1304.0298 | 0.21419 | 1430.4291 | 0.24503 | 126.3994 | 0.030847
569 | MCLU-65to135-ERC-CZ06-2015-19IEER | CZ06 | ERC | 2015 | 65to135 | 12 | 19 | 5.8188 | 1351.255 | 0.21187 | 1477.3177 | 0.23808 | 126.0627 | 0.026204
570 | MCLU-65to135-ERC-CZ06-2020-19IEER | CZ06 | ERC | 2020 | 65to135 | 12 | 19 | 5.5974 | 1224.6413 | 0.19437 | 1312.3109 | 0.20905 | 87.6696 | 0.014677
571 | MCLU-65to135-ESe-CZ06-2003-19IEER | CZ06 | ESe | 2003 | 65to135 | 12 | 19 | 471.4362 | 1603.2171 | 0.30702 | 1714.6727 | 0.36781 | 111.4556 | 0.060794
572 | MCLU-65to135-ESe-CZ06-2007-19IEER | CZ06 | ESe | 2007 | 65to135 | 12 | 19 | 471.4362 | 1603.2171 | 0.30702 | 1714.6727 | 0.36781 | 111.4556 | 0.060794
573 | MCLU-65to135-ESe-CZ06-2011-19IEER | CZ06 | ESe | 2011 | 65to135 | 12 | 19 | 471.3986 | 1553.3785 | 0.28116 | 1713.9126 | 0.36778 | 160.5342 | 0.08662
574 | MCLU-65to135-ESe-CZ06-2015-19IEER | CZ06 | ESe | 2015 | 65to135 | 12 | 19 | 403.3343 | 1740.5673 | 0.30171 | 1894.8378 | 0.38953 | 154.2705 | 0.087826
575 | MCLU-65to135-ESe-CZ06-2020-19IEER | CZ06 | ESe | 2020 | 65to135 | 12 | 19 | 380.5388 | 1578.8078 | 0.31768 | 1690.664 | 0.37888 | 111.8563 | 0.061191
576 | MCLU-65to135-EUn-CZ06-2003-19IEER | CZ06 | EUn | 2003 | 65to135 | 12 | 19 | 2688.4302 | 2412.2495 | 0.78245 | 2584.2126 | 0.88386 | 171.9631 | 0.10141
577 | MCLU-65to135-EUn-CZ06-2007-19IEER | CZ06 | EUn | 2007 | 65to135 | 12 | 19 | 2688.4302 | 2400.2161 | 0.77538 | 2572.1533 | 0.87676 | 171.9372 | 0.10138
578 | MCLU-65to135-EUn-CZ06-2011-19IEER | CZ06 | EUn | 2011 | 65to135 | 12 | 19 | 2673.2338 | 2341.5796 | 0.73306 | 2581.5417 | 0.87922 | 239.9621 | 0.14616
579 | MCLU-65to135-EUn-CZ06-2015-19IEER | CZ06 | EUn | 2015 | 65to135 | 12 | 19 | 2339.1537 | 2608.9523 | 0.81015 | 2850.9651 | 0.95815 | 242.0128 | 0.148
580 | MCLU-65to135-EUn-CZ06-2020-19IEER | CZ06 | EUn | 2020 | 65to135 | 12 | 19 | 2219.6547 | 2458.2083 | 0.81322 | 2627.5481 | 0.91493 | 169.3398 | 0.10172
581 | MCLU-65to135-Gro-CZ06-2003-19IEER | CZ06 | Gro | 2003 | 65to135 | 12 | 19 | 114.4763 | 14478.3085 | 2.0649 | 14924.9912 | 2.1974 | 446.6827 | 0.1325
582 | MCLU-65to135-Gro-CZ06-2007-19IEER | CZ06 | Gro | 2007 | 65to135 | 12 | 19 | 114.4763 | 13232.4147 | 1.932 | 13659.5081 | 2.0908 | 427.0934 | 0.15879
583 | MCLU-65to135-Gro-CZ06-2011-19IEER | CZ06 | Gro | 2011 | 65to135 | 12 | 19 | 114.4763 | 13232.4147 | 1.932 | 13659.5081 | 2.0908 | 427.0934 | 0.15879
584 | MCLU-65to135-Gro-CZ06-2015-19IEER | CZ06 | Gro | 2015 | 65to135 | 12 | 19 | 108.753 | 13352.8358 | 1.9468 | 13765.3144 | 2.0971 | 412.4786 | 0.15031
585 | MCLU-65to135-Gro-CZ06-2020-19IEER | CZ06 | Gro | 2020 | 65to135 | 12 | 19 | 102.6694 | 13717.7704 | 1.9955 | 14113.4089 | 2.1391 | 395.6385 | 0.1436
586 | MCLU-65to135-Hsp-CZ06-2003-19IEER | CZ06 | Hsp | 2003 | 65to135 | 12 | 19 | 683.8064 | 4213.2645 | 0.73496 | 4548.7806 | 0.84588 | 335.5161 | 0.11093
587 | MCLU-65to135-Hsp-CZ06-2007-19IEER | CZ06 | Hsp | 2007 | 65to135 | 12 | 19 | 683.8064 | 4213.2645 | 0.73496 | 4548.7806 | 0.84588 | 335.5161 | 0.11093
588 | MCLU-65to135-Hsp-CZ06-2011-19IEER | CZ06 | Hsp | 2011 | 65to135 | 12 | 19 | 683.8064 | 4131.7671 | 0.69476 | 4548.7806 | 0.84588 | 417.0136 | 0.15113
589 | MCLU-65to135-Hsp-CZ06-2015-19IEER | CZ06 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 4099.5409 | 0.6799 | 4511.6658 | 0.82996 | 412.1249 | 0.15006
590 | MCLU-65to135-Hsp-CZ06-2020-19IEER | CZ06 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3649.1925 | 0.64463 | 3989.5246 | 0.75226 | 340.3321 | 0.10763
591 | MCLU-65to135-Htl-CZ06-2003-19IEER | CZ06 | Htl | 2003 | 65to135 | 12 | 19 | 280.9994 | 2915.4595 | 0.69618 | 2989.4999 | 0.72476 | 74.0404 | 0.028577
592 | MCLU-65to135-Htl-CZ06-2007-19IEER | CZ06 | Htl | 2007 | 65to135 | 12 | 19 | 280.9994 | 2810.2158 | 0.65505 | 2884.2885 | 0.68352 | 74.0727 | 0.028463
593 | MCLU-65to135-Htl-CZ06-2011-19IEER | CZ06 | Htl | 2011 | 65to135 | 12 | 19 | 273.6002 | 2839.9121 | 0.65036 | 2934.5042 | 0.69096 | 94.5921 | 0.040602
594 | MCLU-65to135-Htl-CZ06-2015-19IEER | CZ06 | Htl | 2015 | 65to135 | 12 | 19 | 236.6292 | 3000.1495 | 0.66153 | 3093.7658 | 0.70284 | 93.6163 | 0.041311
595 | MCLU-65to135-Htl-CZ06-2020-19IEER | CZ06 | Htl | 2020 | 65to135 | 12 | 19 | 235.2028 | 2914.6276 | 0.65894 | 2986.0649 | 0.68753 | 71.4373 | 0.028597
596 | MCLU-65to135-MBT-CZ06-2003-19IEER | CZ06 | MBT | 2003 | 65to135 | 12 | 19 | 376.7791 | 3940.0511 | 0.54969 | 4103.4764 | 0.63193 | 163.4253 | 0.082235
597 | MCLU-65to135-MBT-CZ06-2007-19IEER | CZ06 | MBT | 2007 | 65to135 | 12 | 19 | 376.7791 | 3940.0511 | 0.54969 | 4103.4764 | 0.63193 | 163.4253 | 0.082235
598 | MCLU-65to135-MBT-CZ06-2011-19IEER | CZ06 | MBT | 2011 | 65to135 | 12 | 19 | 370.4147 | 3878.3689 | 0.51953 | 4116.876 | 0.63206 | 238.5071 | 0.11253
599 | MCLU-65to135-MBT-CZ06-2015-19IEER | CZ06 | MBT | 2015 | 65to135 | 12 | 19 | 342.9845 | 4124.6789 | 0.54515 | 4362.0385 | 0.65805 | 237.3595 | 0.1129
600 | MCLU-65to135-MBT-CZ06-2020-19IEER | CZ06 | MBT | 2020 | 65to135 | 12 | 19 | 311.3014 | 4146.8427 | 0.56695 | 4304.7298 | 0.64879 | 157.8871 | 0.08184
601 | MCLU-65to135-MLI-CZ06-2003-19IEER | CZ06 | MLI | 2003 | 65to135 | 12 | 19 | 227.113 | 2901.7531 | 0.40465 | 3069.6238 | 0.46349 | 167.8707 | 0.058842
602 | MCLU-65to135-MLI-CZ06-2007-19IEER | CZ06 | MLI | 2007 | 65to135 | 12 | 19 | 227.113 | 2901.7531 | 0.40465 | 3069.6238 | 0.46349 | 167.8707 | 0.058842
603 | MCLU-65to135-MLI-CZ06-2011-19IEER | CZ06 | MLI | 2011 | 65to135 | 12 | 19 | 227.113 | 2860.2822 | 0.38164 | 3069.6238 | 0.46349 | 209.3416 | 0.081846
604 | MCLU-65to135-MLI-CZ06-2015-19IEER | CZ06 | MLI | 2015 | 65to135 | 12 | 19 | 223.8975 | 2878.627 | 0.38349 | 3087.7026 | 0.46533 | 209.0756 | 0.081837
605 | MCLU-65to135-MLI-CZ06-2020-19IEER | CZ06 | MLI | 2020 | 65to135 | 12 | 19 | 203.4913 | 2679.6457 | 0.3817 | 2845.1905 | 0.44028 | 165.5448 | 0.058582
606 | MCLU-65to135-Mtl-CZ06-2003-19IEER | CZ06 | Mtl | 2003 | 65to135 | 12 | 19 | 52.9 | 2691.0716 | 0.59406 | 2755.8125 | 0.61549 | 64.7409 | 0.021431
607 | MCLU-65to135-Mtl-CZ06-2007-19IEER | CZ06 | Mtl | 2007 | 65to135 | 12 | 19 | 52.9 | 2584.9003 | 0.55457 | 2649.9112 | 0.57594 | 65.0109 | 0.021376
608 | MCLU-65to135-Mtl-CZ06-2011-19IEER | CZ06 | Mtl | 2011 | 65to135 | 12 | 19 | 51.3846 | 2628.4308 | 0.55203 | 2710.348 | 0.58156 | 81.9173 | 0.029535
609 | MCLU-65to135-Mtl-CZ06-2015-19IEER | CZ06 | Mtl | 2015 | 65to135 | 12 | 19 | 44.1089 | 2770.5282 | 0.55626 | 2857.9838 | 0.58831 | 87.4556 | 0.032056
610 | MCLU-65to135-Mtl-CZ06-2020-19IEER | CZ06 | Mtl | 2020 | 65to135 | 12 | 19 | 43.6382 | 2729.0062 | 0.55425 | 2796.7597 | 0.57736 | 67.7535 | 0.023113
611 | MCLU-65to135-Nrs-CZ06-2003-19IEER | CZ06 | Nrs | 2003 | 65to135 | 12 | 19 | 188.1573 | 4473.4992 | 0.83709 | 4633.7938 | 0.89005 | 160.2945 | 0.052958
612 | MCLU-65to135-Nrs-CZ06-2007-19IEER | CZ06 | Nrs | 2007 | 65to135 | 12 | 19 | 188.1573 | 4377.9677 | 0.80861 | 4538.3964 | 0.86153 | 160.4286 | 0.052919
613 | MCLU-65to135-Nrs-CZ06-2011-19IEER | CZ06 | Nrs | 2011 | 65to135 | 12 | 19 | 188.1573 | 4338.5447 | 0.78767 | 4538.3964 | 0.86153 | 199.8517 | 0.073851
614 | MCLU-65to135-Nrs-CZ06-2015-19IEER | CZ06 | Nrs | 2015 | 65to135 | 12 | 19 | 181.6964 | 4253.5687 | 0.73901 | 4441.0363 | 0.80957 | 187.4675 | 0.070563
615 | MCLU-65to135-Nrs-CZ06-2020-19IEER | CZ06 | Nrs | 2020 | 65to135 | 12 | 19 | 181.607 | 3910.2055 | 0.69892 | 4063.5911 | 0.74759 | 153.3856 | 0.048672
616 | MCLU-65to135-OfL-CZ06-2003-19IEER | CZ06 | OfL | 2003 | 65to135 | 12 | 19 | 549.4111 | 2896.8884 | 0.43385 | 3059.7038 | 0.47653 | 162.8154 | 0.042682
617 | MCLU-65to135-OfL-CZ06-2007-19IEER | CZ06 | OfL | 2007 | 65to135 | 12 | 19 | 549.4111 | 2896.8884 | 0.43385 | 3059.7038 | 0.47653 | 162.8154 | 0.042682
618 | MCLU-65to135-OfL-CZ06-2011-19IEER | CZ06 | OfL | 2011 | 65to135 | 12 | 19 | 540.7324 | 2832.3681 | 0.41595 | 3068.6935 | 0.47626 | 236.3254 | 0.060315
619 | MCLU-65to135-OfL-CZ06-2015-19IEER | CZ06 | OfL | 2015 | 65to135 | 12 | 19 | 508.3919 | 2951.7874 | 0.43186 | 3184.6661 | 0.4921 | 232.8787 | 0.060237
620 | MCLU-65to135-OfL-CZ06-2020-19IEER | CZ06 | OfL | 2020 | 65to135 | 12 | 19 | 488.9941 | 2912.6133 | 0.43603 | 3072.1587 | 0.47806 | 159.5455 | 0.042032
621 | MCLU-65to135-OfS-CZ06-2003-19IEER | CZ06 | OfS | 2003 | 65to135 | 12 | 19 | 36.2167 | 2198.7862 | 0.33031 | 2367.2471 | 0.37286 | 168.461 | 0.042549
622 | MCLU-65to135-OfS-CZ06-2007-19IEER | CZ06 | OfS | 2007 | 65to135 | 12 | 19 | 36.2167 | 2198.7862 | 0.33031 | 2367.2471 | 0.37286 | 168.461 | 0.042549
623 | MCLU-65to135-OfS-CZ06-2011-19IEER | CZ06 | OfS | 2011 | 65to135 | 12 | 19 | 36.1116 | 2117.8237 | 0.31077 | 2349.7098 | 0.37065 | 231.886 | 0.059884
624 | MCLU-65to135-OfS-CZ06-2015-19IEER | CZ06 | OfS | 2015 | 65to135 | 12 | 19 | 29.4044 | 2519.9028 | 0.35904 | 2753.0114 | 0.41886 | 233.1086 | 0.05982
625 | MCLU-65to135-OfS-CZ06-2020-19IEER | CZ06 | OfS | 2020 | 65to135 | 12 | 19 | 28.605 | 2438.9092 | 0.35679 | 2605.3357 | 0.39872 | 166.4265 | 0.04193
626 | MCLU-65to135-RFF-CZ06-2003-19IEER | CZ06 | RFF | 2003 | 65to135 | 12 | 19 | 8.5556 | 4760.3025 | 1.0035 | 5018.8511 | 1.1056 | 258.5487 | 0.10206
627 | MCLU-65to135-RFF-CZ06-2007-19IEER | CZ06 | RFF | 2007 | 65to135 | 12 | 19 | 8.5556 | 4760.3025 | 1.0035 | 5018.8511 | 1.1056 | 258.5487 | 0.10206
628 | MCLU-65to135-RFF-CZ06-2011-19IEER | CZ06 | RFF | 2011 | 65to135 | 12 | 19 | 8.5556 | 4654.5334 | 0.94827 | 5018.8511 | 1.1056 | 364.3177 | 0.15734
629 | MCLU-65to135-RFF-CZ06-2015-19IEER | CZ06 | RFF | 2015 | 65to135 | 12 | 19 | 8.1078 | 4654.0175 | 0.95445 | 5021.9773 | 1.1134 | 367.9598 | 0.15897
630 | MCLU-65to135-RFF-CZ06-2020-19IEER | CZ06 | RFF | 2020 | 65to135 | 12 | 19 | 7.4827 | 4481.1255 | 0.977 | 4768.8351 | 1.0841 | 287.7096 | 0.10709
631 | MCLU-65to135-RSD-CZ06-2003-19IEER | CZ06 | RSD | 2003 | 65to135 | 12 | 19 | 14.8336 | 4993.5012 | 1.0712 | 5270.3075 | 1.1839 | 276.8063 | 0.11267
632 | MCLU-65to135-RSD-CZ06-2007-19IEER | CZ06 | RSD | 2007 | 65to135 | 12 | 19 | 14.8336 | 4993.5012 | 1.0712 | 5270.3075 | 1.1839 | 276.8063 | 0.11267
633 | MCLU-65to135-RSD-CZ06-2011-19IEER | CZ06 | RSD | 2011 | 65to135 | 12 | 19 | 14.8336 | 4884.0515 | 1.0183 | 5270.3075 | 1.1839 | 386.256 | 0.1656
634 | MCLU-65to135-RSD-CZ06-2015-19IEER | CZ06 | RSD | 2015 | 65to135 | 12 | 19 | 13.5902 | 5008.8127 | 1.0515 | 5405.5852 | 1.216 | 396.7725 | 0.1645
635 | MCLU-65to135-RSD-CZ06-2020-19IEER | CZ06 | RSD | 2020 | 65to135 | 12 | 19 | 12.1356 | 4787.1365 | 1.0706 | 5074.8675 | 1.1841 | 287.731 | 0.11348
636 | MCLU-65to135-Rt3-CZ06-2003-19IEER | CZ06 | Rt3 | 2003 | 65to135 | 12 | 19 | 232.7173 | 5991.4182 | 1.2338 | 6199.5558 | 1.3548 | 208.1376 | 0.121
637 | MCLU-65to135-Rt3-CZ06-2007-19IEER | CZ06 | Rt3 | 2007 | 65to135 | 12 | 19 | 232.7173 | 5991.4182 | 1.2338 | 6199.5558 | 1.3548 | 208.1376 | 0.121
638 | MCLU-65to135-Rt3-CZ06-2011-19IEER | CZ06 | Rt3 | 2011 | 65to135 | 12 | 19 | 232.7173 | 5860.6786 | 1.1832 | 6199.5558 | 1.3548 | 338.8772 | 0.17157
639 | MCLU-65to135-Rt3-CZ06-2015-19IEER | CZ06 | Rt3 | 2015 | 65to135 | 12 | 19 | 219.9102 | 5584.5895 | 1.1488 | 5919.3583 | 1.3209 | 334.7688 | 0.17212
640 | MCLU-65to135-Rt3-CZ06-2020-19IEER | CZ06 | Rt3 | 2020 | 65to135 | 12 | 19 | 210.0915 | 5291.4057 | 1.1365 | 5502.696 | 1.2585 | 211.2903 | 0.12197
641 | MCLU-65to135-RtL-CZ06-2003-19IEER | CZ06 | RtL | 2003 | 65to135 | 12 | 19 | 195.1278 | 6798.0739 | 1.3721 | 7079.152 | 1.4903 | 281.0781 | 0.11821
642 | MCLU-65to135-RtL-CZ06-2007-19IEER | CZ06 | RtL | 2007 | 65to135 | 12 | 19 | 195.1278 | 6798.0739 | 1.3721 | 7079.152 | 1.4903 | 281.0781 | 0.11821
643 | MCLU-65to135-RtL-CZ06-2011-19IEER | CZ06 | RtL | 2011 | 65to135 | 12 | 19 | 195.1278 | 6663.733 | 1.3297 | 7079.152 | 1.4903 | 415.4189 | 0.16057
644 | MCLU-65to135-RtL-CZ06-2015-19IEER | CZ06 | RtL | 2015 | 65to135 | 12 | 19 | 186.0682 | 6501.505 | 1.33 | 6925.0701 | 1.4881 | 423.5652 | 0.15817
645 | MCLU-65to135-RtL-CZ06-2020-19IEER | CZ06 | RtL | 2020 | 65to135 | 12 | 19 | 172.0912 | 6486.3059 | 1.3824 | 6788.6461 | 1.4994 | 302.3402 | 0.11703
646 | MCLU-65to135-RtS-CZ06-2003-19IEER | CZ06 | RtS | 2003 | 65to135 | 12 | 19 | 15.5385 | 3789.4865 | 0.80848 | 4006.5434 | 0.9164 | 217.0569 | 0.10792
647 | MCLU-65to135-RtS-CZ06-2007-19IEER | CZ06 | RtS | 2007 | 65to135 | 12 | 19 | 15.5385 | 3789.4865 | 0.80848 | 4006.5434 | 0.9164 | 217.0569 | 0.10792
648 | MCLU-65to135-RtS-CZ06-2011-19IEER | CZ06 | RtS | 2011 | 65to135 | 12 | 19 | 15.5385 | 3691.1117 | 0.76532 | 4006.5434 | 0.9164 | 315.4317 | 0.15108
649 | MCLU-65to135-RtS-CZ06-2015-19IEER | CZ06 | RtS | 2015 | 65to135 | 12 | 19 | 14.3514 | 3644.4048 | 0.76687 | 3958.2249 | 0.91824 | 313.8201 | 0.15137
650 | MCLU-65to135-RtS-CZ06-2020-19IEER | CZ06 | RtS | 2020 | 65to135 | 12 | 19 | 13.7287 | 3530.4418 | 0.77567 | 3749.8729 | 0.8844 | 219.4311 | 0.10872
651 | MCLU-65to135-SCn-CZ06-2003-19IEER | CZ06 | SCn | 2003 | 65to135 | 12 | 19 | 321.0033 | 2307.6188 | 0.29736 | 2496.1039 | 0.35539 | 188.4851 | 0.058032
652 | MCLU-65to135-SCn-CZ06-2007-19IEER | CZ06 | SCn | 2007 | 65to135 | 12 | 19 | 321.0033 | 2307.6188 | 0.29736 | 2496.1039 | 0.35539 | 188.4851 | 0.058032
653 | MCLU-65to135-SCn-CZ06-2011-19IEER | CZ06 | SCn | 2011 | 65to135 | 12 | 19 | 321.0033 | 2283.9676 | 0.27487 | 2496.1039 | 0.35539 | 212.1362 | 0.080521
654 | MCLU-65to135-SCn-CZ06-2015-19IEER | CZ06 | SCn | 2015 | 65to135 | 12 | 19 | 319.5854 | 2290.4391 | 0.27457 | 2505.1147 | 0.35486 | 214.6756 | 0.080296
655 | MCLU-65to135-SCn-CZ06-2020-19IEER | CZ06 | SCn | 2020 | 65to135 | 12 | 19 | 313.7329 | 2034.036 | 0.26101 | 2214.8995 | 0.31486 | 180.8635 | 0.053857
656 | MCLU-65to135-WRf-CZ06-2003-19IEER | CZ06 | WRf | 2003 | 65to135 | 12 | 19 | 14.7421 | 270999.5655 | 35.5244 | 271382.9623 | 35.6129 | 383.3968 | 0.088582
657 | MCLU-65to135-WRf-CZ06-2007-19IEER | CZ06 | WRf | 2007 | 65to135 | 12 | 19 | 14.7421 | 264050.1145 | 33.8207 | 264433.4049 | 33.9095 | 383.2904 | 0.088835
658 | MCLU-65to135-WRf-CZ06-2011-19IEER | CZ06 | WRf | 2011 | 65to135 | 12 | 19 | 14.4446 | 263700.7495 | 33.7865 | 264092.2591 | 33.874 | 391.5096 | 0.087557
659 | MCLU-65to135-WRf-CZ06-2015-19IEER | CZ06 | WRf | 2015 | 65to135 | 12 | 19 | 13.7511 | 276974.1203 | 35.479 | 277365.6678 | 35.5647 | 391.5476 | 0.08567
660 | MCLU-65to135-WRf-CZ06-2020-19IEER | CZ06 | WRf | 2020 | 65to135 | 12 | 19 | 12.4082 | 278464.6471 | 34.4812 | 278863.5032 | 34.561 | 398.8561 | 0.079782
661 | MCLU-65to135-Asm-CZ07-2003-19IEER | CZ07 | Asm | 2003 | 65to135 | 12 | 19 | 373.013 | 1878.4067 | 0.49625 | 2097.1413 | 0.59197 | 218.7346 | 0.095722
662 | MCLU-65to135-Asm-CZ07-2007-19IEER | CZ07 | Asm | 2007 | 65to135 | 12 | 19 | 373.013 | 1878.4067 | 0.49625 | 2097.1413 | 0.59197 | 218.7346 | 0.095722
663 | MCLU-65to135-Asm-CZ07-2011-19IEER | CZ07 | Asm | 2011 | 65to135 | 12 | 19 | 368.7658 | 1822.3592 | 0.45996 | 2113.3459 | 0.59784 | 290.9867 | 0.13788
664 | MCLU-65to135-Asm-CZ07-2015-19IEER | CZ07 | Asm | 2015 | 65to135 | 12 | 19 | 321.4765 | 1984.6395 | 0.50304 | 2265.1434 | 0.64233 | 280.5039 | 0.13929
665 | MCLU-65to135-Asm-CZ07-2020-19IEER | CZ07 | Asm | 2020 | 65to135 | 12 | 19 | 307.9536 | 1937.6253 | 0.5283 | 2154.6405 | 0.62438 | 217.0152 | 0.096082
666 | MCLU-65to135-ECC-CZ07-2003-19IEER | CZ07 | ECC | 2003 | 65to135 | 12 | 19 | 897.9636 | 2257.0411 | 0.60549 | 2388.1106 | 0.70451 | 131.0695 | 0.099024
667 | MCLU-65to135-ECC-CZ07-2007-19IEER | CZ07 | ECC | 2007 | 65to135 | 12 | 19 | 897.9636 | 2257.0411 | 0.60549 | 2388.1106 | 0.70451 | 131.0695 | 0.099024
668 | MCLU-65to135-ECC-CZ07-2011-19IEER | CZ07 | ECC | 2011 | 65to135 | 12 | 19 | 897.2893 | 2192.352 | 0.5612 | 2387.4366 | 0.7033 | 195.0845 | 0.1421
669 | MCLU-65to135-ECC-CZ07-2015-19IEER | CZ07 | ECC | 2015 | 65to135 | 12 | 19 | 796.8913 | 2435.7201 | 0.62155 | 2636.676 | 0.76668 | 200.9559 | 0.14512
670 | MCLU-65to135-ECC-CZ07-2020-19IEER | CZ07 | ECC | 2020 | 65to135 | 12 | 19 | 753.1698 | 2216.9306 | 0.62582 | 2356.4754 | 0.72577 | 139.5449 | 0.099948
671 | MCLU-65to135-EPr-CZ07-2003-19IEER | CZ07 | EPr | 2003 | 65to135 | 12 | 19 | 140.8581 | 1540.0147 | 0.31497 | 1627.0096 | 0.36625 | 86.9949 | 0.051281
672 | MCLU-65to135-EPr-CZ07-2007-19IEER | CZ07 | EPr | 2007 | 65to135 | 12 | 19 | 140.8581 | 1540.0147 | 0.31497 | 1627.0096 | 0.36625 | 86.9949 | 0.051281
673 | MCLU-65to135-EPr-CZ07-2011-19IEER | CZ07 | EPr | 2011 | 65to135 | 12 | 19 | 140.4386 | 1507.5347 | 0.29381 | 1631.0018 | 0.36577 | 123.4671 | 0.071966
674 | MCLU-65to135-EPr-CZ07-2015-19IEER | CZ07 | EPr | 2015 | 65to135 | 12 | 19 | 123.9319 | 1664.8073 | 0.31899 | 1796.3274 | 0.39234 | 131.5201 | 0.073356
675 | MCLU-65to135-EPr-CZ07-2020-19IEER | CZ07 | EPr | 2020 | 65to135 | 12 | 19 | 117.5967 | 1506.5472 | 0.30718 | 1603.0435 | 0.358 | 96.4963 | 0.050829
676 | MCLU-65to135-ERC-CZ07-2003-19IEER | CZ07 | ERC | 2003 | 65to135 | 12 | 19 | 5.97 | 1358.3618 | 0.20536 | 1428.3998 | 0.21728 | 70.0381 | 0.011914
677 | MCLU-65to135-ERC-CZ07-2007-19IEER | CZ07 | ERC | 2007 | 65to135 | 12 | 19 | 5.9703 | 1358.2503 | 0.20533 | 1428.2525 | 0.21724 | 70.0022 | 0.011905
678 | MCLU-65to135-ERC-CZ07-2011-19IEER | CZ07 | ERC | 2011 | 65to135 | 12 | 19 | 5.9655 | 1319.1914 | 0.197 | 1429.1878 | 0.21707 | 109.9964 | 0.02008
679 | MCLU-65to135-ERC-CZ07-2015-19IEER | CZ07 | ERC | 2015 | 65to135 | 12 | 19 | 5.594 | 1369.8055 | 0.19922 | 1479.8606 | 0.21563 | 110.0552 | 0.016404
680 | MCLU-65to135-ERC-CZ07-2020-19IEER | CZ07 | ERC | 2020 | 65to135 | 12 | 19 | 5.3773 | 1232.6755 | 0.17627 | 1308.9635 | 0.18497 | 76.288 | 0.0086992
681 | MCLU-65to135-ESe-CZ07-2003-19IEER | CZ07 | ESe | 2003 | 65to135 | 12 | 19 | 464.9591 | 1601.8096 | 0.27871 | 1696.2193 | 0.33151 | 94.4097 | 0.052804
682 | MCLU-65to135-ESe-CZ07-2007-19IEER | CZ07 | ESe | 2007 | 65to135 | 12 | 19 | 464.9591 | 1601.8096 | 0.27871 | 1696.2193 | 0.33151 | 94.4097 | 0.052804
683 | MCLU-65to135-ESe-CZ07-2011-19IEER | CZ07 | ESe | 2011 | 65to135 | 12 | 19 | 463.7759 | 1558.8511 | 0.25634 | 1699.0589 | 0.33175 | 140.2078 | 0.075405
684 | MCLU-65to135-ESe-CZ07-2015-19IEER | CZ07 | ESe | 2015 | 65to135 | 12 | 19 | 395.7356 | 1754.2733 | 0.27818 | 1889.6632 | 0.35383 | 135.3899 | 0.07565
685 | MCLU-65to135-ESe-CZ07-2020-19IEER | CZ07 | ESe | 2020 | 65to135 | 12 | 19 | 373.8211 | 1583.2412 | 0.28835 | 1680.3444 | 0.34126 | 97.1032 | 0.052909
686 | MCLU-65to135-EUn-CZ07-2003-19IEER | CZ07 | EUn | 2003 | 65to135 | 12 | 19 | 2642.8569 | 2394.0941 | 0.72109 | 2538.5945 | 0.81337 | 144.5004 | 0.092284
687 | MCLU-65to135-EUn-CZ07-2007-19IEER | CZ07 | EUn | 2007 | 65to135 | 12 | 19 | 2642.8569 | 2383.1462 | 0.71539 | 2527.6363 | 0.80764 | 144.4901 | 0.092253
688 | MCLU-65to135-EUn-CZ07-2011-19IEER | CZ07 | EUn | 2011 | 65to135 | 12 | 19 | 2621.8811 | 2339.6375 | 0.67902 | 2545.1949 | 0.81177 | 205.5574 | 0.13275
689 | MCLU-65to135-EUn-CZ07-2015-19IEER | CZ07 | EUn | 2015 | 65to135 | 12 | 19 | 2298.3603 | 2609.1048 | 0.75431 | 2816.7329 | 0.88871 | 207.6281 | 0.1344
690 | MCLU-65to135-EUn-CZ07-2020-19IEER | CZ07 | EUn | 2020 | 65to135 | 12 | 19 | 2186.2657 | 2441.9481 | 0.74999 | 2584.5031 | 0.84107 | 142.5549 | 0.091086
691 | MCLU-65to135-Gro-CZ07-2003-19IEER | CZ07 | Gro | 2003 | 65to135 | 12 | 19 | 86.4369 | 19122.2461 | 2.6254 | 19667.5494 | 2.7742 | 545.3033 | 0.14872
692 | MCLU-65to135-Gro-CZ07-2007-19IEER | CZ07 | Gro | 2007 | 65to135 | 12 | 19 | 86.4369 | 17461.0687 | 2.4488 | 17964.1808 | 2.63 | 503.112 | 0.18125
693 | MCLU-65to135-Gro-CZ07-2011-19IEER | CZ07 | Gro | 2011 | 65to135 | 12 | 19 | 85.4652 | 17657.4867 | 2.4753 | 18160.114 | 2.6577 | 502.6274 | 0.18242
694 | MCLU-65to135-Gro-CZ07-2015-19IEER | CZ07 | Gro | 2015 | 65to135 | 12 | 19 | 91.7901 | 15765.9429 | 2.2099 | 16194.6849 | 2.3577 | 428.742 | 0.14789
695 | MCLU-65to135-Gro-CZ07-2020-19IEER | CZ07 | Gro | 2020 | 65to135 | 12 | 19 | 75.7329 | 18535.3142 | 2.6005 | 19015.6881 | 2.7587 | 480.3739 | 0.15818
696 | MCLU-65to135-Hsp-CZ07-2003-19IEER | CZ07 | Hsp | 2003 | 65to135 | 12 | 19 | 682.8266 | 4191.2939 | 0.69953 | 4495.9918 | 0.79425 | 304.6979 | 0.094721
697 | MCLU-65to135-Hsp-CZ07-2007-19IEER | CZ07 | Hsp | 2007 | 65to135 | 12 | 19 | 682.8266 | 4191.2939 | 0.69953 | 4495.9918 | 0.79425 | 304.6979 | 0.094721
698 | MCLU-65to135-Hsp-CZ07-2011-19IEER | CZ07 | Hsp | 2011 | 65to135 | 12 | 19 | 682.8248 | 4113.9452 | 0.6635 | 4495.4757 | 0.79371 | 381.5305 | 0.13021
699 | MCLU-65to135-Hsp-CZ07-2015-19IEER | CZ07 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 4074.0273 | 0.6514 | 4450.6851 | 0.78111 | 376.6578 | 0.12971
700 | MCLU-65to135-Hsp-CZ07-2020-19IEER | CZ07 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3615.7759 | 0.61337 | 3928.6141 | 0.70582 | 312.8383 | 0.092449
701 | MCLU-65to135-Htl-CZ07-2003-19IEER | CZ07 | Htl | 2003 | 65to135 | 12 | 19 | 275.0415 | 2848.7878 | 0.5997 | 2920.2546 | 0.62459 | 71.4669 | 0.024889
702 | MCLU-65to135-Htl-CZ07-2007-19IEER | CZ07 | Htl | 2007 | 65to135 | 12 | 19 | 275.0415 | 2746.7003 | 0.56729 | 2818.3551 | 0.59207 | 71.6548 | 0.02478
703 | MCLU-65to135-Htl-CZ07-2011-19IEER | CZ07 | Htl | 2011 | 65to135 | 12 | 19 | 268.045 | 2795.1708 | 0.5656 | 2884.2606 | 0.60061 | 89.0899 | 0.035016
704 | MCLU-65to135-Htl-CZ07-2015-19IEER | CZ07 | Htl | 2015 | 65to135 | 12 | 19 | 233.0831 | 2949.2165 | 0.57778 | 3040.3798 | 0.61427 | 91.1633 | 0.036485
705 | MCLU-65to135-Htl-CZ07-2020-19IEER | CZ07 | Htl | 2020 | 65to135 | 12 | 19 | 231.6939 | 2859.4836 | 0.57379 | 2931.8477 | 0.59916 | 72.364 | 0.025365
706 | MCLU-65to135-MBT-CZ07-2003-19IEER | CZ07 | MBT | 2003 | 65to135 | 12 | 19 | 369.9747 | 3947.0622 | 0.51554 | 4092.3635 | 0.58424 | 145.3013 | 0.068705
707 | MCLU-65to135-MBT-CZ07-2007-19IEER | CZ07 | MBT | 2007 | 65to135 | 12 | 19 | 369.9747 | 3947.0622 | 0.51554 | 4092.3635 | 0.58424 | 145.3013 | 0.068705
708 | MCLU-65to135-MBT-CZ07-2011-19IEER | CZ07 | MBT | 2011 | 65to135 | 12 | 19 | 360.5101 | 3927.7586 | 0.49304 | 4143.2345 | 0.58776 | 215.4759 | 0.09472
709 | MCLU-65to135-MBT-CZ07-2015-19IEER | CZ07 | MBT | 2015 | 65to135 | 12 | 19 | 333.9669 | 4175.7166 | 0.51816 | 4391.1428 | 0.61273 | 215.4262 | 0.094569
710 | MCLU-65to135-MBT-CZ07-2020-19IEER | CZ07 | MBT | 2020 | 65to135 | 12 | 19 | 306.9175 | 4136.1175 | 0.52975 | 4279.0667 | 0.59692 | 142.9491 | 0.067172
711 | MCLU-65to135-MLI-CZ07-2003-19IEER | CZ07 | MLI | 2003 | 65to135 | 12 | 19 | 214.5997 | 3014.7808 | 0.39117 | 3163.4176 | 0.43867 | 148.6368 | 0.047506
712 | MCLU-65to135-MLI-CZ07-2007-19IEER | CZ07 | MLI | 2007 | 65to135 | 12 | 19 | 214.5997 | 3014.7808 | 0.39117 | 3163.4176 | 0.43867 | 148.6368 | 0.047506
713 | MCLU-65to135-MLI-CZ07-2011-19IEER | CZ07 | MLI | 2011 | 65to135 | 12 | 19 | 211.1083 | 3027.3102 | 0.37732 | 3210.8933 | 0.44376 | 183.5832 | 0.066445
714 | MCLU-65to135-MLI-CZ07-2015-19IEER | CZ07 | MLI | 2015 | 65to135 | 12 | 19 | 208.0232 | 3048.3761 | 0.37933 | 3231.7616 | 0.44571 | 183.3855 | 0.066375
715 | MCLU-65to135-MLI-CZ07-2020-19IEER | CZ07 | MLI | 2020 | 65to135 | 12 | 19 | 192.1218 | 2784.4109 | 0.36665 | 2932.311 | 0.41305 | 147.9 | 0.046394
716 | MCLU-65to135-Mtl-CZ07-2003-19IEER | CZ07 | Mtl | 2003 | 65to135 | 12 | 19 | 52.0049 | 2668.9437 | 0.5116 | 2725.7515 | 0.52996 | 56.8078 | 0.018359
717 | MCLU-65to135-Mtl-CZ07-2007-19IEER | CZ07 | Mtl | 2007 | 65to135 | 12 | 19 | 52.0049 | 2564.5209 | 0.48088 | 2621.7612 | 0.4992 | 57.2403 | 0.018319
718 | MCLU-65to135-Mtl-CZ07-2011-19IEER | CZ07 | Mtl | 2011 | 65to135 | 12 | 19 | 50.7261 | 2617.0176 | 0.47957 | 2690.0593 | 0.50486 | 73.0417 | 0.025284
719 | MCLU-65to135-Mtl-CZ07-2015-19IEER | CZ07 | Mtl | 2015 | 65to135 | 12 | 19 | 43.5484 | 2766.8087 | 0.4901 | 2844.8588 | 0.51749 | 78.0501 | 0.02739
720 | MCLU-65to135-Mtl-CZ07-2020-19IEER | CZ07 | Mtl | 2020 | 65to135 | 12 | 19 | 43.4163 | 2710.5701 | 0.4883 | 2770.0994 | 0.50767 | 59.5293 | 0.019366
721 | MCLU-65to135-Nrs-CZ07-2003-19IEER | CZ07 | Nrs | 2003 | 65to135 | 12 | 19 | 187.2062 | 4489.7393 | 0.77627 | 4634.4412 | 0.82073 | 144.7019 | 0.044458
722 | MCLU-65to135-Nrs-CZ07-2007-19IEER | CZ07 | Nrs | 2007 | 65to135 | 12 | 19 | 187.2062 | 4391.533 | 0.75213 | 4536.2729 | 0.79655 | 144.7399 | 0.044416
723 | MCLU-65to135-Nrs-CZ07-2011-19IEER | CZ07 | Nrs | 2011 | 65to135 | 12 | 19 | 187.1919 | 4357.8522 | 0.73396 | 4537.1604 | 0.79582 | 179.3083 | 0.061865
724 | MCLU-65to135-Nrs-CZ07-2015-19IEER | CZ07 | Nrs | 2015 | 65to135 | 12 | 19 | 181.6779 | 4244.955 | 0.69345 | 4413.2183 | 0.75181 | 168.2633 | 0.058365
725 | MCLU-65to135-Nrs-CZ07-2020-19IEER | CZ07 | Nrs | 2020 | 65to135 | 12 | 19 | 181.607 | 3896.0577 | 0.652 | 4036.5473 | 0.69206 | 140.4896 | 0.040062
726 | MCLU-65to135-OfL-CZ07-2003-19IEER | CZ07 | OfL | 2003 | 65to135 | 12 | 19 | 537.8352 | 2918.6593 | 0.42593 | 3050.367 | 0.4645 | 131.7076 | 0.038566
727 | MCLU-65to135-OfL-CZ07-2007-19IEER | CZ07 | OfL | 2007 | 65to135 | 12 | 19 | 537.8352 | 2918.6593 | 0.42593 | 3050.367 | 0.4645 | 131.7076 | 0.038566
728 | MCLU-65to135-OfL-CZ07-2011-19IEER | CZ07 | OfL | 2011 | 65to135 | 12 | 19 | 529.359 | 2860.8388 | 0.41025 | 3059.1926 | 0.46456 | 198.3538 | 0.054311
729 | MCLU-65to135-OfL-CZ07-2015-19IEER | CZ07 | OfL | 2015 | 65to135 | 12 | 19 | 496.632 | 2989.5083 | 0.42809 | 3183.9965 | 0.48237 | 194.4882 | 0.054279
730 | MCLU-65to135-OfL-CZ07-2020-19IEER | CZ07 | OfL | 2020 | 65to135 | 12 | 19 | 478.1206 | 2938.5675 | 0.43105 | 3066.2345 | 0.469 | 127.6669 | 0.037951
731 | MCLU-65to135-OfS-CZ07-2003-19IEER | CZ07 | OfS | 2003 | 65to135 | 12 | 19 | 35.3369 | 2209.1806 | 0.31773 | 2349.9472 | 0.35566 | 140.7666 | 0.037927
732 | MCLU-65to135-OfS-CZ07-2007-19IEER | CZ07 | OfS | 2007 | 65to135 | 12 | 19 | 35.3369 | 2209.1806 | 0.31773 | 2349.9472 | 0.35566 | 140.7666 | 0.037927
733 | MCLU-65to135-OfS-CZ07-2011-19IEER | CZ07 | OfS | 2011 | 65to135 | 12 | 19 | 35.2239 | 2134.8887 | 0.30009 | 2332.2254 | 0.35311 | 197.3367 | 0.053019
734 | MCLU-65to135-OfS-CZ07-2015-19IEER | CZ07 | OfS | 2015 | 65to135 | 12 | 19 | 28.712 | 2546.1535 | 0.35057 | 2743.7483 | 0.40441 | 197.5948 | 0.053839
735 | MCLU-65to135-OfS-CZ07-2020-19IEER | CZ07 | OfS | 2020 | 65to135 | 12 | 19 | 27.9302 | 2455.4498 | 0.34679 | 2593.2575 | 0.38451 | 137.8077 | 0.037722
736 | MCLU-65to135-RFF-CZ07-2003-19IEER | CZ07 | RFF | 2003 | 65to135 | 12 | 19 | 8.2751 | 4882.0445 | 0.9623 | 5117.3058 | 1.054 | 235.2613 | 0.091747
737 | MCLU-65to135-RFF-CZ07-2007-19IEER | CZ07 | RFF | 2007 | 65to135 | 12 | 19 | 8.2751 | 4882.0445 | 0.9623 | 5117.3058 | 1.054 | 235.2613 | 0.091747
738 | MCLU-65to135-RFF-CZ07-2011-19IEER | CZ07 | RFF | 2011 | 65to135 | 12 | 19 | 8.2155 | 4814.858 | 0.91601 | 5154.7743 | 1.0597 | 339.9163 | 0.14372
739 | MCLU-65to135-RFF-CZ07-2015-19IEER | CZ07 | RFF | 2015 | 65to135 | 12 | 19 | 7.7627 | 4823.877 | 0.92359 | 5169.9567 | 1.0686 | 346.0797 | 0.14504
740 | MCLU-65to135-RFF-CZ07-2020-19IEER | CZ07 | RFF | 2020 | 65to135 | 12 | 19 | 7.2491 | 4579.4507 | 0.92776 | 4850.0067 | 1.024 | 270.5559 | 0.096248
741 | MCLU-65to135-RSD-CZ07-2003-19IEER | CZ07 | RSD | 2003 | 65to135 | 12 | 19 | 14.3822 | 5096.4986 | 1.03 | 5364.7567 | 1.1346 | 268.258 | 0.10466
742 | MCLU-65to135-RSD-CZ07-2007-19IEER | CZ07 | RSD | 2007 | 65to135 | 12 | 19 | 14.3822 | 5096.4986 | 1.03 | 5364.7567 | 1.1346 | 268.258 | 0.10466
743 | MCLU-65to135-RSD-CZ07-2011-19IEER | CZ07 | RSD | 2011 | 65to135 | 12 | 19 | 14.2105 | 5054.4691 | 0.9916 | 5433.0831 | 1.146 | 378.614 | 0.15442
744 | MCLU-65to135-RSD-CZ07-2015-19IEER | CZ07 | RSD | 2015 | 65to135 | 12 | 19 | 13.0012 | 5182.6458 | 1.0179 | 5557.4306 | 1.1746 | 374.7848 | 0.15668
745 | MCLU-65to135-RSD-CZ07-2020-19IEER | CZ07 | RSD | 2020 | 65to135 | 12 | 19 | 11.809 | 4848.7699 | 1.0013 | 5114.4677 | 1.1066 | 265.6978 | 0.10529
746 | MCLU-65to135-Rt3-CZ07-2003-19IEER | CZ07 | Rt3 | 2003 | 65to135 | 12 | 19 | 226.5997 | 6122.6517 | 1.1997 | 6293.4473 | 1.3056 | 170.7956 | 0.1059
747 | MCLU-65to135-Rt3-CZ07-2007-19IEER | CZ07 | Rt3 | 2007 | 65to135 | 12 | 19 | 226.5997 | 6122.6517 | 1.1997 | 6293.4473 | 1.3056 | 170.7956 | 0.1059
748 | MCLU-65to135-Rt3-CZ07-2011-19IEER | CZ07 | Rt3 | 2011 | 65to135 | 12 | 19 | 226.5393 | 5997.2968 | 1.1501 | 6294.4053 | 1.3046 | 297.1085 | 0.15446
749 | MCLU-65to135-Rt3-CZ07-2015-19IEER | CZ07 | Rt3 | 2015 | 65to135 | 12 | 19 | 213.6633 | 5723.7633 | 1.1151 | 6015.8273 | 1.2692 | 292.064 | 0.15409
750 | MCLU-65to135-Rt3-CZ07-2020-19IEER | CZ07 | Rt3 | 2020 | 65to135 | 12 | 19 | 203.9114 | 5419.1648 | 1.1015 | 5592.1035 | 1.207 | 172.9386 | 0.1055
751 | MCLU-65to135-RtL-CZ07-2003-19IEER | CZ07 | RtL | 2003 | 65to135 | 12 | 19 | 191.2938 | 6877.8577 | 1.3138 | 7134.9418 | 1.4184 | 257.084 | 0.10461
752 | MCLU-65to135-RtL-CZ07-2007-19IEER | CZ07 | RtL | 2007 | 65to135 | 12 | 19 | 191.2938 | 6877.8577 | 1.3138 | 7134.9418 | 1.4184 | 257.084 | 0.10461
753 | MCLU-65to135-RtL-CZ07-2011-19IEER | CZ07 | RtL | 2011 | 65to135 | 12 | 19 | 190.0807 | 6792.2052 | 1.2782 | 7180.9556 | 1.425 | 388.7504 | 0.14681
754 | MCLU-65to135-RtL-CZ07-2015-19IEER | CZ07 | RtL | 2015 | 65to135 | 12 | 19 | 181.3114 | 6623.7573 | 1.2719 | 7019.4048 | 1.4188 | 395.6475 | 0.1469
755 | MCLU-65to135-RtL-CZ07-2020-19IEER | CZ07 | RtL | 2020 | 65to135 | 12 | 19 | 168.6487 | 6564.8385 | 1.3184 | 6845.6347 | 1.4221 | 280.7962 | 0.10377
756 | MCLU-65to135-RtS-CZ07-2003-19IEER | CZ07 | RtS | 2003 | 65to135 | 12 | 19 | 15.0244 | 3869.4126 | 0.76467 | 4047.3357 | 0.85319 | 177.923 | 0.088521
757 | MCLU-65to135-RtS-CZ07-2007-19IEER | CZ07 | RtS | 2007 | 65to135 | 12 | 19 | 15.0244 | 3869.4126 | 0.76467 | 4047.3357 | 0.85319 | 177.923 | 0.088521
758 | MCLU-65to135-RtS-CZ07-2011-19IEER | CZ07 | RtS | 2011 | 65to135 | 12 | 19 | 14.8675 | 3815.404 | 0.73022 | 4084.8933 | 0.85897 | 269.4893 | 0.12874
759 | MCLU-65to135-RtS-CZ07-2015-19IEER | CZ07 | RtS | 2015 | 65to135 | 12 | 19 | 13.8032 | 3745.4264 | 0.72446 | 4013.3448 | 0.85235 | 267.9184 | 0.12788
760 | MCLU-65to135-RtS-CZ07-2020-19IEER | CZ07 | RtS | 2020 | 65to135 | 12 | 19 | 13.4252 | 3561.6076 | 0.7222 | 3743.8262 | 0.80979 | 182.2186 | 0.087595
761 | MCLU-65to135-SCn-CZ07-2003-19IEER | CZ07 | SCn | 2003 | 65to135 | 12 | 19 | 311.0332 | 2342.4639 | 0.26569 | 2522.2611 | 0.30483 | 179.7972 | 0.039144
762 | MCLU-65to135-SCn-CZ07-2007-19IEER | CZ07 | SCn | 2007 | 65to135 | 12 | 19 | 311.0332 | 2342.4639 | 0.26569 | 2522.2611 | 0.30483 | 179.7972 | 0.039144
763 | MCLU-65to135-SCn-CZ07-2011-19IEER | CZ07 | SCn | 2011 | 65to135 | 12 | 19 | 309.8197 | 2330.1249 | 0.24845 | 2527.7085 | 0.30323 | 197.5836 | 0.054781
764 | MCLU-65to135-SCn-CZ07-2015-19IEER | CZ07 | SCn | 2015 | 65to135 | 12 | 19 | 308.538 | 2337.0834 | 0.24804 | 2534.1121 | 0.30238 | 197.0288 | 0.054345
765 | MCLU-65to135-SCn-CZ07-2020-19IEER | CZ07 | SCn | 2020 | 65to135 | 12 | 19 | 304.2047 | 2065.6075 | 0.22969 | 2240.8129 | 0.26458 | 175.2054 | 0.034889
766 | MCLU-65to135-WRf-CZ07-2003-19IEER | CZ07 | WRf | 2003 | 65to135 | 12 | 19 | 12.9158 | 310674.3145 | 39.5804 | 311062.051 | 39.6596 | 387.7365 | 0.079153
767 | MCLU-65to135-WRf-CZ07-2007-19IEER | CZ07 | WRf | 2007 | 65to135 | 12 | 19 | 12.9158 | 302019.1054 | 37.6227 | 302408.6138 | 37.7016 | 389.5084 | 0.078921
768 | MCLU-65to135-WRf-CZ07-2011-19IEER | CZ07 | WRf | 2011 | 65to135 | 12 | 19 | 12.4538 | 300535.2049 | 37.4029 | 300937.582 | 37.4789 | 402.3771 | 0.075987
769 | MCLU-65to135-WRf-CZ07-2015-19IEER | CZ07 | WRf | 2015 | 65to135 | 12 | 19 | 11.7938 | 317326.5446 | 39.4869 | 317730.0431 | 39.5626 | 403.4985 | 0.075657
770 | MCLU-65to135-WRf-CZ07-2020-19IEER | CZ07 | WRf | 2020 | 65to135 | 12 | 19 | 10.7775 | 321753.5222 | 39.1438 | 322158.1964 | 39.2162 | 404.6742 | 0.072435
771 | MCLU-65to135-Asm-CZ08-2003-19IEER | CZ08 | Asm | 2003 | 65to135 | 12 | 19 | 352.1784 | 2199.2223 | 0.63286 | 2480.408 | 0.74279 | 281.1857 | 0.10993
772 | MCLU-65to135-Asm-CZ08-2007-19IEER | CZ08 | Asm | 2007 | 65to135 | 12 | 19 | 352.1784 | 2199.2223 | 0.63286 | 2480.408 | 0.74279 | 281.1857 | 0.10993
773 | MCLU-65to135-Asm-CZ08-2011-19IEER | CZ08 | Asm | 2011 | 65to135 | 12 | 19 | 349.82 | 2108.5748 | 0.58766 | 2491.7806 | 0.74609 | 383.2058 | 0.15844
774 | MCLU-65to135-Asm-CZ08-2015-19IEER | CZ08 | Asm | 2015 | 65to135 | 12 | 19 | 318.2073 | 2202.1461 | 0.61473 | 2575.9147 | 0.77342 | 373.7686 | 0.15869
775 | MCLU-65to135-Asm-CZ08-2020-19IEER | CZ08 | Asm | 2020 | 65to135 | 12 | 19 | 307.528 | 2174.8399 | 0.64401 | 2451.8311 | 0.75318 | 276.9912 | 0.10917
776 | MCLU-65to135-ECC-CZ08-2003-19IEER | CZ08 | ECC | 2003 | 65to135 | 12 | 19 | 839.3842 | 2543.965 | 0.72437 | 2732.3551 | 0.83993 | 188.39 | 0.11555
777 | MCLU-65to135-ECC-CZ08-2007-19IEER | CZ08 | ECC | 2007 | 65to135 | 12 | 19 | 839.3842 | 2543.965 | 0.72437 | 2732.3551 | 0.83993 | 188.39 | 0.11555
778 | MCLU-65to135-ECC-CZ08-2011-19IEER | CZ08 | ECC | 2011 | 65to135 | 12 | 19 | 837.5994 | 2458.4412 | 0.67404 | 2734.8761 | 0.83968 | 276.4349 | 0.16563
779 | MCLU-65to135-ECC-CZ08-2015-19IEER | CZ08 | ECC | 2015 | 65to135 | 12 | 19 | 781.2318 | 2587.6183 | 0.70179 | 2863.1006 | 0.86901 | 275.4824 | 0.16722
780 | MCLU-65to135-ECC-CZ08-2020-19IEER | CZ08 | ECC | 2020 | 65to135 | 12 | 19 | 748.4518 | 2356.1583 | 0.70401 | 2545.8721 | 0.82028 | 189.7137 | 0.11626
781 | MCLU-65to135-EPr-CZ08-2003-19IEER | CZ08 | EPr | 2003 | 65to135 | 12 | 19 | 142.2681 | 1634.1132 | 0.3569 | 1748.8597 | 0.41685 | 114.7465 | 0.059955
782 | MCLU-65to135-EPr-CZ08-2007-19IEER | CZ08 | EPr | 2007 | 65to135 | 12 | 19 | 142.2681 | 1634.1132 | 0.3569 | 1748.8597 | 0.41685 | 114.7465 | 0.059955
783 | MCLU-65to135-EPr-CZ08-2011-19IEER | CZ08 | EPr | 2011 | 65to135 | 12 | 19 | 140.9212 | 1596.4774 | 0.33144 | 1762.4217 | 0.41831 | 165.9442 | 0.086863
784 | MCLU-65to135-EPr-CZ08-2015-19IEER | CZ08 | EPr | 2015 | 65to135 | 12 | 19 | 128.3888 | 1698.8107 | 0.34685 | 1867.451 | 0.43418 | 168.6403 | 0.087322
785 | MCLU-65to135-EPr-CZ08-2020-19IEER | CZ08 | EPr | 2020 | 65to135 | 12 | 19 | 121.0632 | 1568.3007 | 0.34341 | 1690.8349 | 0.40376 | 122.5342 | 0.060348
786 | MCLU-65to135-ERC-CZ08-2003-19IEER | CZ08 | ERC | 2003 | 65to135 | 12 | 19 | 6.259 | 1387.6297 | 0.23067 | 1483.3001 | 0.24916 | 95.6704 | 0.018485
787 | MCLU-65to135-ERC-CZ08-2007-19IEER | CZ08 | ERC | 2007 | 65to135 | 12 | 19 | 6.2593 | 1387.4855 | 0.23064 | 1483.1431 | 0.24912 | 95.6576 | 0.018477
788 | MCLU-65to135-ERC-CZ08-2011-19IEER | CZ08 | ERC | 2011 | 65to135 | 12 | 19 | 6.2335 | 1342.2905 | 0.21679 | 1488.3657 | 0.24943 | 146.0752 | 0.032636
789 | MCLU-65to135-ERC-CZ08-2015-19IEER | CZ08 | ERC | 2015 | 65to135 | 12 | 19 | 6.0153 | 1348.0305 | 0.21356 | 1487.0016 | 0.24273 | 138.9711 | 0.029165
790 | MCLU-65to135-ERC-CZ08-2020-19IEER | CZ08 | ERC | 2020 | 65to135 | 12 | 19 | 5.8083 | 1227.1557 | 0.19786 | 1322.5501 | 0.21403 | 95.3945 | 0.016168
791 | MCLU-65to135-ESe-CZ08-2003-19IEER | CZ08 | ESe | 2003 | 65to135 | 12 | 19 | 441.2718 | 1795.8683 | 0.33579 | 1928.1471 | 0.39612 | 132.2788 | 0.060333
792 | MCLU-65to135-ESe-CZ08-2007-19IEER | CZ08 | ESe | 2007 | 65to135 | 12 | 19 | 441.2718 | 1795.8683 | 0.33579 | 1928.1471 | 0.39612 | 132.2788 | 0.060333
793 | MCLU-65to135-ESe-CZ08-2011-19IEER | CZ08 | ESe | 2011 | 65to135 | 12 | 19 | 439.6932 | 1737.3484 | 0.30827 | 1932.8873 | 0.39649 | 195.5388 | 0.088219
794 | MCLU-65to135-ESe-CZ08-2015-19IEER | CZ08 | ESe | 2015 | 65to135 | 12 | 19 | 401.6907 | 1809.8822 | 0.30768 | 1992.4628 | 0.3965 | 182.5806 | 0.088822
795 | MCLU-65to135-ESe-CZ08-2020-19IEER | CZ08 | ESe | 2020 | 65to135 | 12 | 19 | 384.2597 | 1635.2135 | 0.32077 | 1764.1184 | 0.38161 | 128.9049 | 0.060842
796 | MCLU-65to135-EUn-CZ08-2003-19IEER | CZ08 | EUn | 2003 | 65to135 | 12 | 19 | 2474.6502 | 2732.9795 | 0.86842 | 2930.5672 | 0.9689 | 197.5877 | 0.10048
797 | MCLU-65to135-EUn-CZ08-2007-19IEER | CZ08 | EUn | 2007 | 65to135 | 12 | 19 | 2474.6502 | 2717.7602 | 0.86052 | 2915.3139 | 0.96097 | 197.5537 | 0.10045
798 | MCLU-65to135-EUn-CZ08-2011-19IEER | CZ08 | EUn | 2011 | 65to135 | 12 | 19 | 2445.6291 | 2657.0196 | 0.82075 | 2940.7426 | 0.96783 | 283.7229 | 0.14708
799 | MCLU-65to135-EUn-CZ08-2015-19IEER | CZ08 | EUn | 2015 | 65to135 | 12 | 19 | 2223.662 | 2838.1442 | 0.87027 | 3123.3554 | 1.0192 | 285.2112 | 0.14893
800 | MCLU-65to135-EUn-CZ08-2020-19IEER | CZ08 | EUn | 2020 | 65to135 | 12 | 19 | 2118.3984 | 2679.7266 | 0.86962 | 2879.5026 | 0.97124 | 199.776 | 0.10162
801 | MCLU-65to135-Gro-CZ08-2003-19IEER | CZ08 | Gro | 2003 | 65to135 | 12 | 19 | 122.5525 | 13619.9413 | 1.9375 | 14053.8507 | 2.064 | 433.9095 | 0.12654
802 | MCLU-65to135-Gro-CZ08-2007-19IEER | CZ08 | Gro | 2007 | 65to135 | 12 | 19 | 122.5525 | 12439.0566 | 1.8175 | 12867.2683 | 1.9617 | 428.2116 | 0.14419
803 | MCLU-65to135-Gro-CZ08-2011-19IEER | CZ08 | Gro | 2011 | 65to135 | 12 | 19 | 114.9541 | 13252.8471 | 1.9383 | 13684.3022 | 2.0832 | 431.4551 | 0.14494
804 | MCLU-65to135-Gro-CZ08-2015-19IEER | CZ08 | Gro | 2015 | 65to135 | 12 | 19 | 109.1527 | 13376.0569 | 1.9498 | 13794.2229 | 2.0878 | 418.166 | 0.13792
805 | MCLU-65to135-Gro-CZ08-2020-19IEER | CZ08 | Gro | 2020 | 65to135 | 12 | 19 | 103.8478 | 13629.1301 | 1.9802 | 14035.863 | 2.1155 | 406.7329 | 0.13537
806 | MCLU-65to135-Hsp-CZ08-2003-19IEER | CZ08 | Hsp | 2003 | 65to135 | 12 | 19 | 685.4697 | 4291.8954 | 0.74215 | 4653.3527 | 0.84767 | 361.4573 | 0.10552
807 | MCLU-65to135-Hsp-CZ08-2007-19IEER | CZ08 | Hsp | 2007 | 65to135 | 12 | 19 | 685.4697 | 4291.8954 | 0.74215 | 4653.3527 | 0.84767 | 361.4573 | 0.10552
808 | MCLU-65to135-Hsp-CZ08-2011-19IEER | CZ08 | Hsp | 2011 | 65to135 | 12 | 19 | 685.4666 | 4194.8268 | 0.70081 | 4652.4752 | 0.84695 | 457.6484 | 0.14614
809 | MCLU-65to135-Hsp-CZ08-2015-19IEER | CZ08 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 4168.2256 | 0.68805 | 4620.6737 | 0.83353 | 452.448 | 0.14549
810 | MCLU-65to135-Hsp-CZ08-2020-19IEER | CZ08 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3728.8249 | 0.65345 | 4092.8851 | 0.75645 | 364.0602 | 0.10301
811 | MCLU-65to135-Htl-CZ08-2003-19IEER | CZ08 | Htl | 2003 | 65to135 | 12 | 19 | 253.4147 | 3340.417 | 0.77058 | 3427.5127 | 0.79733 | 87.0957 | 0.026751
812 | MCLU-65to135-Htl-CZ08-2007-19IEER | CZ08 | Htl | 2007 | 65to135 | 12 | 19 | 253.4147 | 3210.9823 | 0.72456 | 3297.9178 | 0.75126 | 86.9355 | 0.026695
813 | MCLU-65to135-Htl-CZ08-2011-19IEER | CZ08 | Htl | 2011 | 65to135 | 12 | 19 | 244.9298 | 3261.2823 | 0.72392 | 3376.8751 | 0.76322 | 115.5928 | 0.039295
814 | MCLU-65to135-Htl-CZ08-2015-19IEER | CZ08 | Htl | 2015 | 65to135 | 12 | 19 | 210.5105 | 3460.9932 | 0.74209 | 3583.7143 | 0.78392 | 122.7211 | 0.041821
815 | MCLU-65to135-Htl-CZ08-2020-19IEER | CZ08 | Htl | 2020 | 65to135 | 12 | 19 | 208.4066 | 3381.3052 | 0.74234 | 3474.0499 | 0.77057 | 92.7447 | 0.028237
816 | MCLU-65to135-MBT-CZ08-2003-19IEER | CZ08 | MBT | 2003 | 65to135 | 12 | 19 | 378.2697 | 3979.9903 | 0.55339 | 4166.5454 | 0.63445 | 186.5552 | 0.081055
817 | MCLU-65to135-MBT-CZ08-2007-19IEER | CZ08 | MBT | 2007 | 65to135 | 12 | 19 | 378.2697 | 3979.9903 | 0.55339 | 4166.5454 | 0.63445 | 186.5552 | 0.081055
818 | MCLU-65to135-MBT-CZ08-2011-19IEER | CZ08 | MBT | 2011 | 65to135 | 12 | 19 | 361.4981 | 4021.6377 | 0.53149 | 4294.0819 | 0.64451 | 272.4442 | 0.11302
819 | MCLU-65to135-MBT-CZ08-2015-19IEER | CZ08 | MBT | 2015 | 65to135 | 12 | 19 | 336.3204 | 4250.7468 | 0.55405 | 4521.2683 | 0.66802 | 270.5216 | 0.11397
820 | MCLU-65to135-MBT-CZ08-2020-19IEER | CZ08 | MBT | 2020 | 65to135 | 12 | 19 | 309.8243 | 4236.7091 | 0.57573 | 4412.5958 | 0.65577 | 175.8867 | 0.080037
821 | MCLU-65to135-MLI-CZ08-2003-19IEER | CZ08 | MLI | 2003 | 65to135 | 12 | 19 | 225.4652 | 3006.9451 | 0.42453 | 3184.4866 | 0.48202 | 177.5414 | 0.057498
822 | MCLU-65to135-MLI-CZ08-2007-19IEER | CZ08 | MLI | 2007 | 65to135 | 12 | 19 | 225.4652 | 3006.9451 | 0.42453 | 3184.4866 | 0.48202 | 177.5414 | 0.057498
823 | MCLU-65to135-MLI-CZ08-2011-19IEER | CZ08 | MLI | 2011 | 65to135 | 12 | 19 | 221.4902 | 3000.5067 | 0.40424 | 3232.7775 | 0.48738 | 232.2708 | 0.083135
824 | MCLU-65to135-MLI-CZ08-2015-19IEER | CZ08 | MLI | 2015 | 65to135 | 12 | 19 | 217.5991 | 3030.3953 | 0.40783 | 3262.1323 | 0.49136 | 231.737 | 0.083533
825 | MCLU-65to135-MLI-CZ08-2020-19IEER | CZ08 | MLI | 2020 | 65to135 | 12 | 19 | 200.4201 | 2803.6509 | 0.4052 | 2979.3244 | 0.46251 | 175.6735 | 0.05731
826 | MCLU-65to135-Mtl-CZ08-2003-19IEER | CZ08 | Mtl | 2003 | 65to135 | 12 | 19 | 45.143 | 3303.2075 | 0.71014 | 3369.9253 | 0.72838 | 66.7178 | 0.018245
827 | MCLU-65to135-Mtl-CZ08-2007-19IEER | CZ08 | Mtl | 2007 | 65to135 | 12 | 19 | 45.143 | 3162.5275 | 0.66265 | 3229.2641 | 0.68087 | 66.7366 | 0.018223
828 | MCLU-65to135-Mtl-CZ08-2011-19IEER | CZ08 | Mtl | 2011 | 65to135 | 12 | 19 | 43.1359 | 3249.9045 | 0.6652 | 3339.7342 | 0.69089 | 89.8297 | 0.025697
829 | MCLU-65to135-Mtl-CZ08-2015-19IEER | CZ08 | Mtl | 2015 | 65to135 | 12 | 19 | 36.8083 | 3446.0618 | 0.67938 | 3542.0822 | 0.70789 | 96.0204 | 0.028508
830 | MCLU-65to135-Mtl-CZ08-2020-19IEER | CZ08 | Mtl | 2020 | 65to135 | 12 | 19 | 36.6743 | 3383.013 | 0.67732 | 3454.0767 | 0.69671 | 71.0637 | 0.019387
831 | MCLU-65to135-Nrs-CZ08-2003-19IEER | CZ08 | Nrs | 2003 | 65to135 | 12 | 19 | 191.8434 | 4507.2322 | 0.82594 | 4680.977 | 0.87781 | 173.7448 | 0.051863
832 | MCLU-65to135-Nrs-CZ08-2007-19IEER | CZ08 | Nrs | 2007 | 65to135 | 12 | 19 | 191.8434 | 4404.8299 | 0.79761 | 4578.677 | 0.84944 | 173.8471 | 0.05183
833 | MCLU-65to135-Nrs-CZ08-2011-19IEER | CZ08 | Nrs | 2011 | 65to135 | 12 | 19 | 191.7625 | 4360.4901 | 0.77595 | 4580.0785 | 0.8486 | 219.5883 | 0.072655
834 | MCLU-65to135-Nrs-CZ08-2015-19IEER | CZ08 | Nrs | 2015 | 65to135 | 12 | 19 | 181.7752 | 4339.6875 | 0.74395 | 4548.6392 | 0.81418 | 208.9517 | 0.070231
835 | MCLU-65to135-Nrs-CZ08-2020-19IEER | CZ08 | Nrs | 2020 | 65to135 | 12 | 19 | 181.639 | 4001.0535 | 0.70529 | 4167.8441 | 0.75393 | 166.7907 | 0.048644
836 | MCLU-65to135-OfL-CZ08-2003-19IEER | CZ08 | OfL | 2003 | 65to135 | 12 | 19 | 480.1592 | 3389.1143 | 0.50605 | 3572.5952 | 0.54729 | 183.4809 | 0.041233
837 | MCLU-65to135-OfL-CZ08-2007-19IEER | CZ08 | OfL | 2007 | 65to135 | 12 | 19 | 480.1592 | 3389.1143 | 0.50605 | 3572.5952 | 0.54729 | 183.4809 | 0.041233
838 | MCLU-65to135-OfL-CZ08-2011-19IEER | CZ08 | OfL | 2011 | 65to135 | 12 | 19 | 462.4795 | 3384.9581 | 0.49517 | 3659.8072 | 0.55469 | 274.8492 | 0.05952
839 | MCLU-65to135-OfL-CZ08-2015-19IEER | CZ08 | OfL | 2015 | 65to135 | 12 | 19 | 436.4957 | 3512.4189 | 0.5124 | 3782.6572 | 0.5719 | 270.2384 | 0.059501
840 | MCLU-65to135-OfL-CZ08-2020-19IEER | CZ08 | OfL | 2020 | 65to135 | 12 | 19 | 424.512 | 3430.7322 | 0.5122 | 3609.6286 | 0.55321 | 178.8964 | 0.041002
841 | MCLU-65to135-OfS-CZ08-2003-19IEER | CZ08 | OfS | 2003 | 65to135 | 12 | 19 | 32.8087 | 2506.0055 | 0.37388 | 2691.5946 | 0.41556 | 185.5891 | 0.041687
842 | MCLU-65to135-OfS-CZ08-2007-19IEER | CZ08 | OfS | 2007 | 65to135 | 12 | 19 | 32.8087 | 2506.0055 | 0.37388 | 2691.5946 | 0.41556 | 185.5891 | 0.041687
843 | MCLU-65to135-OfS-CZ08-2011-19IEER | CZ08 | OfS | 2011 | 65to135 | 12 | 19 | 32.6627 | 2410.7765 | 0.35332 | 2675.0862 | 0.41307 | 264.3097 | 0.05975
844 | MCLU-65to135-OfS-CZ08-2015-19IEER | CZ08 | OfS | 2015 | 65to135 | 12 | 19 | 27.6112 | 2751.7403 | 0.39277 | 3012.0039 | 0.45231 | 260.2636 | 0.059537
845 | MCLU-65to135-OfS-CZ08-2020-19IEER | CZ08 | OfS | 2020 | 65to135 | 12 | 19 | 26.8023 | 2680.4991 | 0.39115 | 2860.5319 | 0.43219 | 180.0328 | 0.041037
846 | MCLU-65to135-RFF-CZ08-2003-19IEER | CZ08 | RFF | 2003 | 65to135 | 12 | 19 | 7.5762 | 5568.0157 | 1.1648 | 5910.9177 | 1.28 | 342.902 | 0.11517
847 | MCLU-65to135-RFF-CZ08-2007-19IEER | CZ08 | RFF | 2007 | 65to135 | 12 | 19 | 7.5762 | 5568.0157 | 1.1648 | 5910.9177 | 1.28 | 342.902 | 0.11517
848 | MCLU-65to135-RFF-CZ08-2011-19IEER | CZ08 | RFF | 2011 | 65to135 | 12 | 19 | 7.5056 | 5478.6201 | 1.1219 | 5962.9836 | 1.2885 | 484.3634 | 0.16663
849 | MCLU-65to135-RFF-CZ08-2015-19IEER | CZ08 | RFF | 2015 | 65to135 | 12 | 19 | 7.2218 | 5399.1211 | 1.1128 | 5881.3634 | 1.2809 | 482.2424 | 0.16809
850 | MCLU-65to135-RFF-CZ08-2020-19IEER | CZ08 | RFF | 2020 | 65to135 | 12 | 19 | 6.7943 | 5137.3732 | 1.1125 | 5495.1593 | 1.2279 | 357.786 | 0.11548
851 | MCLU-65to135-RSD-CZ08-2003-19IEER | CZ08 | RSD | 2003 | 65to135 | 12 | 19 | 14.6018 | 5234.2465 | 1.1063 | 5528.3453 | 1.2191 | 294.0989 | 0.11284
852 | MCLU-65to135-RSD-CZ08-2007-19IEER | CZ08 | RSD | 2007 | 65to135 | 12 | 19 | 14.6018 | 5234.2465 | 1.1063 | 5528.3453 | 1.2191 | 294.0989 | 0.11284
853 | MCLU-65to135-RSD-CZ08-2011-19IEER | CZ08 | RSD | 2011 | 65to135 | 12 | 19 | 14.4539 | 5153.8484 | 1.0607 | 5580.9179 | 1.2277 | 427.0695 | 0.16697
854 | MCLU-65to135-RSD-CZ08-2015-19IEER | CZ08 | RSD | 2015 | 65to135 | 12 | 19 | 13.5847 | 5158.6299 | 1.0633 | 5579.8115 | 1.2308 | 421.1816 | 0.16756
855 | MCLU-65to135-RSD-CZ08-2020-19IEER | CZ08 | RSD | 2020 | 65to135 | 12 | 19 | 12.5834 | 4795.4917 | 1.0402 | 5103.0716 | 1.1552 | 307.5799 | 0.11499
856 | MCLU-65to135-Rt3-CZ08-2003-19IEER | CZ08 | Rt3 | 2003 | 65to135 | 12 | 19 | 256.8227 | 5560.3023 | 1.1328 | 5796.6773 | 1.2507 | 236.3749 | 0.11796
857 | MCLU-65to135-Rt3-CZ08-2007-19IEER | CZ08 | Rt3 | 2007 | 65to135 | 12 | 19 | 256.8227 | 5560.3023 | 1.1328 | 5796.6773 | 1.2507 | 236.3749 | 0.11796
858 | MCLU-65to135-Rt3-CZ08-2011-19IEER | CZ08 | Rt3 | 2011 | 65to135 | 12 | 19 | 256.0112 | 5436.9669 | 1.0809 | 5813.1364 | 1.2526 | 376.1694 | 0.17175
859 | MCLU-65to135-Rt3-CZ08-2015-19IEER | CZ08 | Rt3 | 2015 | 65to135 | 12 | 19 | 246.2802 | 5096.9573 | 1.0289 | 5467.4625 | 1.2014 | 370.5052 | 0.17256
860 | MCLU-65to135-Rt3-CZ08-2020-19IEER | CZ08 | Rt3 | 2020 | 65to135 | 12 | 19 | 235.2777 | 4861.3878 | 1.0291 | 5097.7909 | 1.1471 | 236.4032 | 0.11803
861 | MCLU-65to135-RtL-CZ08-2003-19IEER | CZ08 | RtL | 2003 | 65to135 | 12 | 19 | 231.606 | 5863.6762 | 1.1526 | 6114.2613 | 1.2671 | 250.5851 | 0.11452
862 | MCLU-65to135-RtL-CZ08-2007-19IEER | CZ08 | RtL | 2007 | 65to135 | 12 | 19 | 231.606 | 5863.6762 | 1.1526 | 6114.2613 | 1.2671 | 250.5851 | 0.11452
863 | MCLU-65to135-RtL-CZ08-2011-19IEER | CZ08 | RtL | 2011 | 65to135 | 12 | 19 | 228.3212 | 5800.6675 | 1.1141 | 6195.166 | 1.2806 | 394.4985 | 0.1665
864 | MCLU-65to135-RtL-CZ08-2015-19IEER | CZ08 | RtL | 2015 | 65to135 | 12 | 19 | 220.3641 | 5599.9473 | 1.0968 | 5996.1038 | 1.2637 | 396.1565 | 0.16693
865 | MCLU-65to135-RtL-CZ08-2020-19IEER | CZ08 | RtL | 2020 | 65to135 | 12 | 19 | 205.1775 | 5580.4317 | 1.1509 | 5839.6165 | 1.2654 | 259.1848 | 0.11456
866 | MCLU-65to135-RtS-CZ08-2003-19IEER | CZ08 | RtS | 2003 | 65to135 | 12 | 19 | 17.4238 | 3519.682 | 0.73447 | 3767.1919 | 0.83493 | 247.5099 | 0.10045
867 | MCLU-65to135-RtS-CZ08-2007-19IEER | CZ08 | RtS | 2007 | 65to135 | 12 | 19 | 17.4238 | 3519.682 | 0.73447 | 3767.1919 | 0.83493 | 247.5099 | 0.10045
868 | MCLU-65to135-RtS-CZ08-2011-19IEER | CZ08 | RtS | 2011 | 65to135 | 12 | 19 | 17.2087 | 3448.2474 | 0.69515 | 3805.6114 | 0.84056 | 357.364 | 0.14541
869 | MCLU-65to135-RtS-CZ08-2015-19IEER | CZ08 | RtS | 2015 | 65to135 | 12 | 19 | 16.3513 | 3316.8179 | 0.67562 | 3669.7976 | 0.82169 | 352.9796 | 0.14607
870 | MCLU-65to135-RtS-CZ08-2020-19IEER | CZ08 | RtS | 2020 | 65to135 | 12 | 19 | 15.5006 | 3273.2363 | 0.70237 | 3519.7344 | 0.80236 | 246.4981 | 0.099989
871 | MCLU-65to135-SCn-CZ08-2003-19IEER | CZ08 | SCn | 2003 | 65to135 | 12 | 19 | 292.4207 | 2627.6209 | 0.34662 | 2846.1719 | 0.40261 | 218.551 | 0.055991
872 | MCLU-65to135-SCn-CZ08-2007-19IEER | CZ08 | SCn | 2007 | 65to135 | 12 | 19 | 292.4207 | 2627.6209 | 0.34662 | 2846.1719 | 0.40261 | 218.551 | 0.055991
873 | MCLU-65to135-SCn-CZ08-2011-19IEER | CZ08 | SCn | 2011 | 65to135 | 12 | 19 | 276.9794 | 2708.6792 | 0.33274 | 2974.9703 | 0.41783 | 266.2912 | 0.085087
874 | MCLU-65to135-SCn-CZ08-2015-19IEER | CZ08 | SCn | 2015 | 65to135 | 12 | 19 | 283.0796 | 2649.7932 | 0.32344 | 2912.387 | 0.40705 | 262.5938 | 0.083602
875 | MCLU-65to135-SCn-CZ08-2020-19IEER | CZ08 | SCn | 2020 | 65to135 | 12 | 19 | 242.7788 | 2691.0272 | 0.35378 | 2914.0962 | 0.41249 | 223.069 | 0.058716
876 | MCLU-65to135-WRf-CZ08-2003-19IEER | CZ08 | WRf | 2003 | 65to135 | 12 | 19 | 16.4283 | 243241.2116 | 31.6291 | 243650.9898 | 31.7247 | 409.7782 | 0.095608
877 | MCLU-65to135-WRf-CZ08-2007-19IEER | CZ08 | WRf | 2007 | 65to135 | 12 | 19 | 16.4283 | 237357.3894 | 30.1009 | 237765.3085 | 30.1964 | 407.9191 | 0.09553
878 | MCLU-65to135-WRf-CZ08-2011-19IEER | CZ08 | WRf | 2011 | 65to135 | 12 | 19 | 15.3611 | 240134.1289 | 29.8071 | 240554.2073 | 29.8991 | 420.0784 | 0.092004
879 | MCLU-65to135-WRf-CZ08-2015-19IEER | CZ08 | WRf | 2015 | 65to135 | 12 | 19 | 14.6151 | 252355.7271 | 31.3179 | 252777.9906 | 31.4107 | 422.2636 | 0.092826
880 | MCLU-65to135-WRf-CZ08-2020-19IEER | CZ08 | WRf | 2020 | 65to135 | 12 | 19 | 13.6187 | 252440.0624 | 30.931 | 252848.9277 | 31.0177 | 408.8653 | 0.086727
881 | MCLU-65to135-Asm-CZ09-2003-19IEER | CZ09 | Asm | 2003 | 65to135 | 12 | 19 | 455.7975 | 1681.8182 | 0.61933 | 2053.3698 | 0.79906 | 371.5516 | 0.17974
882 | MCLU-65to135-Asm-CZ09-2007-19IEER | CZ09 | Asm | 2007 | 65to135 | 12 | 19 | 455.7975 | 1681.8182 | 0.61933 | 2053.3698 | 0.79906 | 371.5516 | 0.17974
883 | MCLU-65to135-Asm-CZ09-2011-19IEER | CZ09 | Asm | 2011 | 65to135 | 12 | 19 | 444.8757 | 1714.6744 | 0.62927 | 2088.7556 | 0.80767 | 374.0812 | 0.17839
884 | MCLU-65to135-Asm-CZ09-2015-19IEER | CZ09 | Asm | 2015 | 65to135 | 12 | 19 | 410.821 | 1771.9485 | 0.64689 | 2137.1985 | 0.82648 | 365.25 | 0.17959
885 | MCLU-65to135-Asm-CZ09-2020-19IEER | CZ09 | Asm | 2020 | 65to135 | 12 | 19 | 403.4637 | 1659.7453 | 0.62532 | 2022.5737 | 0.80509 | 362.8284 | 0.17977
886 | MCLU-65to135-ECC-CZ09-2003-19IEER | CZ09 | ECC | 2003 | 65to135 | 12 | 19 | 1026.5816 | 2030.0234 | 0.67414 | 2300.4512 | 0.87642 | 270.4278 | 0.20228
887 | MCLU-65to135-ECC-CZ09-2007-19IEER | CZ09 | ECC | 2007 | 65to135 | 12 | 19 | 1026.5816 | 2030.0234 | 0.67414 | 2300.4512 | 0.87642 | 270.4278 | 0.20228
888 | MCLU-65to135-ECC-CZ09-2011-19IEER | CZ09 | ECC | 2011 | 65to135 | 12 | 19 | 1019.0119 | 2040.2747 | 0.672 | 2309.4649 | 0.87377 | 269.1903 | 0.20177
889 | MCLU-65to135-ECC-CZ09-2015-19IEER | CZ09 | ECC | 2015 | 65to135 | 12 | 19 | 958.0853 | 2129.1021 | 0.6863 | 2392.9129 | 0.89132 | 263.8108 | 0.20502
890 | MCLU-65to135-ECC-CZ09-2020-19IEER | CZ09 | ECC | 2020 | 65to135 | 12 | 19 | 928.6497 | 1857.905 | 0.64146 | 2118.4002 | 0.84725 | 260.4952 | 0.20579
891 | MCLU-65to135-EPr-CZ09-2003-19IEER | CZ09 | EPr | 2003 | 65to135 | 12 | 19 | 181.6289 | 1251.4207 | 0.32876 | 1415.4745 | 0.44504 | 164.0538 | 0.11629
892 | MCLU-65to135-EPr-CZ09-2007-19IEER | CZ09 | EPr | 2007 | 65to135 | 12 | 19 | 181.6289 | 1251.4207 | 0.32876 | 1415.4745 | 0.44504 | 164.0538 | 0.11629
893 | MCLU-65to135-EPr-CZ09-2011-19IEER | CZ09 | EPr | 2011 | 65to135 | 12 | 19 | 172.8001 | 1310.5726 | 0.33442 | 1474.3316 | 0.44934 | 163.759 | 0.11492
894 | MCLU-65to135-EPr-CZ09-2015-19IEER | CZ09 | EPr | 2015 | 65to135 | 12 | 19 | 159.2486 | 1379.8605 | 0.34354 | 1539.4856 | 0.45916 | 159.6251 | 0.11562
895 | MCLU-65to135-EPr-CZ09-2020-19IEER | CZ09 | EPr | 2020 | 65to135 | 12 | 19 | 153.3689 | 1231.826 | 0.31746 | 1385.8653 | 0.43249 | 154.0393 | 0.11502
896 | MCLU-65to135-ERC-CZ09-2003-19IEER | CZ09 | ERC | 2003 | 65to135 | 12 | 19 | 8.2995 | 1026.3719 | 0.20848 | 1164.1338 | 0.25618 | 137.7619 | 0.0477
897 | MCLU-65to135-ERC-CZ09-2007-19IEER | CZ09 | ERC | 2007 | 65to135 | 12 | 19 | 8.2999 | 1026.2974 | 0.20846 | 1164.0269 | 0.25615 | 137.7295 | 0.047692
898 | MCLU-65to135-ERC-CZ09-2011-19IEER | CZ09 | ERC | 2011 | 65to135 | 12 | 19 | 7.9233 | 1064.7531 | 0.2052 | 1199.6016 | 0.2474 | 134.8485 | 0.042206
899 | MCLU-65to135-ERC-CZ09-2015-19IEER | CZ09 | ERC | 2015 | 65to135 | 12 | 19 | 7.6402 | 1069.2458 | 0.20027 | 1196.2851 | 0.23751 | 127.0393 | 0.037236
900 | MCLU-65to135-ERC-CZ09-2020-19IEER | CZ09 | ERC | 2020 | 65to135 | 12 | 19 | 7.4577 | 931.9566 | 0.17721 | 1056.655 | 0.21203 | 124.6984 | 0.034818
901 | MCLU-65to135-ESe-CZ09-2003-19IEER | CZ09 | ESe | 2003 | 65to135 | 12 | 19 | 545.6841 | 1419.6409 | 0.31978 | 1612.6839 | 0.43432 | 193.043 | 0.11454
902 | MCLU-65to135-ESe-CZ09-2007-19IEER | CZ09 | ESe | 2007 | 65to135 | 12 | 19 | 545.6841 | 1419.6409 | 0.31978 | 1612.6839 | 0.43432 | 193.043 | 0.11454
903 | MCLU-65to135-ESe-CZ09-2011-19IEER | CZ09 | ESe | 2011 | 65to135 | 12 | 19 | 538.6553 | 1434.8351 | 0.31968 | 1627.5491 | 0.43415 | 192.714 | 0.11448
904 | MCLU-65to135-ESe-CZ09-2015-19IEER | CZ09 | ESe | 2015 | 65to135 | 12 | 19 | 499.0982 | 1472.9967 | 0.30712 | 1649.9324 | 0.42406 | 176.9357 | 0.11694
905 | MCLU-65to135-ESe-CZ09-2020-19IEER | CZ09 | ESe | 2020 | 65to135 | 12 | 19 | 483.8306 | 1278.0941 | 0.29334 | 1452.3432 | 0.41048 | 174.2491 | 0.11714
906 | MCLU-65to135-EUn-CZ09-2003-19IEER | CZ09 | EUn | 2003 | 65to135 | 12 | 19 | 3067.1034 | 2178.5831 | 0.81034 | 2458.0221 | 0.98685 | 279.439 | 0.17651
907 | MCLU-65to135-EUn-CZ09-2007-19IEER | CZ09 | EUn | 2007 | 65to135 | 12 | 19 | 3067.1034 | 2164.4525 | 0.80099 | 2443.8465 | 0.97747 | 279.3939 | 0.17648
908 | MCLU-65to135-EUn-CZ09-2011-19IEER | CZ09 | EUn | 2011 | 65to135 | 12 | 19 | 2990.8022 | 2207.1225 | 0.81325 | 2487.4629 | 0.99017 | 280.3404 | 0.17692
909 | MCLU-65to135-EUn-CZ09-2015-19IEER | CZ09 | EUn | 2015 | 65to135 | 12 | 19 | 2747.4488 | 2328.4147 | 0.84287 | 2605.5696 | 1.023 | 277.1549 | 0.18016
910 | MCLU-65to135-EUn-CZ09-2020-19IEER | CZ09 | EUn | 2020 | 65to135 | 12 | 19 | 2654.1653 | 2112.0694 | 0.79788 | 2385.7849 | 0.97782 | 273.7155 | 0.17994
911 | MCLU-65to135-Gro-CZ09-2003-19IEER | CZ09 | Gro | 2003 | 65to135 | 12 | 19 | 150.0035 | 11187.523 | 1.7676 | 11617.6759 | 1.9472 | 430.1528 | 0.17962
912 | MCLU-65to135-Gro-CZ09-2007-19IEER | CZ09 | Gro | 2007 | 65to135 | 12 | 19 | 150.0035 | 10202.2332 | 1.636 | 10636.7462 | 1.8409 | 434.5129 | 0.20487
913 | MCLU-65to135-Gro-CZ09-2011-19IEER | CZ09 | Gro | 2011 | 65to135 | 12 | 19 | 146.6376 | 10420.1111 | 1.6591 | 10845.3152 | 1.8623 | 425.2041 | 0.20321
914 | MCLU-65to135-Gro-CZ09-2015-19IEER | CZ09 | Gro | 2015 | 65to135 | 12 | 19 | 140.0392 | 10455.9077 | 1.6634 | 10867.9956 | 1.8626 | 412.0879 | 0.19918
915 | MCLU-65to135-Gro-CZ09-2020-19IEER | CZ09 | Gro | 2020 | 65to135 | 12 | 19 | 138.7593 | 10234.0406 | 1.6265 | 10636.0703 | 1.8209 | 402.0297 | 0.19444
916 | MCLU-65to135-Hsp-CZ09-2003-19IEER | CZ09 | Hsp | 2003 | 65to135 | 12 | 19 | 700.0547 | 4128.2027 | 0.78068 | 4626.4007 | 0.96719 | 498.1979 | 0.18651
917 | MCLU-65to135-Hsp-CZ09-2007-19IEER | CZ09 | Hsp | 2007 | 65to135 | 12 | 19 | 700.0547 | 4128.2027 | 0.78068 | 4626.4007 | 0.96719 | 498.1979 | 0.18651
918 | MCLU-65to135-Hsp-CZ09-2011-19IEER | CZ09 | Hsp | 2011 | 65to135 | 12 | 19 | 699.2933 | 4130.0539 | 0.77864 | 4626.9513 | 0.9641 | 496.8975 | 0.18545
919 | MCLU-65to135-Hsp-CZ09-2015-19IEER | CZ09 | Hsp | 2015 | 65to135 | 12 | 19 | 681.5129 | 4176.8815 | 0.77363 | 4673.3912 | 0.96138 | 496.5097 | 0.18776
920 | MCLU-65to135-Hsp-CZ09-2020-19IEER | CZ09 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3664.2955 | 0.69485 | 4154.9283 | 0.88094 | 490.6328 | 0.18609
921 | MCLU-65to135-Htl-CZ09-2003-19IEER | CZ09 | Htl | 2003 | 65to135 | 12 | 19 | 310.5483 | 2856.2361 | 0.83778 | 2972.1548 | 0.88588 | 115.9187 | 0.048105
922 | MCLU-65to135-Htl-CZ09-2007-19IEER | CZ09 | Htl | 2007 | 65to135 | 12 | 19 | 310.5483 | 2738.4518 | 0.78079 | 2854.3181 | 0.8288 | 115.8663 | 0.04801
923 | MCLU-65to135-Htl-CZ09-2011-19IEER | CZ09 | Htl | 2011 | 65to135 | 12 | 19 | 299.3542 | 2796.4982 | 0.78709 | 2914.7903 | 0.83611 | 118.2921 | 0.049021
924 | MCLU-65to135-Htl-CZ09-2015-19IEER | CZ09 | Htl | 2015 | 65to135 | 12 | 19 | 261.282 | 2906.8346 | 0.78296 | 3030.6578 | 0.83575 | 123.8232 | 0.052789
925 | MCLU-65to135-Htl-CZ09-2020-19IEER | CZ09 | Htl | 2020 | 65to135 | 12 | 19 | 259.2903 | 2818.6731 | 0.77258 | 2939.6114 | 0.82434 | 120.9383 | 0.051758
926 | MCLU-65to135-MBT-CZ09-2003-19IEER | CZ09 | MBT | 2003 | 65to135 | 12 | 19 | 461.1237 | 3205.2111 | 0.49877 | 3474.5179 | 0.64422 | 269.3069 | 0.14545
927 | MCLU-65to135-MBT-CZ09-2007-19IEER | CZ09 | MBT | 2007 | 65to135 | 12 | 19 | 461.1237 | 3205.2111 | 0.49877 | 3474.5179 | 0.64422 | 269.3069 | 0.14545
928 | MCLU-65to135-MBT-CZ09-2011-19IEER | CZ09 | MBT | 2011 | 65to135 | 12 | 19 | 420.7569 | 3458.9937 | 0.51957 | 3727.5553 | 0.66329 | 268.5616 | 0.14372
929 | MCLU-65to135-MBT-CZ09-2015-19IEER | CZ09 | MBT | 2015 | 65to135 | 12 | 19 | 394.2945 | 3628.9007 | 0.53504 | 3894.5711 | 0.68019 | 265.6704 | 0.14515
930 | MCLU-65to135-MBT-CZ09-2020-19IEER | CZ09 | MBT | 2020 | 65to135 | 12 | 19 | 370.6144 | 3455.3567 | 0.51606 | 3718.0952 | 0.66133 | 262.7385 | 0.14527
931 | MCLU-65to135-MLI-CZ09-2003-19IEER | CZ09 | MLI | 2003 | 65to135 | 12 | 19 | 279.7978 | 2409.0254 | 0.38108 | 2650.5152 | 0.48838 | 241.4899 | 0.1073
932 | MCLU-65to135-MLI-CZ09-2007-19IEER | CZ09 | MLI | 2007 | 65to135 | 12 | 19 | 279.7978 | 2409.0254 | 0.38108 | 2650.5152 | 0.48838 | 241.4899 | 0.1073
933 | MCLU-65to135-MLI-CZ09-2011-19IEER | CZ09 | MLI | 2011 | 65to135 | 12 | 19 | 263.3407 | 2543.0409 | 0.39287 | 2782.2526 | 0.50042 | 239.2117 | 0.10754
934 | MCLU-65to135-MLI-CZ09-2015-19IEER | CZ09 | MLI | 2015 | 65to135 | 12 | 19 | 259.2564 | 2562.793 | 0.39551 | 2801.6081 | 0.50313 | 238.8151 | 0.10762
935 | MCLU-65to135-MLI-CZ09-2020-19IEER | CZ09 | MLI | 2020 | 65to135 | 12 | 19 | 246.1034 | 2267.1148 | 0.36392 | 2502.0496 | 0.47189 | 234.9348 | 0.10798
936 | MCLU-65to135-Mtl-CZ09-2003-19IEER | CZ09 | Mtl | 2003 | 65to135 | 12 | 19 | 53.8702 | 2879.2215 | 0.79605 | 2970.6753 | 0.8289 | 91.4538 | 0.032856
937 | MCLU-65to135-Mtl-CZ09-2007-19IEER | CZ09 | Mtl | 2007 | 65to135 | 12 | 19 | 53.8702 | 2748.8322 | 0.73542 | 2840.4091 | 0.76819 | 91.5769 | 0.032774
938 | MCLU-65to135-Mtl-CZ09-2011-19IEER | CZ09 | Mtl | 2011 | 65to135 | 12 | 19 | 51.4129 | 2836.3714 | 0.7441 | 2927.8552 | 0.77667 | 91.4838 | 0.032569
939 | MCLU-65to135-Mtl-CZ09-2015-19IEER | CZ09 | Mtl | 2015 | 65to135 | 12 | 19 | 44.2967 | 2965.5382 | 0.74302 | 3064.7013 | 0.77923 | 99.1631 | 0.036219
940 | MCLU-65to135-Mtl-CZ09-2020-19IEER | CZ09 | Mtl | 2020 | 65to135 | 12 | 19 | 44.1581 | 2894.7651 | 0.73423 | 2991.9175 | 0.76985 | 97.1524 | 0.03562
941 | MCLU-65to135-Nrs-CZ09-2003-19IEER | CZ09 | Nrs | 2003 | 65to135 | 12 | 19 | 201.2107 | 4320.4869 | 0.92508 | 4550.8904 | 1.0156 | 230.4034 | 0.090474
942 | MCLU-65to135-Nrs-CZ09-2007-19IEER | CZ09 | Nrs | 2007 | 65to135 | 12 | 19 | 201.2107 | 4217.7718 | 0.88653 | 4448.3077 | 0.97696 | 230.5359 | 0.090436
943 | MCLU-65to135-Nrs-CZ09-2011-19IEER | CZ09 | Nrs | 2011 | 65to135 | 12 | 19 | 197.5532 | 4309.8786 | 0.88628 | 4541.4823 | 0.97622 | 231.6038 | 0.089936
944 | MCLU-65to135-Nrs-CZ09-2015-19IEER | CZ09 | Nrs | 2015 | 65to135 | 12 | 19 | 183.08 | 4363.8542 | 0.84743 | 4590.4855 | 0.93824 | 226.6313 | 0.090815
945 | MCLU-65to135-Nrs-CZ09-2020-19IEER | CZ09 | Nrs | 2020 | 65to135 | 12 | 19 | 182.412 | 4001.912 | 0.78887 | 4224.2716 | 0.87832 | 222.3596 | 0.089446
946 | MCLU-65to135-OfL-CZ09-2003-19IEER | CZ09 | OfL | 2003 | 65to135 | 12 | 19 | 553.385 | 2868.8553 | 0.47321 | 3139.4448 | 0.54855 | 270.5895 | 0.075339
947 | MCLU-65to135-OfL-CZ09-2007-19IEER | CZ09 | OfL | 2007 | 65to135 | 12 | 19 | 553.385 | 2868.8553 | 0.47321 | 3139.4448 | 0.54855 | 270.5895 | 0.075339
948 | MCLU-65to135-OfL-CZ09-2011-19IEER | CZ09 | OfL | 2011 | 65to135 | 12 | 19 | 531.6898 | 2943.2796 | 0.47647 | 3213.101 | 0.55153 | 269.8214 | 0.075058
949 | MCLU-65to135-OfL-CZ09-2015-19IEER | CZ09 | OfL | 2015 | 65to135 | 12 | 19 | 505.5934 | 3030.308 | 0.48665 | 3295.6204 | 0.56243 | 265.3124 | 0.075786
950 | MCLU-65to135-OfL-CZ09-2020-19IEER | CZ09 | OfL | 2020 | 65to135 | 12 | 19 | 494.6411 | 2868.2996 | 0.46757 | 3131.9239 | 0.54296 | 263.6243 | 0.075387
951 | MCLU-65to135-OfS-CZ09-2003-19IEER | CZ09 | OfS | 2003 | 65to135 | 12 | 19 | 38.4675 | 2088.3755 | 0.35572 | 2353.0793 | 0.43147 | 264.7038 | 0.07575
952 | MCLU-65to135-OfS-CZ09-2007-19IEER | CZ09 | OfS | 2007 | 65to135 | 12 | 19 | 38.4675 | 2088.3755 | 0.35572 | 2353.0793 | 0.43147 | 264.7038 | 0.07575
953 | MCLU-65to135-OfS-CZ09-2011-19IEER | CZ09 | OfS | 2011 | 65to135 | 12 | 19 | 37.3262 | 2126.0341 | 0.35593 | 2390.7774 | 0.431 | 264.7433 | 0.075074
954 | MCLU-65to135-OfS-CZ09-2015-19IEER | CZ09 | OfS | 2015 | 65to135 | 12 | 19 | 31.9674 | 2389.8281 | 0.3807 | 2649.2005 | 0.45605 | 259.3724 | 0.075343
955 | MCLU-65to135-OfS-CZ09-2020-19IEER | CZ09 | OfS | 2020 | 65to135 | 12 | 19 | 31.2068 | 2249.9997 | 0.3614 | 2508.048 | 0.43651 | 258.0483 | 0.075107
956 | MCLU-65to135-RFF-CZ09-2003-19IEER | CZ09 | RFF | 2003 | 65to135 | 12 | 19 | 9.9166 | 4206.4376 | 1.0134 | 4646.2499 | 1.2084 | 439.8123 | 0.19509
957 | MCLU-65to135-RFF-CZ09-2007-19IEER | CZ09 | RFF | 2007 | 65to135 | 12 | 19 | 9.9166 | 4206.4376 | 1.0134 | 4646.2499 | 1.2084 | 439.8123 | 0.19509
958 | MCLU-65to135-RFF-CZ09-2011-19IEER | CZ09 | RFF | 2011 | 65to135 | 12 | 19 | 9.5969 | 4335.3758 | 1.0346 | 4780.0924 | 1.2291 | 444.7165 | 0.19448
959 | MCLU-65to135-RFF-CZ09-2015-19IEER | CZ09 | RFF | 2015 | 65to135 | 12 | 19 | 9.3033 | 4251.0983 | 1.0207 | 4691.2686 | 1.2173 | 440.1703 | 0.19656
960 | MCLU-65to135-RFF-CZ09-2020-19IEER | CZ09 | RFF | 2020 | 65to135 | 12 | 19 | 8.9377 | 3882.7597 | 0.96711 | 4320.6353 | 1.1636 | 437.8756 | 0.19645
961 | MCLU-65to135-RSD-CZ09-2003-19IEER | CZ09 | RSD | 2003 | 65to135 | 12 | 19 | 18.7425 | 4031.1621 | 0.98003 | 4408.1363 | 1.178 | 376.9741 | 0.19796
962 | MCLU-65to135-RSD-CZ09-2007-19IEER | CZ09 | RSD | 2007 | 65to135 | 12 | 19 | 18.7425 | 4031.1621 | 0.98003 | 4408.1363 | 1.178 | 376.9741 | 0.19796
963 | MCLU-65to135-RSD-CZ09-2011-19IEER | CZ09 | RSD | 2011 | 65to135 | 12 | 19 | 17.7871 | 4242.2694 | 1.0149 | 4633.1913 | 1.2113 | 390.922 | 0.19641
964 | MCLU-65to135-RSD-CZ09-2015-19IEER | CZ09 | RSD | 2015 | 65to135 | 12 | 19 | 16.8052 | 4230.0666 | 1.0153 | 4618.466 | 1.2112 | 388.3993 | 0.1959
965 | MCLU-65to135-RSD-CZ09-2020-19IEER | CZ09 | RSD | 2020 | 65to135 | 12 | 19 | 15.9833 | 3758.9702 | 0.93738 | 4146.0937 | 1.1304 | 387.1235 | 0.19304
966 | MCLU-65to135-Rt3-CZ09-2003-19IEER | CZ09 | Rt3 | 2003 | 65to135 | 12 | 19 | 321.815 | 4310.8621 | 0.97363 | 4701.3679 | 1.1871 | 390.5058 | 0.21343
967 | MCLU-65to135-Rt3-CZ09-2007-19IEER | CZ09 | Rt3 | 2007 | 65to135 | 12 | 19 | 321.815 | 4310.8621 | 0.97363 | 4701.3679 | 1.1871 | 390.5058 | 0.21343
968 | MCLU-65to135-Rt3-CZ09-2011-19IEER | CZ09 | Rt3 | 2011 | 65to135 | 12 | 19 | 317.9174 | 4359.5518 | 0.97806 | 4749.0517 | 1.1911 | 389.4999 | 0.21305
969 | MCLU-65to135-Rt3-CZ09-2015-19IEER | CZ09 | Rt3 | 2015 | 65to135 | 12 | 19 | 307.5161 | 4068.9589 | 0.93137 | 4457.0621 | 1.1467 | 388.1033 | 0.21528
970 | MCLU-65to135-Rt3-CZ09-2020-19IEER | CZ09 | Rt3 | 2020 | 65to135 | 12 | 19 | 296.8893 | 3743.5635 | 0.88029 | 4130.2476 | 1.0972 | 386.6841 | 0.21694
971 | MCLU-65to135-RtL-CZ09-2003-19IEER | CZ09 | RtL | 2003 | 65to135 | 12 | 19 | 287.7665 | 4597.1746 | 1.015 | 5009.3021 | 1.226 | 412.1275 | 0.211
972 | MCLU-65to135-RtL-CZ09-2007-19IEER | CZ09 | RtL | 2007 | 65to135 | 12 | 19 | 287.7665 | 4597.1746 | 1.015 | 5009.3021 | 1.226 | 412.1275 | 0.211
973 | MCLU-65to135-RtL-CZ09-2011-19IEER | CZ09 | RtL | 2011 | 65to135 | 12 | 19 | 273.184 | 4831.0601 | 1.0506 | 5241.6593 | 1.2622 | 410.5993 | 0.21157
974 | MCLU-65to135-RtL-CZ09-2015-19IEER | CZ09 | RtL | 2015 | 65to135 | 12 | 19 | 265.1265 | 4644.2321 | 1.0323 | 5052.9847 | 1.2449 | 408.7526 | 0.21263
975 | MCLU-65to135-RtL-CZ09-2020-19IEER | CZ09 | RtL | 2020 | 65to135 | 12 | 19 | 252.1274 | 4425.7188 | 1.0179 | 4831.745 | 1.2321 | 406.0262 | 0.21422
976 | MCLU-65to135-RtS-CZ09-2003-19IEER | CZ09 | RtS | 2003 | 65to135 | 12 | 19 | 22.0784 | 2715.3898 | 0.6553 | 3092.5244 | 0.83903 | 377.1345 | 0.18373
977 | MCLU-65to135-RtS-CZ09-2007-19IEER | CZ09 | RtS | 2007 | 65to135 | 12 | 19 | 22.0784 | 2715.3898 | 0.6553 | 3092.5244 | 0.83903 | 377.1345 | 0.18373
978 | MCLU-65to135-RtS-CZ09-2011-19IEER | CZ09 | RtS | 2011 | 65to135 | 12 | 19 | 21.0559 | 2830.5927 | 0.66925 | 3206.1706 | 0.85297 | 375.5779 | 0.18372
979 | MCLU-65to135-RtS-CZ09-2015-19IEER | CZ09 | RtS | 2015 | 65to135 | 12 | 19 | 20.1959 | 2702.7812 | 0.64656 | 3075.2974 | 0.83184 | 372.5161 | 0.18528
980 | MCLU-65to135-RtS-CZ09-2020-19IEER | CZ09 | RtS | 2020 | 65to135 | 12 | 19 | 19.515 | 2540.6533 | 0.62253 | 2911.3924 | 0.80866 | 370.7391 | 0.18613
981 | MCLU-65to135-SCn-CZ09-2003-19IEER | CZ09 | SCn | 2003 | 65to135 | 12 | 19 | 393.9382 | 1979.3405 | 0.30922 | 2254.0627 | 0.41882 | 274.7221 | 0.1096
982 | MCLU-65to135-SCn-CZ09-2007-19IEER | CZ09 | SCn | 2007 | 65to135 | 12 | 19 | 393.9382 | 1979.3405 | 0.30922 | 2254.0627 | 0.41882 | 274.7221 | 0.1096
983 | MCLU-65to135-SCn-CZ09-2011-19IEER | CZ09 | SCn | 2011 | 65to135 | 12 | 19 | 322.8537 | 2358.6703 | 0.35725 | 2634.2052 | 0.46568 | 275.5349 | 0.10843
984 | MCLU-65to135-SCn-CZ09-2015-19IEER | CZ09 | SCn | 2015 | 65to135 | 12 | 19 | 329.7366 | 2309.0542 | 0.34357 | 2580.3891 | 0.45378 | 271.3349 | 0.1102
985 | MCLU-65to135-SCn-CZ09-2020-19IEER | CZ09 | SCn | 2020 | 65to135 | 12 | 19 | 300.786 | 2186.081 | 0.33929 | 2458.6693 | 0.44684 | 272.5883 | 0.10755
986 | MCLU-65to135-WRf-CZ09-2003-19IEER | CZ09 | WRf | 2003 | 65to135 | 12 | 19 | 18.0615 | 221490.4784 | 31.4982 | 221889.0486 | 31.6181 | 398.5703 | 0.11995
987 | MCLU-65to135-WRf-CZ09-2007-19IEER | CZ09 | WRf | 2007 | 65to135 | 12 | 19 | 15.1807 | 257355.1908 | 36.2728 | 257829.585 | 36.4155 | 474.3941 | 0.14267
988 | MCLU-65to135-WRf-CZ09-2011-19IEER | CZ09 | WRf | 2011 | 65to135 | 12 | 19 | 18.0615 | 198367.2362 | 26.1001 | 198724.3256 | 26.1962 | 357.0894 | 0.096045
989 | MCLU-65to135-WRf-CZ09-2015-19IEER | CZ09 | WRf | 2015 | 65to135 | 12 | 19 | 16.0098 | 223753.9206 | 29.4298 | 224137.9611 | 29.5341 | 384.0405 | 0.10428
990 | MCLU-65to135-WRf-CZ09-2020-19IEER | CZ09 | WRf | 2020 | 65to135 | 12 | 19 | 14.3883 | 235143.5163 | 30.9518 | 235539.2587 | 31.0539 | 395.7424 | 0.1021
991 | MCLU-65to135-Asm-CZ10-2003-19IEER | CZ10 | Asm | 2003 | 65to135 | 12 | 19 | 386.2762 | 1988.2608 | 0.71789 | 2391.0174 | 0.89778 | 402.7566 | 0.17988
992 | MCLU-65to135-Asm-CZ10-2007-19IEER | CZ10 | Asm | 2007 | 65to135 | 12 | 19 | 383.3941 | 2000.2619 | 0.72175 | 2403.4102 | 0.90143 | 403.1482 | 0.17967
993 | MCLU-65to135-Asm-CZ10-2011-19IEER | CZ10 | Asm | 2011 | 65to135 | 12 | 19 | 380.5003 | 2012.5255 | 0.72563 | 2416.0934 | 0.90507 | 403.5679 | 0.17944
994 | MCLU-65to135-Asm-CZ10-2015-19IEER | CZ10 | Asm | 2015 | 65to135 | 12 | 19 | 370.9854 | 2025.2431 | 0.72772 | 2426.2135 | 0.90855 | 400.9704 | 0.18083
995 | MCLU-65to135-Asm-CZ10-2020-19IEER | CZ10 | Asm | 2020 | 65to135 | 12 | 19 | 363.617 | 1904.5092 | 0.70536 | 2303.7108 | 0.88609 | 399.2016 | 0.18073
996 | MCLU-65to135-ECC-CZ10-2003-19IEER | CZ10 | ECC | 2003 | 65to135 | 12 | 19 | 915.1853 | 2305.5529 | 0.75311 | 2598.2775 | 0.95496 | 292.7245 | 0.20185
997 | MCLU-65to135-ECC-CZ10-2007-19IEER | CZ10 | ECC | 2007 | 65to135 | 12 | 19 | 913.1887 | 2309.6284 | 0.75297 | 2602.1263 | 0.95466 | 292.4979 | 0.20169
998 | MCLU-65to135-ECC-CZ10-2011-19IEER | CZ10 | ECC | 2011 | 65to135 | 12 | 19 | 911.0812 | 2312.2444 | 0.75249 | 2604.5121 | 0.95404 | 292.2677 | 0.20155
999 | MCLU-65to135-ECC-CZ10-2015-19IEER | CZ10 | ECC | 2015 | 65to135 | 12 | 19 | 877.4425 | 2360.469 | 0.75614 | 2648.333 | 0.95973 | 287.864 | 0.2036
1000 | MCLU-65to135-ECC-CZ10-2020-19IEER | CZ10 | ECC | 2020 | 65to135 | 12 | 19 | 846.8777 | 2070.9231 | 0.71053 | 2356.7338 | 0.91463 | 285.8107 | 0.2041
1001 | MCLU-65to135-EPr-CZ10-2003-19IEER | CZ10 | EPr | 2003 | 65to135 | 12 | 19 | 156.5924 | 1470.6966 | 0.3819 | 1652.9686 | 0.49724 | 182.2721 | 0.11534
1002 | MCLU-65to135-EPr-CZ10-2007-19IEER | CZ10 | EPr | 2007 | 65to135 | 12 | 19 | 154.9639 | 1499.5098 | 0.38499 | 1677.5285 | 0.49975 | 178.0187 | 0.11475
1003 | MCLU-65to135-EPr-CZ10-2011-19IEER | CZ10 | EPr | 2011 | 65to135 | 12 | 19 | 151.3611 | 1532.4196 | 0.38823 | 1711.5832 | 0.50279 | 179.1636 | 0.11456
1004 | MCLU-65to135-EPr-CZ10-2015-19IEER | CZ10 | EPr | 2015 | 65to135 | 12 | 19 | 143.3575 | 1570.5356 | 0.39052 | 1746.6152 | 0.50557 | 176.0796 | 0.11504
1005 | MCLU-65to135-EPr-CZ10-2020-19IEER | CZ10 | EPr | 2020 | 65to135 | 12 | 19 | 137.3748 | 1392.8014 | 0.36052 | 1568.1182 | 0.47447 | 175.3169 | 0.11395
1006 | MCLU-65to135-ERC-CZ10-2003-19IEER | CZ10 | ERC | 2003 | 65to135 | 12 | 19 | 7.1248 | 1211.5079 | 0.23767 | 1363.5321 | 0.28747 | 152.0241 | 0.049797
1007 | MCLU-65to135-ERC-CZ10-2007-19IEER | CZ10 | ERC | 2007 | 65to135 | 12 | 19 | 7.0969 | 1215.4694 | 0.23766 | 1367.2506 | 0.28696 | 151.7811 | 0.049299
1008 | MCLU-65to135-ERC-CZ10-2011-19IEER | CZ10 | ERC | 2011 | 65to135 | 12 | 19 | 6.9066 | 1240.2522 | 0.23628 | 1390.0386 | 0.28253 | 149.7864 | 0.046249
1009 | MCLU-65to135-ERC-CZ10-2015-19IEER | CZ10 | ERC | 2015 | 65to135 | 12 | 19 | 6.7793 | 1238.8549 | 0.23413 | 1382.6471 | 0.27786 | 143.7922 | 0.043733
1010 | MCLU-65to135-ERC-CZ10-2020-19IEER | CZ10 | ERC | 2020 | 65to135 | 12 | 19 | 6.6018 | 1085.2166 | 0.2084 | 1226.5044 | 0.24964 | 141.2878 | 0.041241
1011 | MCLU-65to135-ESe-CZ10-2003-19IEER | CZ10 | ESe | 2003 | 65to135 | 12 | 19 | 467.0812 | 1635.7545 | 0.3562 | 1836.7726 | 0.47226 | 201.0181 | 0.11606
1012 | MCLU-65to135-ESe-CZ10-2007-19IEER | CZ10 | ESe | 2007 | 65to135 | 12 | 19 | 465.2619 | 1641.2465 | 0.35637 | 1842.2105 | 0.47237 | 200.964 | 0.116
1013 | MCLU-65to135-ESe-CZ10-2011-19IEER | CZ10 | ESe | 2011 | 65to135 | 12 | 19 | 463.3332 | 1646.2577 | 0.35667 | 1847.2056 | 0.47236 | 200.9478 | 0.11569
1014 | MCLU-65to135-ESe-CZ10-2015-19IEER | CZ10 | ESe | 2015 | 65to135 | 12 | 19 | 452.6228 | 1654.6467 | 0.34835 | 1850.3495 | 0.46555 | 195.7028 | 0.11719
1015 | MCLU-65to135-ESe-CZ10-2020-19IEER | CZ10 | ESe | 2020 | 65to135 | 12 | 19 | 436.6911 | 1444.2187 | 0.33543 | 1637.9106 | 0.45214 | 193.6919 | 0.11672
1016 | MCLU-65to135-EUn-CZ10-2003-19IEER | CZ10 | EUn | 2003 | 65to135 | 12 | 19 | 2711.4893 | 2498.3013 | 0.9099 | 2799.1381 | 1.0825 | 300.8368 | 0.17262
1017 | MCLU-65to135-EUn-CZ10-2007-19IEER | CZ10 | EUn | 2007 | 65to135 | 12 | 19 | 2696.7832 | 2493.2896 | 0.90348 | 2793.9899 | 1.0758 | 300.7003 | 0.17231
1018 | MCLU-65to135-EUn-CZ10-2011-19IEER | CZ10 | EUn | 2011 | 65to135 | 12 | 19 | 2668.6215 | 2511.194 | 0.90852 | 2812.8976 | 1.0812 | 301.7036 | 0.17272
1019 | MCLU-65to135-EUn-CZ10-2015-19IEER | CZ10 | EUn | 2015 | 65to135 | 12 | 19 | 2530.6601 | 2577.2748 | 0.92536 | 2878.0981 | 1.1006 | 300.8233 | 0.1752
1020 | MCLU-65to135-EUn-CZ10-2020-19IEER | CZ10 | EUn | 2020 | 65to135 | 12 | 19 | 2436.9831 | 2348.9228 | 0.87924 | 2646.7432 | 1.054 | 297.8204 | 0.17475
1021 | MCLU-65to135-Gro-CZ10-2003-19IEER | CZ10 | Gro | 2003 | 65to135 | 12 | 19 | 135.7533 | 12383.7165 | 1.9465 | 12822.7862 | 2.1221 | 439.0697 | 0.17555
1022 | MCLU-65to135-Gro-CZ10-2007-19IEER | CZ10 | Gro | 2007 | 65to135 | 12 | 19 | 133.6875 | 11462.4206 | 1.8373 | 11899.6797 | 2.0305 | 437.2591 | 0.19316
1023 | MCLU-65to135-Gro-CZ10-2011-19IEER | CZ10 | Gro | 2011 | 65to135 | 12 | 19 | 131.5975 | 11638.056 | 1.8622 | 12073.0795 | 2.0558 | 435.0235 | 0.19353
1024 | MCLU-65to135-Gro-CZ10-2015-19IEER | CZ10 | Gro | 2015 | 65to135 | 12 | 19 | 127.2762 | 11533.5838 | 1.8455 | 11956.7618 | 2.0354 | 423.178 | 0.18988
1025 | MCLU-65to135-Gro-CZ10-2020-19IEER | CZ10 | Gro | 2020 | 65to135 | 12 | 19 | 123.4746 | 11523.3296 | 1.8393 | 11937.9462 | 2.0268 | 414.6166 | 0.18757
1026 | MCLU-65to135-Hsp-CZ10-2003-19IEER | CZ10 | Hsp | 2003 | 65to135 | 12 | 19 | 681.5543 | 4238.4973 | 0.78289 | 4743.9351 | 0.96568 | 505.4378 | 0.18279
1027 | MCLU-65to135-Hsp-CZ10-2007-19IEER | CZ10 | Hsp | 2007 | 65to135 | 12 | 19 | 681.5532 | 4237.8026 | 0.78209 | 4742.8347 | 0.96458 | 505.0321 | 0.18249
1028 | MCLU-65to135-Hsp-CZ10-2011-19IEER | CZ10 | Hsp | 2011 | 65to135 | 12 | 19 | 681.5521 | 4237.0964 | 0.78126 | 4741.7149 | 0.96346 | 504.6185 | 0.1822
1029 | MCLU-65to135-Hsp-CZ10-2015-19IEER | CZ10 | Hsp | 2015 | 65to135 | 12 | 19 | 680.6818 | 4209.3085 | 0.76982 | 4712.2733 | 0.95279 | 502.9647 | 0.18298
1030 | MCLU-65to135-Hsp-CZ10-2020-19IEER | CZ10 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3690.8897 | 0.69074 | 4188.6401 | 0.8721 | 497.7505 | 0.18136
1031 | MCLU-65to135-Htl-CZ10-2003-19IEER | CZ10 | Htl | 2003 | 65to135 | 12 | 19 | 273.5987 | 3230.5587 | 0.88945 | 3354.8518 | 0.93684 | 124.2932 | 0.047393
1032 | MCLU-65to135-Htl-CZ10-2007-19IEER | CZ10 | Htl | 2007 | 65to135 | 12 | 19 | 273.2653 | 3101.5919 | 0.83077 | 3225.891 | 0.8781 | 124.2991 | 0.047332
1033 | MCLU-65to135-Htl-CZ10-2011-19IEER | CZ10 | Htl | 2011 | 65to135 | 12 | 19 | 266.3102 | 3145.3635 | 0.83619 | 3271.6749 | 0.88432 | 126.3114 | 0.048133
1034 | MCLU-65to135-Htl-CZ10-2015-19IEER | CZ10 | Htl | 2015 | 65to135 | 12 | 19 | 239.6051 | 3240.9926 | 0.84154 | 3372.783 | 0.89258 | 131.7903 | 0.051047
1035 | MCLU-65to135-Htl-CZ10-2020-19IEER | CZ10 | Htl | 2020 | 65to135 | 12 | 19 | 237.6665 | 3146.3482 | 0.83044 | 3275.2258 | 0.88057 | 128.8775 | 0.05013
1036 | MCLU-65to135-MBT-CZ10-2003-19IEER | CZ10 | MBT | 2003 | 65to135 | 12 | 19 | 402.0631 | 3689.5443 | 0.56407 | 3971.7947 | 0.70969 | 282.2504 | 0.14562
1037 | MCLU-65to135-MBT-CZ10-2007-19IEER | CZ10 | MBT | 2007 | 65to135 | 12 | 19 | 395.8077 | 3746.3233 | 0.56902 | 4028.4818 | 0.71433 | 282.1584 | 0.14531
1038 | MCLU-65to135-MBT-CZ10-2011-19IEER | CZ10 | MBT | 2011 | 65to135 | 12 | 19 | 374.3653 | 3902.9871 | 0.58198 | 4185.2957 | 0.7264 | 282.3087 | 0.14443
1039 | MCLU-65to135-MBT-CZ10-2015-19IEER | CZ10 | MBT | 2015 | 65to135 | 12 | 19 | 365.3972 | 3957.1918 | 0.58632 | 4238.6327 | 0.73075 | 281.441 | 0.14443
1040 | MCLU-65to135-MBT-CZ10-2020-19IEER | CZ10 | MBT | 2020 | 65to135 | 12 | 19 | 341.9782 | 3785.693 | 0.56847 | 4064.9077 | 0.71297 | 279.2147 | 0.1445
1041 | MCLU-65to135-MLI-CZ10-2003-19IEER | CZ10 | MLI | 2003 | 65to135 | 12 | 19 | 253.0875 | 2690.3445 | 0.43707 | 2943.565 | 0.54374 | 253.2205 | 0.10668
1042 | MCLU-65to135-MLI-CZ10-2007-19IEER | CZ10 | MLI | 2007 | 65to135 | 12 | 19 | 248.2777 | 2737.3371 | 0.4419 | 2990.0265 | 0.54876 | 252.6894 | 0.10685
1043 | MCLU-65to135-MLI-CZ10-2011-19IEER | CZ10 | MLI | 2011 | 65to135 | 12 | 19 | 243.3677 | 2787.4479 | 0.44703 | 3039.6728 | 0.55395 | 252.225 | 0.10691
1044 | MCLU-65to135-MLI-CZ10-2015-19IEER | CZ10 | MLI | 2015 | 65to135 | 12 | 19 | 240.8468 | 2796.4692 | 0.44864 | 3048.3066 | 0.55551 | 251.8373 | 0.10686
1045 | MCLU-65to135-MLI-CZ10-2020-19IEER | CZ10 | MLI | 2020 | 65to135 | 12 | 19 | 227.1543 | 2491.9902 | 0.41685 | 2740.9081 | 0.52438 | 248.9179 | 0.10753
1046 | MCLU-65to135-Mtl-CZ10-2003-19IEER | CZ10 | Mtl | 2003 | 65to135 | 12 | 19 | 49.6297 | 3121.7107 | 0.8386 | 3218.2205 | 0.87123 | 96.5098 | 0.032633
1047 | MCLU-65to135-Mtl-CZ10-2007-19IEER | CZ10 | Mtl | 2007 | 65to135 | 12 | 19 | 49.6297 | 2985.8338 | 0.77556 | 3082.321 | 0.80814 | 96.4871 | 0.03258
1048 | MCLU-65to135-Mtl-CZ10-2011-19IEER | CZ10 | Mtl | 2011 | 65to135 | 12 | 19 | 48.2103 | 3028.2789 | 0.78006 | 3125.2576 | 0.8127 | 96.9787 | 0.032643
1049 | MCLU-65to135-Mtl-CZ10-2015-19IEER | CZ10 | Mtl | 2015 | 65to135 | 12 | 19 | 41.1817 | 3257.894 | 0.78981 | 3361.6526 | 0.82516 | 103.7587 | 0.035347
1050 | MCLU-65to135-Mtl-CZ10-2020-19IEER | CZ10 | Mtl | 2020 | 65to135 | 12 | 19 | 41.0503 | 3182.0274 | 0.78027 | 3283.7946 | 0.81514 | 101.7672 | 0.034869
1051 | MCLU-65to135-Nrs-CZ10-2003-19IEER | CZ10 | Nrs | 2003 | 65to135 | 12 | 19 | 183.7569 | 4599.2155 | 0.93546 | 4837.652 | 1.0269 | 238.4365 | 0.091413
1052 | MCLU-65to135-Nrs-CZ10-2007-19IEER | CZ10 | Nrs | 2007 | 65to135 | 12 | 19 | 183.7048 | 4501.142 | 0.89855 | 4739.5085 | 0.98969 | 238.3665 | 0.09114
1053 | MCLU-65to135-Nrs-CZ10-2011-19IEER | CZ10 | Nrs | 2011 | 65to135 | 12 | 19 | 183.2332 | 4522.7409 | 0.89064 | 4760.242 | 0.98106 | 237.5011 | 0.090422
1054 | MCLU-65to135-Nrs-CZ10-2015-19IEER | CZ10 | Nrs | 2015 | 65to135 | 12 | 19 | 182.2252 | 4413.0163 | 0.84265 | 4646.6512 | 0.93259 | 233.6349 | 0.089941
1055 | MCLU-65to135-Nrs-CZ10-2020-19IEER | CZ10 | Nrs | 2020 | 65to135 | 12 | 19 | 181.8171 | 4043.1682 | 0.7829 | 4272.7844 | 0.87167 | 229.6162 | 0.088774
1056 | MCLU-65to135-OfL-CZ10-2003-19IEER | CZ10 | OfL | 2003 | 65to135 | 12 | 19 | 489.1262 | 3278.7286 | 0.53558 | 3563.9314 | 0.60909 | 285.2028 | 0.073511
1057 | MCLU-65to135-OfL-CZ10-2007-19IEER | CZ10 | OfL | 2007 | 65to135 | 12 | 19 | 488.3953 | 3283.3089 | 0.53612 | 3568.5681 | 0.6096 | 285.2592 | 0.073483
1058 | MCLU-65to135-OfL-CZ10-2011-19IEER | CZ10 | OfL | 2011 | 65to135 | 12 | 19 | 467.8037 | 3381.2426 | 0.54333 | 3666.8511 | 0.61682 | 285.6086 | 0.073487
1059 | MCLU-65to135-OfL-CZ10-2015-19IEER | CZ10 | OfL | 2015 | 65to135 | 12 | 19 | 468.6707 | 3315.2369 | 0.53822 | 3596.4184 | 0.61218 | 281.1815 | 0.073964
1060 | MCLU-65to135-OfL-CZ10-2020-19IEER | CZ10 | OfL | 2020 | 65to135 | 12 | 19 | 456.4715 | 3153.656 | 0.5205 | 3433.8475 | 0.59441 | 280.1916 | 0.073911
1061 | MCLU-65to135-OfS-CZ10-2003-19IEER | CZ10 | OfS | 2003 | 65to135 | 12 | 19 | 33.4442 | 2420.0803 | 0.40439 | 2700.2003 | 0.4776 | 280.12 | 0.073208
1062 | MCLU-65to135-OfS-CZ10-2007-19IEER | CZ10 | OfS | 2007 | 65to135 | 12 | 19 | 33.3534 | 2425.6565 | 0.40451 | 2705.6773 | 0.47774 | 280.0208 | 0.07323
1063 | MCLU-65to135-OfS-CZ10-2011-19IEER | CZ10 | OfS | 2011 | 65to135 | 12 | 19 | 32.716 | 2445.3692 | 0.40416 | 2725.5238 | 0.47719 | 280.1547 | 0.073035
1064 | MCLU-65to135-OfS-CZ10-2015-19IEER | CZ10 | OfS | 2015 | 65to135 | 12 | 19 | 29.7921 | 2607.0914 | 0.42168 | 2882.4946 | 0.49547 | 275.4032 | 0.073784
1065 | MCLU-65to135-OfS-CZ10-2020-19IEER | CZ10 | OfS | 2020 | 65to135 | 12 | 19 | 29.041 | 2459.8488 | 0.40173 | 2734.0803 | 0.47521 | 274.2315 | 0.073485
1066 | MCLU-65to135-RFF-CZ10-2003-19IEER | CZ10 | RFF | 2003 | 65to135 | 12 | 19 | 8.4822 | 4962.7509 | 1.1913 | 5444.7215 | 1.3751 | 481.9706 | 0.18383
1067 | MCLU-65to135-RFF-CZ10-2007-19IEER | CZ10 | RFF | 2007 | 65to135 | 12 | 19 | 8.3993 | 5008.0243 | 1.1995 | 5492.2904 | 1.3829 | 484.2661 | 0.18341
1068 | MCLU-65to135-RFF-CZ10-2011-19IEER | CZ10 | RFF | 2011 | 65to135 | 12 | 19 | 8.3132 | 5055.9561 | 1.2086 | 5543.0952 | 1.3913 | 487.1391 | 0.18273
1069 | MCLU-65to135-RFF-CZ10-2015-19IEER | CZ10 | RFF | 2015 | 65to135 | 12 | 19 | 8.3278 | 4813.1205 | 1.1619 | 5294.7124 | 1.347 | 481.5919 | 0.18505
1070 | MCLU-65to135-RFF-CZ10-2020-19IEER | CZ10 | RFF | 2020 | 65to135 | 12 | 19 | 7.9767 | 4409.5033 | 1.1051 | 4894.0002 | 1.2904 | 484.4969 | 0.18522
1071 | MCLU-65to135-RSD-CZ10-2003-19IEER | CZ10 | RSD | 2003 | 65to135 | 12 | 19 | 15.8914 | 4744.764 | 1.128 | 5179.6148 | 1.3175 | 434.8508 | 0.18953
1072 | MCLU-65to135-RSD-CZ10-2007-19IEER | CZ10 | RSD | 2007 | 65to135 | 12 | 19 | 15.7133 | 4795.733 | 1.1373 | 5233.8582 | 1.3266 | 438.1252 | 0.18932
1073 | MCLU-65to135-RSD-CZ10-2011-19IEER | CZ10 | RSD | 2011 | 65to135 | 12 | 19 | 15.3981 | 4893.4126 | 1.1523 | 5338.563 | 1.3413 | 445.1504 | 0.189
1074 | MCLU-65to135-RSD-CZ10-2015-19IEER | CZ10 | RSD | 2015 | 65to135 | 12 | 19 | 15.2366 | 4718.7887 | 1.1221 | 5154.3335 | 1.3118 | 435.5447 | 0.18976
1075 | MCLU-65to135-RSD-CZ10-2020-19IEER | CZ10 | RSD | 2020 | 65to135 | 12 | 19 | 14.4004 | 4224.2609 | 1.0433 | 4656.6864 | 1.2327 | 432.4255 | 0.18933
1076 | MCLU-65to135-Rt3-CZ10-2003-19IEER | CZ10 | Rt3 | 2003 | 65to135 | 12 | 19 | 292.3969 | 4816.4257 | 1.0821 | 5227.0637 | 1.2875 | 410.6381 | 0.20549
1077 | MCLU-65to135-Rt3-CZ10-2007-19IEER | CZ10 | Rt3 | 2007 | 65to135 | 12 | 19 | 291.4187 | 4831.4248 | 1.0835 | 5241.8475 | 1.289 | 410.4227 | 0.20544
1078 | MCLU-65to135-Rt3-CZ10-2011-19IEER | CZ10 | Rt3 | 2011 | 65to135 | 12 | 19 | 290.4428 | 4846.4525 | 1.085 | 5256.6776 | 1.2904 | 410.2251 | 0.2054
1079 | MCLU-65to135-Rt3-CZ10-2015-19IEER | CZ10 | Rt3 | 2015 | 65to135 | 12 | 19 | 281.8416 | 4515.0639 | 1.0327 | 4924.0797 | 1.2404 | 409.0158 | 0.20769
1080 | MCLU-65to135-Rt3-CZ10-2020-19IEER | CZ10 | Rt3 | 2020 | 65to135 | 12 | 19 | 271.2678 | 4169.7241 | 0.97997 | 4577.7474 | 1.1891 | 408.0233 | 0.20911
1081 | MCLU-65to135-RtL-CZ10-2003-19IEER | CZ10 | RtL | 2003 | 65to135 | 12 | 19 | 257.8681 | 5190.9783 | 1.1306 | 5625.1522 | 1.3335 | 434.1739 | 0.20292
1082 | MCLU-65to135-RtL-CZ10-2007-19IEER | CZ10 | RtL | 2007 | 65to135 | 12 | 19 | 254.0047 | 5266.4636 | 1.1427 | 5700.4853 | 1.3459 | 434.0217 | 0.20325
1083 | MCLU-65to135-RtL-CZ10-2011-19IEER | CZ10 | RtL | 2011 | 65to135 | 12 | 19 | 250.0477 | 5346.5057 | 1.1557 | 5780.4346 | 1.3589 | 433.9289 | 0.20321
1084 | MCLU-65to135-RtL-CZ10-2015-19IEER | CZ10 | RtL | 2015 | 65to135 | 12 | 19 | 243.1062 | 5135.4559 | 1.1348 | 5568.3324 | 1.3389 | 432.8765 | 0.20409
1085 | MCLU-65to135-RtL-CZ10-2020-19IEER | CZ10 | RtL | 2020 | 65to135 | 12 | 19 | 229.95 | 4922.8178 | 1.1252 | 5353.8559 | 1.3302 | 431.0381 | 0.20498
1086 | MCLU-65to135-RtS-CZ10-2003-19IEER | CZ10 | RtS | 2003 | 65to135 | 12 | 19 | 19.3178 | 3150.8139 | 0.75089 | 3550.7837 | 0.93272 | 399.9698 | 0.18184
1087 | MCLU-65to135-RtS-CZ10-2007-19IEER | CZ10 | RtS | 2007 | 65to135 | 12 | 19 | 19.0543 | 3189.3535 | 0.75611 | 3589.0831 | 0.93771 | 399.7296 | 0.1816
1088 | MCLU-65to135-RtS-CZ10-2011-19IEER | CZ10 | RtS | 2011 | 65to135 | 12 | 19 | 18.7846 | 3230.1422 | 0.76153 | 3629.6198 | 0.94309 | 399.4776 | 0.18156
1089 | MCLU-65to135-RtS-CZ10-2015-19IEER | CZ10 | RtS | 2015 | 65to135 | 12 | 19 | 18.5345 | 3009.192 | 0.72274 | 3406.1803 | 0.90557 | 396.9883 | 0.18283
1090 | MCLU-65to135-RtS-CZ10-2020-19IEER | CZ10 | RtS | 2020 | 65to135 | 12 | 19 | 17.83 | 2843.6802 | 0.70028 | 3239.9197 | 0.88358 | 396.2395 | 0.1833
1091 | MCLU-65to135-SCn-CZ10-2003-19IEER | CZ10 | SCn | 2003 | 65to135 | 12 | 19 | 322.8126 | 2419.2913 | 0.38628 | 2722.4795 | 0.49855 | 303.1882 | 0.11227
1092 | MCLU-65to135-SCn-CZ10-2007-19IEER | CZ10 | SCn | 2007 | 65to135 | 12 | 19 | 305.7687 | 2537.2783 | 0.40286 | 2842.6513 | 0.51363 | 305.373 | 0.11077
1093 | MCLU-65to135-SCn-CZ10-2011-19IEER | CZ10 | SCn | 2011 | 65to135 | 12 | 19 | 293.4673 | 2627.0635 | 0.41282 | 2929.6379 | 0.52239 | 302.5744 | 0.10957
1094 | MCLU-65to135-SCn-CZ10-2015-19IEER | CZ10 | SCn | 2015 | 65to135 | 12 | 19 | 295.6877 | 2605.1972 | 0.40506 | 2906.0131 | 0.51671 | 300.8159 | 0.11165
1095 | MCLU-65to135-SCn-CZ10-2020-19IEER | CZ10 | SCn | 2020 | 65to135 | 12 | 19 | 270.4463 | 2468.6759 | 0.40302 | 2765.2982 | 0.50899 | 296.6222 | 0.10596
1096 | MCLU-65to135-WRf-CZ10-2003-19IEER | CZ10 | WRf | 2003 | 65to135 | 12 | 19 | 13.339 | 289157.3793 | 39.6727 | 289636.5308 | 39.8095 | 479.1514 | 0.13676
1097 | MCLU-65to135-WRf-CZ10-2007-19IEER | CZ10 | WRf | 2007 | 65to135 | 12 | 19 | 13.4835 | 274958.9933 | 36.4231 | 275422.4849 | 36.5524 | 463.4916 | 0.12929
1098 | MCLU-65to135-WRf-CZ10-2011-19IEER | CZ10 | WRf | 2011 | 65to135 | 12 | 19 | 15.14 | 236492.162 | 30.3593 | 236900.5029 | 30.465 | 408.3409 | 0.10571
1099 | MCLU-65to135-WRf-CZ10-2015-19IEER | CZ10 | WRf | 2015 | 65to135 | 12 | 19 | 14.8547 | 241031.7626 | 30.9448 | 241413.483 | 31.0406 | 381.7204 | 0.095795
1100 | MCLU-65to135-WRf-CZ10-2020-19IEER | CZ10 | WRf | 2020 | 65to135 | 12 | 19 | 14.7384 | 229441.0923 | 29.3577 | 229816.3486 | 29.4529 | 375.2563 | 0.095193
1101 | MCLU-65to135-Asm-CZ11-2003-19IEER | CZ11 | Asm | 2003 | 65to135 | 12 | 19 | 431.3541 | 1820.7511 | 0.68601 | 2222.7981 | 0.89049 | 402.0469 | 0.20448
1102 | MCLU-65to135-Asm-CZ11-2007-19IEER | CZ11 | Asm | 2007 | 65to135 | 12 | 19 | 427.7739 | 1832.7468 | 0.68959 | 2234.9898 | 0.89382 | 402.2429 | 0.20423
1103 | MCLU-65to135-Asm-CZ11-2011-19IEER | CZ11 | Asm | 2011 | 65to135 | 12 | 19 | 410.6343 | 1896.3299 | 0.69204 | 2299.7866 | 0.89673 | 403.4567 | 0.20469
1104 | MCLU-65to135-Asm-CZ11-2015-19IEER | CZ11 | Asm | 2015 | 65to135 | 12 | 19 | 398.8772 | 1912.9974 | 0.69134 | 2313.824 | 0.89697 | 400.8266 | 0.20563
1105 | MCLU-65to135-Asm-CZ11-2020-19IEER | CZ11 | Asm | 2020 | 65to135 | 12 | 19 | 390.6875 | 1803.8184 | 0.67108 | 2203.5458 | 0.87664 | 399.7274 | 0.20557
1106 | MCLU-65to135-ECC-CZ11-2003-19IEER | CZ11 | ECC | 2003 | 65to135 | 12 | 19 | 906.5521 | 2345.4076 | 0.45376 | 2659.1468 | 0.63204 | 313.7392 | 0.17827
1107 | MCLU-65to135-ECC-CZ11-2007-19IEER | CZ11 | ECC | 2007 | 65to135 | 12 | 19 | 904.1514 | 2350.3312 | 0.45322 | 2663.7198 | 0.63117 | 313.3886 | 0.17795
1108 | MCLU-65to135-ECC-CZ11-2011-19IEER | CZ11 | ECC | 2011 | 65to135 | 12 | 19 | 880.3452 | 2392.9697 | 0.44039 | 2702.0652 | 0.61693 | 309.0955 | 0.17654
1109 | MCLU-65to135-ECC-CZ11-2015-19IEER | CZ11 | ECC | 2015 | 65to135 | 12 | 19 | 841.0557 | 2454.2971 | 0.43191 | 2759.7588 | 0.60973 | 305.4617 | 0.17782
1110 | MCLU-65to135-ECC-CZ11-2020-19IEER | CZ11 | ECC | 2020 | 65to135 | 12 | 19 | 810.6202 | 2159.5701 | 0.40715 | 2464.4887 | 0.58373 | 304.9186 | 0.17659
1111 | MCLU-65to135-EPr-CZ11-2003-19IEER | CZ11 | EPr | 2003 | 65to135 | 12 | 19 | 155.297 | 1497.6272 | 0.11773 | 1685.0983 | 0.18484 | 187.4711 | 0.067112
1112 | MCLU-65to135-EPr-CZ11-2007-19IEER | CZ11 | EPr | 2007 | 65to135 | 12 | 19 | 153.8205 | 1508.6963 | 0.11539 | 1695.8364 | 0.18106 | 187.1401 | 0.065669
1113 | MCLU-65to135-EPr-CZ11-2011-19IEER | CZ11 | EPr | 2011 | 65to135 | 12 | 19 | 150.2955 | 1538.3382 | 0.11176 | 1725.2369 | 0.17425 | 186.8986 | 0.062488
1114 | MCLU-65to135-EPr-CZ11-2015-19IEER | CZ11 | EPr | 2015 | 65to135 | 12 | 19 | 142.0382 | 1573.0187 | 0.092636 | 1753.079 | 0.14103 | 180.0603 | 0.048389
1115 | MCLU-65to135-EPr-CZ11-2020-19IEER | CZ11 | EPr | 2020 | 65to135 | 12 | 19 | 135.2058 | 1404.7638 | 0.076274 | 1583.8067 | 0.11929 | 179.0429 | 0.04302
1116 | MCLU-65to135-ERC-CZ11-2003-19IEER | CZ11 | ERC | 2003 | 65to135 | 12 | 19 | 7.1857 | 1212.2937 | 0.15866 | 1377.9056 | 0.25737 | 165.612 | 0.098716
1117 | MCLU-65to135-ERC-CZ11-2007-19IEER | CZ11 | ERC | 2007 | 65to135 | 12 | 19 | 7.1603 | 1215.4408 | 0.15753 | 1380.3411 | 0.25434 | 164.9002 | 0.096808
1118 | MCLU-65to135-ERC-CZ11-2011-19IEER | CZ11 | ERC | 2011 | 65to135 | 12 | 19 | 6.9447 | 1241.6716 | 0.14931 | 1402.246 | 0.23748 | 160.5744 | 0.08817
1119 | MCLU-65to135-ERC-CZ11-2015-19IEER | CZ11 | ERC | 2015 | 65to135 | 12 | 19 | 6.8383 | 1234.4461 | 0.14132 | 1388.1535 | 0.22395 | 153.7074 | 0.082634
1120 | MCLU-65to135-ERC-CZ11-2020-19IEER | CZ11 | ERC | 2020 | 65to135 | 12 | 19 | 6.5485 | 1095.5134 | 0.12907 | 1246.1865 | 0.20589 | 150.6731 | 0.076821
1121 | MCLU-65to135-ESe-CZ11-2003-19IEER | CZ11 | ESe | 2003 | 65to135 | 12 | 19 | 459.0353 | 1670.7846 | 0.17137 | 1890.1258 | 0.25551 | 219.3412 | 0.08414
1122 | MCLU-65to135-ESe-CZ11-2007-19IEER | CZ11 | ESe | 2007 | 65to135 | 12 | 19 | 457.1405 | 1676.493 | 0.17086 | 1895.6274 | 0.25426 | 219.1344 | 0.083397
1123 | MCLU-65to135-ESe-CZ11-2011-19IEER | CZ11 | ESe | 2011 | 65to135 | 12 | 19 | 444.5822 | 1706.4002 | 0.15865 | 1918.7419 | 0.2312 | 212.3417 | 0.072543
1124 | MCLU-65to135-ESe-CZ11-2015-19IEER | CZ11 | ESe | 2015 | 65to135 | 12 | 19 | 431.9189 | 1719.4476 | 0.14614 | 1924.8081 | 0.20925 | 205.3604 | 0.063113
1125 | MCLU-65to135-ESe-CZ11-2020-19IEER | CZ11 | ESe | 2020 | 65to135 | 12 | 19 | 416.3355 | 1502.3286 | 0.12984 | 1706.981 | 0.19116 | 204.6524 | 0.06132
1126 | MCLU-65to135-EUn-CZ11-2003-19IEER | CZ11 | EUn | 2003 | 65to135 | 12 | 19 | 2737.0244 | 2557.7961 | 0.68812 | 2870.0369 | 0.87505 | 312.2409 | 0.18694
1127 | MCLU-65to135-EUn-CZ11-2007-19IEER | CZ11 | EUn | 2007 | 65to135 | 12 | 19 | 2719.6547 | 2550.024 | 0.67897 | 2862.2048 | 0.86601 | 312.1808 | 0.18704
1128 | MCLU-65to135-EUn-CZ11-2011-19IEER | CZ11 | EUn | 2011 | 65to135 | 12 | 19 | 2614.7085 | 2629.168 | 0.67898 | 2941.4385 | 0.86705 | 312.2705 | 0.18807
1129 | MCLU-65to135-EUn-CZ11-2015-19IEER | CZ11 | EUn | 2015 | 65to135 | 12 | 19 | 2462.5801 | 2705.9658 | 0.67434 | 3018.2706 | 0.86715 | 312.3047 | 0.19281
1130 | MCLU-65to135-EUn-CZ11-2020-19IEER | CZ11 | EUn | 2020 | 65to135 | 12 | 19 | 2373.1591 | 2475.1911 | 0.65276 | 2785.9017 | 0.84388 | 310.7106 | 0.19112
1131 | MCLU-65to135-Gro-CZ11-2003-19IEER | CZ11 | Gro | 2003 | 65to135 | 12 | 19 | 143.8444 | 11710.8514 | 1.8854 | 12144.1297 | 2.077 | 433.2783 | 0.19165
1132 | MCLU-65to135-Gro-CZ11-2007-19IEER | CZ11 | Gro | 2007 | 65to135 | 12 | 19 | 141.3917 | 10776.7476 | 1.7592 | 11215.6461 | 1.9703 | 438.8985 | 0.21109
1133 | MCLU-65to135-Gro-CZ11-2011-19IEER | CZ11 | Gro | 2011 | 65to135 | 12 | 19 | 131.1774 | 11580.8966 | 1.8561 | 12013.2946 | 2.0655 | 432.398 | 0.20933
1134 | MCLU-65to135-Gro-CZ11-2015-19IEER | CZ11 | Gro | 2015 | 65to135 | 12 | 19 | 126.7072 | 11482.2236 | 1.8348 | 11902.7249 | 2.0389 | 420.5013 | 0.20415
1135 | MCLU-65to135-Gro-CZ11-2020-19IEER | CZ11 | Gro | 2020 | 65to135 | 12 | 19 | 122.2884 | 11525.68 | 1.8319 | 11936.9351 | 2.0319 | 411.2551 | 0.19993
1136 | MCLU-65to135-Hsp-CZ11-2003-19IEER | CZ11 | Hsp | 2003 | 65to135 | 12 | 19 | 686.1528 | 4254.3984 | 0.82075 | 4807.7076 | 1.0465 | 553.3092 | 0.22572
1137 | MCLU-65to135-Hsp-CZ11-2007-19IEER | CZ11 | Hsp | 2007 | 65to135 | 12 | 19 | 685.9837 | 4254.4742 | 0.81985 | 4807.3699 | 1.0453 | 552.8957 | 0.22542
1138 | MCLU-65to135-Hsp-CZ11-2011-19IEER | CZ11 | Hsp | 2011 | 65to135 | 12 | 19 | 680.4571 | 4260.0916 | 0.79261 | 4809.2486 | 1.0203 | 549.157 | 0.22771
1139 | MCLU-65to135-Hsp-CZ11-2015-19IEER | CZ11 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 4224.9902 | 0.7759 | 4772.7584 | 1.0048 | 547.7683 | 0.22892
1140 | MCLU-65to135-Hsp-CZ11-2020-19IEER | CZ11 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3709.9622 | 0.69473 | 4251.0238 | 0.92159 | 541.0616 | 0.22686
1141 | MCLU-65to135-Htl-CZ11-2003-19IEER | CZ11 | Htl | 2003 | 65to135 | 12 | 19 | 300.4398 | 3260.3032 | 0.9736 | 3390.8209 | 1.0319 | 130.5177 | 0.058294
1142 | MCLU-65to135-Htl-CZ11-2007-19IEER | CZ11 | Htl | 2007 | 65to135 | 12 | 19 | 300.0181 | 3120.463 | 0.90459 | 3251.0746 | 0.96289 | 130.6116 | 0.058293
1143 | MCLU-65to135-Htl-CZ11-2011-19IEER | CZ11 | Htl | 2011 | 65to135 | 12 | 19 | 289.7445 | 3159.8887 | 0.90813 | 3290.632 | 0.96666 | 130.7433 | 0.058529
1144 | MCLU-65to135-Htl-CZ11-2015-19IEER | CZ11 | Htl | 2015 | 65to135 | 12 | 19 | 259.8157 | 3251.6875 | 0.9036 | 3388.8362 | 0.96605 | 137.1487 | 0.062452
1145 | MCLU-65to135-Htl-CZ11-2020-19IEER | CZ11 | Htl | 2020 | 65to135 | 12 | 19 | 257.7548 | 3165.0388 | 0.89382 | 3299.4669 | 0.95501 | 134.4281 | 0.061192
1146 | MCLU-65to135-MBT-CZ11-2003-19IEER | CZ11 | MBT | 2003 | 65to135 | 12 | 19 | 442.2437 | 3344.7392 | 0.53977 | 3629.2983 | 0.71628 | 284.5591 | 0.17651
1147 | MCLU-65to135-MBT-CZ11-2007-19IEER | CZ11 | MBT | 2007 | 65to135 | 12 | 19 | 434.7723 | 3398.6559 | 0.54339 | 3681.9264 | 0.71961 | 283.2706 | 0.17622
1148 | MCLU-65to135-MBT-CZ11-2011-19IEER | CZ11 | MBT | 2011 | 65to135 | 12 | 19 | 410.6182 | 3537.8085 | 0.55124 | 3818.7763 | 0.72787 | 280.9678 | 0.17663
1149 | MCLU-65to135-MBT-CZ11-2015-19IEER | CZ11 | MBT | 2015 | 65to135 | 12 | 19 | 401.2922 | 3580.9009 | 0.55294 | 3860.8544 | 0.73016 | 279.9535 | 0.17722
1150 | MCLU-65to135-MBT-CZ11-2020-19IEER | CZ11 | MBT | 2020 | 65to135 | 12 | 19 | 376.047 | 3423.0165 | 0.53608 | 3701.1999 | 0.71417 | 278.1834 | 0.17809
1151 | MCLU-65to135-MLI-CZ11-2003-19IEER | CZ11 | MLI | 2003 | 65to135 | 12 | 19 | 280.0058 | 2465.0454 | 0.42402 | 2729.3386 | 0.55781 | 264.2932 | 0.13379
1152 | MCLU-65to135-MLI-CZ11-2007-19IEER | CZ11 | MLI | 2007 | 65to135 | 12 | 19 | 274.5528 | 2507.9135 | 0.42599 | 2771.7801 | 0.55968 | 263.8667 | 0.13369
1153 | MCLU-65to135-MLI-CZ11-2011-19IEER | CZ11 | MLI | 2011 | 65to135 | 12 | 19 | 242.0528 | 2804.3733 | 0.43762 | 3065.5117 | 0.56851 | 261.1384 | 0.13089
1154 | MCLU-65to135-MLI-CZ11-2015-19IEER | CZ11 | MLI | 2015 | 65to135 | 12 | 19 | 239.9279 | 2808.7529 | 0.4377 | 3069.5312 | 0.56864 | 260.7783 | 0.13094
1155 | MCLU-65to135-MLI-CZ11-2020-19IEER | CZ11 | MLI | 2020 | 65to135 | 12 | 19 | 224.9492 | 2520.107 | 0.40645 | 2778.6001 | 0.53837 | 258.493 | 0.13192
1156 | MCLU-65to135-Mtl-CZ11-2003-19IEER | CZ11 | Mtl | 2003 | 65to135 | 12 | 19 | 54.1337 | 3259.996 | 0.93429 | 3363.6507 | 0.97391 | 103.6547 | 0.039619
1157 | MCLU-65to135-Mtl-CZ11-2007-19IEER | CZ11 | Mtl | 2007 | 65to135 | 12 | 19 | 54.1337 | 3107.4 | 0.85948 | 3210.8355 | 0.89904 | 103.4354 | 0.039558
1158 | MCLU-65to135-Mtl-CZ11-2011-19IEER | CZ11 | Mtl | 2011 | 65to135 | 12 | 19 | 51.77 | 3140.1086 | 0.865 | 3244.3859 | 0.90474 | 104.2773 | 0.039747
1159 | MCLU-65to135-Mtl-CZ11-2015-19IEER | CZ11 | Mtl | 2015 | 65to135 | 12 | 19 | 43.8146 | 3287.0109 | 0.86232 | 3399.4841 | 0.90524 | 112.4731 | 0.042923
1160 | MCLU-65to135-Mtl-CZ11-2020-19IEER | CZ11 | Mtl | 2020 | 65to135 | 12 | 19 | 43.6834 | 3217.1038 | 0.85334 | 3327.3441 | 0.89582 | 110.2402 | 0.042483
1161 | MCLU-65to135-Nrs-CZ11-2003-19IEER | CZ11 | Nrs | 2003 | 65to135 | 12 | 19 | 186.1819 | 4500.9583 | 1.0129 | 4768.1639 | 1.1237 | 267.2056 | 0.11084
1162 | MCLU-65to135-Nrs-CZ11-2007-19IEER | CZ11 | Nrs | 2007 | 65to135 | 12 | 19 | 186.0018 | 4408.199 | 0.9694 | 4675.3136 | 1.0799 | 267.1147 | 0.1105
1163 | MCLU-65to135-Nrs-CZ11-2011-19IEER | CZ11 | Nrs | 2011 | 65to135 | 12 | 19 | 184.4902 | 4450.5826 | 0.96328 | 4717.1618 | 1.0735 | 266.5793 | 0.11018
1164 | MCLU-65to135-Nrs-CZ11-2015-19IEER | CZ11 | Nrs | 2015 | 65to135 | 12 | 19 | 182.8281 | 4354.9145 | 0.90404 | 4618.3334 | 1.0143 | 263.4189 | 0.11028
1165 | MCLU-65to135-Nrs-CZ11-2020-19IEER | CZ11 | Nrs | 2020 | 65to135 | 12 | 19 | 182.1377 | 3999.0954 | 0.83826 | 4258.5596 | 0.94678 | 259.4641 | 0.10852
1166 | MCLU-65to135-OfL-CZ11-2003-19IEER | CZ11 | OfL | 2003 | 65to135 | 12 | 19 | 517.0593 | 3086.5195 | 0.52134 | 3370.0359 | 0.61892 | 283.5164 | 0.097577
1167 | MCLU-65to135-OfL-CZ11-2007-19IEER | CZ11 | OfL | 2007 | 65to135 | 12 | 19 | 516.5121 | 3089.2332 | 0.52143 | 3372.6617 | 0.61897 | 283.4285 | 0.09754
1168 | MCLU-65to135-OfL-CZ11-2011-19IEER | CZ11 | OfL | 2011 | 65to135 | 12 | 19 | 492.7112 | 3184.7167 | 0.52488 | 3465.944 | 0.62005 | 281.2272 | 0.095173
1169 | MCLU-65to135-OfL-CZ11-2015-19IEER | CZ11 | OfL | 2015 | 65to135 | 12 | 19 | 494.9529 | 3120.9862 | 0.51812 | 3399.3265 | 0.61257 | 278.3403 | 0.094451
1170 | MCLU-65to135-OfL-CZ11-2020-19IEER | CZ11 | OfL | 2020 | 65to135 | 12 | 19 | 482.9731 | 2966.4582 | 0.49987 | 3244.4919 | 0.59381 | 278.0337 | 0.093939
1171 | MCLU-65to135-OfS-CZ11-2003-19IEER | CZ11 | OfS | 2003 | 65to135 | 12 | 19 | 35.6629 | 2277.7992 | 0.40559 | 2559.0142 | 0.50671 | 281.215 | 0.10113
1172 | MCLU-65to135-OfS-CZ11-2007-19IEER | CZ11 | OfS | 2007 | 65to135 | 12 | 19 | 35.5497 | 2283.6764 | 0.40546 | 2564.6243 | 0.50632 | 280.9479 | 0.10085
1173 | MCLU-65to135-OfS-CZ11-2011-19IEER | CZ11 | OfS | 2011 | 65to135 | 12 | 19 | 34.8226 | 2302.2582 | 0.40286 | 2582.5027 | 0.50186 | 280.2445 | 0.098996
1174 | MCLU-65to135-OfS-CZ11-2015-19IEER | CZ11 | OfS | 2015 | 65to135 | 12 | 19 | 31.84 | 2442.1362 | 0.40758 | 2716.7573 | 0.50162 | 274.6211 | 0.094041
1175 | MCLU-65to135-OfS-CZ11-2020-19IEER | CZ11 | OfS | 2020 | 65to135 | 12 | 19 | 30.7425 | 2327.5362 | 0.38925 | 2601.3427 | 0.48225 | 273.8065 | 0.093001
1176 | MCLU-65to135-RFF-CZ11-2003-19IEER | CZ11 | RFF | 2003 | 65to135 | 12 | 19 | 9.6801 | 4419.8811 | 1.092 | 4907.9837 | 1.3146 | 488.1026 | 0.22265
1177 | MCLU-65to135-RFF-CZ11-2007-19IEER | CZ11 | RFF | 2007 | 65to135 | 12 | 19 | 9.5739 | 4464.0239 | 1.0995 | 4953.6743 | 1.3218 | 489.6505 | 0.2223
1178 | MCLU-65to135-RFF-CZ11-2011-19IEER | CZ11 | RFF | 2011 | 65to135 | 12 | 19 | 8.9934 | 4715.9092 | 1.1298 | 5210.5819 | 1.352 | 494.6727 | 0.22217
1179 | MCLU-65to135-RFF-CZ11-2015-19IEER | CZ11 | RFF | 2015 | 65to135 | 12 | 19 | 8.9656 | 4516.8391 | 1.0933 | 5008.8032 | 1.3166 | 491.9642 | 0.22327
1180 | MCLU-65to135-RFF-CZ11-2020-19IEER | CZ11 | RFF | 2020 | 65to135 | 12 | 19 | 8.6052 | 4143.0661 | 1.0368 | 4634.8018 | 1.261 | 491.7357 | 0.22417
1181 | MCLU-65to135-RSD-CZ11-2003-19IEER | CZ11 | RSD | 2003 | 65to135 | 12 | 19 | 17.8337 | 4253.2309 | 1.0476 | 4674.9905 | 1.2792 | 421.7596 | 0.2316
1182 | MCLU-65to135-RSD-CZ11-2007-19IEER | CZ11 | RSD | 2007 | 65to135 | 12 | 19 | 17.6182 | 4300.1991 | 1.0548 | 4723.5735 | 1.286 | 423.3744 | 0.23118
1183 | MCLU-65to135-RSD-CZ11-2011-19IEER | CZ11 | RSD | 2011 | 65to135 | 12 | 19 | 17.21 | 4394.8618 | 1.0688 | 4821.7207 | 1.2989 | 426.8589 | 0.2301
1184 | MCLU-65to135-RSD-CZ11-2015-19IEER | CZ11 | RSD | 2015 | 65to135 | 12 | 19 | 17.0193 | 4249.113 | 1.0444 | 4672.9076 | 1.2736 | 423.7945 | 0.22927
1185 | MCLU-65to135-RSD-CZ11-2020-19IEER | CZ11 | RSD | 2020 | 65to135 | 12 | 19 | 16.0179 | 3833.3502 | 0.978 | 4259.2134 | 1.2027 | 425.8632 | 0.2247
1186 | MCLU-65to135-Rt3-CZ11-2003-19IEER | CZ11 | Rt3 | 2003 | 65to135 | 12 | 19 | 325.5228 | 4316.2786 | 0.98527 | 4739.9825 | 1.2352 | 423.7039 | 0.24992
1187 | MCLU-65to135-Rt3-CZ11-2007-19IEER | CZ11 | Rt3 | 2007 | 65to135 | 12 | 19 | 324.3101 | 4330.597 | 0.98616 | 4753.9482 | 1.236 | 423.3512 | 0.24983
1188 | MCLU-65to135-Rt3-CZ11-2011-19IEER | CZ11 | Rt3 | 2011 | 65to135 | 12 | 19 | 303.7541 | 4599.8256 | 1.0071 | 5018.3179 | 1.2612 | 418.4923 | 0.25412
1189 | MCLU-65to135-Rt3-CZ11-2015-19IEER | CZ11 | Rt3 | 2015 | 65to135 | 12 | 19 | 294.5854 | 4289.8178 | 0.95526 | 4709.6431 | 1.2114 | 419.8253 | 0.25617
1190 | MCLU-65to135-Rt3-CZ11-2020-19IEER | CZ11 | Rt3 | 2020 | 65to135 | 12 | 19 | 282.807 | 3974.4636 | 0.90502 | 4395.3991 | 1.1634 | 420.9356 | 0.25842
1191 | MCLU-65to135-RtL-CZ11-2003-19IEER | CZ11 | RtL | 2003 | 65to135 | 12 | 19 | 285.2637 | 4678.2291 | 1.0719 | 5137.4403 | 1.3299 | 459.2111 | 0.25801
1192 | MCLU-65to135-RtL-CZ11-2007-19IEER | CZ11 | RtL | 2007 | 65to135 | 12 | 19 | 280.7426 | 4747.7174 | 1.0804 | 5206.098 | 1.3393 | 458.3806 | 0.25889
1193 | MCLU-65to135-RtL-CZ11-2011-19IEER | CZ11 | RtL | 2011 | 65to135 | 12 | 19 | 266.8031 | 4984.5325 | 1.1053 | 5439.8383 | 1.3683 | 455.3058 | 0.26302
1194 | MCLU-65to135-RtL-CZ11-2015-19IEER | CZ11 | RtL | 2015 | 65to135 | 12 | 19 | 259.1444 | 4794.8518 | 1.0881 | 5251.3833 | 1.353 | 456.5314 | 0.26491
1195 | MCLU-65to135-RtL-CZ11-2020-19IEER | CZ11 | RtL | 2020 | 65to135 | 12 | 19 | 244.2456 | 4613.9843 | 1.0805 | 5070.9633 | 1.3495 | 456.979 | 0.26904
1196 | MCLU-65to135-RtS-CZ11-2003-19IEER | CZ11 | RtS | 2003 | 65to135 | 12 | 19 | 21.5382 | 2870.2838 | 0.7416 | 3286.6782 | 0.95712 | 416.3944 | 0.21552
1197 | MCLU-65to135-RtS-CZ11-2007-19IEER | CZ11 | RtS | 2007 | 65to135 | 12 | 19 | 21.2092 | 2908.398 | 0.74567 | 3324.6421 | 0.96158 | 416.2441 | 0.21591
1198 | MCLU-65to135-RtS-CZ11-2011-19IEER | CZ11 | RtS | 2011 | 65to135 | 12 | 19 | 19.8508 | 3076.3653 | 0.75634 | 3489.7842 | 0.9745 | 413.4189 | 0.21815
1199 | MCLU-65to135-RtS-CZ11-2015-19IEER | CZ11 | RtS | 2015 | 65to135 | 12 | 19 | 19.6253 | 2866.5746 | 0.71625 | 3278.426 | 0.936 | 411.8514 | 0.21974
1200 | MCLU-65to135-RtS-CZ11-2020-19IEER | CZ11 | RtS | 2020 | 65to135 | 12 | 19 | 18.828 | 2719.5953 | 0.69442 | 3131.4269 | 0.9161 | 411.8316 | 0.22168
1201 | MCLU-65to135-SCn-CZ11-2003-19IEER | CZ11 | SCn | 2003 | 65to135 | 12 | 19 | 376.4214 | 2150.1407 | 0.35181 | 2478.4532 | 0.49026 | 328.3125 | 0.13845
1202 | MCLU-65to135-SCn-CZ11-2007-19IEER | CZ11 | SCn | 2007 | 65to135 | 12 | 19 | 361.1687 | 2225.1522 | 0.35641 | 2553.2124 | 0.49634 | 328.0603 | 0.13993
1203 | MCLU-65to135-SCn-CZ11-2011-19IEER | CZ11 | SCn | 2011 | 65to135 | 12 | 19 | 313.523 | 2515.264 | 0.37521 | 2849.5803 | 0.51495 | 334.3162 | 0.13974
1204 | MCLU-65to135-SCn-CZ11-2015-19IEER | CZ11 | SCn | 2015 | 65to135 | 12 | 19 | 312.1473 | 2522.394 | 0.37483 | 2856.4005 | 0.5148 | 334.0065 | 0.13997
1205 | MCLU-65to135-SCn-CZ11-2020-19IEER | CZ11 | SCn | 2020 | 65to135 | 12 | 19 | 286.1362 | 2390.9032 | 0.36728 | 2724.6841 | 0.50283 | 333.7809 | 0.13556
1206 | MCLU-65to135-WRf-CZ11-2003-19IEER | CZ11 | WRf | 2003 | 65to135 | 12 | 19 | 14.7372 | 259096.4515 | 36.0408 | 259555.7227 | 36.2012 | 459.2712 | 0.16038
1207 | MCLU-65to135-WRf-CZ11-2007-19IEER | CZ11 | WRf | 2007 | 65to135 | 12 | 19 | 14.2877 | 258497.7298 | 34.1292 | 258969.7372 | 34.294 | 472.0073 | 0.16481
1208 | MCLU-65to135-WRf-CZ11-2011-19IEER | CZ11 | WRf | 2011 | 65to135 | 12 | 19 | 16.6535 | 213735.9009 | 27.3083 | 214103.2362 | 27.428 | 367.3353 | 0.11966
1209 | MCLU-65to135-WRf-CZ11-2015-19IEER | CZ11 | WRf | 2015 | 65to135 | 12 | 19 | 16.7427 | 212572.9823 | 27.1468 | 212923.7294 | 27.2557 | 350.7471 | 0.10891
1210 | MCLU-65to135-WRf-CZ11-2020-19IEER | CZ11 | WRf | 2020 | 65to135 | 12 | 19 | 15.2308 | 220603.1542 | 28.1353 | 220965.1567 | 28.2501 | 362.0025 | 0.11481
1211 | MCLU-65to135-Asm-CZ12-2003-19IEER | CZ12 | Asm | 2003 | 65to135 | 12 | 19 | 380.6442 | 1935.02 | 0.78026 | 2293.8106 | 0.96083 | 358.7906 | 0.18058
1212 | MCLU-65to135-Asm-CZ12-2007-19IEER | CZ12 | Asm | 2007 | 65to135 | 12 | 19 | 377.4628 | 1948.3224 | 0.78433 | 2307.3599 | 0.96444 | 359.0374 | 0.18011
1213 | MCLU-65to135-Asm-CZ12-2011-19IEER | CZ12 | Asm | 2011 | 65to135 | 12 | 19 | 369.7725 | 1984.818 | 0.78934 | 2345.1141 | 0.96853 | 360.2961 | 0.17919
1214 | MCLU-65to135-Asm-CZ12-2015-19IEER | CZ12 | Asm | 2015 | 65to135 | 12 | 19 | 359.1749 | 2006.1886 | 0.79117 | 2364.1276 | 0.9703 | 357.9391 | 0.17914
1215 | MCLU-65to135-Asm-CZ12-2020-19IEER | CZ12 | Asm | 2020 | 65to135 | 12 | 19 | 351.4238 | 1885.8928 | 0.76904 | 2242.6447 | 0.94766 | 356.7519 | 0.17863
1216 | MCLU-65to135-ECC-CZ12-2003-19IEER | CZ12 | ECC | 2003 | 65to135 | 12 | 19 | 812.4751 | 2507.4542 | 0.49128 | 2777.1266 | 0.63946 | 269.6724 | 0.14818
1217 | MCLU-65to135-ECC-CZ12-2007-19IEER | CZ12 | ECC | 2007 | 65to135 | 12 | 19 | 810.5417 | 2512.5107 | 0.49111 | 2782.1154 | 0.6391 | 269.6047 | 0.14799
1218 | MCLU-65to135-ECC-CZ12-2011-19IEER | CZ12 | ECC | 2011 | 65to135 | 12 | 19 | 800.8689 | 2536.7835 | 0.48714 | 2806.4582 | 0.63459 | 269.6746 | 0.14745
1219 | MCLU-65to135-ECC-CZ12-2015-19IEER | CZ12 | ECC | 2015 | 65to135 | 12 | 19 | 766.7351 | 2604.6571 | 0.47889 | 2872.0619 | 0.62757 | 267.4048 | 0.14869
1220 | MCLU-65to135-ECC-CZ12-2020-19IEER | CZ12 | ECC | 2020 | 65to135 | 12 | 19 | 737.2413 | 2285.2728 | 0.45202 | 2552.5344 | 0.59892 | 267.2616 | 0.1469
1221 | MCLU-65to135-EPr-CZ12-2003-19IEER | CZ12 | EPr | 2003 | 65to135 | 12 | 19 | 132.5815 | 1672.2415 | 0.083261 | 1838.8553 | 0.11898 | 166.6138 | 0.03572
1222 | MCLU-65to135-EPr-CZ12-2007-19IEER | CZ12 | EPr | 2007 | 65to135 | 12 | 19 | 131.1161 | 1687.9425 | 0.082375 | 1855.0743 | 0.11744 | 167.1318 | 0.035066
1223 | MCLU-65to135-EPr-CZ12-2011-19IEER | CZ12 | EPr | 2011 | 65to135 | 12 | 19 | 127.9742 | 1726.2645 | 0.078805 | 1894.7731 | 0.11181 | 168.5086 | 0.033007
1224 | MCLU-65to135-EPr-CZ12-2015-19IEER | CZ12 | EPr | 2015 | 65to135 | 12 | 19 | 120.4366 | 1783.4164 | 0.058629 | 1948.7291 | 0.078576 | 165.3127 | 0.019946
1225 | MCLU-65to135-EPr-CZ12-2020-19IEER | CZ12 | EPr | 2020 | 65to135 | 12 | 19 | 114.8852 | 1583.8938 | 0.042096 | 1748.5898 | 0.05763 | 164.696 | 0.015534
1226 | MCLU-65to135-ERC-CZ12-2003-19IEER | CZ12 | ERC | 2003 | 65to135 | 12 | 19 | 6.1812 | 1319.8231 | 0.1361 | 1455.6326 | 0.20031 | 135.8095 | 0.064211
1227 | MCLU-65to135-ERC-CZ12-2007-19IEER | CZ12 | ERC | 2007 | 65to135 | 12 | 19 | 6.1597 | 1323.4657 | 0.13517 | 1459.3558 | 0.19845 | 135.8902 | 0.063284
1228 | MCLU-65to135-ERC-CZ12-2011-19IEER | CZ12 | ERC | 2011 | 65to135 | 12 | 19 | 5.9943 | 1349.437 | 0.12272 | 1484.6874 | 0.17915 | 135.2504 | 0.056429
1229 | MCLU-65to135-ERC-CZ12-2015-19IEER | CZ12 | ERC | 2015 | 65to135 | 12 | 19 | 5.8717 | 1351.6301 | 0.11286 | 1482.7303 | 0.16399 | 131.1002 | 0.051126
1230 | MCLU-65to135-ERC-CZ12-2020-19IEER | CZ12 | ERC | 2020 | 65to135 | 12 | 19 | 5.6899 | 1180.9518 | 0.10286 | 1312.4716 | 0.15402 | 131.5198 | 0.051161
1231 | MCLU-65to135-ESe-CZ12-2003-19IEER | CZ12 | ESe | 2003 | 65to135 | 12 | 19 | 404.5589 | 1807.477 | 0.16184 | 1992.2949 | 0.22607 | 184.8179 | 0.064225
1232 | MCLU-65to135-ESe-CZ12-2007-19IEER | CZ12 | ESe | 2007 | 65to135 | 12 | 19 | 402.9157 | 1813.8968 | 0.16135 | 1998.7799 | 0.225 | 184.8831 | 0.063655
1233 | MCLU-65to135-ESe-CZ12-2011-19IEER | CZ12 | ESe | 2011 | 65to135 | 12 | 19 | 398.3478 | 1829.9943 | 0.15606 | 2014.6205 | 0.21427 | 184.6262 | 0.058201
1234 | MCLU-65to135-ESe-CZ12-2015-19IEER | CZ12 | ESe | 2015 | 65to135 | 12 | 19 | 386.8141 | 1851.7488 | 0.14257 | 2032.1028 | 0.19186 | 180.354 | 0.049286
1235 | MCLU-65to135-ESe-CZ12-2020-19IEER | CZ12 | ESe | 2020 | 65to135 | 12 | 19 | 371.0465 | 1618.0872 | 0.12316 | 1797.8666 | 0.17099 | 179.7793 | 0.047828
1236 | MCLU-65to135-EUn-CZ12-2003-19IEER | CZ12 | EUn | 2003 | 65to135 | 12 | 19 | 2455.3315 | 2711.49 | 0.74166 | 2982.3573 | 0.89849 | 270.8673 | 0.15683
1237 | MCLU-65to135-EUn-CZ12-2007-19IEER | CZ12 | EUn | 2007 | 65to135 | 12 | 19 | 2439.519 | 2707.8453 | 0.73359 | 2978.7086 | 0.89012 | 270.8633 | 0.15653
1238 | MCLU-65to135-EUn-CZ12-2011-19IEER | CZ12 | EUn | 2011 | 65to135 | 12 | 19 | 2387.9124 | 2751.2945 | 0.73669 | 3024.3915 | 0.89373 | 273.0969 | 0.15705
1239 | MCLU-65to135-EUn-CZ12-2015-19IEER | CZ12 | EUn | 2015 | 65to135 | 12 | 19 | 2245.6464 | 2845.7764 | 0.73748 | 3119.6179 | 0.89735 | 273.8415 | 0.15987
1240 | MCLU-65to135-EUn-CZ12-2020-19IEER | CZ12 | EUn | 2020 | 65to135 | 12 | 19 | 2158.8405 | 2595.6365 | 0.7143 | 2867.9374 | 0.8715 | 272.3009 | 0.1572
1241 | MCLU-65to135-Gro-CZ12-2003-19IEER | CZ12 | Gro | 2003 | 65to135 | 12 | 19 | 146.9813 | 11308.6497 | 1.8313 | 11705.4544 | 2.0127 | 396.8047 | 0.18145
1242 | MCLU-65to135-Gro-CZ12-2007-19IEER | CZ12 | Gro | 2007 | 65to135 | 12 | 19 | 144.5012 | 10413.4197 | 1.7241 | 10800.1987 | 1.9212 | 386.779 | 0.19715
1243 | MCLU-65to135-Gro-CZ12-2011-19IEER | CZ12 | Gro | 2011 | 65to135 | 12 | 19 | 139.3952 | 10783.3403 | 1.7728 | 11167.4974 | 1.9693 | 384.1572 | 0.19654
1244 | MCLU-65to135-Gro-CZ12-2015-19IEER | CZ12 | Gro | 2015 | 65to135 | 12 | 19 | 135.0202 | 10662.9678 | 1.7506 | 11037.9059 | 1.9434 | 374.9381 | 0.1928
1245 | MCLU-65to135-Gro-CZ12-2020-19IEER | CZ12 | Gro | 2020 | 65to135 | 12 | 19 | 130.6412 | 10677.5618 | 1.7487 | 11045.428 | 1.9377 | 367.8662 | 0.189
1246 | MCLU-65to135-Hsp-CZ12-2003-19IEER | CZ12 | Hsp | 2003 | 65to135 | 12 | 19 | 680.6169 | 4170.2838 | 0.79338 | 4635.4886 | 0.98639 | 465.2047 | 0.19301
1247 | MCLU-65to135-Hsp-CZ12-2007-19IEER | CZ12 | Hsp | 2007 | 65to135 | 12 | 19 | 680.6169 | 4169.6697 | 0.79254 | 4634.5707 | 0.9852 | 464.901 | 0.19266
1248 | MCLU-65to135-Hsp-CZ12-2011-19IEER | CZ12 | Hsp | 2011 | 65to135 | 12 | 19 | 680.4571 | 4164.1946 | 0.78096 | 4627.8988 | 0.97404 | 463.7043 | 0.19308
1249 | MCLU-65to135-Hsp-CZ12-2015-19IEER | CZ12 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 4133.07 | 0.76695 | 4595.382 | 0.96025 | 462.312 | 0.1933
1250 | MCLU-65to135-Hsp-CZ12-2020-19IEER | CZ12 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3623.2179 | 0.68772 | 4082.3447 | 0.87864 | 459.1268 | 0.19092
1251 | MCLU-65to135-Htl-CZ12-2003-19IEER | CZ12 | Htl | 2003 | 65to135 | 12 | 19 | 275.1867 | 3259.2651 | 0.96671 | 3367.8946 | 1.0151 | 108.6294 | 0.048376
1252 | MCLU-65to135-Htl-CZ12-2007-19IEER | CZ12 | Htl | 2007 | 65to135 | 12 | 19 | 274.8347 | 3133.5448 | 0.90055 | 3242.3057 | 0.94887 | 108.7609 | 0.048324
1253 | MCLU-65to135-Htl-CZ12-2011-19IEER | CZ12 | Htl | 2011 | 65to135 | 12 | 19 | 266.8449 | 3168.0449 | 0.90644 | 3278.3367 | 0.95532 | 110.2918 | 0.048881
1254 | MCLU-65to135-Htl-CZ12-2015-19IEER | CZ12 | Htl | 2015 | 65to135 | 12 | 19 | 238.6573 | 3287.8821 | 0.90831 | 3403.141 | 0.95973 | 115.2589 | 0.05142
1255 | MCLU-65to135-Htl-CZ12-2020-19IEER | CZ12 | Htl | 2020 | 65to135 | 12 | 19 | 236.7502 | 3193.6811 | 0.89726 | 3306.5223 | 0.94751 | 112.8412 | 0.050256
1256 | MCLU-65to135-MBT-CZ12-2003-19IEER | CZ12 | MBT | 2003 | 65to135 | 12 | 19 | 397.2394 | 3646.4855 | 0.57834 | 3889.4447 | 0.73119 | 242.9592 | 0.15286
1257 | MCLU-65to135-MBT-CZ12-2007-19IEER | CZ12 | MBT | 2007 | 65to135 | 12 | 19 | 390.4364 | 3708.7046 | 0.58402 | 3950.786 | 0.7364 | 242.0813 | 0.15239
1258 | MCLU-65to135-MBT-CZ12-2011-19IEER | CZ12 | MBT | 2011 | 65to135 | 12 | 19 | 368.244 | 3873.9186 | 0.59831 | 4114.4043 | 0.75024 | 240.4857 | 0.15192
1259 | MCLU-65to135-MBT-CZ12-2015-19IEER | CZ12 | MBT | 2015 | 65to135 | 12 | 19 | 359.2227 | 3930.4427 | 0.60203 | 4170.0525 | 0.75409 | 239.6098 | 0.15207
1260 | MCLU-65to135-MBT-CZ12-2020-19IEER | CZ12 | MBT | 2020 | 65to135 | 12 | 19 | 334.9562 | 3771.5802 | 0.58737 | 4010.1356 | 0.73793 | 238.5554 | 0.15056
1261 | MCLU-65to135-MLI-CZ12-2003-19IEER | CZ12 | MLI | 2003 | 65to135 | 12 | 19 | 251.1333 | 2657.0745 | 0.44333 | 2883.4803 | 0.55393 | 226.4058 | 0.1106
1262 | MCLU-65to135-MLI-CZ12-2007-19IEER | CZ12 | MLI | 2007 | 65to135 | 12 | 19 | 246.1253 | 2706.152 | 0.44783 | 2932.013 | 0.55841 | 225.861 | 0.11058
1263 | MCLU-65to135-MLI-CZ12-2011-19IEER | CZ12 | MLI | 2011 | 65to135 | 12 | 19 | 232.4193 | 2852.6267 | 0.45866 | 3077.5791 | 0.56923 | 224.9524 | 0.11057
1264 | MCLU-65to135-MLI-CZ12-2015-19IEER | CZ12 | MLI | 2015 | 65to135 | 12 | 19 | 230.2305 | 2859.3423 | 0.4594 | 3084.0797 | 0.56979 | 224.7375 | 0.11038
1265 | MCLU-65to135-MLI-CZ12-2020-19IEER | CZ12 | MLI | 2020 | 65to135 | 12 | 19 | 215.8927 | 2559.1551 | 0.42617 | 2781.8812 | 0.53677 | 222.7261 | 0.11061
1266 | MCLU-65to135-Mtl-CZ12-2003-19IEER | CZ12 | Mtl | 2003 | 65to135 | 12 | 19 | 50.1952 | 3198.5022 | 0.91161 | 3283.5707 | 0.94388 | 85.0684 | 0.032274
1267 | MCLU-65to135-Mtl-CZ12-2007-19IEER | CZ12 | Mtl | 2007 | 65to135 | 12 | 19 | 50.1952 | 3064.6561 | 0.84115 | 3149.6777 | 0.87339 | 85.0216 | 0.032244
1268 | MCLU-65to135-Mtl-CZ12-2011-19IEER | CZ12 | Mtl | 2011 | 65to135 | 12 | 19 | 48.7702 | 3090.453 | 0.84465 | 3175.8907 | 0.87702 | 85.4377 | 0.032371
1269 | MCLU-65to135-Mtl-CZ12-2015-19IEER | CZ12 | Mtl | 2015 | 65to135 | 12 | 19 | 41.3832 | 3270.5722 | 0.8513 | 3362.4965 | 0.88591 | 91.9243 | 0.034607
1270 | MCLU-65to135-Mtl-CZ12-2020-19IEER | CZ12 | Mtl | 2020 | 65to135 | 12 | 19 | 41.2546 | 3196.8609 | 0.8417 | 3287.1205 | 0.87582 | 90.2596 | 0.034113
1271 | MCLU-65to135-Nrs-CZ12-2003-19IEER | CZ12 | Nrs | 2003 | 65to135 | 12 | 19 | 183.3158 | 4406.8792 | 0.97215 | 4636.7742 | 1.0684 | 229.895 | 0.096216
1272 | MCLU-65to135-Nrs-CZ12-2007-19IEER | CZ12 | Nrs | 2007 | 65to135 | 12 | 19 | 183.2688 | 4322.1057 | 0.93239 | 4551.9602 | 1.0284 | 229.8545 | 0.095977
1273 | MCLU-65to135-Nrs-CZ12-2011-19IEER | CZ12 | Nrs | 2011 | 65to135 | 12 | 19 | 182.8853 | 4345.6844 | 0.92328 | 4574.3446 | 1.0187 | 228.6602 | 0.095385
1274 | MCLU-65to135-Nrs-CZ12-2015-19IEER | CZ12 | Nrs | 2015 | 65to135 | 12 | 19 | 182.0027 | 4249.8047 | 0.86714 | 4475.3604 | 0.96222 | 225.5557 | 0.095077
1275 | MCLU-65to135-Nrs-CZ12-2020-19IEER | CZ12 | Nrs | 2020 | 65to135 | 12 | 19 | 181.7415 | 3882.0344 | 0.80562 | 4105.1356 | 0.89948 | 223.1012 | 0.09386
1276 | MCLU-65to135-OfL-CZ12-2003-19IEER | CZ12 | OfL | 2003 | 65to135 | 12 | 19 | 481.8151 | 3233.0602 | 0.54681 | 3474.7318 | 0.62839 | 241.6716 | 0.081586
1277 | MCLU-65to135-OfL-CZ12-2007-19IEER | CZ12 | OfL | 2007 | 65to135 | 12 | 19 | 481.3578 | 3235.7789 | 0.54698 | 3477.3776 | 0.62856 | 241.5988 | 0.081577
1278 | MCLU-65to135-OfL-CZ12-2011-19IEER | CZ12 | OfL | 2011 | 65to135 | 12 | 19 | 460.7977 | 3332.6687 | 0.55209 | 3572.2322 | 0.63276 | 239.5635 | 0.08067
1279 | MCLU-65to135-OfL-CZ12-2015-19IEER | CZ12 | OfL | 2015 | 65to135 | 12 | 19 | 460.6322 | 3278.6442 | 0.54732 | 3515.9335 | 0.62663 | 237.2893 | 0.079305
1280 | MCLU-65to135-OfL-CZ12-2020-19IEER | CZ12 | OfL | 2020 | 65to135 | 12 | 19 | 448.7498 | 3116.7245 | 0.52871 | 3354.068 | 0.60811 | 237.3435 | 0.079401
1281 | MCLU-65to135-OfS-CZ12-2003-19IEER | CZ12 | OfS | 2003 | 65to135 | 12 | 19 | 33.0084 | 2372.766 | 0.41642 | 2614.5717 | 0.50051 | 241.8057 | 0.084093
1282 | MCLU-65to135-OfS-CZ12-2007-19IEER | CZ12 | OfS | 2007 | 65to135 | 12 | 19 | 32.9143 | 2378.6895 | 0.41659 | 2620.3791 | 0.50058 | 241.6896 | 0.083987
1283 | MCLU-65to135-OfS-CZ12-2011-19IEER | CZ12 | OfS | 2011 | 65to135 | 12 | 19 | 32.2683 | 2398.8012 | 0.41601 | 2640.2002 | 0.49879 | 241.399 | 0.082785
1284 | MCLU-65to135-OfS-CZ12-2015-19IEER | CZ12 | OfS | 2015 | 65to135 | 12 | 19 | 29.2538 | 2574.2457 | 0.4294 | 2810.7788 | 0.5084 | 236.533 | 0.079
1285 | MCLU-65to135-OfS-CZ12-2020-19IEER | CZ12 | OfS | 2020 | 65to135 | 12 | 19 | 28.4943 | 2429.0592 | 0.40924 | 2665.0476 | 0.48807 | 235.9884 | 0.078828
1286 | MCLU-65to135-RFF-CZ12-2003-19IEER | CZ12 | RFF | 2003 | 65to135 | 12 | 19 | 8.4998 | 4827.8997 | 1.2316 | 5252.6939 | 1.4159 | 424.7942 | 0.18423
1287 | MCLU-65to135-RFF-CZ12-2007-19IEER | CZ12 | RFF | 2007 | 65to135 | 12 | 19 | 8.4058 | 4877.9739 | 1.2409 | 5304.7142 | 1.4246 | 426.7403 | 0.18372
1288 | MCLU-65to135-RFF-CZ12-2011-19IEER | CZ12 | RFF | 2011 | 65to135 | 12 | 19 | 8.1571 | 5015.6863 | 1.2606 | 5448.1276 | 1.4435 | 432.4413 | 0.18286
1289 | MCLU-65to135-RFF-CZ12-2015-19IEER | CZ12 | RFF | 2015 | 65to135 | 12 | 19 | 8.1117 | 4811.2535 | 1.2226 | 5240.182 | 1.4066 | 428.9285 | 0.18397
1290 | MCLU-65to135-RFF-CZ12-2020-19IEER | CZ12 | RFF | 2020 | 65to135 | 12 | 19 | 7.7707 | 4402.4468 | 1.1631 | 4833.8763 | 1.3459 | 431.4295 | 0.18281
1291 | MCLU-65to135-RSD-CZ12-2003-19IEER | CZ12 | RSD | 2003 | 65to135 | 12 | 19 | 15.6598 | 4703.282 | 1.2025 | 5088.3288 | 1.3922 | 385.0468 | 0.18977
1292 | MCLU-65to135-RSD-CZ12-2007-19IEER | CZ12 | RSD | 2007 | 65to135 | 12 | 19 | 15.4703 | 4757.7131 | 1.2124 | 5144.7042 | 1.4017 | 386.9911 | 0.18929
1293 | MCLU-65to135-RSD-CZ12-2011-19IEER | CZ12 | RSD | 2011 | 65to135 | 12 | 19 | 15.1254 | 4863.9128 | 1.2303 | 5254.6991 | 1.4197 | 390.7863 | 0.1894
1294 | MCLU-65to135-RSD-CZ12-2015-19IEER | CZ12 | RSD | 2015 | 65to135 | 12 | 19 | 14.9449 | 4700.1894 | 1.2003 | 5084.0191 | 1.389 | 383.8296 | 0.1887
1295 | MCLU-65to135-RSD-CZ12-2020-19IEER | CZ12 | RSD | 2020 | 65to135 | 12 | 19 | 14.0679 | 4223.699 | 1.1261 | 4606.3179 | 1.3116 | 382.6189 | 0.18541
1296 | MCLU-65to135-Rt3-CZ12-2003-19IEER | CZ12 | Rt3 | 2003 | 65to135 | 12 | 19 | 291.6676 | 4705.8222 | 1.0859 | 5070.2355 | 1.3002 | 364.4133 | 0.2143
1297 | MCLU-65to135-Rt3-CZ12-2007-19IEER | CZ12 | Rt3 | 2007 | 65to135 | 12 | 19 | 290.6772 | 4720.6926 | 1.0873 | 5084.8402 | 1.3014 | 364.1476 | 0.21406
1298 | MCLU-65to135-Rt3-CZ12-2011-19IEER | CZ12 | Rt3 | 2011 | 65to135 | 12 | 19 | 283.4412 | 4837.9276 | 1.0975 | 5200.1876 | 1.3123 | 362.26 | 0.21476
1299 | MCLU-65to135-Rt3-CZ12-2015-19IEER | CZ12 | Rt3 | 2015 | 65to135 | 12 | 19 | 274.5667 | 4511.7537 | 1.0439 | 4875.1021 | 1.2599 | 363.3485 | 0.21594
1300 | MCLU-65to135-Rt3-CZ12-2020-19IEER | CZ12 | Rt3 | 2020 | 65to135 | 12 | 19 | 263.8343 | 4169.5556 | 0.98989 | 4533.7595 | 1.2068 | 364.2039 | 0.21686
1301 | MCLU-65to135-RtL-CZ12-2003-19IEER | CZ12 | RtL | 2003 | 65to135 | 12 | 19 | 254.9818 | 5126.4454 | 1.1714 | 5505.9727 | 1.3838 | 379.5272 | 0.21242
1302 | MCLU-65to135-RtL-CZ12-2007-19IEER | CZ12 | RtL | 2007 | 65to135 | 12 | 19 | 250.6144 | 5212.9839 | 1.1859 | 5591.4343 | 1.3982 | 378.4504 | 0.21237
1303 | MCLU-65to135-RtL-CZ12-2011-19IEER | CZ12 | RtL | 2011 | 65to135 | 12 | 19 | 243.3703 | 5367.8806 | 1.2085 | 5743.636 | 1.4213 | 375.7554 | 0.21279
1304 | MCLU-65to135-RtL-CZ12-2015-19IEER | CZ12 | RtL | 2015 | 65to135 | 12 | 19 | 236.1983 | 5162.4565 | 1.1895 | 5539.4937 | 1.4035 | 377.0372 | 0.21397
1305 | MCLU-65to135-RtL-CZ12-2020-19IEER | CZ12 | RtL | 2020 | 65to135 | 12 | 19 | 222.4438 | 4966.4633 | 1.1851 | 5343.8403 | 1.3991 | 377.377 | 0.21394
1306 | MCLU-65to135-RtS-CZ12-2003-19IEER | CZ12 | RtS | 2003 | 65to135 | 12 | 19 | 18.9803 | 3116.081 | 0.79081 | 3475.4289 | 0.97317 | 359.348 | 0.18236
1307 | MCLU-65to135-RtS-CZ12-2007-19IEER | CZ12 | RtS | 2007 | 65to135 | 12 | 19 | 18.6905 | 3159.5617 | 0.79684 | 3518.6422 | 0.97916 | 359.0805 | 0.18232
1308 | MCLU-65to135-RtS-CZ12-2011-19IEER | CZ12 | RtS | 2011 | 65to135 | 12 | 19 | 18.0643 | 3259.6316 | 0.80742 | 3617.9072 | 0.98955 | 358.2755 | 0.18213
1309 | MCLU-65to135-RtS-CZ12-2015-19IEER | CZ12 | RtS | 2015 | 65to135 | 12 | 19 | 17.8052 | 3039.4689 | 0.76556 | 3396.2906 | 0.94931 | 356.8217 | 0.18375
1310 | MCLU-65to135-RtS-CZ12-2020-19IEER | CZ12 | RtS | 2020 | 65to135 | 12 | 19 | 17.0613 | 2879.9758 | 0.74438 | 3236.609 | 0.92868 | 356.6332 | 0.1843
1311 | MCLU-65to135-SCn-CZ12-2003-19IEER | CZ12 | SCn | 2003 | 65to135 | 12 | 19 | 325.0942 | 2351.5255 | 0.37278 | 2622.4572 | 0.48521 | 270.9317 | 0.11243
1312 | MCLU-65to135-SCn-CZ12-2007-19IEER | CZ12 | SCn | 2007 | 65to135 | 12 | 19 | 311.3279 | 2440.2741 | 0.38027 | 2710.4456 | 0.49276 | 270.1715 | 0.11249
1313 | MCLU-65to135-SCn-CZ12-2011-19IEER | CZ12 | SCn | 2011 | 65to135 | 12 | 19 | 287.4767 | 2621.3771 | 0.39448 | 2895.8508 | 0.50705 | 274.4737 | 0.11257
1314 | MCLU-65to135-SCn-CZ12-2015-19IEER | CZ12 | SCn | 2015 | 65to135 | 12 | 19 | 285.4311 | 2637.7653 | 0.39581 | 2910.5131 | 0.50821 | 272.7478 | 0.1124
1315 | MCLU-65to135-SCn-CZ12-2020-19IEER | CZ12 | SCn | 2020 | 65to135 | 12 | 19 | 261.9832 | 2487.7664 | 0.38714 | 2757.1415 | 0.49361 | 269.375 | 0.10647
1316 | MCLU-65to135-WRf-CZ12-2003-19IEER | CZ12 | WRf | 2003 | 65to135 | 12 | 19 | 15.1153 | 250605.4516 | 35.0301 | 251008.4452 | 35.1791 | 402.9936 | 0.14896
1317 | MCLU-65to135-WRf-CZ12-2007-19IEER | CZ12 | WRf | 2007 | 65to135 | 12 | 19 | 14.9123 | 245379.2588 | 32.5257 | 245794.1912 | 32.6776 | 414.9323 | 0.1519
1318 | MCLU-65to135-WRf-CZ12-2011-19IEER | CZ12 | WRf | 2011 | 65to135 | 12 | 19 | 16.9856 | 208552.4032 | 26.67 | 208881.7589 | 26.7801 | 329.3557 | 0.11018
1319 | MCLU-65to135-WRf-CZ12-2015-19IEER | CZ12 | WRf | 2015 | 65to135 | 12 | 19 | 17.3266 | 204428.4134 | 26.1301 | 204740.0327 | 26.2296 | 311.6193 | 0.099516
1320 | MCLU-65to135-WRf-CZ12-2020-19IEER | CZ12 | WRf | 2020 | 65to135 | 12 | 19 | 15.5839 | 214591.3256 | 27.391 | 214926.2744 | 27.4974 | 334.9488 | 0.10641
1321 | MCLU-65to135-Asm-CZ13-2003-19IEER | CZ13 | Asm | 2003 | 65to135 | 12 | 19 | 434.9821 | 1840.4223 | 0.66056 | 2253.9514 | 0.85618 | 413.5291 | 0.19563
1322 | MCLU-65to135-Asm-CZ13-2007-19IEER | CZ13 | Asm | 2007 | 65to135 | 12 | 19 | 431.4582 | 1850.995 | 0.66355 | 2264.5349 | 0.85865 | 413.5399 | 0.1951
1323 | MCLU-65to135-Asm-CZ13-2011-19IEER | CZ13 | Asm | 2011 | 65to135 | 12 | 19 | 418.4703 | 1894.4916 | 0.66559 | 2308.584 | 0.86073 | 414.0924 | 0.19514
1324 | MCLU-65to135-Asm-CZ13-2015-19IEER | CZ13 | Asm | 2015 | 65to135 | 12 | 19 | 406.5164 | 1912.4516 | 0.66776 | 2324.3527 | 0.86315 | 411.9011 | 0.19539
1325 | MCLU-65to135-Asm-CZ13-2020-19IEER | CZ13 | Asm | 2020 | 65to135 | 12 | 19 | 398.4688 | 1802.5749 | 0.6455 | 2212.9176 | 0.84095 | 410.3427 | 0.19546
1326 | MCLU-65to135-ECC-CZ13-2003-19IEER | CZ13 | ECC | 2003 | 65to135 | 12 | 19 | 920.3765 | 2348.7258 | 0.42628 | 2669.3466 | 0.58208 | 320.6208 | 0.1558
1327 | MCLU-65to135-ECC-CZ13-2007-19IEER | CZ13 | ECC | 2007 | 65to135 | 12 | 19 | 918.2849 | 2352.3159 | 0.42563 | 2672.3565 | 0.58123 | 320.0406 | 0.1556
1328 | MCLU-65to135-ECC-CZ13-2011-19IEER | CZ13 | ECC | 2011 | 65to135 | 12 | 19 | 899.9591 | 2381.6821 | 0.4183 | 2697.657 | 0.57251 | 315.9749 | 0.1542
1329 | MCLU-65to135-ECC-CZ13-2015-19IEER | CZ13 | ECC | 2015 | 65to135 | 12 | 19 | 864.6516 | 2431.4087 | 0.41053 | 2742.5928 | 0.5655 | 311.1841 | 0.15497
1330 | MCLU-65to135-ECC-CZ13-2020-19IEER | CZ13 | ECC | 2020 | 65to135 | 12 | 19 | 834.1208 | 2141.7602 | 0.38414 | 2452.1163 | 0.53824 | 310.3561 | 0.1541
1331 | MCLU-65to135-EPr-CZ13-2003-19IEER | CZ13 | EPr | 2003 | 65to135 | 12 | 19 | 156.9838 | 1517.3265 | 0.096752 | 1714.5407 | 0.14368 | 197.2141 | 0.046932
1332 | MCLU-65to135-EPr-CZ13-2007-19IEER | CZ13 | EPr | 2007 | 65to135 | 12 | 19 | 155.5418 | 1526.8511 | 0.094955 | 1723.373 | 0.13971 | 196.5219 | 0.044758
1333 | MCLU-65to135-EPr-CZ13-2011-19IEER | CZ13 | EPr | 2011 | 65to135 | 12 | 19 | 152.1903 | 1553.159 | 0.091785 | 1748.7998 | 0.13419 | 195.6407 | 0.042406
1334 | MCLU-65to135-EPr-CZ13-2015-19IEER | CZ13 | EPr | 2015 | 65to135 | 12 | 19 | 144.5344 | 1581.9783 | 0.073543 | 1770.0935 | 0.10454 | 188.1152 | 0.030998
1335 | MCLU-65to135-EPr-CZ13-2020-19IEER | CZ13 | EPr | 2020 | 65to135 | 12 | 19 | 138.9087 | 1402.6046 | 0.061675 | 1589.1304 | 0.090014 | 186.5257 | 0.028339
1336 | MCLU-65to135-ERC-CZ13-2003-19IEER | CZ13 | ERC | 2003 | 65to135 | 12 | 19 | 7.3103 | 1224.8507 | 0.13336 | 1398.2649 | 0.20077 | 173.4141 | 0.067407
1337 | MCLU-65to135-ERC-CZ13-2007-19IEER | CZ13 | ERC | 2007 | 65to135 | 12 | 19 | 7.2872 | 1226.9978 | 0.13243 | 1399.4509 | 0.19829 | 172.4532 | 0.065854
1338 | MCLU-65to135-ERC-CZ13-2011-19IEER | CZ13 | ERC | 2011 | 65to135 | 12 | 19 | 7.1008 | 1245.609 | 0.12574 | 1413.3411 | 0.1852 | 167.7321 | 0.059466
1339 | MCLU-65to135-ERC-CZ13-2015-19IEER | CZ13 | ERC | 2015 | 65to135 | 12 | 19 | 6.9677 | 1244.5884 | 0.11812 | 1406.5074 | 0.17283 | 161.919 | 0.054712
1340 | MCLU-65to135-ERC-CZ13-2020-19IEER | CZ13 | ERC | 2020 | 65to135 | 12 | 19 | 6.7901 | 1095.7107 | 0.11009 | 1255.0826 | 0.16286 | 159.3718 | 0.052774
1341 | MCLU-65to135-ESe-CZ13-2003-19IEER | CZ13 | ESe | 2003 | 65to135 | 12 | 19 | 465.6304 | 1686.9016 | 0.15455 | 1915.2103 | 0.21803 | 228.3088 | 0.063481
1342 | MCLU-65to135-ESe-CZ13-2007-19IEER | CZ13 | ESe | 2007 | 65to135 | 12 | 19 | 464.0671 | 1690.9117 | 0.15435 | 1918.6916 | 0.21672 | 227.7799 | 0.062369
1343 | MCLU-65to135-ESe-CZ13-2011-19IEER | CZ13 | ESe | 2011 | 65to135 | 12 | 19 | 456.0969 | 1704.4003 | 0.14533 | 1926.2962 | 0.20077 | 221.8959 | 0.055441
1344 | MCLU-65to135-ESe-CZ13-2015-19IEER | CZ13 | ESe | 2015 | 65to135 | 12 | 19 | 443.9292 | 1715.3738 | 0.13458 | 1930.6775 | 0.18295 | 215.3037 | 0.048368
1345 | MCLU-65to135-ESe-CZ13-2020-19IEER | CZ13 | ESe | 2020 | 65to135 | 12 | 19 | 428.3595 | 1502.3668 | 0.11821 | 1716.1536 | 0.16523 | 213.7869 | 0.047026
1346 | MCLU-65to135-EUn-CZ13-2003-19IEER | CZ13 | EUn | 2003 | 65to135 | 12 | 19 | 2785.8962 | 2546.328 | 0.63657 | 2863.9231 | 0.80282 | 317.5951 | 0.16625
1347 | MCLU-65to135-EUn-CZ13-2007-19IEER | CZ13 | EUn | 2007 | 65to135 | 12 | 19 | 2769.3564 | 2536.9557 | 0.62827 | 2854.2185 | 0.79457 | 317.2628 | 0.1663
1348 | MCLU-65to135-EUn-CZ13-2011-19IEER | CZ13 | EUn | 2011 | 65to135 | 12 | 19 | 2682.3776 | 2597.0463 | 0.63055 | 2914.1569 | 0.79734 | 317.1106 | 0.16679
1349 | MCLU-65to135-EUn-CZ13-2015-19IEER | CZ13 | EUn | 2015 | 65to135 | 12 | 19 | 2532.2884 | 2668.2792 | 0.62957 | 2985.1513 | 0.79909 | 316.8721 | 0.16952
1350 | MCLU-65to135-EUn-CZ13-2020-19IEER | CZ13 | EUn | 2020 | 65to135 | 12 | 19 | 2447.5031 | 2435.6513 | 0.60329 | 2750.3207 | 0.7718 | 314.6694 | 0.16851
1351 | MCLU-65to135-Gro-CZ13-2003-19IEER | CZ13 | Gro | 2003 | 65to135 | 12 | 19 | 147.2032 | 11543.248 | 1.8517 | 12000.5316 | 2.0404 | 457.2836 | 0.18866
1352 | MCLU-65to135-Gro-CZ13-2007-19IEER | CZ13 | Gro | 2007 | 65to135 | 12 | 19 | 144.5506 | 10680.409 | 1.7387 | 11134.7905 | 1.9445 | 454.3815 | 0.20577
1353 | MCLU-65to135-Gro-CZ13-2011-19IEER | CZ13 | Gro | 2011 | 65to135 | 12 | 19 | 136.9146 | 11245.7728 | 1.8113 | 11694.4818 | 2.0159 | 448.709 | 0.20466
1354 | MCLU-65to135-Gro-CZ13-2015-19IEER | CZ13 | Gro | 2015 | 65to135 | 12 | 19 | 132.509 | 11131.37 | 1.7939 | 11570.4456 | 1.9949 | 439.0756 | 0.20092
1355 | MCLU-65to135-Gro-CZ13-2020-19IEER | CZ13 | Gro | 2020 | 65to135 | 12 | 19 | 127.7896 | 11181.0445 | 1.798 | 11612.5354 | 1.997 | 431.4909 | 0.199
1356 | MCLU-65to135-Hsp-CZ13-2003-19IEER | CZ13 | Hsp | 2003 | 65to135 | 12 | 19 | 686.6347 | 4296.8557 | 0.79915 | 4852.3226 | 0.99601 | 555.4669 | 0.19686
1357 | MCLU-65to135-Hsp-CZ13-2007-19IEER | CZ13 | Hsp | 2007 | 65to135 | 12 | 19 | 686.4721 | 4296.597 | 0.79836 | 4851.5629 | 0.99488 | 554.9659 | 0.19652
1358 | MCLU-65to135-Hsp-CZ13-2011-19IEER | CZ13 | Hsp | 2011 | 65to135 | 12 | 19 | 680.5569 | 4309.2868 | 0.78366 | 4861.4087 | 0.9809 | 552.1219 | 0.19723
1359 | MCLU-65to135-Hsp-CZ13-2015-19IEER | CZ13 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 4274.8809 | 0.77003 | 4825.6439 | 0.96783 | 550.7629 | 0.19779
1360 | MCLU-65to135-Hsp-CZ13-2020-19IEER | CZ13 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3756.566 | 0.68975 | 4300.8315 | 0.8851 | 544.2654 | 0.19535
1361 | MCLU-65to135-Htl-CZ13-2003-19IEER | CZ13 | Htl | 2003 | 65to135 | 12 | 19 | 306.074 | 3199.5949 | 0.86388 | 3330.4913 | 0.91614 | 130.8964 | 0.052267
1362 | MCLU-65to135-Htl-CZ13-2007-19IEER | CZ13 | Htl | 2007 | 65to135 | 12 | 19 | 305.6628 | 3060.2004 | 0.80426 | 3191.1598 | 0.85648 | 130.9594 | 0.052217
1363 | MCLU-65to135-Htl-CZ13-2011-19IEER | CZ13 | Htl | 2011 | 65to135 | 12 | 19 | 295.8362 | 3097.4404 | 0.80872 | 3228.9854 | 0.86117 | 131.5449 | 0.052455
1364 | MCLU-65to135-Htl-CZ13-2015-19IEER | CZ13 | Htl | 2015 | 65to135 | 12 | 19 | 266.4099 | 3180.5492 | 0.80723 | 3318.4953 | 0.86298 | 137.9461 | 0.055748
1365 | MCLU-65to135-Htl-CZ13-2020-19IEER | CZ13 | Htl | 2020 | 65to135 | 12 | 19 | 264.4042 | 3094.1234 | 0.79629 | 3229.4318 | 0.85125 | 135.3084 | 0.054963
1366 | MCLU-65to135-MBT-CZ13-2003-19IEER | CZ13 | MBT | 2003 | 65to135 | 12 | 19 | 445.8188 | 3351.7747 | 0.5173 | 3642.0666 | 0.67066 | 290.2919 | 0.15337
1367 | MCLU-65to135-MBT-CZ13-2007-19IEER | CZ13 | MBT | 2007 | 65to135 | 12 | 19 | 438.304 | 3403.8597 | 0.5212 | 3692.4653 | 0.67398 | 288.6056 | 0.15279
1368 | MCLU-65to135-MBT-CZ13-2011-19IEER | CZ13 | MBT | 2011 | 65to135 | 12 | 19 | 413.956 | 3540.065 | 0.53133 | 3825.4978 | 0.68318 | 285.4328 | 0.15186
1369 | MCLU-65to135-MBT-CZ13-2015-19IEER | CZ13 | MBT | 2015 | 65to135 | 12 | 19 | 404.1633 | 3587.0467 | 0.53434 | 3871.5306 | 0.68667 | 284.4839 | 0.15233
1370 | MCLU-65to135-MBT-CZ13-2020-19IEER | CZ13 | MBT | 2020 | 65to135 | 12 | 19 | 379.0199 | 3425.414 | 0.51621 | 3707.4077 | 0.66848 | 281.9937 | 0.15227
1371 | MCLU-65to135-MLI-CZ13-2003-19IEER | CZ13 | MLI | 2003 | 65to135 | 12 | 19 | 282.2346 | 2480.8041 | 0.3939 | 2750.6964 | 0.50447 | 269.8922 | 0.11057
1372 | MCLU-65to135-MLI-CZ13-2007-19IEER | CZ13 | MLI | 2007 | 65to135 | 12 | 19 | 276.5799 | 2523.9429 | 0.39772 | 2793.0271 | 0.50832 | 269.0841 | 0.1106
1373 | MCLU-65to135-MLI-CZ13-2011-19IEER | CZ13 | MLI | 2011 | 65to135 | 12 | 19 | 251.9734 | 2736.828 | 0.41428 | 3002.9545 | 0.52503 | 266.1265 | 0.11076
1374 | MCLU-65to135-MLI-CZ13-2015-19IEER | CZ13 | MLI | 2015 | 65to135 | 12 | 19 | 249.5876 | 2743.2321 | 0.41521 | 3008.9886 | 0.52583 | 265.7565 | 0.11062
1375 | MCLU-65to135-MLI-CZ13-2020-19IEER | CZ13 | MLI | 2020 | 65to135 | 12 | 19 | 235.0697 | 2453.3038 | 0.3837 | 2716.285 | 0.49491 | 262.9812 | 0.11121
1376 | MCLU-65to135-Mtl-CZ13-2003-19IEER | CZ13 | Mtl | 2003 | 65to135 | 12 | 19 | 55.3036 | 3181.4725 | 0.82684 | 3283.7604 | 0.86218 | 102.2879 | 0.035338
1377 | MCLU-65to135-Mtl-CZ13-2007-19IEER | CZ13 | Mtl | 2007 | 65to135 | 12 | 19 | 55.3036 | 3029.8015 | 0.76247 | 3131.9267 | 0.79774 | 102.1252 | 0.035263
1378 | MCLU-65to135-Mtl-CZ13-2011-19IEER | CZ13 | Mtl | 2011 | 65to135 | 12 | 19 | 53.7024 | 3055.3402 | 0.76563 | 3157.9207 | 0.80087 | 102.5806 | 0.035236
1379 | MCLU-65to135-Mtl-CZ13-2015-19IEER | CZ13 | Mtl | 2015 | 65to135 | 12 | 19 | 45.8278 | 3190.5437 | 0.76641 | 3301.3952 | 0.80481 | 110.8515 | 0.038396
1380 | MCLU-65to135-Mtl-CZ13-2020-19IEER | CZ13 | Mtl | 2020 | 65to135 | 12 | 19 | 45.693 | 3123.3092 | 0.75771 | 3231.9532 | 0.79556 | 108.6439 | 0.037851
1381 | MCLU-65to135-Nrs-CZ13-2003-19IEER | CZ13 | Nrs | 2003 | 65to135 | 12 | 19 | 186.7716 | 4588.8291 | 0.96918 | 4845.8528 | 1.0678 | 257.0236 | 0.098628
1382 | MCLU-65to135-Nrs-CZ13-2007-19IEER | CZ13 | Nrs | 2007 | 65to135 | 12 | 19 | 186.5963 | 4490.4633 | 0.92916 | 4747.314 | 1.0275 | 256.8507 | 0.098369
1383 | MCLU-65to135-Nrs-CZ13-2011-19IEER | CZ13 | Nrs | 2011 | 65to135 | 12 | 19 | 185.0923 | 4529.8499 | 0.92448 | 4786.0584 | 1.0226 | 256.2085 | 0.098076
1384 | MCLU-65to135-Nrs-CZ13-2015-19IEER | CZ13 | Nrs | 2015 | 65to135 | 12 | 19 | 182.9982 | 4443.8135 | 0.87575 | 4697.4142 | 0.97348 | 253.6007 | 0.097735
1385 | MCLU-65to135-Nrs-CZ13-2020-19IEER | CZ13 | Nrs | 2020 | 65to135 | 12 | 19 | 182.3542 | 4080.8289 | 0.81629 | 4330.8361 | 0.91276 | 250.0072 | 0.096462
1386 | MCLU-65to135-OfL-CZ13-2003-19IEER | CZ13 | OfL | 2003 | 65to135 | 12 | 19 | 524.9748 | 3065.3946 | 0.49145 | 3353.7459 | 0.57091 | 288.3513 | 0.079467
1387 | MCLU-65to135-OfL-CZ13-2007-19IEER | CZ13 | OfL | 2007 | 65to135 | 12 | 19 | 524.4135 | 3067.9159 | 0.49158 | 3356.1224 | 0.571 | 288.2065 | 0.079415
1388 | MCLU-65to135-OfL-CZ13-2011-19IEER | CZ13 | OfL | 2011 | 65to135 | 12 | 19 | 500.9734 | 3155.4041 | 0.49828 | 3440.5945 | 0.57607 | 285.1904 | 0.07778
1389 | MCLU-65to135-OfL-CZ13-2015-19IEER | CZ13 | OfL | 2015 | 65to135 | 12 | 19 | 502.6908 | 3099.6432 | 0.49226 | 3383.1112 | 0.57036 | 283.468 | 0.078097
1390 | MCLU-65to135-OfL-CZ13-2020-19IEER | CZ13 | OfL | 2020 | 65to135 | 12 | 19 | 490.625 | 2946.4166 | 0.4744 | 3229.5828 | 0.55218 | 283.1662 | 0.077786
1391 | MCLU-65to135-OfS-CZ13-2003-19IEER | CZ13 | OfS | 2003 | 65to135 | 12 | 19 | 36.2548 | 2263.5201 | 0.37055 | 2549.6551 | 0.45106 | 286.135 | 0.080508
1392 | MCLU-65to135-OfS-CZ13-2007-19IEER | CZ13 | OfS | 2007 | 65to135 | 12 | 19 | 36.1437 | 2268.6716 | 0.3706 | 2554.397 | 0.4509 | 285.7254 | 0.080302
1393 | MCLU-65to135-OfS-CZ13-2011-19IEER | CZ13 | OfS | 2011 | 65to135 | 12 | 19 | 35.4097 | 2285.6089 | 0.3698 | 2570.3241 | 0.44893 | 284.7153 | 0.079138
1394 | MCLU-65to135-OfS-CZ13-2015-19IEER | CZ13 | OfS | 2015 | 65to135 | 12 | 19 | 32.4013 | 2423.2433 | 0.38067 | 2702.7286 | 0.45768 | 279.4853 | 0.077013
1395 | MCLU-65to135-OfS-CZ13-2020-19IEER | CZ13 | OfS | 2020 | 65to135 | 12 | 19 | 31.6167 | 2287.9251 | 0.36171 | 2566.691 | 0.43845 | 278.766 | 0.076733
1396 | MCLU-65to135-RFF-CZ13-2003-19IEER | CZ13 | RFF | 2003 | 65to135 | 12 | 19 | 9.6982 | 4470.7155 | 1.0724 | 4975.8927 | 1.2794 | 505.1772 | 0.207
1397 | MCLU-65to135-RFF-CZ13-2007-19IEER | CZ13 | RFF | 2007 | 65to135 | 12 | 19 | 9.5946 | 4512.7064 | 1.0794 | 5019.1562 | 1.2861 | 506.4498 | 0.20673
1398 | MCLU-65to135-RFF-CZ13-2011-19IEER | CZ13 | RFF | 2011 | 65to135 | 12 | 19 | 9.1587 | 4694.8754 | 1.1018 | 5204.8047 | 1.3078 | 509.9293 | 0.20596
1399 | MCLU-65to135-RFF-CZ13-2015-19IEER | CZ13 | RFF | 2015 | 65to135 | 12 | 19 | 9.1235 | 4506.3445 | 1.067 | 5013.3865 | 1.2739 | 507.042 | 0.20689
1400 | MCLU-65to135-RFF-CZ13-2020-19IEER | CZ13 | RFF | 2020 | 65to135 | 12 | 19 | 8.7592 | 4135.9473 | 1.0104 | 4642.4697 | 1.2171 | 506.5223 | 0.20668
1401 | MCLU-65to135-RSD-CZ13-2003-19IEER | CZ13 | RSD | 2003 | 65to135 | 12 | 19 | 17.9837 | 4264.4262 | 1.0396 | 4698.8128 | 1.252 | 434.3867 | 0.21238
1402 | MCLU-65to135-RSD-CZ13-2007-19IEER | CZ13 | RSD | 2007 | 65to135 | 12 | 19 | 17.7669 | 4309.6286 | 1.047 | 4745.3135 | 1.2588 | 435.6849 | 0.21178
1403 | MCLU-65to135-RSD-CZ13-2011-19IEER | CZ13 | RSD | 2011 | 65to135 | 12 | 19 | 17.3516 | 4402.4711 | 1.0622 | 4841.3103 | 1.2728 | 438.8391 | 0.2106
1404 | MCLU-65to135-RSD-CZ13-2015-19IEER | CZ13 | RSD | 2015 | 65to135 | 12 | 19 | 17.1687 | 4256.6855 | 1.0357 | 4692.3142 | 1.2464 | 435.6286 | 0.21066
1405 | MCLU-65to135-RSD-CZ13-2020-19IEER | CZ13 | RSD | 2020 | 65to135 | 12 | 19 | 16.2525 | 3821.5901 | 0.96372 | 4257.0434 | 1.1714 | 435.4533 | 0.20771
1406 | MCLU-65to135-Rt3-CZ13-2003-19IEER | CZ13 | Rt3 | 2003 | 65to135 | 12 | 19 | 326.0871 | 4357.3003 | 0.97657 | 4787.1064 | 1.2015 | 429.8061 | 0.22495
1407 | MCLU-65to135-Rt3-CZ13-2007-19IEER | CZ13 | Rt3 | 2007 | 65to135 | 12 | 19 | 324.8538 | 4371.3601 | 0.97765 | 4800.6971 | 1.2023 | 429.3371 | 0.22463
1408 | MCLU-65to135-Rt3-CZ13-2011-19IEER | CZ13 | Rt3 | 2011 | 65to135 | 12 | 19 | 309.8186 | 4560.2584 | 0.99461 | 4985.8605 | 1.2202 | 425.6022 | 0.22561
1409 | MCLU-65to135-Rt3-CZ13-2015-19IEER | CZ13 | Rt3 | 2015 | 65to135 | 12 | 19 | 300.8335 | 4252.2355 | 0.94336 | 4678.6583 | 1.1707 | 426.4228 | 0.22736
1410 | MCLU-65to135-Rt3-CZ13-2020-19IEER | CZ13 | Rt3 | 2020 | 65to135 | 12 | 19 | 289.4048 | 3935.233 | 0.89255 | 4362.0139 | 1.1202 | 426.7808 | 0.22764
1411 | MCLU-65to135-RtL-CZ13-2003-19IEER | CZ13 | RtL | 2003 | 65to135 | 12 | 19 | 286.6598 | 4708.4378 | 1.0493 | 5171.3382 | 1.2755 | 462.9004 | 0.22619
1412 | MCLU-65to135-RtL-CZ13-2007-19IEER | CZ13 | RtL | 2007 | 65to135 | 12 | 19 | 282.1455 | 4775.698 | 1.0586 | 5237.2023 | 1.2851 | 461.5043 | 0.22644
1413 | MCLU-65to135-RtL-CZ13-2011-19IEER | CZ13 | RtL | 2011 | 65to135 | 12 | 19 | 270.5723 | 4965.7809 | 1.0835 | 5423.8752 | 1.3105 | 458.0942 | 0.22702
1414 | MCLU-65to135-RtL-CZ13-2015-19IEER | CZ13 | RtL | 2015 | 65to135 | 12 | 19 | 263.0452 | 4774.6342 | 1.0648 | 5234.1096 | 1.2928 | 459.4753 | 0.22797
1415 | MCLU-65to135-RtL-CZ13-2020-19IEER | CZ13 | RtL | 2020 | 65to135 | 12 | 19 | 248.4226 | 4585.0111 | 1.0548 | 5044.1841 | 1.2844 | 459.173 | 0.22962
1416 | MCLU-65to135-RtS-CZ13-2003-19IEER | CZ13 | RtS | 2003 | 65to135 | 12 | 19 | 21.7444 | 2885.5014 | 0.69888 | 3308.6149 | 0.88959 | 423.1134 | 0.19071
1417 | MCLU-65to135-RtS-CZ13-2007-19IEER | CZ13 | RtS | 2007 | 65to135 | 12 | 19 | 21.4307 | 2919.5265 | 0.7025 | 3341.9794 | 0.89306 | 422.4529 | 0.19057
1418 | MCLU-65to135-RtS-CZ13-2011-19IEER | CZ13 | RtS | 2011 | 65to135 | 12 | 19 | 20.3893 | 3040.3701 | 0.71268 | 3459.9362 | 0.90341 | 419.5661 | 0.19073
1419 | MCLU-65to135-RtS-CZ13-2015-19IEER | CZ13 | RtS | 2015 | 65to135 | 12 | 19 | 20.1361 | 2843.606 | 0.67631 | 3261.6249 | 0.86862 | 418.0189 | 0.19231
1420 | MCLU-65to135-RtS-CZ13-2020-19IEER | CZ13 | RtS | 2020 | 65to135 | 12 | 19 | 19.3858 | 2689.7456 | 0.65236 | 3106.8674 | 0.84547 | 417.1218 | 0.19311
1421 | MCLU-65to135-SCn-CZ13-2003-19IEER | CZ13 | SCn | 2003 | 65to135 | 12 | 19 | 383.1443 | 2154.3635 | 0.31832 | 2491.6357 | 0.4341 | 337.2722 | 0.11578
1422 | MCLU-65to135-SCn-CZ13-2007-19IEER | CZ13 | SCn | 2007 | 65to135 | 12 | 19 | 360.4834 | 2270.092 | 0.33008 | 2601.9482 | 0.44909 | 331.8561 | 0.11901
1423 | MCLU-65to135-SCn-CZ13-2011-19IEER | CZ13 | SCn | 2011 | 65to135 | 12 | 19 | 321.6145 | 2497.5649 | 0.34513 | 2840.8318 | 0.46577 | 343.2669 | 0.12063
1424 | MCLU-65to135-SCn-CZ13-2015-19IEER | CZ13 | SCn | 2015 | 65to135 | 12 | 19 | 323.8433 | 2477.7229 | 0.33967 | 2819.453 | 0.45979 | 341.7301 | 0.12011
1425 | MCLU-65to135-SCn-CZ13-2020-19IEER | CZ13 | SCn | 2020 | 65to135 | 12 | 19 | 294.2458 | 2366.6266 | 0.33273 | 2710.9855 | 0.4519 | 344.3589 | 0.11916
1426 | MCLU-65to135-WRf-CZ13-2003-19IEER | CZ13 | WRf | 2003 | 65to135 | 12 | 19 | 16.1166 | 239222.3015 | 33.3685 | 239674.1002 | 33.5127 | 451.7986 | 0.14414
1427 | MCLU-65to135-WRf-CZ13-2007-19IEER | CZ13 | WRf | 2007 | 65to135 | 12 | 19 | 15.2881 | 243400.9431 | 32.6301 | 243867.1919 | 32.7765 | 466.2488 | 0.14638
1428 | MCLU-65to135-WRf-CZ13-2011-19IEER | CZ13 | WRf | 2011 | 65to135 | 12 | 19 | 16.9112 | 211272.7614 | 27.2936 | 211684.8643 | 27.413 | 412.1028 | 0.1194
1429 | MCLU-65to135-WRf-CZ13-2015-19IEER | CZ13 | WRf | 2015 | 65to135 | 12 | 19 | 16.623 | 214912.4872 | 27.7549 | 215318.2109 | 27.8704 | 405.7236 | 0.11551
1430 | MCLU-65to135-WRf-CZ13-2020-19IEER | CZ13 | WRf | 2020 | 65to135 | 12 | 19 | 16.6173 | 202789.1901 | 26.2005 | 203164.0517 | 26.3063 | 374.8615 | 0.10571
1431 | MCLU-65to135-Asm-CZ14-2003-19IEER | CZ14 | Asm | 2003 | 65to135 | 12 | 19 | 438.2576 | 1792.6318 | 0.46876 | 2201.4755 | 0.63058 | 408.8437 | 0.16181
1432 | MCLU-65to135-Asm-CZ14-2007-19IEER | CZ14 | Asm | 2007 | 65to135 | 12 | 19 | 434.9347 | 1802.7578 | 0.47086 | 2211.7319 | 0.6325 | 408.9741 | 0.16164
1433 | MCLU-65to135-Asm-CZ14-2011-19IEER | CZ14 | Asm | 2011 | 65to135 | 12 | 19 | 418.897 | 1857.9312 | 0.4733 | 2267.9114 | 0.63317 | 409.9803 | 0.15987
1434 | MCLU-65to135-Asm-CZ14-2015-19IEER | CZ14 | Asm | 2015 | 65to135 | 12 | 19 | 407.1967 | 1872.2834 | 0.47367 | 2279.3743 | 0.63392 | 407.0909 | 0.16025
1435 | MCLU-65to135-Asm-CZ14-2020-19IEER | CZ14 | Asm | 2020 | 65to135 | 12 | 19 | 399.1788 | 1763.3448 | 0.45265 | 2168.8541 | 0.61266 | 405.5093 | 0.16
1436 | MCLU-65to135-ECC-CZ14-2003-19IEER | CZ14 | ECC | 2003 | 65to135 | 12 | 19 | 967.9134 | 2200.8323 | 0.60644 | 2513.2428 | 0.77431 | 312.4105 | 0.16787
1437 | MCLU-65to135-ECC-CZ14-2007-19IEER | CZ14 | ECC | 2007 | 65to135 | 12 | 19 | 966.0733 | 2203.6388 | 0.60639 | 2515.5479 | 0.77383 | 311.9091 | 0.16744
1438 | MCLU-65to135-ECC-CZ14-2011-19IEER | CZ14 | ECC | 2011 | 65to135 | 12 | 19 | 941.9427 | 2243.0882 | 0.60314 | 2550.2999 | 0.7685 | 307.2117 | 0.16536
1439 | MCLU-65to135-ECC-CZ14-2015-19IEER | CZ14 | ECC | 2015 | 65to135 | 12 | 19 | 907.3372 | 2282.6606 | 0.6051 | 2583.8662 | 0.77089 | 301.2056 | 0.16579
1440 | MCLU-65to135-ECC-CZ14-2020-19IEER | CZ14 | ECC | 2020 | 65to135 | 12 | 19 | 874.5422 | 2009.4489 | 0.55884 | 2309.2433 | 0.72447 | 299.7944 | 0.16563
1441 | MCLU-65to135-EPr-CZ14-2003-19IEER | CZ14 | EPr | 2003 | 65to135 | 12 | 19 | 167.7341 | 1399.3511 | 0.34578 | 1595.1753 | 0.44949 | 195.8242 | 0.1037
1442 | MCLU-65to135-EPr-CZ14-2007-19IEER | CZ14 | EPr | 2007 | 65to135 | 12 | 19 | 166.207 | 1409.6072 | 0.34718 | 1604.8007 | 0.4506 | 195.1935 | 0.10342
1443 | MCLU-65to135-EPr-CZ14-2011-19IEER | CZ14 | EPr | 2011 | 65to135 | 12 | 19 | 162.7005 | 1435.6257 | 0.35063 | 1629.9934 | 0.45377 | 194.3677 | 0.10314
1444 | MCLU-65to135-EPr-CZ14-2015-19IEER | CZ14 | EPr | 2015 | 65to135 | 12 | 19 | 155.0627 | 1473.093 | 0.35423 | 1655.6322 | 0.4576 | 182.5392 | 0.10337
1445 | MCLU-65to135-EPr-CZ14-2020-19IEER | CZ14 | EPr | 2020 | 65to135 | 12 | 19 | 149.2783 | 1305.3171 | 0.32206 | 1486.1628 | 0.4253 | 180.8457 | 0.10325
1446 | MCLU-65to135-ERC-CZ14-2003-19IEER | CZ14 | ERC | 2003 | 65to135 | 12 | 19 | 7.8057 | 1139.9757 | 0.2448 | 1309.076 | 0.29188 | 169.1002 | 0.047082
1447 | MCLU-65to135-ERC-CZ14-2007-19IEER | CZ14 | ERC | 2007 | 65to135 | 12 | 19 | 7.7794 | 1142.4847 | 0.24477 | 1310.858 | 0.29157 | 168.3733 | 0.046802
1448 | MCLU-65to135-ERC-CZ14-2011-19IEER | CZ14 | ERC | 2011 | 65to135 | 12 | 19 | 7.5738 | 1162.0228 | 0.24346 | 1326.1395 | 0.28774 | 164.1167 | 0.044281
1449 | MCLU-65to135-ERC-CZ14-2015-19IEER | CZ14 | ERC | 2015 | 65to135 | 12 | 19 | 7.4636 | 1154.759 | 0.24023 | 1313.2634 | 0.28197 | 158.5044 | 0.041741
1450 | MCLU-65to135-ERC-CZ14-2020-19IEER | CZ14 | ERC | 2020 | 65to135 | 12 | 19 | 7.2808 | 1015.3602 | 0.2124 | 1171.922 | 0.25203 | 156.5618 | 0.039634
1451 | MCLU-65to135-ESe-CZ14-2003-19IEER | CZ14 | ESe | 2003 | 65to135 | 12 | 19 | 497.114 | 1559.6306 | 0.33048 | 1777.8812 | 0.43426 | 218.2507 | 0.10378
1452 | MCLU-65to135-ESe-CZ14-2007-19IEER | CZ14 | ESe | 2007 | 65to135 | 12 | 19 | 495.4443 | 1563.6712 | 0.33067 | 1781.5403 | 0.43425 | 217.8691 | 0.10358
1453 | MCLU-65to135-ESe-CZ14-2011-19IEER | CZ14 | ESe | 2011 | 65to135 | 12 | 19 | 484.0533 | 1586.6202 | 0.32571 | 1798.8428 | 0.42828 | 212.2226 | 0.10257
1454 | MCLU-65to135-ESe-CZ14-2015-19IEER | CZ14 | ESe | 2015 | 65to135 | 12 | 19 | 472.1788 | 1592.7469 | 0.32098 | 1798.1939 | 0.42389 | 205.4469 | 0.10291
1455 | MCLU-65to135-ESe-CZ14-2020-19IEER | CZ14 | ESe | 2020 | 65to135 | 12 | 19 | 455.541 | 1393.7882 | 0.30006 | 1597.1862 | 0.40303 | 203.3979 | 0.10297
1456 | MCLU-65to135-EUn-CZ14-2003-19IEER | CZ14 | EUn | 2003 | 65to135 | 12 | 19 | 2856.858 | 2443.9192 | 0.72129 | 2759.5269 | 0.87009 | 315.6076 | 0.1488
1457 | MCLU-65to135-EUn-CZ14-2007-19IEER | CZ14 | EUn | 2007 | 65to135 | 12 | 19 | 2841.3491 | 2435.0066 | 0.71655 | 2750.4163 | 0.86532 | 315.4096 | 0.14878
1458 | MCLU-65to135-EUn-CZ14-2011-19IEER | CZ14 | EUn | 2011 | 65to135 | 12 | 19 | 2740.5652 | 2501.6381 | 0.7258 | 2816.4153 | 0.87469 | 314.7772 | 0.14889
1459 | MCLU-65to135-EUn-CZ14-2015-19IEER | CZ14 | EUn | 2015 | 65to135 | 12 | 19 | 2613.1809 | 2558.2245 | 0.73763 | 2872.1409 | 0.88826 | 313.9164 | 0.15063
1460 | MCLU-65to135-EUn-CZ14-2020-19IEER | CZ14 | EUn | 2020 | 65to135 | 12 | 19 | 2519.24 | 2339.2677 | 0.69076 | 2651.102 | 0.84096 | 311.8342 | 0.1502
1461 | MCLU-65to135-Gro-CZ14-2003-19IEER | CZ14 | Gro | 2003 | 65to135 | 12 | 19 | 154.9342 | 10785.9544 | 1.603 | 11200.5301 | 1.7453 | 414.5757 | 0.1423
1462 | MCLU-65to135-Gro-CZ14-2007-19IEER | CZ14 | Gro | 2007 | 65to135 | 12 | 19 | 152.5802 | 9910.6793 | 1.5161 | 10338.9084 | 1.6715 | 428.2291 | 0.15541
1463 | MCLU-65to135-Gro-CZ14-2011-19IEER | CZ14 | Gro | 2011 | 65to135 | 12 | 19 | 143.784 | 10485.5073 | 1.5841 | 10905.843 | 1.7364 | 420.3357 | 0.15223
1464 | MCLU-65to135-Gro-CZ14-2015-19IEER | CZ14 | Gro | 2015 | 65to135 | 12 | 19 | 139.2932 | 10361.1973 | 1.5636 | 10767.1104 | 1.7118 | 405.9131 | 0.1482
1465 | MCLU-65to135-Gro-CZ14-2020-19IEER | CZ14 | Gro | 2020 | 65to135 | 12 | 19 | 135.6144 | 10306.3121 | 1.5489 | 10702.263 | 1.6958 | 395.9509 | 0.14693
1466 | MCLU-65to135-Hsp-CZ14-2003-19IEER | CZ14 | Hsp | 2003 | 65to135 | 12 | 19 | 686.5657 | 4252.8559 | 0.7031 | 4806.7132 | 0.86287 | 553.8573 | 0.15977
1467 | MCLU-65to135-Hsp-CZ14-2007-19IEER | CZ14 | Hsp | 2007 | 65to135 | 12 | 19 | 686.3582 | 4253.1545 | 0.70274 | 4806.576 | 0.86224 | 553.4214 | 0.1595
1468 | MCLU-65to135-Hsp-CZ14-2011-19IEER | CZ14 | Hsp | 2011 | 65to135 | 12 | 19 | 680.4571 | 4264.4123 | 0.6899 | 4814.7236 | 0.84858 | 550.3113 | 0.15869
1469 | MCLU-65to135-Hsp-CZ14-2015-19IEER | CZ14 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 4229.5763 | 0.68004 | 4778.2509 | 0.83835 | 548.6745 | 0.15831
1470 | MCLU-65to135-Hsp-CZ14-2020-19IEER | CZ14 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3715.4924 | 0.6066 | 4256.9357 | 0.76168 | 541.4434 | 0.15508
1471 | MCLU-65to135-Htl-CZ14-2003-19IEER | CZ14 | Htl | 2003 | 65to135 | 12 | 19 | 314.1184 | 3239.1058 | 0.6592 | 3368.0696 | 0.70277 | 128.9638 | 0.043571
1472 | MCLU-65to135-Htl-CZ14-2007-19IEER | CZ14 | Htl | 2007 | 65to135 | 12 | 19 | 313.7047 | 3099.5271 | 0.61672 | 3228.4923 | 0.66024 | 128.9652 | 0.04352
1473 | MCLU-65to135-Htl-CZ14-2011-19IEER | CZ14 | Htl | 2011 | 65to135 | 12 | 19 | 303.5869 | 3127.7895 | 0.62149 | 3256.4482 | 0.66464 | 128.6587 | 0.043145
1474 | MCLU-65to135-Htl-CZ14-2015-19IEER | CZ14 | Htl | 2015 | 65to135 | 12 | 19 | 269.5236 | 3184.9388 | 0.62725 | 3321.8445 | 0.67373 | 136.9057 | 0.046483
1475 | MCLU-65to135-Htl-CZ14-2020-19IEER | CZ14 | Htl | 2020 | 65to135 | 12 | 19 | 267.3769 | 3101.5328 | 0.61706 | 3235.4553 | 0.66251 | 133.9225 | 0.045445
1476 | MCLU-65to135-MBT-CZ14-2003-19IEER | CZ14 | MBT | 2003 | 65to135 | 12 | 19 | 447.5687 | 3320.4303 | 0.5326 | 3618.6984 | 0.66021 | 298.2682 | 0.12761
1477 | MCLU-65to135-MBT-CZ14-2007-19IEER | CZ14 | MBT | 2007 | 65to135 | 12 | 19 | 440.0412 | 3373.0039 | 0.53867 | 3669.8597 | 0.66585 | 296.8558 | 0.12718
1478 | MCLU-65to135-MBT-CZ14-2011-19IEER | CZ14 | MBT | 2011 | 65to135 | 12 | 19 | 415.8387 | 3508.0901 | 0.55306 | 3802.8205 | 0.67976 | 294.7304 | 0.1267
1479 | MCLU-65to135-MBT-CZ14-2015-19IEER | CZ14 | MBT | 2015 | 65to135 | 12 | 19 | 406.0856 | 3553.405 | 0.55742 | 3847.1477 | 0.68461 | 293.7427 | 0.12719
1480 | MCLU-65to135-MBT-CZ14-2020-19IEER | CZ14 | MBT | 2020 | 65to135 | 12 | 19 | 381.1159 | 3391.1376 | 0.53564 | 3683.0855 | 0.66282 | 291.9479 | 0.12718
1481 | MCLU-65to135-MLI-CZ14-2003-19IEER | CZ14 | MLI | 2003 | 65to135 | 12 | 19 | 281.5122 | 2465.1631 | 0.40329 | 2741.5088 | 0.50497 | 276.3458 | 0.10169
1482 | MCLU-65to135-MLI-CZ14-2007-19IEER | CZ14 | MLI | 2007 | 65to135 | 12 | 19 | 276.3047 | 2505.0131 | 0.40813 | 2780.8579 | 0.50991 | 275.8448 | 0.10178
1483 | MCLU-65to135-MLI-CZ14-2011-19IEER | CZ14 | MLI | 2011 | 65to135 | 12 | 19 | 244.977 | 2784.0677 | 0.43796 | 3058.4027 | 0.53954 | 274.3351 | 0.10158
1484 | MCLU-65to135-MLI-CZ14-2015-19IEER | CZ14 | MLI | 2015 | 65to135 | 12 | 19 | 242.0468 | 2797.215 | 0.43974 | 3071.4189 | 0.54213 | 274.204 | 0.10239
1485 | MCLU-65to135-MLI-CZ14-2020-19IEER | CZ14 | MLI | 2020 | 65to135 | 12 | 19 | 227.6369 | 2502.2815 | 0.40292 | 2773.3511 | 0.50472 | 271.0696 | 0.1018
1486 | MCLU-65to135-Mtl-CZ14-2003-19IEER | CZ14 | Mtl | 2003 | 65to135 | 12 | 19 | 55.8255 | 3216.038 | 0.63932 | 3315.8568 | 0.66795 | 99.8188 | 0.028623
1487 | MCLU-65to135-Mtl-CZ14-2007-19IEER | CZ14 | Mtl | 2007 | 65to135 | 12 | 19 | 55.8255 | 3065.3216 | 0.59306 | 3164.9533 | 0.62164 | 99.6318 | 0.028582
1488 | MCLU-65to135-Mtl-CZ14-2011-19IEER | CZ14 | Mtl | 2011 | 65to135 | 12 | 19 | 53.3217 | 3098.1418 | 0.60099 | 3198.2124 | 0.62964 | 100.0706 | 0.028653
1489 | MCLU-65to135-Mtl-CZ14-2015-19IEER | CZ14 | Mtl | 2015 | 65to135 | 12 | 19 | 45.6791 | 3193.217 | 0.6081 | 3301.546 | 0.63959 | 108.329 | 0.031491
1490 | MCLU-65to135-Mtl-CZ14-2020-19IEER | CZ14 | Mtl | 2020 | 65to135 | 12 | 19 | 45.5375 | 3126.9244 | 0.59982 | 3232.9161 | 0.63058 | 105.9917 | 0.030752
1491 | MCLU-65to135-Nrs-CZ14-2003-19IEER | CZ14 | Nrs | 2003 | 65to135 | 12 | 19 | 187.1257 | 4480.5038 | 0.82967 | 4748.5666 | 0.90701 | 268.0628 | 0.077342
1492 | MCLU-65to135-Nrs-CZ14-2007-19IEER | CZ14 | Nrs | 2007 | 65to135 | 12 | 19 | 186.9516 | 4388.2086 | 0.79971 | 4655.9109 | 0.8768 | 267.7022 | 0.077091
1493 | MCLU-65to135-Nrs-CZ14-2011-19IEER | CZ14 | Nrs | 2011 | 65to135 | 12 | 19 | 185.4681 | 4426.5919 | 0.79816 | 4693.1893 | 0.87491 | 266.5974 | 0.076751
1494 | MCLU-65to135-Nrs-CZ14-2015-19IEER | CZ14 | Nrs | 2015 | 65to135 | 12 | 19 | 183.2233 | 4338.6363 | 0.76247 | 4602.8392 | 0.83883 | 264.2029 | 0.076365
1495 | MCLU-65to135-Nrs-CZ14-2020-19IEER | CZ14 | Nrs | 2020 | 65to135 | 12 | 19 | 182.4954 | 3980.4797 | 0.70781 | 4241.013 | 0.78247 | 260.5333 | 0.074665
1496 | MCLU-65to135-OfL-CZ14-2003-19IEER | CZ14 | OfL | 2003 | 65to135 | 12 | 19 | 527.0961 | 3041.8417 | 0.50422 | 3339.2391 | 0.58771 | 297.3974 | 0.083491
1497 | MCLU-65to135-OfL-CZ14-2007-19IEER | CZ14 | OfL | 2007 | 65to135 | 12 | 19 | 526.3863 | 3045.3329 | 0.5046 | 3342.6365 | 0.58807 | 297.3036 | 0.083468
1498 | MCLU-65to135-OfL-CZ14-2011-19IEER | CZ14 | OfL | 2011 | 65to135 | 12 | 19 | 503.3612 | 3131.4661 | 0.51243 | 3426.7083 | 0.59551 | 295.2422 | 0.08309
1499 | MCLU-65to135-OfL-CZ14-2015-19IEER | CZ14 | OfL | 2015 | 65to135 | 12 | 19 | 507.8081 | 3059.8353 | 0.50376 | 3352.906 | 0.58684 | 293.0707 | 0.083082
1500 | MCLU-65to135-OfL-CZ14-2020-19IEER | CZ14 | OfL | 2020 | 65to135 | 12 | 19 | 495.5062 | 2908.8285 | 0.48373 | 3201.4652 | 0.56681 | 292.6367 | 0.083084
1501 | MCLU-65to135-OfS-CZ14-2003-19IEER | CZ14 | OfS | 2003 | 65to135 | 12 | 19 | 36.0845 | 2262.7697 | 0.38902 | 2556.4457 | 0.47202 | 293.676 | 0.082999
1502 | MCLU-65to135-OfS-CZ14-2007-19IEER | CZ14 | OfS | 2007 | 65to135 | 12 | 19 | 35.9752 | 2268.0593 | 0.38931 | 2561.3539 | 0.4722 | 293.2945 | 0.082894
1503 | MCLU-65to135-OfS-CZ14-2011-19IEER | CZ14 | OfS | 2011 | 65to135 | 12 | 19 | 35.2714 | 2284.0705 | 0.38933 | 2576.6609 | 0.47205 | 292.5905 | 0.082721
1504 | MCLU-65to135-OfS-CZ14-2015-19IEER | CZ14 | OfS | 2015 | 65to135 | 12 | 19 | 32.5787 | 2404.0564 | 0.40309 | 2692.2988 | 0.48512 | 288.2424 | 0.082029
1505 | MCLU-65to135-OfS-CZ14-2020-19IEER | CZ14 | OfS | 2020 | 65to135 | 12 | 19 | 31.7908 | 2269.3995 | 0.38226 | 2556.7979 | 0.46411 | 287.3984 | 0.081846
1506 | MCLU-65to135-RFF-CZ14-2003-19IEER | CZ14 | RFF | 2003 | 65to135 | 12 | 19 | 9.6926 | 4397.0577 | 0.86328 | 4883.4901 | 1.0298 | 486.4324 | 0.16655
1507 | MCLU-65to135-RFF-CZ14-2007-19IEER | CZ14 | RFF | 2007 | 65to135 | 12 | 19 | 9.5922 | 4437.6611 | 0.86935 | 4925.3423 | 1.0362 | 487.6812 | 0.16689
1508 | MCLU-65to135-RFF-CZ14-2011-19IEER | CZ14 | RFF | 2011 | 65to135 | 12 | 19 | 9.0271 | 4681.5041 | 0.89829 | 5173.8874 | 1.0648 | 492.3833 | 0.16647
1509 | MCLU-65to135-RFF-CZ14-2015-19IEER | CZ14 | RFF | 2015 | 65to135 | 12 | 19 | 8.9968 | 4483.5886 | 0.86388 | 4973.497 | 1.0307 | 489.9084 | 0.16681
1510 | MCLU-65to135-RFF-CZ14-2020-19IEER | CZ14 | RFF | 2020 | 65to135 | 12 | 19 | 8.6363 | 4108.6584 | 0.80701 | 4598.0302 | 0.97407 | 489.3719 | 0.16706
1511 | MCLU-65to135-RSD-CZ14-2003-19IEER | CZ14 | RSD | 2003 | 65to135 | 12 | 19 | 18.1151 | 4181.3457 | 0.81108 | 4603.3152 | 0.97868 | 421.9694 | 0.1676
1512 | MCLU-65to135-RSD-CZ14-2007-19IEER | CZ14 | RSD | 2007 | 65to135 | 12 | 19 | 17.9002 | 4226.0798 | 0.81759 | 4649.6618 | 0.98534 | 423.582 | 0.16775
1513 | MCLU-65to135-RSD-CZ14-2011-19IEER | CZ14 | RSD | 2011 | 65to135 | 12 | 19 | 17.5059 | 4313.3221 | 0.82952 | 4740.3727 | 0.99754 | 427.0506 | 0.16801
1514 | MCLU-65to135-RSD-CZ14-2015-19IEER | CZ14 | RSD | 2015 | 65to135 | 12 | 19 | 17.3178 | 4167.6676 | 0.8052 | 4591.6904 | 0.97327 | 424.0227 | 0.16807
1515 | MCLU-65to135-RSD-CZ14-2020-19IEER | CZ14 | RSD | 2020 | 65to135 | 12 | 19 | 16.3993 | 3736.2652 | 0.73643 | 4161.192 | 0.90344 | 424.9269 | 0.16701
1516 | MCLU-65to135-Rt3-CZ14-2003-19IEER | CZ14 | Rt3 | 2003 | 65to135 | 12 | 19 | 328.6503 | 4269.7148 | 0.80842 | 4707.3251 | 0.98078 | 437.6103 | 0.17236
1517 | MCLU-65to135-Rt3-CZ14-2007-19IEER | CZ14 | Rt3 | 2007 | 65to135 | 12 | 19 | 327.4777 | 4282.9549 | 0.80996 | 4720.1489 | 0.98216 | 437.1939 | 0.1722
1518 | MCLU-65to135-Rt3-CZ14-2011-19IEER | CZ14 | Rt3 | 2011 | 65to135 | 12 | 19 | 306.4806 | 4554.216 | 0.83842 | 4987.8898 | 1.0112 | 433.6738 | 0.17277
1519 | MCLU-65to135-Rt3-CZ14-2015-19IEER | CZ14 | Rt3 | 2015 | 65to135 | 12 | 19 | 297.22 | 4246.9825 | 0.7909 | 4681.1999 | 0.96322 | 434.2174 | 0.17232
1520 | MCLU-65to135-Rt3-CZ14-2020-19IEER | CZ14 | Rt3 | 2020 | 65to135 | 12 | 19 | 285.5845 | 3930.3802 | 0.7427 | 4364.693 | 0.91536 | 434.3128 | 0.17266
1521 | MCLU-65to135-RtL-CZ14-2003-19IEER | CZ14 | RtL | 2003 | 65to135 | 12 | 19 | 288.7503 | 4618.0918 | 0.87487 | 5089.1074 | 1.0512 | 471.0157 | 0.17632
1522 | MCLU-65to135-RtL-CZ14-2007-19IEER | CZ14 | RtL | 2007 | 65to135 | 12 | 19 | 284.2964 | 4683.8144 | 0.8845 | 5153.8456 | 1.061 | 470.0312 | 0.17652
1523 | MCLU-65to135-RtL-CZ14-2011-19IEER | CZ14 | RtL | 2011 | 65to135 | 12 | 19 | 270.708 | 4906.9018 | 0.91334 | 5374.8053 | 1.0905 | 467.9035 | 0.17713
1524 | MCLU-65to135-RtL-CZ14-2015-19IEER | CZ14 | RtL | 2015 | 65to135 | 12 | 19 | 263.2302 | 4714.1861 | 0.88842 | 5182.8796 | 1.0667 | 468.6935 | 0.17827
1525 | MCLU-65to135-RtL-CZ14-2020-19IEER | CZ14 | RtL | 2020 | 65to135 | 12 | 19 | 248.6705 | 4523.2566 | 0.86867 | 4991.9517 | 1.0484 | 468.6951 | 0.17973
1526 | MCLU-65to135-RtS-CZ14-2003-19IEER | CZ14 | RtS | 2003 | 65to135 | 12 | 19 | 21.7422 | 2844.1379 | 0.57078 | 3273.1616 | 0.7184 | 429.0237 | 0.14762
1527 | MCLU-65to135-RtS-CZ14-2007-19IEER | CZ14 | RtS | 2007 | 65to135 | 12 | 19 | 21.4359 | 2877.8295 | 0.57527 | 3306.4465 | 0.72265 | 428.617 | 0.14738
1528 | MCLU-65to135-RtS-CZ14-2011-19IEER | CZ14 | RtS | 2011 | 65to135 | 12 | 19 | 20.1184 | 3036.5215 | 0.59266 | 3462.0961 | 0.73874 | 425.5746 | 0.14609
1529 | MCLU-65to135-RtS-CZ14-2015-19IEER | CZ14 | RtS | 2015 | 65to135 | 12 | 19 | 19.8445 | 2834.8231 | 0.55825 | 3257.7608 | 0.70372 | 422.9377 | 0.14547
1530 | MCLU-65to135-RtS-CZ14-2020-19IEER | CZ14 | RtS | 2020 | 65to135 | 12 | 19 | 19.0541 | 2685.9113 | 0.53584 | 3108.1953 | 0.68198 | 422.284 | 0.14614
1531 | MCLU-65to135-SCn-CZ14-2003-19IEER | CZ14 | SCn | 2003 | 65to135 | 12 | 19 | 382.4155 | 2131.2765 | 0.31669 | 2481.0879 | 0.42692 | 349.8114 | 0.11022
1532 | MCLU-65to135-SCn-CZ14-2007-19IEER | CZ14 | SCn | 2007 | 65to135 | 12 | 19 | 360.7893 | 2240.9252 | 0.33067 | 2593.6947 | 0.44335 | 352.7696 | 0.11268
1533 | MCLU-65to135-SCn-CZ14-2011-19IEER | CZ14 | SCn | 2011 | 65to135 | 12 | 19 | 306.6162 | 2585.0908 | 0.36794 | 2946.1104 | 0.48184 | 361.0196 | 0.11389
1534 | MCLU-65to135-SCn-CZ14-2015-19IEER | CZ14 | SCn | 2015 | 65to135 | 12 | 19 | 315.9332 | 2507.5091 | 0.35221 | 2864.4326 | 0.46668 | 356.9235 | 0.11447
1535 | MCLU-65to135-SCn-CZ14-2020-19IEER | CZ14 | SCn | 2020 | 65to135 | 12 | 19 | 281.9873 | 2441.5567 | 0.35157 | 2798.5443 | 0.46319 | 356.9877 | 0.11162
1536 | MCLU-65to135-WRf-CZ14-2003-19IEER | CZ14 | WRf | 2003 | 65to135 | 12 | 19 | 13.2786 | 287233.8083 | 39.302 | 287705.3301 | 39.4369 | 471.5218 | 0.13487
1537 | MCLU-65to135-WRf-CZ14-2007-19IEER | CZ14 | WRf | 2007 | 65to135 | 12 | 19 | 12.5235 | 294092.8195 | 39.1962 | 294579.7832 | 39.334 | 486.9637 | 0.13779
1538 | MCLU-65to135-WRf-CZ14-2011-19IEER | CZ14 | WRf | 2011 | 65to135 | 12 | 19 | 14.9707 | 237322.5918 | 30.7591 | 237705.0444 | 30.8573 | 382.4526 | 0.098211
1539 | MCLU-65to135-WRf-CZ14-2015-19IEER | CZ14 | WRf | 2015 | 65to135 | 12 | 19 | 14.6897 | 241832.3954 | 31.336 | 242206.9252 | 31.4333 | 374.5298 | 0.097275
1540 | MCLU-65to135-WRf-CZ14-2020-19IEER | CZ14 | WRf | 2020 | 65to135 | 12 | 19 | 13.7346 | 244206.1044 | 31.6714 | 244572.305 | 31.7641 | 366.2006 | 0.092726
1541 | MCLU-65to135-Asm-CZ15-2003-19IEER | CZ15 | Asm | 2003 | 65to135 | 12 | 19 | 586.9822 | 1686.0076 | 0.46205 | 2277.6055 | 0.68831 | 591.5979 | 0.22627
1542 | MCLU-65to135-Asm-CZ15-2007-19IEER | CZ15 | Asm | 2007 | 65to135 | 12 | 19 | 583.0138 | 1692.2053 | 0.46299 | 2283.4217 | 0.68907 | 591.2164 | 0.22608
1543 | MCLU-65to135-Asm-CZ15-2011-19IEER | CZ15 | Asm | 2011 | 65to135 | 12 | 19 | 560.8509 | 1725.9296 | 0.45902 | 2313.6056 | 0.68347 | 587.676 | 0.22445
1544 | MCLU-65to135-Asm-CZ15-2015-19IEER | CZ15 | Asm | 2015 | 65to135 | 12 | 19 | 546.9875 | 1728.3431 | 0.45809 | 2312.7336 | 0.68246 | 584.3905 | 0.22437
1545 | MCLU-65to135-Asm-CZ15-2020-19IEER | CZ15 | Asm | 2020 | 65to135 | 12 | 19 | 536.9143 | 1644.3495 | 0.44102 | 2226.588 | 0.6644 | 582.2385 | 0.22338
1546 | MCLU-65to135-ECC-CZ15-2003-19IEER | CZ15 | ECC | 2003 | 65to135 | 12 | 19 | 1306.492 | 1946.5034 | 0.56465 | 2425.3493 | 0.7906 | 478.8459 | 0.22594
1547 | MCLU-65to135-ECC-CZ15-2007-19IEER | CZ15 | ECC | 2007 | 65to135 | 12 | 19 | 1303.323 | 1948.241 | 0.56412 | 2426.0437 | 0.7898 | 477.8027 | 0.22568
1548 | MCLU-65to135-ECC-CZ15-2011-19IEER | CZ15 | ECC | 2011 | 65to135 | 12 | 19 | 1265.6759 | 1961.6087 | 0.55462 | 2426.3307 | 0.7774 | 464.722 | 0.22278
1549 | MCLU-65to135-ECC-CZ15-2015-19IEER | CZ15 | ECC | 2015 | 65to135 | 12 | 19 | 1225.0354 | 1974.8268 | 0.55249 | 2431.0378 | 0.77535 | 456.211 | 0.22286
1550 | MCLU-65to135-ECC-CZ15-2020-19IEER | CZ15 | ECC | 2020 | 65to135 | 12 | 19 | 1191.7487 | 1755.1242 | 0.51587 | 2205.7649 | 0.73864 | 450.6407 | 0.22277
1551 | MCLU-65to135-EPr-CZ15-2003-19IEER | CZ15 | EPr | 2003 | 65to135 | 12 | 19 | 236.6059 | 1213.1598 | 0.2743 | 1525.2533 | 0.3994 | 312.0935 | 0.1251
1552 | MCLU-65to135-EPr-CZ15-2007-19IEER | CZ15 | EPr | 2007 | 65to135 | 12 | 19 | 234.397 | 1218.8733 | 0.27458 | 1529.234 | 0.39926 | 310.3606 | 0.12468
1553 | MCLU-65to135-EPr-CZ15-2011-19IEER | CZ15 | EPr | 2011 | 65to135 | 12 | 19 | 227.8361 | 1235.1568 | 0.27295 | 1539.6034 | 0.3962 | 304.4466 | 0.12326
1554 | MCLU-65to135-EPr-CZ15-2015-19IEER | CZ15 | EPr | 2015 | 65to135 | 12 | 19 | 219.9396 | 1229.871 | 0.26838 | 1523.0006 | 0.39157 | 293.1296 | 0.12319
1555 | MCLU-65to135-EPr-CZ15-2020-19IEER | CZ15 | EPr | 2020 | 65to135 | 12 | 19 | 213.4852 | 1100.6487 | 0.24636 | 1388.3471 | 0.36932 | 287.6984 | 0.12296
1556 | MCLU-65to135-ERC-CZ15-2003-19IEER | CZ15 | ERC | 2003 | 65to135 | 12 | 19 | 10.8337 | 1074.5085 | 0.20891 | 1373.3761 | 0.26786 | 298.8676 | 0.058944
1557 | MCLU-65to135-ERC-CZ15-2007-19IEER | CZ15 | ERC | 2007 | 65to135 | 12 | 19 | 10.79 | 1075.2152 | 0.20863 | 1372.2754 | 0.26688 | 297.0603 | 0.05825
1558 | MCLU-65to135-ERC-CZ15-2011-19IEER | CZ15 | ERC | 2011 | 65to135 | 12 | 19 | 10.2725 | 1085.262 | 0.20018 | 1368.4824 | 0.25073 | 283.2204 | 0.050549
1559 | MCLU-65to135-ERC-CZ15-2015-19IEER | CZ15 | ERC | 2015 | 65to135 | 12 | 19 | 10.2039 | 1069.7613 | 0.19652 | 1345.3511 | 0.24477 | 275.5899 | 0.048247
1560 | MCLU-65to135-ERC-CZ15-2020-19IEER | CZ15 | ERC | 2020 | 65to135 | 12 | 19 | 9.9937 | 960.5679 | 0.17823 | 1231.9501 | 0.22431 | 271.3822 | 0.046077
1561 | MCLU-65to135-ESe-CZ15-2003-19IEER | CZ15 | ESe | 2003 | 65to135 | 12 | 19 | 679.2773 | 1399.1206 | 0.26248 | 1753.231 | 0.38692 | 354.1105 | 0.12444
1562 | MCLU-65to135-ESe-CZ15-2007-19IEER | CZ15 | ESe | 2007 | 65to135 | 12 | 19 | 676.7987 | 1401.6136 | 0.26228 | 1754.7757 | 0.38651 | 353.1621 | 0.12423
1563 | MCLU-65to135-ESe-CZ15-2011-19IEER | CZ15 | ESe | 2011 | 65to135 | 12 | 19 | 658.0912 | 1400.1564 | 0.25238 | 1736.0976 | 0.3726 | 335.9412 | 0.12021
1564 | MCLU-65to135-ESe-CZ15-2015-19IEER | CZ15 | ESe | 2015 | 65to135 | 12 | 19 | 645.1341 | 1390.8108 | 0.24699 | 1716.5543 | 0.36671 | 325.7435 | 0.11973
1565 | MCLU-65to135-ESe-CZ15-2020-19IEER | CZ15 | ESe | 2020 | 65to135 | 12 | 19 | 627.9627 | 1233.387 | 0.23522 | 1554.4495 | 0.35494 | 321.0625 | 0.11972
1566 | MCLU-65to135-EUn-CZ15-2003-19IEER | CZ15 | EUn | 2003 | 65to135 | 12 | 19 | 3821.3904 | 2165.3115 | 0.67551 | 2635.9018 | 0.87809 | 470.5903 | 0.20258
1567 | MCLU-65to135-EUn-CZ15-2007-19IEER | CZ15 | EUn | 2007 | 65to135 | 12 | 19 | 3802.3333 | 2149.0683 | 0.6683 | 2619.1841 | 0.87087 | 470.1158 | 0.20257
1568 | MCLU-65to135-EUn-CZ15-2011-19IEER | CZ15 | EUn | 2011 | 65to135 | 12 | 19 | 3658.5237 | 2194.6178 | 0.67027 | 2661.2149 | 0.87259 | 466.5972 | 0.20232
1569 | MCLU-65to135-EUn-CZ15-2015-19IEER | CZ15 | EUn | 2015 | 65to135 | 12 | 19 | 3513.9087 | 2214.0602 | 0.67338 | 2679.4487 | 0.87779 | 465.3885 | 0.20441
1570 | MCLU-65to135-EUn-CZ15-2020-19IEER | CZ15 | EUn | 2020 | 65to135 | 12 | 19 | 3407.6056 | 2040.3539 | 0.63526 | 2501.5145 | 0.83919 | 461.1606 | 0.20393
1571 | MCLU-65to135-Gro-CZ15-2003-19IEER | CZ15 | Gro | 2003 | 65to135 | 12 | 19 | 193.6878 | 8617.1379 | 1.1878 | 9200.7709 | 1.3842 | 583.633 | 0.19645
1572 | MCLU-65to135-Gro-CZ15-2007-19IEER | CZ15 | Gro | 2007 | 65to135 | 12 | 19 | 190.8124 | 8002.9744 | 1.1658 | 8638.4291 | 1.3785 | 635.4548 | 0.21263
1573 | MCLU-65to135-Gro-CZ15-2011-19IEER | CZ15 | Gro | 2011 | 65to135 | 12 | 19 | 178.8178 | 8476.8997 | 1.2102 | 9101.4981 | 1.4189 | 624.5984 | 0.20869
1574 | MCLU-65to135-Gro-CZ15-2015-19IEER | CZ15 | Gro | 2015 | 65to135 | 12 | 19 | 173.9116 | 8333.0707 | 1.1836 | 8943.5369 | 1.3888 | 610.4662 | 0.20521
1575 | MCLU-65to135-Gro-CZ15-2020-19IEER | CZ15 | Gro | 2020 | 65to135 | 12 | 19 | 168.4869 | 8315.0799 | 1.1725 | 8914.744 | 1.3759 | 599.6642 | 0.20346
1576 | MCLU-65to135-Hsp-CZ15-2003-19IEER | CZ15 | Hsp | 2003 | 65to135 | 12 | 19 | 758.9354 | 4274.7032 | 0.75032 | 5073.558 | 0.97323 | 798.8548 | 0.22291
1577 | MCLU-65to135-Hsp-CZ15-2007-19IEER | CZ15 | Hsp | 2007 | 65to135 | 12 | 19 | 758.5112 | 4274.9614 | 0.74982 | 5073.0205 | 0.97241 | 798.0592 | 0.22259
1578 | MCLU-65to135-Hsp-CZ15-2011-19IEER | CZ15 | Hsp | 2011 | 65to135 | 12 | 19 | 727.054 | 4395.1618 | 0.75326 | 5194.3345 | 0.97862 | 799.1727 | 0.22536
1579 | MCLU-65to135-Hsp-CZ15-2015-19IEER | CZ15 | Hsp | 2015 | 65to135 | 12 | 19 | 720.5464 | 4391.0665 | 0.74799 | 5190.1001 | 0.9745 | 799.0336 | 0.22651
1580 | MCLU-65to135-Hsp-CZ15-2020-19IEER | CZ15 | Hsp | 2020 | 65to135 | 12 | 19 | 710.2418 | 3932.4988 | 0.68325 | 4722.9562 | 0.90948 | 790.4573 | 0.22624
1581 | MCLU-65to135-Htl-CZ15-2003-19IEER | CZ15 | Htl | 2003 | 65to135 | 12 | 19 | 392.9883 | 3019.1387 | 0.74232 | 3224.306 | 0.80691 | 205.1673 | 0.064591
1582 | MCLU-65to135-Htl-CZ15-2007-19IEER | CZ15 | Htl | 2007 | 65to135 | 12 | 19 | 392.4501 | 2854.8267 | 0.68852 | 3059.7622 | 0.75308 | 204.9355 | 0.064559
1583 | MCLU-65to135-Htl-CZ15-2011-19IEER | CZ15 | Htl | 2011 | 65to135 | 12 | 19 | 379.9386 | 2888.5374 | 0.68797 | 3092.4438 | 0.75244 | 203.9064 | 0.064462
1584 | MCLU-65to135-Htl-CZ15-2015-19IEER | CZ15 | Htl | 2015 | 65to135 | 12 | 19 | 339.5957 | 2945.9047 | 0.67645 | 3162.5467 | 0.74572 | 216.642 | 0.069279
1585 | MCLU-65to135-Htl-CZ15-2020-19IEER | CZ15 | Htl | 2020 | 65to135 | 12 | 19 | 337.6664 | 2872.0618 | 0.66684 | 3085.1769 | 0.73546 | 213.1151 | 0.068619
1586 | MCLU-65to135-MBT-CZ15-2003-19IEER | CZ15 | MBT | 2003 | 65to135 | 12 | 19 | 576.5547 | 2839.5335 | 0.42144 | 3279.1558 | 0.58965 | 439.6223 | 0.16821
1587 | MCLU-65to135-MBT-CZ15-2007-19IEER | CZ15 | MBT | 2007 | 65to135 | 12 | 19 | 568.0004 | 2871.3244 | 0.42302 | 3308.6708 | 0.59049 | 437.3464 | 0.16747
1588 | MCLU-65to135-MBT-CZ15-2011-19IEER | CZ15 | MBT | 2011 | 65to135 | 12 | 19 | 540.0302 | 2948.8671 | 0.42499 | 3380.9918 | 0.59107 | 432.1247 | 0.16608
1589 | MCLU-65to135-MBT-CZ15-2015-19IEER | CZ15 | MBT | 2015 | 65to135 | 12 | 19 | 530.8689 | 2963.0344 | 0.42461 | 3393.2992 | 0.59149 | 430.2649 | 0.16688
1590 | MCLU-65to135-MBT-CZ15-2020-19IEER | CZ15 | MBT | 2020 | 65to135 | 12 | 19 | 504.3903 | 2798.7727 | 0.40461 | 3223.8527 | 0.57162 | 425.0801 | 0.16701
1591 | MCLU-65to135-MLI-CZ15-2003-19IEER | CZ15 | MLI | 2003 | 65to135 | 12 | 19 | 356.8215 | 2224.2839 | 0.34622 | 2637.8924 | 0.47239 | 413.6085 | 0.12616
1592 | MCLU-65to135-MLI-CZ15-2007-19IEER | CZ15 | MLI | 2007 | 65to135 | 12 | 19 | 351.5227 | 2247.0575 | 0.34782 | 2659.1775 | 0.47379 | 412.1199 | 0.12597
1593 | MCLU-65to135-MLI-CZ15-2011-19IEER | CZ15 | MLI | 2011 | 65to135 | 12 | 19 | 314.7924 | 2432.0551 | 0.34974 | 2835.7924 | 0.47043 | 403.7372 | 0.12069
1594 | MCLU-65to135-MLI-CZ15-2015-19IEER | CZ15 | MLI | 2015 | 65to135 | 12 | 19 | 312.0668 | 2434.9861 | 0.35021 | 2838.1179 | 0.47089 | 403.1318 | 0.12067
1595 | MCLU-65to135-MLI-CZ15-2020-19IEER | CZ15 | MLI | 2020 | 65to135 | 12 | 19 | 297.0503 | 2174.8737 | 0.32219 | 2570.9814 | 0.44221 | 396.1077 | 0.12002
1596 | MCLU-65to135-Mtl-CZ15-2003-19IEER | CZ15 | Mtl | 2003 | 65to135 | 12 | 19 | 69.9772 | 3048.816 | 0.72295 | 3196.5466 | 0.76389 | 147.7306 | 0.040942
1597 | MCLU-65to135-Mtl-CZ15-2007-19IEER | CZ15 | Mtl | 2007 | 65to135 | 12 | 19 | 69.9772 | 2864.1049 | 0.66445 | 3011.5947 | 0.70531 | 147.4899 | 0.040858
1598 | MCLU-65to135-Mtl-CZ15-2011-19IEER | CZ15 | Mtl | 2011 | 65to135 | 12 | 19 | 66.9706 | 2921.6199 | 0.66676 | 3070.4456 | 0.70838 | 148.8257 | 0.04162
1599 | MCLU-65to135-Mtl-CZ15-2015-19IEER | CZ15 | Mtl | 2015 | 65to135 | 12 | 19 | 57.7014 | 3037.0937 | 0.65076 | 3198.4354 | 0.69649 | 161.3417 | 0.045732
1600 | MCLU-65to135-Mtl-CZ15-2020-19IEER | CZ15 | Mtl | 2020 | 65to135 | 12 | 19 | 57.5512 | 2981.3538 | 0.64395 | 3139.9296 | 0.68911 | 158.5758 | 0.045166
1601 | MCLU-65to135-Nrs-CZ15-2003-19IEER | CZ15 | Nrs | 2003 | 65to135 | 12 | 19 | 210.005 | 4755.3409 | 0.9208 | 5129.5437 | 1.0289 | 374.2028 | 0.10806
1602 | MCLU-65to135-Nrs-CZ15-2007-19IEER | CZ15 | Nrs | 2007 | 65to135 | 12 | 19 | 209.5553 | 4618.6028 | 0.88123 | 4992.475 | 0.98891 | 373.8722 | 0.10768
1603 | MCLU-65to135-Nrs-CZ15-2011-19IEER | CZ15 | Nrs | 2011 | 65to135 | 12 | 19 | 202.5183 | 4735.1321 | 0.88658 | 5113.8272 | 0.99563 | 378.6951 | 0.10905
1604 | MCLU-65to135-Nrs-CZ15-2015-19IEER | CZ15 | Nrs | 2015 | 65to135 | 12 | 19 | 196.3228 | 4675.7671 | 0.85537 | 5055.3169 | 0.96549 | 379.5498 | 0.11011
1605 | MCLU-65to135-Nrs-CZ15-2020-19IEER | CZ15 | Nrs | 2020 | 65to135 | 12 | 19 | 193.696 | 4363.0826 | 0.80804 | 4735.9428 | 0.91657 | 372.8602 | 0.10853
1606 | MCLU-65to135-OfL-CZ15-2003-19IEER | CZ15 | OfL | 2003 | 65to135 | 12 | 19 | 638.5777 | 2782.7157 | 0.41665 | 3218.6891 | 0.50244 | 435.9734 | 0.085798
1607 | MCLU-65to135-OfL-CZ15-2007-19IEER | CZ15 | OfL | 2007 | 65to135 | 12 | 19 | 638.3271 | 2782.5502 | 0.41644 | 3218.0948 | 0.50214 | 435.5446 | 0.085698
1608 | MCLU-65to135-OfL-CZ15-2011-19IEER | CZ15 | OfL | 2011 | 65to135 | 12 | 19 | 609.3801 | 2845.2621 | 0.41865 | 3277.0004 | 0.50206 | 431.7383 | 0.083411
1609 | MCLU-65to135-OfL-CZ15-2015-19IEER | CZ15 | OfL | 2015 | 65to135 | 12 | 19 | 616.76 | 2783.7338 | 0.41412 | 3212.5245 | 0.49783 | 428.7907 | 0.083713
1610 | MCLU-65to135-OfL-CZ15-2020-19IEER | CZ15 | OfL | 2020 | 65to135 | 12 | 19 | 604.0998 | 2647.8233 | 0.39822 | 3074.2411 | 0.4813 | 426.4178 | 0.083073
1611 | MCLU-65to135-OfS-CZ15-2003-19IEER | CZ15 | OfS | 2003 | 65to135 | 12 | 19 | 43.9026 | 2144.2788 | 0.32606 | 2577.2715 | 0.41442 | 432.9927 | 0.088363
1612 | MCLU-65to135-OfS-CZ15-2007-19IEER | CZ15 | OfS | 2007 | 65to135 | 12 | 19 | 43.7703 | 2147.3543 | 0.32583 | 2579.5173 | 0.41395 | 432.1631 | 0.088121
1613 | MCLU-65to135-OfS-CZ15-2011-19IEER | CZ15 | OfS | 2011 | 65to135 | 12 | 19 | 42.2248 | 2178.649 | 0.32275 | 2606.8042 | 0.40797 | 428.1552 | 0.085216
1614 | MCLU-65to135-OfS-CZ15-2015-19IEER | CZ15 | OfS | 2015 | 65to135 | 12 | 19 | 39.3311 | 2256.959 | 0.32768 | 2678.4437 | 0.41101 | 421.4846 | 0.083321
1615 | MCLU-65to135-OfS-CZ15-2020-19IEER | CZ15 | OfS | 2020 | 65to135 | 12 | 19 | 38.4948 | 2136.1993 | 0.31052 | 2555.0686 | 0.39345 | 418.8693 | 0.082938
1616 | MCLU-65to135-RFF-CZ15-2003-19IEER | CZ15 | RFF | 2003 | 65to135 | 12 | 19 | 13.1313 | 3819.0306 | 0.81299 | 4526.932 | 1.027 | 707.9014 | 0.21403
1617 | MCLU-65to135-RFF-CZ15-2007-19IEER | CZ15 | RFF | 2007 | 65to135 | 12 | 19 | 13.0162 | 3845.1738 | 0.81642 | 4553.0737 | 1.0311 | 707.8999 | 0.21471
1618 | MCLU-65to135-RFF-CZ15-2011-19IEER | CZ15 | RFF | 2011 | 65to135 | 12 | 19 | 12.3618 | 3978.6326 | 0.82206 | 4679.6253 | 1.0337 | 700.9927 | 0.2116
1619 | MCLU-65to135-RFF-CZ15-2015-19IEER | CZ15 | RFF | 2015 | 65to135 | 12 | 19 | 12.3792 | 3814.2466 | 0.7963 | 4508.624 | 1.0087 | 694.3773 | 0.2124
1620 | MCLU-65to135-RFF-CZ15-2020-19IEER | CZ15 | RFF | 2020 | 65to135 | 12 | 19 | 11.9645 | 3517.4749 | 0.74983 | 4208.784 | 0.96335 | 691.3091 | 0.21353
1621 | MCLU-65to135-RSD-CZ15-2003-19IEER | CZ15 | RSD | 2003 | 65to135 | 12 | 19 | 24.6557 | 3504.8526 | 0.75725 | 4088.8107 | 0.97047 | 583.958 | 0.21322
1622 | MCLU-65to135-RSD-CZ15-2007-19IEER | CZ15 | RSD | 2007 | 65to135 | 12 | 19 | 24.4028 | 3531.0131 | 0.75997 | 4115.8809 | 0.97343 | 584.8678 | 0.21346
1623 | MCLU-65to135-RSD-CZ15-2011-19IEER | CZ15 | RSD | 2011 | 65to135 | 12 | 19 | 23.6468 | 3615.7821 | 0.76658 | 4203.7089 | 0.98033 | 587.9268 | 0.21375
1624 | MCLU-65to135-RSD-CZ15-2015-19IEER | CZ15 | RSD | 2015 | 65to135 | 12 | 19 | 23.4658 | 3494.9291 | 0.74766 | 4079.3267 | 0.96201 | 584.3976 | 0.21435
1625 | MCLU-65to135-RSD-CZ15-2020-19IEER | CZ15 | RSD | 2020 | 65to135 | 12 | 19 | 22.4805 | 3135.1953 | 0.68489 | 3714.8268 | 0.89842 | 579.6316 | 0.21353
1626 | MCLU-65to135-Rt3-CZ15-2003-19IEER | CZ15 | Rt3 | 2003 | 65to135 | 12 | 19 | 422.9597 | 3731.7609 | 0.77293 | 4361.748 | 1.0082 | 629.9871 | 0.23529
1627 | MCLU-65to135-Rt3-CZ15-2007-19IEER | CZ15 | Rt3 | 2007 | 65to135 | 12 | 19 | 421.4752 | 3740.6976 | 0.77342 | 4370.1979 | 1.0085 | 629.5004 | 0.23504
1628 | MCLU-65to135-Rt3-CZ15-2011-19IEER | CZ15 | Rt3 | 2011 | 65to135 | 12 | 19 | 395.6744 | 3914.9039 | 0.78265 | 4540.9395 | 1.0185 | 626.0356 | 0.23585
1629 | MCLU-65to135-Rt3-CZ15-2015-19IEER | CZ15 | Rt3 | 2015 | 65to135 | 12 | 19 | 386.2847 | 3649.6973 | 0.74015 | 4271.825 | 0.97701 | 622.1276 | 0.23685
1630 | MCLU-65to135-Rt3-CZ15-2020-19IEER | CZ15 | Rt3 | 2020 | 65to135 | 12 | 19 | 374.2694 | 3375.1712 | 0.69617 | 3993.4239 | 0.93293 | 618.2527 | 0.23676
1631 | MCLU-65to135-RtL-CZ15-2003-19IEER | CZ15 | RtL | 2003 | 65to135 | 12 | 19 | 378.3708 | 3933.5298 | 0.79676 | 4615.4904 | 1.0434 | 681.9606 | 0.24667
1632 | MCLU-65to135-RtL-CZ15-2007-19IEER | CZ15 | RtL | 2007 | 65to135 | 12 | 19 | 373.3698 | 3971.615 | 0.8005 | 4652.6326 | 1.0469 | 681.0176 | 0.24639
1633 | MCLU-65to135-RtL-CZ15-2011-19IEER | CZ15 | RtL | 2011 | 65to135 | 12 | 19 | 357.4909 | 4105.2603 | 0.80918 | 4785.3194 | 1.0559 | 680.0592 | 0.24668
1634 | MCLU-65to135-RtL-CZ15-2015-19IEER | CZ15 | RtL | 2015 | 65to135 | 12 | 19 | 349.3322 | 3940.8553 | 0.79183 | 4619.6948 | 1.0405 | 678.8395 | 0.2487
1635 | MCLU-65to135-RtL-CZ15-2020-19IEER | CZ15 | RtL | 2020 | 65to135 | 12 | 19 | 333.2696 | 3758.0534 | 0.77386 | 4435.108 | 1.0241 | 677.0546 | 0.25026
1636 | MCLU-65to135-RtS-CZ15-2003-19IEER | CZ15 | RtS | 2003 | 65to135 | 12 | 19 | 28.4767 | 2596.5052 | 0.56435 | 3212.5587 | 0.77495 | 616.0534 | 0.2106
1637 | MCLU-65to135-RtS-CZ15-2007-19IEER | CZ15 | RtS | 2007 | 65to135 | 12 | 19 | 28.1028 | 2618.9964 | 0.56636 | 3234.6323 | 0.77683 | 615.6359 | 0.21047
1638 | MCLU-65to135-RtS-CZ15-2011-19IEER | CZ15 | RtS | 2011 | 65to135 | 12 | 19 | 26.5539 | 2703.499 | 0.56592 | 3310.727 | 0.77409 | 607.228 | 0.20817
1639 | MCLU-65to135-RtS-CZ15-2015-19IEER | CZ15 | RtS | 2015 | 65to135 | 12 | 19 | 26.4026 | 2529.7944 | 0.53973 | 3130.4024 | 0.74678 | 600.6079 | 0.20706
1640 | MCLU-65to135-RtS-CZ15-2020-19IEER | CZ15 | RtS | 2020 | 65to135 | 12 | 19 | 25.5958 | 2394.7193 | 0.51838 | 2992.9399 | 0.72584 | 598.2206 | 0.20746
1641 | MCLU-65to135-SCn-CZ15-2003-19IEER | CZ15 | SCn | 2003 | 65to135 | 12 | 19 | 531.7048 | 1835.3463 | 0.25274 | 2336.8025 | 0.38254 | 501.4561 | 0.1298
1642 | MCLU-65to135-SCn-CZ15-2007-19IEER | CZ15 | SCn | 2007 | 65to135 | 12 | 19 | 508.009 | 1897.1419 | 0.25833 | 2399.2539 | 0.38946 | 502.112 | 0.13113
1643 | MCLU-65to135-SCn-CZ15-2011-19IEER | CZ15 | SCn | 2011 | 65to135 | 12 | 19 | 448.3538 | 2067.6974 | 0.2612 | 2574.5768 | 0.39245 | 506.8793 | 0.13125
1644 | MCLU-65to135-SCn-CZ15-2015-19IEER | CZ15 | SCn | 2015 | 65to135 | 12 | 19 | 452.8382 | 2043.9257 | 0.25784 | 2547.9758 | 0.38792 | 504.0501 | 0.13008
1645 | MCLU-65to135-SCn-CZ15-2020-19IEER | CZ15 | SCn | 2020 | 65to135 | 12 | 19 | 416.6383 | 1948.0892 | 0.24872 | 2453.2613 | 0.38102 | 505.1721 | 0.1323
1646 | MCLU-65to135-WRf-CZ15-2003-19IEER | CZ15 | WRf | 2003 | 65to135 | 12 | 19 | 19.4163 | 210491.8646 | 27.6828 | 211081.6503 | 27.8279 | 589.7857 | 0.1451
1647 | MCLU-65to135-WRf-CZ15-2007-19IEER | CZ15 | WRf | 2007 | 65to135 | 12 | 19 | 18.531 | 211237.8282 | 26.7914 | 211858.447 | 26.9438 | 620.6188 | 0.15237
1648 | MCLU-65to135-WRf-CZ15-2011-19IEER | CZ15 | WRf | 2011 | 65to135 | 12 | 19 | 17.1958 | 215588.562 | 26.5765 | 216335.9035 | 26.749 | 747.3415 | 0.1725
1649 | MCLU-65to135-WRf-CZ15-2015-19IEER | CZ15 | WRf | 2015 | 65to135 | 12 | 19 | 17.4724 | 212136.2088 | 26.1375 | 212847.565 | 26.2912 | 711.3562 | 0.15368
1650 | MCLU-65to135-WRf-CZ15-2020-19IEER | CZ15 | WRf | 2020 | 65to135 | 12 | 19 | 20.0001 | 174868.8832 | 21.4741 | 175447.7469 | 21.6 | 578.8637 | 0.12592
1651 | MCLU-65to135-Asm-CZ16-2003-19IEER | CZ16 | Asm | 2003 | 65to135 | 12 | 19 | 350.5668 | 1842.1332 | 0.50305 | 2080.9696 | 0.65469 | 238.8364 | 0.15164
1652 | MCLU-65to135-Asm-CZ16-2007-19IEER | CZ16 | Asm | 2007 | 65to135 | 12 | 19 | 346.5197 | 1854.3111 | 0.50741 | 2096.7078 | 0.65914 | 242.3967 | 0.15173
1653 | MCLU-65to135-Asm-CZ16-2011-19IEER | CZ16 | Asm | 2011 | 65to135 | 12 | 19 | 329.8939 | 1930.4216 | 0.51761 | 2179.0553 | 0.6679 | 248.6337 | 0.15029
1654 | MCLU-65to135-Asm-CZ16-2015-19IEER | CZ16 | Asm | 2015 | 65to135 | 12 | 19 | 314.6541 | 1990.2802 | 0.528 | 2236.6078 | 0.6783 | 246.3276 | 0.1503
1655 | MCLU-65to135-Asm-CZ16-2020-19IEER | CZ16 | Asm | 2020 | 65to135 | 12 | 19 | 303.234 | 1877.9347 | 0.50747 | 2123.6805 | 0.65712 | 245.7459 | 0.14965
1656 | MCLU-65to135-ECC-CZ16-2003-19IEER | CZ16 | ECC | 2003 | 65to135 | 12 | 19 | 858.1499 | 2201.9251 | 0.32614 | 2375.7604 | 0.4257 | 173.8354 | 0.099566
1657 | MCLU-65to135-ECC-CZ16-2007-19IEER | CZ16 | ECC | 2007 | 65to135 | 12 | 19 | 857.7126 | 2202.7572 | 0.32564 | 2376.4196 | 0.42498 | 173.6624 | 0.099344
1658 | MCLU-65to135-ECC-CZ16-2011-19IEER | CZ16 | ECC | 2011 | 65to135 | 12 | 19 | 843.8792 | 2231.0553 | 0.31971 | 2401.6131 | 0.41577 | 170.5579 | 0.096063
1659 | MCLU-65to135-ECC-CZ16-2015-19IEER | CZ16 | ECC | 2015 | 65to135 | 12 | 19 | 790.7932 | 2348.503 | 0.32677 | 2519.0139 | 0.42245 | 170.511 | 0.095672
1660 | MCLU-65to135-ECC-CZ16-2020-19IEER | CZ16 | ECC | 2020 | 65to135 | 12 | 19 | 748.523 | 2078.2808 | 0.30132 | 2250.8722 | 0.39675 | 172.5914 | 0.095431
1661 | MCLU-65to135-EPr-CZ16-2003-19IEER | CZ16 | EPr | 2003 | 65to135 | 12 | 19 | 131.4661 | 1542.4474 | 0.037109 | 1650.9458 | 0.045556 | 108.4984 | 0.0084465
1662 | MCLU-65to135-EPr-CZ16-2007-19IEER | CZ16 | EPr | 2007 | 65to135 | 12 | 19 | 131.0508 | 1546.7998 | 0.036811 | 1655.0352 | 0.04493 | 108.2354 | 0.0081189
1663 | MCLU-65to135-EPr-CZ16-2011-19IEER | CZ16 | EPr | 2011 | 65to135 | 12 | 19 | 129.3225 | 1566.4783 | 0.036831 | 1674.623 | 0.044769 | 108.1447 | 0.0079382
1664 | MCLU-65to135-EPr-CZ16-2015-19IEER | CZ16 | EPr | 2015 | 65to135 | 12 | 19 | 119.5471 | 1658.7332 | 0.029469 | 1766.0914 | 0.031839 | 107.3582 | 0.0023694
1665 | MCLU-65to135-EPr-CZ16-2020-19IEER | CZ16 | EPr | 2020 | 65to135 | 12 | 19 | 114.0665 | 1463.5159 | 0.019803 | 1570.9465 | 0.021683 | 107.4305 | 0.0018803
1666 | MCLU-65to135-ERC-CZ16-2003-19IEER | CZ16 | ERC | 2003 | 65to135 | 12 | 19 | 5.7931 | 1267.8634 | 0.0508 | 1359.9586 | 0.065089 | 92.0952 | 0.014289
1667 | MCLU-65to135-ERC-CZ16-2007-19IEER | CZ16 | ERC | 2007 | 65to135 | 12 | 19 | 5.7895 | 1268.4895 | 0.050514 | 1360.5373 | 0.06456 | 92.0478 | 0.014046
1668 | MCLU-65to135-ERC-CZ16-2011-19IEER | CZ16 | ERC | 2011 | 65to135 | 12 | 19 | 5.6685 | 1290.7366 | 0.04809 | 1382.6724 | 0.0607 | 91.9358 | 0.01261
1669 | MCLU-65to135-ERC-CZ16-2015-19IEER | CZ16 | ERC | 2015 | 65to135 | 12 | 19 | 5.4807 | 1321.4295 | 0.038199 | 1413.9752 | 0.045425 | 92.5457 | 0.0072257
1670 | MCLU-65to135-ERC-CZ16-2020-19IEER | CZ16 | ERC | 2020 | 65to135 | 12 | 19 | 5.2203 | 1164.1887 | 0.028896 | 1259.0423 | 0.036017 | 94.8537 | 0.0071216
1671 | MCLU-65to135-ESe-CZ16-2003-19IEER | CZ16 | ESe | 2003 | 65to135 | 12 | 19 | 421.9102 | 1608.5127 | 0.10254 | 1729.7725 | 0.13095 | 121.2598 | 0.028415
1672 | MCLU-65to135-ESe-CZ16-2007-19IEER | CZ16 | ESe | 2007 | 65to135 | 12 | 19 | 420.9615 | 1611.8331 | 0.1022 | 1733.0119 | 0.13024 | 121.1788 | 0.028039
1673 | MCLU-65to135-ESe-CZ16-2011-19IEER | CZ16 | ESe | 2011 | 65to135 | 12 | 19 | 408.4824 | 1654.6988 | 0.095198 | 1773.2982 | 0.11659 | 118.5994 | 0.021389
1674 | MCLU-65to135-ESe-CZ16-2015-19IEER | CZ16 | ESe | 2015 | 65to135 | 12 | 19 | 389.0472 | 1714.792 | 0.088874 | 1832.3025 | 0.10484 | 117.5104 | 0.01597
1675 | MCLU-65to135-ESe-CZ16-2020-19IEER | CZ16 | ESe | 2020 | 65to135 | 12 | 19 | 369.3755 | 1502.7825 | 0.07049 | 1621.3254 | 0.084449 | 118.5428 | 0.013959
1676 | MCLU-65to135-EUn-CZ16-2003-19IEER | CZ16 | EUn | 2003 | 65to135 | 12 | 19 | 2597.709 | 2492.6128 | 0.50072 | 2667.5917 | 0.6106 | 174.9789 | 0.10988
1677 | MCLU-65to135-EUn-CZ16-2007-19IEER | CZ16 | EUn | 2007 | 65to135 | 12 | 19 | 2591.4496 | 2475.2274 | 0.49407 | 2649.9641 | 0.60375 | 174.7367 | 0.10968
1678 | MCLU-65to135-EUn-CZ16-2011-19IEER | CZ16 | EUn | 2011 | 65to135 | 12 | 19 | 2528.1588 | 2514.4515 | 0.49582 | 2687.8415 | 0.60387 | 173.39 | 0.10805
1679 | MCLU-65to135-EUn-CZ16-2015-19IEER | CZ16 | EUn | 2015 | 65to135 | 12 | 19 | 2264.6466 | 2735.4631 | 0.51321 | 2912.0389 | 0.624 | 176.5758 | 0.11079
1680 | MCLU-65to135-EUn-CZ16-2020-19IEER | CZ16 | EUn | 2020 | 65to135 | 12 | 19 | 2164.7174 | 2518.1083 | 0.48772 | 2692.6835 | 0.59718 | 174.5752 | 0.10947
1681 | MCLU-65to135-Gro-CZ16-2003-19IEER | CZ16 | Gro | 2003 | 65to135 | 12 | 19 | 94.8282 | 16536.1831 | 2.3991 | 16872.157 | 2.5239 | 335.9739 | 0.12483
1682 | MCLU-65to135-Gro-CZ16-2007-19IEER | CZ16 | Gro | 2007 | 65to135 | 12 | 19 | 93.0624 | 15149.8578 | 2.3142 | 15457.8267 | 2.4548 | 307.9689 | 0.14052
1683 | MCLU-65to135-Gro-CZ16-2011-19IEER | CZ16 | Gro | 2011 | 65to135 | 12 | 19 | 87.2896 | 16140.9275 | 2.4372 | 16429.2389 | 2.572 | 288.3113 | 0.13484
1684 | MCLU-65to135-Gro-CZ16-2015-19IEER | CZ16 | Gro | 2015 | 65to135 | 12 | 19 | 83.3122 | 16178.1389 | 2.4316 | 16440.3902 | 2.5563 | 262.2513 | 0.12461
1685 | MCLU-65to135-Gro-CZ16-2020-19IEER | CZ16 | Gro | 2020 | 65to135 | 12 | 19 | 80.4867 | 16214.8707 | 2.4282 | 16452.5306 | 2.5452 | 237.6599 | 0.11707
1686 | MCLU-65to135-Hsp-CZ16-2003-19IEER | CZ16 | Hsp | 2003 | 65to135 | 12 | 19 | 680.4571 | 4028.5621 | 0.66954 | 4397.1176 | 0.80009 | 368.5554 | 0.13055
1687 | MCLU-65to135-Hsp-CZ16-2007-19IEER | CZ16 | Hsp | 2007 | 65to135 | 12 | 19 | 680.4571 | 4028.26 | 0.66899 | 4396.7064 | 0.7993 | 368.4465 | 0.13031
1688 | MCLU-65to135-Hsp-CZ16-2011-19IEER | CZ16 | Hsp | 2011 | 65to135 | 12 | 19 | 680.4571 | 4018.3153 | 0.65353 | 4384.0985 | 0.78148 | 365.7832 | 0.12795
1689 | MCLU-65to135-Hsp-CZ16-2015-19IEER | CZ16 | Hsp | 2015 | 65to135 | 12 | 19 | 680.4571 | 3992.8747 | 0.64618 | 4357.433 | 0.77347 | 364.5583 | 0.12729
1690 | MCLU-65to135-Hsp-CZ16-2020-19IEER | CZ16 | Hsp | 2020 | 65to135 | 12 | 19 | 680.4571 | 3498.6647 | 0.57647 | 3860.5922 | 0.69931 | 361.9276 | 0.12284
1691 | MCLU-65to135-Htl-CZ16-2003-19IEER | CZ16 | Htl | 2003 | 65to135 | 12 | 19 | 277.982 | 3829.4477 | 0.6695 | 3908.1288 | 0.70583 | 78.6812 | 0.036328
1692 | MCLU-65to135-Htl-CZ16-2007-19IEER | CZ16 | Htl | 2007 | 65to135 | 12 | 19 | 277.9519 | 3682.8644 | 0.62845 | 3761.9111 | 0.66467 | 79.0468 | 0.036219
1693 | MCLU-65to135-Htl-CZ16-2011-19IEER | CZ16 | Htl | 2011 | 65to135 | 12 | 19 | 271.401 | 3642.1798 | 0.63053 | 3723.0483 | 0.66639 | 80.8686 | 0.035861
1694 | MCLU-65to135-Htl-CZ16-2015-19IEER | CZ16 | Htl | 2015 | 65to135 | 12 | 19 | 236.1628 | 3819.1748 | 0.63284 | 3904.1274 | 0.67071 | 84.9526 | 0.037877
1695 | MCLU-65to135-Htl-CZ16-2020-19IEER | CZ16 | Htl | 2020 | 65to135 | 12 | 19 | 234.7166 | 3716.912 | 0.62018 | 3799.6624 | 0.65703 | 82.7504 | 0.036844
1696 | MCLU-65to135-MBT-CZ16-2003-19IEER | CZ16 | MBT | 2003 | 65to135 | 12 | 19 | 347.0636 | 3993.754 | 0.52475 | 4171.7066 | 0.62672 | 177.9526 | 0.10197
1697 | MCLU-65to135-MBT-CZ16-2007-19IEER | CZ16 | MBT | 2007 | 65to135 | 12 | 19 | 343.3077 | 4036.6698 | 0.52807 | 4214.1304 | 0.62932 | 177.4606 | 0.10125
1698 | MCLU-65to135-MBT-CZ16-2011-19IEER | CZ16 | MBT | 2011 | 65to135 | 12 | 19 | 328.744 | 4153.2618 | 0.5368 | 4329.8325 | 0.63708 | 176.5707 | 0.10028
1699 | MCLU-65to135-MBT-CZ16-2015-19IEER | CZ16 | MBT | 2015 | 65to135 | 12 | 19 | 320.1871 | 4224.1925 | 0.54224 | 4400.3056 | 0.64206 | 176.1131 | 0.099824
1700 | MCLU-65to135-MBT-CZ16-2020-19IEER | CZ16 | MBT | 2020 | 65to135 | 12 | 19 | 299.0378 | 4043.5942 | 0.52124 | 4217.4503 | 0.61947 | 173.8561 | 0.098232
1701 | MCLU-65to135-MLI-CZ16-2003-19IEER | CZ16 | MLI | 2003 | 65to135 | 12 | 19 | 229.1762 | 2798.6961 | 0.36429 | 2973.8721 | 0.43654 | 175.176 | 0.072243
1702 | MCLU-65to135-MLI-CZ16-2007-19IEER | CZ16 | MLI | 2007 | 65to135 | 12 | 19 | 224.9575 | 2847.7322 | 0.36883 | 3022.5642 | 0.44127 | 174.8319 | 0.072434
1703 | MCLU-65to135-MLI-CZ16-2011-19IEER | CZ16 | MLI | 2011 | 65to135 | 12 | 19 | 185.0945 | 3429.964 | 0.42978 | 3603.3391 | 0.50226 | 173.3751 | 0.07248
1704 | MCLU-65to135-MLI-CZ16-2015-19IEER | CZ16 | MLI | 2015 | 65to135 | 12 | 19 | 183.3792 | 3438.0074 | 0.42992 | 3611.5406 | 0.50241 | 173.5332 | 0.07249
1705 | MCLU-65to135-MLI-CZ16-2020-19IEER | CZ16 | MLI | 2020 | 65to135 | 12 | 19 | 169.0019 | 3118.0445 | 0.39488 | 3290.312 | 0.46582 | 172.2675 | 0.07094
1706 | MCLU-65to135-Mtl-CZ16-2003-19IEER | CZ16 | Mtl | 2003 | 65to135 | 12 | 19 | 51.7648 | 3836.9547 | 0.57495 | 3910.671 | 0.60068 | 73.7163 | 0.025731
1707 | MCLU-65to135-Mtl-CZ16-2007-19IEER | CZ16 | Mtl | 2007 | 65to135 | 12 | 19 | 51.7648 | 3692.9352 | 0.53703 | 3766.4301 | 0.56273 | 73.4949 | 0.025698
1708 | MCLU-65to135-Mtl-CZ16-2011-19IEER | CZ16 | Mtl | 2011 | 65to135 | 12 | 19 | 50.7442 | 3641.5109 | 0.53573 | 3716.1052 | 0.56147 | 74.5942 | 0.025738
1709 | MCLU-65to135-Mtl-CZ16-2015-19IEER | CZ16 | Mtl | 2015 | 65to135 | 12 | 19 | 42.6203 | 3740.2833 | 0.55093 | 3823.4508 | 0.57933 | 83.1676 | 0.028401
1710 | MCLU-65to135-Mtl-CZ16-2020-19IEER | CZ16 | Mtl | 2020 | 65to135 | 12 | 19 | 42.4849 | 3674.1707 | 0.54191 | 3755.4972 | 0.56961 | 81.3265 | 0.0277
1711 | MCLU-65to135-Nrs-CZ16-2003-19IEER | CZ16 | Nrs | 2003 | 65to135 | 12 | 19 | 182.1413 | 4136.6922 | 0.7622 | 4317.6917 | 0.82648 | 180.9995 | 0.064283
1712 | MCLU-65to135-Nrs-CZ16-2007-19IEER | CZ16 | Nrs | 2007 | 65to135 | 12 | 19 | 182.1377 | 4077.4953 | 0.73792 | 4257.9545 | 0.80195 | 180.4592 | 0.064032
1713 | MCLU-65to135-Nrs-CZ16-2011-19IEER | CZ16 | Nrs | 2011 | 65to135 | 12 | 19 | 181.9545 | 4058.0264 | 0.73335 | 4236.4336 | 0.79687 | 178.4072 | 0.063517
1714 | MCLU-65to135-Nrs-CZ16-2015-19IEER | CZ16 | Nrs | 2015 | 65to135 | 12 | 19 | 181.6475 | 3960.7054 | 0.6968 | 4135.5096 | 0.75924 | 174.8042 | 0.06244
1715 | MCLU-65to135-Nrs-CZ16-2020-19IEER | CZ16 | Nrs | 2020 | 65to135 | 12 | 19 | 181.607 | 3605.7251 | 0.6408 | 3779.415 | 0.70089 | 173.6899 | 0.060083
1716 | MCLU-65to135-OfL-CZ16-2003-19IEER | CZ16 | OfL | 2003 | 65to135 | 12 | 19 | 521.9947 | 2849.6456 | 0.4323 | 3024.6772 | 0.49194 | 175.0316 | 0.059639
1717 | MCLU-65to135-OfL-CZ16-2007-19IEER | CZ16 | OfL | 2007 | 65to135 | 12 | 19 | 521.5582 | 2851.8371 | 0.43249 | 3026.8218 | 0.49211 | 174.9848 | 0.059625
1718 | MCLU-65to135-OfL-CZ16-2011-19IEER | CZ16 | OfL | 2011 | 65to135 | 12 | 19 | 506.7646 | 2893.6052 | 0.43465 | 3067.4265 | 0.49312 | 173.8212 | 0.058477
1719 | MCLU-65to135-OfL-CZ16-2015-19IEER | CZ16 | OfL | 2015 | 65to135 | 12 | 19 | 503.0886 | 2871.0623 | 0.42896 | 3043.2661 | 0.48575 | 172.2038 | 0.056791
1720 | MCLU-65to135-OfL-CZ16-2020-19IEER | CZ16 | OfL | 2020 | 65to135 | 12 | 19 | 491.0332 | 2722.4629 | 0.41165 | 2894.5708 | 0.46814 | 172.1079 | 0.056488
1721 | MCLU-65to135-OfS-CZ16-2003-19IEER | CZ16 | OfS | 2003 | 65to135 | 12 | 19 | 33.2118 | 2227.256 | 0.33595 | 2403.5092 | 0.39732 | 176.2533 | 0.061368
1722 | MCLU-65to135-OfS-CZ16-2007-19IEER | CZ16 | OfS | 2007 | 65to135 | 12 | 19 | 33.204 | 2227.5393 | 0.33553 | 2403.6311 | 0.3967 | 176.0919 | 0.061173
1723 | MCLU-65to135-OfS-CZ16-2011-19IEER | CZ16 | OfS | 2011 | 65to135 | 12 | 19 | 32.7894 | 2230.3875 | 0.3343 | 2406.0038 | 0.39476 | 175.6163 | 0.06046
1724 | MCLU-65to135-OfS-CZ16-2015-19IEER | CZ16 | OfS | 2015 | 65to135 | 12 | 19 | 28.9953 | 2459.0373 | 0.35512 | 2632.6809 | 0.4122 | 173.6436 | 0.057085
1725 | MCLU-65to135-OfS-CZ16-2020-19IEER | CZ16 | OfS | 2020 | 65to135 | 12 | 19 | 28.269 | 2314.31 | 0.33513 | 2487.5381 | 0.3915 | 173.2281 | 0.056365
1726 | MCLU-65to135-RFF-CZ16-2003-19IEER | CZ16 | RFF | 2003 | 65to135 | 12 | 19 | 8.1895 | 4700.0583 | 0.94988 | 4991.203 | 1.0975 | 291.1448 | 0.14764
1727 | MCLU-65to135-RFF-CZ16-2007-19IEER | CZ16 | RFF | 2007 | 65to135 | 12 | 19 | 8.1032 | 4747.6315 | 0.95688 | 5040.9748 | 1.1052 | 293.3433 | 0.14834
1728 | MCLU-65to135-RFF-CZ16-2011-19IEER | CZ16 | RFF | 2011 | 65to135 | 12 | 19 | 7.5378 | 5080.6433 | 0.99805 | 5387.6111 | 1.1527 | 306.9678 | 0.15466
1729 | MCLU-65to135-RFF-CZ16-2015-19IEER | CZ16 | RFF | 2015 | 65to135 | 12 | 19 | 7.3502 | 4969.9163 | 0.97669 | 5275.8805 | 1.1324 | 305.9642 | 0.15567
1730 | MCLU-65to135-RFF-CZ16-2020-19IEER | CZ16 | RFF | 2020 | 65to135 | 12 | 19 | 6.8833 | 4627.7239 | 0.92391 | 4940.6923 | 1.0838 | 312.9685 | 0.15992
1731 | MCLU-65to135-RSD-CZ16-2003-19IEER | CZ16 | RSD | 2003 | 65to135 | 12 | 19 | 13.5705 | 5061.561 | 1.0195 | 5335.668 | 1.1858 | 274.107 | 0.16632
1732 | MCLU-65to135-RSD-CZ16-2007-19IEER | CZ16 | RSD | 2007 | 65to135 | 12 | 19 | 13.3817 | 5130.3581 | 1.0312 | 5406.1284 | 1.1975 | 275.7703 | 0.1663
1733 | MCLU-65to135-RSD-CZ16-2011-19IEER | CZ16 | RSD | 2011 | 65to135 | 12 | 19 | 13.0573 | 5255.4782 | 1.0512 | 5534.7622 | 1.2183 | 279.2839 | 0.1671
1734 | MCLU-65to135-RSD-CZ16-2015-19IEER | CZ16 | RSD | 2015 | 65to135 | 12 | 19 | 12.6 | 5201.1264 | 1.0436 | 5474.6056 | 1.2111 | 273.4792 | 0.16748
1735 | MCLU-65to135-RSD-CZ16-2020-19IEER | CZ16 | RSD | 2020 | 65to135 | 12 | 19 | 11.5283 | 4784.1562 | 0.97395 | 5045.5552 | 1.1363 | 261.399 | 0.16234
1736 | MCLU-65to135-Rt3-CZ16-2003-19IEER | CZ16 | Rt3 | 2003 | 65to135 | 12 | 19 | 236.5393 | 5486.5672 | 1.0926 | 5750.6544 | 1.2432 | 264.0872 | 0.15059
1737 | MCLU-65to135-Rt3-CZ16-2007-19IEER | CZ16 | Rt3 | 2007 | 65to135 | 12 | 19 | 236.4656 | 5487.7339 | 1.0914 | 5751.6236 | 1.2419 | 263.8897 | 0.15049
1738 | MCLU-65to135-Rt3-CZ16-2011-19IEER | CZ16 | Rt3 | 2011 | 65to135 | 12 | 19 | 219.7642 | 5898.9271 | 1.1411 | 6158.2529 | 1.2901 | 259.3258 | 0.14901
1739 | MCLU-65to135-Rt3-CZ16-2015-19IEER | CZ16 | Rt3 | 2015 | 65to135 | 12 | 19 | 208.0225 | 5615.8893 | 1.098 | 5877.0877 | 1.2464 | 261.1984 | 0.14844
1740 | MCLU-65to135-Rt3-CZ16-2020-19IEER | CZ16 | Rt3 | 2020 | 65to135 | 12 | 19 | 198.0525 | 5221.29 | 1.0364 | 5483.2633 | 1.1838 | 261.9733 | 0.14741
1741 | MCLU-65to135-RtL-CZ16-2003-19IEER | CZ16 | RtL | 2003 | 65to135 | 12 | 19 | 193.3174 | 6334.6573 | 1.2364 | 6636.7383 | 1.3918 | 302.0811 | 0.15537
1742 | MCLU-65to135-RtL-CZ16-2007-19IEER | CZ16 | RtL | 2007 | 65to135 | 12 | 19 | 191.9371 | 6378.9187 | 1.2416 | 6680.7527 | 1.3969 | 301.8341 | 0.15527
1743 | MCLU-65to135-RtL-CZ16-2011-19IEER | CZ16 | RtL | 2011 | 65to135 | 12 | 19 | 184.014 | 6661.7922 | 1.281 | 6964.4407 | 1.4346 | 302.6485 | 0.15352
1744 | MCLU-65to135-RtL-CZ16-2015-19IEER | CZ16 | RtL | 2015 | 65to135 | 12 | 19 | 175.5102 | 6500.2652 | 1.2728 | 6811.8271 | 1.4283 | 311.562 | 0.15545
1745 | MCLU-65to135-RtL-CZ16-2020-19IEER | CZ16 | RtL | 2020 | 65to135 | 12 | 19 | 164.0717 | 6278.7967 | 1.2685 | 6596.2836 | 1.4224 | 317.4869 | 0.1539
1746 | MCLU-65to135-RtS-CZ16-2003-19IEER | CZ16 | RtS | 2003 | 65to135 | 12 | 19 | 14.4446 | 3787.7181 | 0.78452 | 4044.4733 | 0.91246 | 256.7552 | 0.12794
1747 | MCLU-65to135-RtS-CZ16-2007-19IEER | CZ16 | RtS | 2007 | 65to135 | 12 | 19 | 14.349 | 3810.1185 | 0.7853 | 4066.563 | 0.91253 | 256.4445 | 0.12724
1748 | MCLU-65to135-RtS-CZ16-2011-19IEER | CZ16 | RtS | 2011 | 65to135 | 12 | 19 | 13.9097 | 3915.0734 | 0.78245 | 4168.4666 | 0.90839 | 253.3932 | 0.12594
1749 | MCLU-65to135-RtS-CZ16-2015-19IEER | CZ16 | RtS | 2015 | 65to135 | 12 | 19 | 13.5502 | 3687.5903 | 0.73866 | 3938.9908 | 0.86523 | 251.4005 | 0.12657
1750 | MCLU-65to135-RtS-CZ16-2020-19IEER | CZ16 | RtS | 2020 | 65to135 | 12 | 19 | 13.1734 | 3430.8741 | 0.69701 | 3680.5042 | 0.82314 | 249.6301 | 0.12613
1751 | MCLU-65to135-SCn-CZ16-2003-19IEER | CZ16 | SCn | 2003 | 65to135 | 12 | 19 | 360.3383 | 2049.6863 | 0.22936 | 2253.7282 | 0.29608 | 204.042 | 0.066716
1752 | MCLU-65to135-SCn-CZ16-2007-19IEER | CZ16 | SCn | 2007 | 65to135 | 12 | 19 | 358.668 | 2056.008 | 0.22714 | 2259.566 | 0.29207 | 203.5579 | 0.064935
1753 | MCLU-65to135-SCn-CZ16-2011-19IEER | CZ16 | SCn | 2011 | 65to135 | 12 | 19 | 323.5787 | 2260.0276 | 0.2391 | 2460.3171 | 0.30185 | 200.2895 | 0.062752
1754 | MCLU-65to135-SCn-CZ16-2015-19IEER | CZ16 | SCn | 2015 | 65to135 | 12 | 19 | 323.2212 | 2260.9152 | 0.23837 | 2460.8929 | 0.30062 | 199.9777 | 0.062253
1755 | MCLU-65to135-SCn-CZ16-2020-19IEER | CZ16 | SCn | 2020 | 65to135 | 12 | 19 | 320.3503 | 1984.1915 | 0.20706 | 2181.0286 | 0.26471 | 196.8371 | 0.057643
1756 | MCLU-65to135-WRf-CZ16-2003-19IEER | CZ16 | WRf | 2003 | 65to135 | 12 | 19 | 9.9696 | 355400.5975 | 48.0331 | 355749.7186 | 48.1379 | 349.1211 | 0.10477
1757 | MCLU-65to135-WRf-CZ16-2007-19IEER | CZ16 | WRf | 2007 | 65to135 | 12 | 19 | 9.3349 | 369474.8498 | 47.8907 | 369845.2234 | 47.9991 | 370.3736 | 0.10839
1758 | MCLU-65to135-WRf-CZ16-2011-19IEER | CZ16 | WRf | 2011 | 65to135 | 12 | 19 | 11.2148 | 299942.4641 | 37.7362 | 300242.3047 | 37.8164 | 299.8406 | 0.080162
1759 | MCLU-65to135-WRf-CZ16-2015-19IEER | CZ16 | WRf | 2015 | 65to135 | 12 | 19 | 11.0022 | 305719.6703 | 38.4536 | 306011.4081 | 38.5285 | 291.7378 | 0.074884
1760 | MCLU-65to135-WRf-CZ16-2020-19IEER | CZ16 | WRf | 2020 | 65to135 | 12 | 19 | 10.3297 | 306995.0247 | 38.5659 | 307283.4792 | 38.6347 | 288.4545 | 0.068831
1761 | MCLU-135to240-Asm-CZ01-2003-17.5IEER | CZ01 | Asm | 2003 | 135to240 | 12 | 17.5 | 296.0641 | 1918.1829 | 0.37244 | 2067.9845 | 0.43154 | 149.8015 | 0.059103
1762 | MCLU-135to240-Asm-CZ01-2007-17.5IEER | CZ01 | Asm | 2007 | 135to240 | 12 | 17.5 | 294.1847 | 1929.7271 | 0.37478 | 2079.4309 | 0.43404 | 149.7038 | 0.059258
1763 | MCLU-135to240-Asm-CZ01-2011-17.5IEER | CZ01 | Asm | 2011 | 135to240 | 12 | 17.5 | 293.1982 | 1942.3014 | 0.38951 | 2086.4538 | 0.43591 | 144.1524 | 0.046399
1764 | MCLU-135to240-Asm-CZ01-2015-17.5IEER | CZ01 | Asm | 2015 | 135to240 | 12 | 17.5 | 284.2421 | 1982.7265 | 0.39417 | 2126.5276 | 0.44051 | 143.8011 | 0.046336
1765 | MCLU-135to240-Asm-CZ01-2020-17.5IEER | CZ01 | Asm | 2020 | 135to240 | 12 | 17.5 | 277.6027 | 1833.8154 | 0.35047 | 1981.6249 | 0.40846 | 147.8095 | 0.057991
1766 | MCLU-135to240-ECC-CZ01-2003-17.5IEER | CZ01 | ECC | 2003 | 135to240 | 12 | 17.5 | 741.0394 | 2350.8853 | 0.51921 | 2463.7454 | 0.5785 | 112.8601 | 0.05929
1767 | MCLU-135to240-ECC-CZ01-2007-17.5IEER | CZ01 | ECC | 2007 | 135to240 | 12 | 17.5 | 740.7557 | 2351.9272 | 0.51942 | 2464.7149 | 0.57874 | 112.7876 | 0.059322
1768 | MCLU-135to240-ECC-CZ01-2011-17.5IEER | CZ01 | ECC | 2011 | 135to240 | 12 | 17.5 | 740.467 | 2363.4822 | 0.5385 | 2464.7489 | 0.57835 | 101.2667 | 0.039841
1769 | MCLU-135to240-ECC-CZ01-2015-17.5IEER | CZ01 | ECC | 2015 | 135to240 | 12 | 17.5 | 694.6266 | 2498.8053 | 0.56555 | 2602.021 | 0.60774 | 103.2156 | 0.042182
1770 | MCLU-135to240-ECC-CZ01-2020-17.5IEER | CZ01 | ECC | 2020 | 135to240 | 12 | 17.5 | 651.9575 | 2201.2451 | 0.49906 | 2319.3082 | 0.56065 | 118.0631 | 0.061593
1771 | MCLU-135to240-EPr-CZ01-2003-17.5IEER | CZ01 | EPr | 2003 | 135to240 | 12 | 17.5 | 110.0093 | 1731.1069 | 0.28316 | 1813.4209 | 0.31416 | 82.314 | 0.030999
1772 | MCLU-135to240-EPr-CZ01-2007-17.5IEER | CZ01 | EPr | 2007 | 135to240 | 12 | 17.5 | 109.8126 | 1734.2815 | 0.28371 | 1816.457 | 0.31473 | 82.1754 | 0.031019
1773 | MCLU-135to240-EPr-CZ01-2011-17.5IEER | CZ01 | EPr | 2011 | 135to240 | 12 | 17.5 | 109.8126 | 1738.7511 | 0.29116 | 1816.457 | 0.31473 | 77.7059 | 0.023563
1774 | MCLU-135to240-EPr-CZ01-2015-17.5IEER | CZ01 | EPr | 2015 | 135to240 | 12 | 17.5 | 102.3377 | 1837.0379 | 0.30374 | 1916.2392 | 0.32792 | 79.2013 | 0.024178
1775 | MCLU-135to240-EPr-CZ01-2020-17.5IEER | CZ01 | EPr | 2020 | 135to240 | 12 | 17.5 | 98.3971 | 1597.55 | 0.25505 | 1682.0424 | 0.28574 | 84.4924 | 0.03069
1776 | MCLU-135to240-ERC-CZ01-2003-17.5IEER | CZ01 | ERC | 2003 | 135to240 | 12 | 17.5 | 4.7603 | 1451.9708 | 0.20769 | 1539.5736 | 0.21153 | 87.6028 | 0.0038418
1777 | MCLU-135to240-ERC-CZ01-2007-17.5IEER | CZ01 | ERC | 2007 | 135to240 | 12 | 17.5 | 4.7585 | 1453.1808 | 0.20776 | 1541.083 | 0.2116 | 87.9021 | 0.0038418
1778 | MCLU-135to240-ERC-CZ01-2011-17.5IEER | CZ01 | ERC | 2011 | 135to240 | 12 | 17.5 | 4.7585 | 1465.9857 | 0.20901 | 1541.083 | 0.2116 | 75.0972 | 0.0025888
1779 | MCLU-135to240-ERC-CZ01-2015-17.5IEER | CZ01 | ERC | 2015 | 135to240 | 12 | 17.5 | 4.5687 | 1485.3376 | 0.21464 | 1560.5839 | 0.21619 | 75.2463 | 0.001547
1780 | MCLU-135to240-ERC-CZ01-2020-17.5IEER | CZ01 | ERC | 2020 | 135to240 | 12 | 17.5 | 4.3557 | 1292.3352 | 0.18632 | 1374.7298 | 0.18806 | 82.3946 | 0.0017409
1781 | MCLU-135to240-ESe-CZ01-2003-17.5IEER | CZ01 | ESe | 2003 | 135to240 | 12 | 17.5 | 351.4081 | 1797.7418 | 0.23863 | 1885.8991 | 0.26803 | 88.1573 | 0.029404
1782 | MCLU-135to240-ESe-CZ01-2007-17.5IEER | CZ01 | ESe | 2007 | 135to240 | 12 | 17.5 | 350.7218 | 1801.2452 | 0.23908 | 1889.311 | 0.26852 | 88.0657 | 0.029445
1783 | MCLU-135to240-ESe-CZ01-2011-17.5IEER | CZ01 | ESe | 2011 | 135to240 | 12 | 17.5 | 349.8477 | 1812.0848 | 0.24817 | 1893.3829 | 0.26897 | 81.2981 | 0.020793
1784 | MCLU-135to240-ESe-CZ01-2015-17.5IEER | CZ01 | ESe | 2015 | 135to240 | 12 | 17.5 | 334.2487 | 1881.3653 | 0.25376 | 1964.2133 | 0.27501 | 82.848 | 0.021242
1785 | MCLU-135to240-ESe-CZ01-2020-17.5IEER | CZ01 | ESe | 2020 | 135to240 | 12 | 17.5 | 314.3163 | 1646.9389 | 0.22845 | 1738.8331 | 0.2586 | 91.8942 | 0.030148
1786 | MCLU-135to240-EUn-CZ01-2003-17.5IEER | CZ01 | EUn | 2003 | 135to240 | 12 | 17.5 | 2308.8158 | 2460.779 | 0.61504 | 2573.5904 | 0.66525 | 112.8114 | 0.050202
1787 | MCLU-135to240-EUn-CZ01-2007-17.5IEER | CZ01 | EUn | 2007 | 135to240 | 12 | 17.5 | 2306.0824 | 2450.9119 | 0.61252 | 2563.6378 | 0.66268 | 112.7259 | 0.050157
1788 | MCLU-135to240-EUn-CZ01-2011-17.5IEER | CZ01 | EUn | 2011 | 135to240 | 12 | 17.5 | 2296.6497 | 2460.8115 | 0.63521 | 2560.0306 | 0.66668 | 99.219 | 0.031467
1789 | MCLU-135to240-EUn-CZ01-2015-17.5IEER | CZ01 | EUn | 2015 | 135to240 | 12 | 17.5 | 2072.52 | 2686.9782 | 0.68392 | 2788.6709 | 0.71742 | 101.6927 | 0.033496
1790 | MCLU-135to240-EUn-CZ01-2020-17.5IEER | CZ01 | EUn | 2020 | 135to240 | 12 | 17.5 | 1975.3228 | 2432.1697 | 0.60836 | 2550.087 | 0.6605 | 117.9173 | 0.052139
1791 | MCLU-135to240-Gro-CZ01-2003-17.5IEER | CZ01 | Gro | 2003 | 135to240 | 12 | 17.5 | 67.817 | 23341.4801 | 3.0231 | 23778.2466 | 3.0962 | 436.7665 | 0.073077
1792 | MCLU-135to240-Gro-CZ01-2007-17.5IEER | CZ01 | Gro | 2007 | 135to240 | 12 | 17.5 | 67.3187 | 21062.3226 | 2.8383 | 21392.6522 | 2.9 | 330.3296 | 0.061689
1793 | MCLU-135to240-Gro-CZ01-2011-17.5IEER | CZ01 | Gro | 2011 | 135to240 | 12 | 17.5 | 66.7427 | 21246.0236 | 2.8621 | 21573.7617 | 2.9232 | 327.738 | 0.061082
1794 | MCLU-135to240-Gro-CZ01-2015-17.5IEER | CZ01 | Gro | 2015 | 135to240 | 12 | 17.5 | 62.5936 | 21716.0971 | 2.9062 | 22019.5313 | 2.9612 | 303.4342 | 0.055021
1795 | MCLU-135to240-Gro-CZ01-2020-17.5IEER | CZ01 | Gro | 2020 | 135to240 | 12 | 17.5 | 60.2234 | 21895.1744 | 2.9161 | 22170.1202 | 2.9678 | 274.9458 | 0.051689
1796 | MCLU-135to240-Hsp-CZ01-2003-17.5IEER | CZ01 | Hsp | 2003 | 135to240 | 12 | 17.5 | 680.4571 | 3833.7779 | 0.56721 | 4144.6422 | 0.60611 | 310.8643 | 0.038893
1797 | MCLU-135to240-Hsp-CZ01-2007-17.5IEER | CZ01 | Hsp | 2007 | 135to240 | 12 | 17.5 | 680.4571 | 3833.8203 | 0.56722 | 4144.6468 | 0.60612 | 310.8265 | 0.038898
1798 | MCLU-135to240-Hsp-CZ01-2011-17.5IEER | CZ01 | Hsp | 2011 | 135to240 | 12 | 17.5 | 680.4571 | 3841.1993 | 0.57831 | 4144.6397 | 0.60546 | 303.4404 | 0.027147
1799 | MCLU-135to240-Hsp-CZ01-2015-17.5IEER | CZ01 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 3819.5029 | 0.57341 | 4125.2489 | 0.60067 | 305.7459 | 0.027256
1800 | MCLU-135to240-Hsp-CZ01-2020-17.5IEER | CZ01 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3332.2871 | 0.49421 | 3654.0268 | 0.53228 | 321.7396 | 0.038074
1801 | MCLU-135to240-Htl-CZ01-2003-17.5IEER | CZ01 | Htl | 2003 | 135to240 | 12 | 17.5 | 255.2737 | 2955.3547 | 0.43053 | 3017.1502 | 0.44287 | 61.7955 | 0.012342
1802 | MCLU-135to240-Htl-CZ01-2007-17.5IEER | CZ01 | Htl | 2007 | 135to240 | 12 | 17.5 | 255.2529 | 2876.5961 | 0.41409 | 2938.7799 | 0.42652 | 62.1838 | 0.012425
1803 | MCLU-135to240-Htl-CZ01-2011-17.5IEER | CZ01 | Htl | 2011 | 135to240 | 12 | 17.5 | 251.4158 | 2851.8636 | 0.42443 | 2913.2033 | 0.43428 | 61.3397 | 0.0098496
1804 | MCLU-135to240-Htl-CZ01-2015-17.5IEER | CZ01 | Htl | 2015 | 135to240 | 12 | 17.5 | 219.6839 | 3012.3484 | 0.44461 | 3077.4006 | 0.45493 | 65.0522 | 0.010328
1805 | MCLU-135to240-Htl-CZ01-2020-17.5IEER | CZ01 | Htl | 2020 | 135to240 | 12 | 17.5 | 218.229 | 2906.1214 | 0.42925 | 2971.2317 | 0.44185 | 65.1103 | 0.012601
1806 | MCLU-135to240-MBT-CZ01-2003-17.5IEER | CZ01 | MBT | 2003 | 135to240 | 12 | 17.5 | 316.8047 | 4223.751 | 0.47615 | 4323.1324 | 0.51712 | 99.3814 | 0.040967
1807 | MCLU-135to240-MBT-CZ01-2007-17.5IEER | CZ01 | MBT | 2007 | 135to240 | 12 | 17.5 | 313.9712 | 4266.5885 | 0.48105 | 4363.9881 | 0.52222 | 97.3996 | 0.04117
1808 | MCLU-135to240-MBT-CZ01-2011-17.5IEER | CZ01 | MBT | 2011 | 135to240 | 12 | 17.5 | 309.6561 | 4287.5127 | 0.49137 | 4360.5866 | 0.5214 | 73.0738 | 0.030031
1809 | MCLU-135to240-MBT-CZ01-2015-17.5IEER | CZ01 | MBT | 2015 | 135to240 | 12 | 17.5 | 302.3852 | 4354.0503 | 0.4971 | 4426.3254 | 0.52712 | 72.2751 | 0.030017
1810 | MCLU-135to240-MBT-CZ01-2020-17.5IEER | CZ01 | MBT | 2020 | 135to240 | 12 | 17.5 | 278.5111 | 4211.1113 | 0.47144 | 4304.0463 | 0.51225 | 92.935 | 0.040818
1811 | MCLU-135to240-MLI-CZ01-2003-17.5IEER | CZ01 | MLI | 2003 | 135to240 | 12 | 17.5 | 178.503 | 3415.502 | 0.36401 | 3553.4537 | 0.39169 | 137.9517 | 0.027683
1812 | MCLU-135to240-MLI-CZ01-2007-17.5IEER | CZ01 | MLI | 2007 | 135to240 | 12 | 17.5 | 176.2737 | 3457.5216 | 0.3687 | 3595.0137 | 0.39623 | 137.492 | 0.027531
1813 | MCLU-135to240-MLI-CZ01-2011-17.5IEER | CZ01 | MLI | 2011 | 135to240 | 12 | 17.5 | 168.3773 | 3618.6495 | 0.39117 | 3751.44 | 0.41284 | 132.7904 | 0.021675
1814 | MCLU-135to240-MLI-CZ01-2015-17.5IEER | CZ01 | MLI | 2015 | 135to240 | 12 | 17.5 | 167.1338 | 3620.9643 | 0.39085 | 3755.3747 | 0.41261 | 134.4105 | 0.021764
1815 | MCLU-135to240-MLI-CZ01-2020-17.5IEER | CZ01 | MLI | 2020 | 135to240 | 12 | 17.5 | 163.1522 | 3099.8117 | 0.32757 | 3240.3576 | 0.35459 | 140.5459 | 0.027015
1816 | MCLU-135to240-Mtl-CZ01-2003-17.5IEER | CZ01 | Mtl | 2003 | 135to240 | 12 | 17.5 | 47.6985 | 2828.8026 | 0.32434 | 2892.8333 | 0.33246 | 64.0308 | 0.008125
1817 | MCLU-135to240-Mtl-CZ01-2007-17.5IEER | CZ01 | Mtl | 2007 | 135to240 | 12 | 17.5 | 47.6985 | 2753.4484 | 0.31333 | 2817.27 | 0.32161 | 63.8217 | 0.0082816
1818 | MCLU-135to240-Mtl-CZ01-2011-17.5IEER | CZ01 | Mtl | 2011 | 135to240 | 12 | 17.5 | 47.5188 | 2728.3014 | 0.31666 | 2790.743 | 0.32281 | 62.4415 | 0.0061508
1819 | MCLU-135to240-Mtl-CZ01-2015-17.5IEER | CZ01 | Mtl | 2015 | 135to240 | 12 | 17.5 | 40.7872 | 2809.2691 | 0.36087 | 2874.6031 | 0.36704 | 65.3339 | 0.0061701
1820 | MCLU-135to240-Mtl-CZ01-2020-17.5IEER | CZ01 | Mtl | 2020 | 135to240 | 12 | 17.5 | 40.6284 | 2738.2411 | 0.34887 | 2804.8266 | 0.35717 | 66.5855 | 0.0082999
1821 | MCLU-135to240-Nrs-CZ01-2003-17.5IEER | CZ01 | Nrs | 2003 | 135to240 | 12 | 17.5 | 181.7404 | 3904.2153 | 0.61052 | 4049.5273 | 0.63355 | 145.312 | 0.023027
1822 | MCLU-135to240-Nrs-CZ01-2007-17.5IEER | CZ01 | Nrs | 2007 | 135to240 | 12 | 17.5 | 181.7393 | 3861.3928 | 0.59802 | 4007.3133 | 0.62105 | 145.9204 | 0.023028
1823 | MCLU-135to240-Nrs-CZ01-2011-17.5IEER | CZ01 | Nrs | 2011 | 135to240 | 12 | 17.5 | 181.7393 | 3865.2192 | 0.60322 | 4007.3133 | 0.62105 | 142.0941 | 0.017829
1824 | MCLU-135to240-Nrs-CZ01-2015-17.5IEER | CZ01 | Nrs | 2015 | 135to240 | 12 | 17.5 | 181.607 | 3813.6851 | 0.58513 | 3956.5924 | 0.6028 | 142.9072 | 0.017664
1825 | MCLU-135to240-Nrs-CZ01-2020-17.5IEER | CZ01 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.607 | 3457.7038 | 0.5283 | 3608.1219 | 0.55057 | 150.4181 | 0.02227
1826 | MCLU-135to240-OfL-CZ01-2003-17.5IEER | CZ01 | OfL | 2003 | 135to240 | 12 | 17.5 | 463.4295 | 3021.1181 | 0.43314 | 3115.2959 | 0.45664 | 94.1778 | 0.023505
1827 | MCLU-135to240-OfL-CZ01-2007-17.5IEER | CZ01 | OfL | 2007 | 135to240 | 12 | 17.5 | 463.1083 | 3023.3438 | 0.43346 | 3117.4344 | 0.45698 | 94.0906 | 0.023518
1828 | MCLU-135to240-OfL-CZ01-2011-17.5IEER | CZ01 | OfL | 2011 | 135to240 | 12 | 17.5 | 459.9976 | 3020.6833 | 0.44096 | 3095.5788 | 0.45472 | 74.8955 | 0.01376
1829 | MCLU-135to240-OfL-CZ01-2015-17.5IEER | CZ01 | OfL | 2015 | 135to240 | 12 | 17.5 | 450.154 | 3037.7024 | 0.44093 | 3121.7191 | 0.45396 | 84.0167 | 0.013025
1830 | MCLU-135to240-OfL-CZ01-2020-17.5IEER | CZ01 | OfL | 2020 | 135to240 | 12 | 17.5 | 434.8374 | 2890.7471 | 0.41674 | 2989.4716 | 0.4387 | 98.7245 | 0.02196
1831 | MCLU-135to240-OfS-CZ01-2003-17.5IEER | CZ01 | OfS | 2003 | 135to240 | 12 | 17.5 | 29.1747 | 2338.0038 | 0.31283 | 2449.399 | 0.33595 | 111.3951 | 0.023122
1832 | MCLU-135to240-OfS-CZ01-2007-17.5IEER | CZ01 | OfS | 2007 | 135to240 | 12 | 17.5 | 29.17 | 2338.5991 | 0.31292 | 2449.9199 | 0.33605 | 111.3208 | 0.023134
1833 | MCLU-135to240-OfS-CZ01-2011-17.5IEER | CZ01 | OfS | 2011 | 135to240 | 12 | 17.5 | 29.0613 | 2331.4062 | 0.31868 | 2431.31 | 0.33337 | 99.9038 | 0.01469
1834 | MCLU-135to240-OfS-CZ01-2015-17.5IEER | CZ01 | OfS | 2015 | 135to240 | 12 | 17.5 | 25.63 | 2602.1574 | 0.35015 | 2701.3135 | 0.36441 | 99.1561 | 0.014252
1835 | MCLU-135to240-OfS-CZ01-2020-17.5IEER | CZ01 | OfS | 2020 | 135to240 | 12 | 17.5 | 24.8514 | 2440.2202 | 0.32096 | 2552.001 | 0.34292 | 111.7808 | 0.021964
1836 | MCLU-135to240-RFF-CZ01-2003-17.5IEER | CZ01 | RFF | 2003 | 135to240 | 12 | 17.5 | 6.5778 | 5459.3826 | 0.9027 | 5665.3908 | 0.9709 | 206.0082 | 0.068205
1837 | MCLU-135to240-RFF-CZ01-2007-17.5IEER | CZ01 | RFF | 2007 | 135to240 | 12 | 17.5 | 6.5119 | 5513.6879 | 0.91229 | 5721.2738 | 0.98224 | 207.5859 | 0.069945
1838 | MCLU-135to240-RFF-CZ01-2011-17.5IEER | CZ01 | RFF | 2011 | 135to240 | 12 | 17.5 | 6.4504 | 5576.5673 | 0.93834 | 5776.709 | 0.99145 | 200.1417 | 0.053109
1839 | MCLU-135to240-RFF-CZ01-2015-17.5IEER | CZ01 | RFF | 2015 | 135to240 | 12 | 17.5 | 6.2675 | 5481.2562 | 0.9127 | 5683.9665 | 0.96747 | 202.7103 | 0.054773
1840 | MCLU-135to240-RFF-CZ01-2020-17.5IEER | CZ01 | RFF | 2020 | 135to240 | 12 | 17.5 | 5.7458 | 5191.8015 | 0.85165 | 5398.0529 | 0.91807 | 206.2515 | 0.066424
1841 | MCLU-135to240-RSD-CZ01-2003-17.5IEER | CZ01 | RSD | 2003 | 135to240 | 12 | 17.5 | 11.7606 | 5541.2417 | 0.95019 | 5706.282 | 1.0249 | 165.0404 | 0.07467
1842 | MCLU-135to240-RSD-CZ01-2007-17.5IEER | CZ01 | RSD | 2007 | 135to240 | 12 | 17.5 | 11.6202 | 5607.7854 | 0.9628 | 5773.5746 | 1.0384 | 165.7893 | 0.07558
1843 | MCLU-135to240-RSD-CZ01-2011-17.5IEER | CZ01 | RSD | 2011 | 135to240 | 12 | 17.5 | 11.6202 | 5618.1506 | 0.97994 | 5773.5746 | 1.0384 | 155.424 | 0.058439
1844 | MCLU-135to240-RSD-CZ01-2015-17.5IEER | CZ01 | RSD | 2015 | 135to240 | 12 | 17.5 | 11.1607 | 5583.765 | 0.95982 | 5735.2587 | 1.0159 | 151.4938 | 0.056111
1845 | MCLU-135to240-RSD-CZ01-2020-17.5IEER | CZ01 | RSD | 2020 | 135to240 | 12 | 17.5 | 9.9669 | 5241.2952 | 0.87748 | 5392.7818 | 0.93467 | 151.4866 | 0.057189
1846 | MCLU-135to240-Rt3-CZ01-2003-17.5IEER | CZ01 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 204.8049 | 6009.5634 | 1.0314 | 6130.0585 | 1.0873 | 120.4951 | 0.055895
1847 | MCLU-135to240-Rt3-CZ01-2007-17.5IEER | CZ01 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 204.7642 | 6011.3351 | 1.0318 | 6131.5726 | 1.0877 | 120.2374 | 0.055923
1848 | MCLU-135to240-Rt3-CZ01-2011-17.5IEER | CZ01 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 202.2054 | 6143.0536 | 1.0735 | 6219.1618 | 1.1034 | 76.1082 | 0.029916
1849 | MCLU-135to240-Rt3-CZ01-2015-17.5IEER | CZ01 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 190.2505 | 5848.894 | 1.0256 | 5946.5145 | 1.0563 | 97.6205 | 0.030735
1850 | MCLU-135to240-Rt3-CZ01-2020-17.5IEER | CZ01 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 180.7344 | 5387.848 | 0.9289 | 5530.9971 | 0.98583 | 143.1491 | 0.056926
1851 | MCLU-135to240-RtL-CZ01-2003-17.5IEER | CZ01 | RtL | 2003 | 135to240 | 12 | 17.5 | 176.7551 | 6666.8584 | 1.138 | 6858.7931 | 1.2128 | 191.9347 | 0.07478
1852 | MCLU-135to240-RtL-CZ01-2007-17.5IEER | CZ01 | RtL | 2007 | 135to240 | 12 | 17.5 | 175.7491 | 6710.6963 | 1.1461 | 6901.9292 | 1.2218 | 191.2329 | 0.075686
1853 | MCLU-135to240-RtL-CZ01-2011-17.5IEER | CZ01 | RtL | 2011 | 135to240 | 12 | 17.5 | 174.7423 | 6806.826 | 1.1819 | 6952.5573 | 1.2319 | 145.7313 | 0.050011
1854 | MCLU-135to240-RtL-CZ01-2015-17.5IEER | CZ01 | RtL | 2015 | 135to240 | 12 | 17.5 | 166.7211 | 6611.4767 | 1.1656 | 6784.7431 | 1.2193 | 173.2664 | 0.053687
1855 | MCLU-135to240-RtL-CZ01-2020-17.5IEER | CZ01 | RtL | 2020 | 135to240 | 12 | 17.5 | 155.5959 | 6346.3135 | 1.1315 | 6573.0071 | 1.216 | 226.6935 | 0.084455
1856 | MCLU-135to240-RtS-CZ01-2003-17.5IEER | CZ01 | RtS | 2003 | 135to240 | 12 | 17.5 | 12.6372 | 4080.4967 | 0.66596 | 4279.9935 | 0.737 | 199.4967 | 0.071036
1857 | MCLU-135to240-RtS-CZ01-2007-17.5IEER | CZ01 | RtS | 2007 | 135to240 | 12 | 17.5 | 12.6299 | 4084.8889 | 0.66655 | 4285.1748 | 0.73785 | 200.2858 | 0.071294
1858 | MCLU-135to240-RtS-CZ01-2011-17.5IEER | CZ01 | RtS | 2011 | 135to240 | 12 | 17.5 | 12.5812 | 4157.1827 | 0.69188 | 4310.3646 | 0.74062 | 153.1819 | 0.048741
1859 | MCLU-135to240-RtS-CZ01-2015-17.5IEER | CZ01 | RtS | 2015 | 135to240 | 12 | 17.5 | 12.1764 | 3804.0732 | 0.62907 | 3957.7251 | 0.65949 | 153.6518 | 0.030418
1860 | MCLU-135to240-RtS-CZ01-2020-17.5IEER | CZ01 | RtS | 2020 | 135to240 | 12 | 17.5 | 11.8518 | 3509.7734 | 0.57186 | 3676.2494 | 0.61511 | 166.4759 | 0.043256
1861 | MCLU-135to240-SCn-CZ01-2003-17.5IEER | CZ01 | SCn | 2003 | 135to240 | 12 | 17.5 | 323.1711 | 2204.1926 | 0.17695 | 2389.8147 | 0.19759 | 185.622 | 0.020641
1862 | MCLU-135to240-SCn-CZ01-2007-17.5IEER | CZ01 | SCn | 2007 | 135to240 | 12 | 17.5 | 321.3803 | 2214.9762 | 0.17793 | 2395.9929 | 0.19863 | 181.0166 | 0.020696
1863 | MCLU-135to240-SCn-CZ01-2011-17.5IEER | CZ01 | SCn | 2011 | 135to240 | 12 | 17.5 | 314.2027 | 2273.1466 | 0.18293 | 2450.4459 | 0.20263 | 177.2993 | 0.019697
1864 | MCLU-135to240-SCn-CZ01-2015-17.5IEER | CZ01 | SCn | 2015 | 135to240 | 12 | 17.5 | 314.0377 | 2255.9193 | 0.1821 | 2433.3626 | 0.2013 | 177.4433 | 0.0192
1865 | MCLU-135to240-SCn-CZ01-2020-17.5IEER | CZ01 | SCn | 2020 | 135to240 | 12 | 17.5 | 310.3607 | 1976.1312 | 0.157 | 2163.991 | 0.17677 | 187.8598 | 0.019771
1866 | MCLU-135to240-WRf-CZ01-2003-17.5IEER | CZ01 | WRf | 2003 | 135to240 | 12 | 17.5 | 9.5333 | 375512.121 | 45.6947 | 375815.4426 | 45.7353 | 303.3216 | 0.040659
1867 | MCLU-135to240-WRf-CZ01-2007-17.5IEER | CZ01 | WRf | 2007 | 135to240 | 12 | 17.5 | 9.3915 | 374940.5013 | 45.393 | 375255.0086 | 45.4334 | 314.5073 | 0.040433
1868 | MCLU-135to240-WRf-CZ01-2011-17.5IEER | CZ01 | WRf | 2011 | 135to240 | 12 | 17.5 | 9.2519 | 377380.1157 | 45.6222 | 377706.2289 | 45.6628 | 326.1132 | 0.040664
1869 | MCLU-135to240-WRf-CZ01-2015-17.5IEER | CZ01 | WRf | 2015 | 135to240 | 12 | 17.5 | 8.9276 | 390361.4186 | 47.2587 | 390536.7799 | 47.2794 | 175.3612 | 0.02071
1870 | MCLU-135to240-WRf-CZ01-2020-17.5IEER | CZ01 | WRf | 2020 | 135to240 | 12 | 17.5 | 8.0861 | 402016.2124 | 48.4019 | 402195.9349 | 48.423 | 179.7225 | 0.021065
1871 | MCLU-135to240-Asm-CZ02-2003-17.5IEER | CZ02 | Asm | 2003 | 135to240 | 12 | 17.5 | 295.4485 | 2360.3388 | 0.86366 | 2659.6819 | 1.0269 | 299.3431 | 0.1632
1872 | MCLU-135to240-Asm-CZ02-2007-17.5IEER | CZ02 | Asm | 2007 | 135to240 | 12 | 17.5 | 293.0267 | 2488.0157 | 0.8776 | 2756.6212 | 1.0385 | 268.6055 | 0.16095
1873 | MCLU-135to240-Asm-CZ02-2011-17.5IEER | CZ02 | Asm | 2011 | 135to240 | 12 | 17.5 | 290.649 | 2576.2895 | 0.92096 | 2772.926 | 1.0422 | 196.6365 | 0.12119
1874 | MCLU-135to240-Asm-CZ02-2015-17.5IEER | CZ02 | Asm | 2015 | 135to240 | 12 | 17.5 | 280.941 | 2617.7765 | 0.92469 | 2812.8806 | 1.0465 | 195.1042 | 0.12176
1875 | MCLU-135to240-Asm-CZ02-2020-17.5IEER | CZ02 | Asm | 2020 | 135to240 | 12 | 17.5 | 271.7876 | 2420.3839 | 0.86011 | 2685.0785 | 1.022 | 264.6945 | 0.16185
1876 | MCLU-135to240-ECC-CZ02-2003-17.5IEER | CZ02 | ECC | 2003 | 135to240 | 12 | 17.5 | 720.1722 | 2691.5193 | 0.48125 | 2931.964 | 0.62048 | 240.4447 | 0.13923
1877 | MCLU-135to240-ECC-CZ02-2007-17.5IEER | CZ02 | ECC | 2007 | 135to240 | 12 | 17.5 | 718.7675 | 2696.2071 | 0.48107 | 2936.7272 | 0.62001 | 240.5201 | 0.13894
1878 | MCLU-135to240-ECC-CZ02-2011-17.5IEER | CZ02 | ECC | 2011 | 135to240 | 12 | 17.5 | 717.0557 | 2763.0592 | 0.52138 | 2940.471 | 0.61941 | 177.4118 | 0.098027
1879 | MCLU-135to240-ECC-CZ02-2015-17.5IEER | CZ02 | ECC | 2015 | 135to240 | 12 | 17.5 | 684.1807 | 2849.9254 | 0.51635 | 3028.1996 | 0.61494 | 178.2742 | 0.098587
1880 | MCLU-135to240-ECC-CZ02-2020-17.5IEER | CZ02 | ECC | 2020 | 135to240 | 12 | 17.5 | 652.3384 | 2450.9032 | 0.44792 | 2690.162 | 0.58585 | 239.2588 | 0.13793
1881 | MCLU-135to240-EPr-CZ02-2003-17.5IEER | CZ02 | EPr | 2003 | 135to240 | 12 | 17.5 | 113.3911 | 1859.9829 | 0.051683 | 2017.4605 | 0.066246 | 157.4776 | 0.014563
1882 | MCLU-135to240-EPr-CZ02-2007-17.5IEER | CZ02 | EPr | 2007 | 135to240 | 12 | 17.5 | 112.1258 | 1878.7826 | 0.050644 | 2036.9576 | 0.06442 | 158.175 | 0.013776
1883 | MCLU-135to240-EPr-CZ02-2011-17.5IEER | CZ02 | EPr | 2011 | 135to240 | 12 | 17.5 | 109.4956 | 1959.3602 | 0.054403 | 2082.594 | 0.062423 | 123.2338 | 0.0080202
1884 | MCLU-135to240-EPr-CZ02-2015-17.5IEER | CZ02 | EPr | 2015 | 135to240 | 12 | 17.5 | 102.2884 | 2044.2641 | 0.036251 | 2169.0854 | 0.037953 | 124.8213 | 0.0017013
1885 | MCLU-135to240-EPr-CZ02-2020-17.5IEER | CZ02 | EPr | 2020 | 135to240 | 12 | 17.5 | 96.3603 | 1795.5499 | 0.024163 | 1955.3242 | 0.026433 | 159.7743 | 0.0022698
1886 | MCLU-135to240-ERC-CZ02-2003-17.5IEER | CZ02 | ERC | 2003 | 135to240 | 12 | 17.5 | 5.2062 | 1483.854 | 0.092697 | 1636.8784 | 0.13551 | 153.0244 | 0.042809
1887 | MCLU-135to240-ERC-CZ02-2007-17.5IEER | CZ02 | ERC | 2007 | 135to240 | 12 | 17.5 | 5.1852 | 1489.3776 | 0.092126 | 1643.0229 | 0.1345 | 153.6453 | 0.042376
1888 | MCLU-135to240-ERC-CZ02-2011-17.5IEER | CZ02 | ERC | 2011 | 135to240 | 12 | 17.5 | 5.066 | 1559.2722 | 0.097682 | 1673.0608 | 0.12101 | 113.7886 | 0.023324
1889 | MCLU-135to240-ERC-CZ02-2015-17.5IEER | CZ02 | ERC | 2015 | 135to240 | 12 | 17.5 | 4.929 | 1552.5238 | 0.075495 | 1654.3907 | 0.09175 | 101.867 | 0.016256
1890 | MCLU-135to240-ERC-CZ02-2020-17.5IEER | CZ02 | ERC | 2020 | 135to240 | 12 | 17.5 | 4.7533 | 1327.7225 | 0.052277 | 1459.7422 | 0.075745 | 132.0198 | 0.023467
1891 | MCLU-135to240-ESe-CZ02-2003-17.5IEER | CZ02 | ESe | 2003 | 135to240 | 12 | 17.5 | 355.0568 | 1955.8519 | 0.13801 | 2125.0219 | 0.18363 | 169.17 | 0.045619
1892 | MCLU-135to240-ESe-CZ02-2007-17.5IEER | CZ02 | ESe | 2007 | 135to240 | 12 | 17.5 | 353.5822 | 1963.356 | 0.13791 | 2132.6504 | 0.18322 | 169.2944 | 0.045309
1893 | MCLU-135to240-ESe-CZ02-2011-17.5IEER | CZ02 | ESe | 2011 | 135to240 | 12 | 17.5 | 352.0023 | 2009.6946 | 0.15332 | 2139.802 | 0.18222 | 130.1073 | 0.028905
1894 | MCLU-135to240-ESe-CZ02-2015-17.5IEER | CZ02 | ESe | 2015 | 135to240 | 12 | 17.5 | 341.4627 | 2040.5007 | 0.13694 | 2170.1991 | 0.15827 | 129.6984 | 0.021335
1895 | MCLU-135to240-ESe-CZ02-2020-17.5IEER | CZ02 | ESe | 2020 | 135to240 | 12 | 17.5 | 325.377 | 1756.9914 | 0.099882 | 1922.5185 | 0.1294 | 165.5271 | 0.029515
1896 | MCLU-135to240-EUn-CZ02-2003-17.5IEER | CZ02 | EUn | 2003 | 135to240 | 12 | 17.5 | 2171.0467 | 2907.1991 | 0.72679 | 3149.9469 | 0.87205 | 242.7478 | 0.14526
1897 | MCLU-135to240-EUn-CZ02-2007-17.5IEER | CZ02 | EUn | 2007 | 135to240 | 12 | 17.5 | 2158.9947 | 2904.3839 | 0.71989 | 3147.1104 | 0.86452 | 242.7264 | 0.14463
1898 | MCLU-135to240-EUn-CZ02-2011-17.5IEER | CZ02 | EUn | 2011 | 135to240 | 12 | 17.5 | 2134.1864 | 2986.0449 | 0.76709 | 3166.6285 | 0.86866 | 180.5837 | 0.10157
1899 | MCLU-135to240-EUn-CZ02-2015-17.5IEER | CZ02 | EUn | 2015 | 135to240 | 12 | 17.5 | 2007.3697 | 3093.4123 | 0.76911 | 3275.6901 | 0.87187 | 182.2778 | 0.10276
1900 | MCLU-135to240-EUn-CZ02-2020-17.5IEER | CZ02 | EUn | 2020 | 135to240 | 12 | 17.5 | 1914.7673 | 2771.0735 | 0.70308 | 3013.4336 | 0.84759 | 242.3601 | 0.14451
1901 | MCLU-135to240-Gro-CZ02-2003-17.5IEER | CZ02 | Gro | 2003 | 135to240 | 12 | 17.5 | 121.4302 | 13421.3892 | 2.1019 | 13758.3065 | 2.2288 | 336.9173 | 0.12687
1902 | MCLU-135to240-Gro-CZ02-2007-17.5IEER | CZ02 | Gro | 2007 | 135to240 | 12 | 17.5 | 119.4969 | 12326.9979 | 2.0158 | 12623.5984 | 2.1396 | 296.6005 | 0.12387
1903 | MCLU-135to240-Gro-CZ02-2011-17.5IEER | CZ02 | Gro | 2011 | 135to240 | 12 | 17.5 | 117.5826 | 12521.7296 | 2.0422 | 12816.3178 | 2.1659 | 294.5881 | 0.12367
1904 | MCLU-135to240-Gro-CZ02-2015-17.5IEER | CZ02 | Gro | 2015 | 135to240 | 12 | 17.5 | 113.0118 | 12470.3197 | 2.028 | 12760.0615 | 2.1488 | 289.7418 | 0.12086
1905 | MCLU-135to240-Gro-CZ02-2020-17.5IEER | CZ02 | Gro | 2020 | 135to240 | 12 | 17.5 | 109.2669 | 12489.7118 | 2.0222 | 12776.4684 | 2.1437 | 286.7566 | 0.12152
1906 | MCLU-135to240-Hsp-CZ02-2003-17.5IEER | CZ02 | Hsp | 2003 | 135to240 | 12 | 17.5 | 680.4571 | 4056.3862 | 0.73529 | 4466.7595 | 0.90791 | 410.3733 | 0.17262
1907 | MCLU-135to240-Hsp-CZ02-2007-17.5IEER | CZ02 | Hsp | 2007 | 135to240 | 12 | 17.5 | 680.4571 | 4056.0833 | 0.73467 | 4466.2431 | 0.90688 | 410.1598 | 0.17221
1908 | MCLU-135to240-Hsp-CZ02-2011-17.5IEER | CZ02 | Hsp | 2011 | 135to240 | 12 | 17.5 | 680.4571 | 4112.9933 | 0.78079 | 4465.7164 | 0.90584 | 352.7231 | 0.12505
1909 | MCLU-135to240-Hsp-CZ02-2015-17.5IEER | CZ02 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 4083.4975 | 0.76943 | 4436.4026 | 0.89445 | 352.9051 | 0.12502
1910 | MCLU-135to240-Hsp-CZ02-2020-17.5IEER | CZ02 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3525.6441 | 0.64714 | 3932.2442 | 0.81556 | 406.6001 | 0.16842
1911 | MCLU-135to240-Htl-CZ02-2003-17.5IEER | CZ02 | Htl | 2003 | 135to240 | 12 | 17.5 | 232.8449 | 3583.0112 | 0.97347 | 3677.0013 | 1.0144 | 93.9901 | 0.040947
1912 | MCLU-135to240-Htl-CZ02-2007-17.5IEER | CZ02 | Htl | 2007 | 135to240 | 12 | 17.5 | 232.538 | 3462.8922 | 0.91051 | 3556.9383 | 0.95141 | 94.0461 | 0.040906
1913 | MCLU-135to240-Htl-CZ02-2011-17.5IEER | CZ02 | Htl | 2011 | 135to240 | 12 | 17.5 | 226.3784 | 3507.8897 | 0.93039 | 3586.0205 | 0.9608 | 78.1308 | 0.030414
1914 | MCLU-135to240-Htl-CZ02-2015-17.5IEER | CZ02 | Htl | 2015 | 135to240 | 12 | 17.5 | 201.5596 | 3668.7552 | 0.93815 | 3750.299 | 0.96971 | 81.5439 | 0.031566
1915 | MCLU-135to240-Htl-CZ02-2020-17.5IEER | CZ02 | Htl | 2020 | 135to240 | 12 | 17.5 | 199.7465 | 3550.9666 | 0.91389 | 3645.8364 | 0.95611 | 94.8699 | 0.042224
1916 | MCLU-135to240-MBT-CZ02-2003-17.5IEER | CZ02 | MBT | 2003 | 135to240 | 12 | 17.5 | 327.2102 | 4348.7664 | 0.65861 | 4559.1965 | 0.79718 | 210.4302 | 0.13857
1917 | MCLU-135to240-MBT-CZ02-2007-17.5IEER | CZ02 | MBT | 2007 | 135to240 | 12 | 17.5 | 321.4151 | 4427.9828 | 0.66682 | 4638.1675 | 0.80483 | 210.1847 | 0.138
1918 | MCLU-135to240-MBT-CZ02-2011-17.5IEER | CZ02 | MBT | 2011 | 135to240 | 12 | 17.5 | 304.1555 | 4683.2306 | 0.72357 | 4826.5945 | 0.82244 | 143.3639 | 0.098872
1919 | MCLU-135to240-MBT-CZ02-2015-17.5IEER | CZ02 | MBT | 2015 | 135to240 | 12 | 17.5 | 295.6853 | 4768.7309 | 0.73025 | 4911.1156 | 0.82937 | 142.3847 | 0.09912
1920 | MCLU-135to240-MBT-CZ02-2020-17.5IEER | CZ02 | MBT | 2020 | 135to240 | 12 | 17.5 | 273.0057 | 4555.4901 | 0.67896 | 4762.6794 | 0.81629 | 207.1893 | 0.13733
1921 | MCLU-135to240-MLI-CZ02-2003-17.5IEER | CZ02 | MLI | 2003 | 135to240 | 12 | 17.5 | 201.8116 | 3197.2038 | 0.49733 | 3401.2996 | 0.59807 | 204.0957 | 0.10074
1922 | MCLU-135to240-MLI-CZ02-2007-17.5IEER | CZ02 | MLI | 2007 | 135to240 | 12 | 17.5 | 197.1414 | 3267.9159 | 0.50495 | 3471.5934 | 0.60589 | 203.6775 | 0.10094
1923 | MCLU-135to240-MLI-CZ02-2011-17.5IEER | CZ02 | MLI | 2011 | 135to240 | 12 | 17.5 | 192.3799 | 3380.8887 | 0.54316 | 3546.9805 | 0.61409 | 166.0918 | 0.07093
1924 | MCLU-135to240-MLI-CZ02-2015-17.5IEER | CZ02 | MLI | 2015 | 135to240 | 12 | 17.5 | 190.1585 | 3395.6612 | 0.54474 | 3561.8361 | 0.61572 | 166.1749 | 0.070981
1925 | MCLU-135to240-MLI-CZ02-2020-17.5IEER | CZ02 | MLI | 2020 | 135to240 | 12 | 17.5 | 175.8051 | 3037.2527 | 0.48246 | 3238.4897 | 0.58303 | 201.237 | 0.10057
1926 | MCLU-135to240-Mtl-CZ02-2003-17.5IEER | CZ02 | Mtl | 2003 | 135to240 | 12 | 17.5 | 42.722 | 3527.2063 | 0.89391 | 3601.8323 | 0.92213 | 74.626 | 0.028221
1927 | MCLU-135to240-Mtl-CZ02-2007-17.5IEER | CZ02 | Mtl | 2007 | 135to240 | 12 | 17.5 | 42.722 | 3399.2498 | 0.829 | 3473.8507 | 0.85721 | 74.6009 | 0.028211
1928 | MCLU-135to240-Mtl-CZ02-2011-17.5IEER | CZ02 | Mtl | 2011 | 135to240 | 12 | 17.5 | 41.57 | 3426.4583 | 0.84075 | 3487.6516 | 0.86087 | 61.1933 | 0.020119
1929 | MCLU-135to240-Mtl-CZ02-2015-17.5IEER | CZ02 | Mtl | 2015 | 135to240 | 12 | 17.5 | 35.1166 | 3643.7885 | 0.86228 | 3708.4217 | 0.88374 | 64.6332 | 0.021464
1930 | MCLU-135to240-Mtl-CZ02-2020-17.5IEER | CZ02 | Mtl | 2020 | 135to240 | 12 | 17.5 | 34.9717 | 3545.6752 | 0.84304 | 3623.5931 | 0.87237 | 77.9179 | 0.029325
1931 | MCLU-135to240-Nrs-CZ02-2003-17.5IEER | CZ02 | Nrs | 2003 | 135to240 | 12 | 17.5 | 182.3436 | 4248.9905 | 0.88045 | 4451.7941 | 0.96663 | 202.8036 | 0.086177
1932 | MCLU-135to240-Nrs-CZ02-2007-17.5IEER | CZ02 | Nrs | 2007 | 135to240 | 12 | 17.5 | 182.3402 | 4177.5744 | 0.84741 | 4380.5801 | 0.93323 | 203.0057 | 0.085818
1933 | MCLU-135to240-Nrs-CZ02-2011-17.5IEER | CZ02 | Nrs | 2011 | 135to240 | 12 | 17.5 | 182.1443 | 4232.1507 | 0.8647 | 4405.1537 | 0.92561 | 173.003 | 0.06091
1934 | MCLU-135to240-Nrs-CZ02-2015-17.5IEER | CZ02 | Nrs | 2015 | 135to240 | 12 | 17.5 | 181.6554 | 4144.2304 | 0.81497 | 4316.1675 | 0.87544 | 171.937 | 0.060468
1935 | MCLU-135to240-Nrs-CZ02-2020-17.5IEER | CZ02 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.607 | 3748.3841 | 0.73115 | 3946.7471 | 0.81372 | 198.363 | 0.082566
1936 | MCLU-135to240-OfL-CZ02-2003-17.5IEER | CZ02 | OfL | 2003 | 135to240 | 12 | 17.5 | 420.6804 | 3609.619 | 0.60558 | 3830.3281 | 0.67765 | 220.7091 | 0.072067
1937 | MCLU-135to240-OfL-CZ02-2007-17.5IEER | CZ02 | OfL | 2007 | 135to240 | 12 | 17.5 | 420.2797 | 3612.9152 | 0.60587 | 3833.6442 | 0.67788 | 220.729 | 0.072007
1938 | MCLU-135to240-OfL-CZ02-2011-17.5IEER | CZ02 | OfL | 2011 | 135to240 | 12 | 17.5 | 404.9965 | 3776.8525 | 0.63253 | 3925.5734 | 0.6823 | 148.7209 | 0.049763
1939 | MCLU-135to240-OfL-CZ02-2015-17.5IEER | CZ02 | OfL | 2015 | 135to240 | 12 | 17.5 | 400.8161 | 3745.4891 | 0.63131 | 3896.3038 | 0.68087 | 150.8147 | 0.049558
1940 | MCLU-135to240-OfL-CZ02-2020-17.5IEER | CZ02 | OfL | 2020 | 135to240 | 12 | 17.5 | 388.4536 | 3509.5961 | 0.59279 | 3727.2665 | 0.66269 | 217.6704 | 0.069902
1941 | MCLU-135to240-OfS-CZ02-2003-17.5IEER | CZ02 | OfS | 2003 | 135to240 | 12 | 17.5 | 28.3618 | 2661.0772 | 0.45856 | 2882.1575 | 0.53164 | 221.0803 | 0.073077
1942 | MCLU-135to240-OfS-CZ02-2007-17.5IEER | CZ02 | OfS | 2007 | 135to240 | 12 | 17.5 | 28.2907 | 2667.3554 | 0.45887 | 2888.4652 | 0.53177 | 221.1098 | 0.072895
1943 | MCLU-135to240-OfS-CZ02-2011-17.5IEER | CZ02 | OfS | 2011 | 135to240 | 12 | 17.5 | 27.7965 | 2746.5824 | 0.4808 | 2907.7618 | 0.53114 | 161.1795 | 0.050339
1944 | MCLU-135to240-OfS-CZ02-2015-17.5IEER | CZ02 | OfS | 2015 | 135to240 | 12 | 17.5 | 24.7912 | 2995.6147 | 0.50477 | 3153.8082 | 0.55385 | 158.1936 | 0.049081
1945 | MCLU-135to240-OfS-CZ02-2020-17.5IEER | CZ02 | OfS | 2020 | 135to240 | 12 | 17.5 | 24.0284 | 2777.6912 | 0.46231 | 2994.3618 | 0.53211 | 216.6705 | 0.069803
1946 | MCLU-135to240-RFF-CZ02-2003-17.5IEER | CZ02 | RFF | 2003 | 135to240 | 12 | 17.5 | 6.3888 | 6105.097 | 1.4655 | 6517.3032 | 1.6288 | 412.2062 | 0.16333
1947 | MCLU-135to240-RFF-CZ02-2007-17.5IEER | CZ02 | RFF | 2007 | 135to240 | 12 | 17.5 | 6.3104 | 6176.8336 | 1.4795 | 6590.3768 | 1.642 | 413.5432 | 0.16256
1948 | MCLU-135to240-RFF-CZ02-2011-17.5IEER | CZ02 | RFF | 2011 | 135to240 | 12 | 17.5 | 6.234 | 6340.6314 | 1.5296 | 6663.5088 | 1.6547 | 322.8774 | 0.12511
1949 | MCLU-135to240-RFF-CZ02-2015-17.5IEER | CZ02 | RFF | 2015 | 135to240 | 12 | 17.5 | 6.1713 | 6098.6962 | 1.4831 | 6417.6853 | 1.61 | 318.9891 | 0.12696
1950 | MCLU-135to240-RFF-CZ02-2020-17.5IEER | CZ02 | RFF | 2020 | 135to240 | 12 | 17.5 | 5.8362 | 5542.5881 | 1.378 | 5946.5777 | 1.545 | 403.9896 | 0.16698
1951 | MCLU-135to240-RSD-CZ02-2003-17.5IEER | CZ02 | RSD | 2003 | 135to240 | 12 | 17.5 | 11.9858 | 5894.9423 | 1.4015 | 6272.8879 | 1.5776 | 377.9456 | 0.17611
1952 | MCLU-135to240-RSD-CZ02-2007-17.5IEER | CZ02 | RSD | 2007 | 135to240 | 12 | 17.5 | 11.8411 | 5964.7112 | 1.4146 | 6344.8593 | 1.5903 | 380.1481 | 0.17571
1953 | MCLU-135to240-RSD-CZ02-2011-17.5IEER | CZ02 | RSD | 2011 | 135to240 | 12 | 17.5 | 11.6135 | 6158.5473 | 1.48 | 6458.4777 | 1.6091 | 299.9304 | 0.12913
1954 | MCLU-135to240-RSD-CZ02-2015-17.5IEER | CZ02 | RSD | 2015 | 135to240 | 12 | 17.5 | 11.4203 | 5968.0586 | 1.4474 | 6258.6033 | 1.5769 | 290.5447 | 0.12944
1955 | MCLU-135to240-RSD-CZ02-2020-17.5IEER | CZ02 | RSD | 2020 | 135to240 | 12 | 17.5 | 10.6513 | 5303.5138 | 1.313 | 5659.2069 | 1.4875 | 355.6931 | 0.17457
1956 | MCLU-135to240-Rt3-CZ02-2003-17.5IEER | CZ02 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 234.2363 | 5691.2934 | 1.2578 | 6001.4616 | 1.4444 | 310.1682 | 0.18657
1957 | MCLU-135to240-Rt3-CZ02-2007-17.5IEER | CZ02 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 233.5371 | 5707.7829 | 1.2594 | 6017.9769 | 1.4459 | 310.194 | 0.18646
1958 | MCLU-135to240-Rt3-CZ02-2011-17.5IEER | CZ02 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 232.8236 | 5825.2202 | 1.3142 | 6034.9707 | 1.4473 | 209.7505 | 0.13315
1959 | MCLU-135to240-Rt3-CZ02-2015-17.5IEER | CZ02 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 223.3025 | 5475.021 | 1.2618 | 5689.8406 | 1.3961 | 214.8196 | 0.13435
1960 | MCLU-135to240-Rt3-CZ02-2020-17.5IEER | CZ02 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 213.1708 | 4985.6102 | 1.1495 | 5298.9679 | 1.3384 | 313.3577 | 0.18891
1961 | MCLU-135to240-RtL-CZ02-2003-17.5IEER | CZ02 | RtL | 2003 | 135to240 | 12 | 17.5 | 205.9348 | 6169.6008 | 1.3335 | 6500.0274 | 1.5238 | 330.4266 | 0.19038
1962 | MCLU-135to240-RtL-CZ02-2007-17.5IEER | CZ02 | RtL | 2007 | 135to240 | 12 | 17.5 | 202.8564 | 6262.1792 | 1.349 | 6593.3628 | 1.5387 | 331.1836 | 0.1897
1963 | MCLU-135to240-RtL-CZ02-2011-17.5IEER | CZ02 | RtL | 2011 | 135to240 | 12 | 17.5 | 199.7294 | 6468.8353 | 1.4161 | 6691.6182 | 1.5544 | 222.7829 | 0.13825
1964 | MCLU-135to240-RtL-CZ02-2015-17.5IEER | CZ02 | RtL | 2015 | 135to240 | 12 | 17.5 | 192.4683 | 6246.8184 | 1.4001 | 6482.228 | 1.5398 | 235.4096 | 0.13974
1965 | MCLU-135to240-RtL-CZ02-2020-17.5IEER | CZ02 | RtL | 2020 | 135to240 | 12 | 17.5 | 180.1799 | 5926.0282 | 1.3509 | 6274.0432 | 1.5396 | 348.015 | 0.18868
1966 | MCLU-135to240-RtS-CZ02-2003-17.5IEER | CZ02 | RtS | 2003 | 135to240 | 12 | 17.5 | 15.0342 | 3795.2322 | 0.89226 | 4180.7101 | 1.0606 | 385.4779 | 0.16834
1967 | MCLU-135to240-RtS-CZ02-2007-17.5IEER | CZ02 | RtS | 2007 | 135to240 | 12 | 17.5 | 14.7446 | 3866.4948 | 0.90509 | 4253.3883 | 1.073 | 386.8935 | 0.16794
1968 | MCLU-135to240-RtS-CZ02-2011-17.5IEER | CZ02 | RtS | 2011 | 135to240 | 12 | 17.5 | 14.5143 | 4036.5361 | 0.95851 | 4313.1586 | 1.0812 | 276.6224 | 0.12269
1969 | MCLU-135to240-RtS-CZ02-2015-17.5IEER | CZ02 | RtS | 2015 | 135to240 | 12 | 17.5 | 14.1644 | 3705.5603 | 0.9135 | 3936.4106 | 1.0384 | 230.8503 | 0.12491
1970 | MCLU-135to240-RtS-CZ02-2020-17.5IEER | CZ02 | RtS | 2020 | 135to240 | 12 | 17.5 | 13.5438 | 3431.4279 | 0.84228 | 3739.1484 | 1.0125 | 307.7204 | 0.17022
1971 | MCLU-135to240-SCn-CZ02-2003-17.5IEER | CZ02 | SCn | 2003 | 135to240 | 12 | 17.5 | 239.8267 | 3027.2437 | 0.43676 | 3270.0684 | 0.54244 | 242.8247 | 0.10568
1972 | MCLU-135to240-SCn-CZ02-2007-17.5IEER | CZ02 | SCn | 2007 | 135to240 | 12 | 17.5 | 227.7582 | 3175.5124 | 0.45415 | 3418.5208 | 0.55645 | 243.0084 | 0.1023
1973 | MCLU-135to240-SCn-CZ02-2011-17.5IEER | CZ02 | SCn | 2011 | 135to240 | 12 | 17.5 | 215.7313 | 3368.1396 | 0.50168 | 3576.7197 | 0.57105 | 208.5801 | 0.069368
1974 | MCLU-135to240-SCn-CZ02-2015-17.5IEER | CZ02 | SCn | 2015 | 135to240 | 12 | 17.5 | 214.6505 | 3355.9479 | 0.50123 | 3560.278 | 0.5707 | 204.3301 | 0.069467
1975 | MCLU-135to240-SCn-CZ02-2020-17.5IEER | CZ02 | SCn | 2020 | 135to240 | 12 | 17.5 | 192.558 | 3211.1313 | 0.46566 | 3437.4996 | 0.56442 | 226.3683 | 0.098761
1976 | MCLU-135to240-WRf-CZ02-2003-17.5IEER | CZ02 | WRf | 2003 | 135to240 | 12 | 17.5 | 13.9482 | 267840.6077 | 37.2655 | 268155.7477 | 37.3323 | 315.14 | 0.066799
1977 | MCLU-135to240-WRf-CZ02-2007-17.5IEER | CZ02 | WRf | 2007 | 135to240 | 12 | 17.5 | 14.0902 | 256115.7041 | 34.3158 | 256434.3877 | 34.3857 | 318.6836 | 0.069911
1978 | MCLU-135to240-WRf-CZ02-2011-17.5IEER | CZ02 | WRf | 2011 | 135to240 | 12 | 17.5 | 12.7727 | 274658.6211 | 35.2711 | 274998.1366 | 35.3259 | 339.5155 | 0.054744
1979 | MCLU-135to240-WRf-CZ02-2015-17.5IEER | CZ02 | WRf | 2015 | 135to240 | 12 | 17.5 | 12.3642 | 283259.9801 | 36.4183 | 283484.9316 | 36.4729 | 224.9515 | 0.054611
1980 | MCLU-135to240-WRf-CZ02-2020-17.5IEER | CZ02 | WRf | 2020 | 135to240 | 12 | 17.5 | 11.9821 | 275779.478 | 35.3662 | 275996.6649 | 35.4162 | 217.1869 | 0.049968
1981 | MCLU-135to240-Asm-CZ03-2003-17.5IEER | CZ03 | Asm | 2003 | 135to240 | 12 | 17.5 | 353.1051 | 1759.9805 | 0.45893 | 1977.6786 | 0.59708 | 217.6981 | 0.13815
1982 | MCLU-135to240-Asm-CZ03-2007-17.5IEER | CZ03 | Asm | 2007 | 135to240 | 12 | 17.5 | 350.6649 | 1765.5404 | 0.46134 | 1986.5141 | 0.59961 | 220.9737 | 0.13827
1983 | MCLU-135to240-Asm-CZ03-2011-17.5IEER | CZ03 | Asm | 2011 | 135to240 | 12 | 17.5 | 348.2745 | 1812.6635 | 0.5047 | 1997.6364 | 0.60218 | 184.9729 | 0.097479
1984 | MCLU-135to240-Asm-CZ03-2015-17.5IEER | CZ03 | Asm | 2015 | 135to240 | 12 | 17.5 | 303.0916 | 1995.7638 | 0.5415 | 2177.4235 | 0.63873 | 181.6597 | 0.097228
1985 | MCLU-135to240-Asm-CZ03-2020-17.5IEER | CZ03 | Asm | 2020 | 135to240 | 12 | 17.5 | 293.3649 | 1838.2822 | 0.47449 | 2048.1159 | 0.61233 | 209.8337 | 0.13784
1986 | MCLU-135to240-ECC-CZ03-2003-17.5IEER | CZ03 | ECC | 2003 | 135to240 | 12 | 17.5 | 854.3299 | 2160.4286 | 0.3061 | 2304.579 | 0.39964 | 144.1505 | 0.093542
1987 | MCLU-135to240-ECC-CZ03-2007-17.5IEER | CZ03 | ECC | 2007 | 135to240 | 12 | 17.5 | 853.9515 | 2161.3761 | 0.3058 | 2305.4574 | 0.39909 | 144.0814 | 0.093293
1988 | MCLU-135to240-ECC-CZ03-2011-17.5IEER | CZ03 | ECC | 2011 | 135to240 | 12 | 17.5 | 853.5358 | 2194.6267 | 0.33146 | 2304.7036 | 0.39832 | 110.0769 | 0.066853
1989 | MCLU-135to240-ECC-CZ03-2015-17.5IEER | CZ03 | ECC | 2015 | 135to240 | 12 | 17.5 | 755.8077 | 2444.528 | 0.35249 | 2556.9167 | 0.42 | 112.3887 | 0.06751
1990 | MCLU-135to240-ECC-CZ03-2020-17.5IEER | CZ03 | ECC | 2020 | 135to240 | 12 | 17.5 | 714.0925 | 2121.9859 | 0.29928 | 2272.6537 | 0.39166 | 150.6678 | 0.09238
1991 | MCLU-135to240-EPr-CZ03-2003-17.5IEER | CZ03 | EPr | 2003 | 135to240 | 12 | 17.5 | 130.57 | 1535.3168 | 0.026314 | 1638.3239 | 0.027191 | 103.0071 | 0.00087708
1992 | MCLU-135to240-EPr-CZ03-2007-17.5IEER | CZ03 | EPr | 2007 | 135to240 | 12 | 17.5 | 130.2535 | 1538.9431 | 0.026358 | 1641.8116 | 0.027232 | 102.8685 | 0.0008739
1993 | MCLU-135to240-EPr-CZ03-2011-17.5IEER | CZ03 | EPr | 2011 | 135to240 | 12 | 17.5 | 129.9247 | 1562.9703 | 0.02684 | 1645.4838 | 0.027275 | 82.5136 | 0.00043571
1994 | MCLU-135to240-EPr-CZ03-2015-17.5IEER | CZ03 | EPr | 2015 | 135to240 | 12 | 17.5 | 113.9824 | 1738.4666 | 0.028419 | 1828.4528 | 0.028625 | 89.9862 | 0.00020559
1995 | MCLU-135to240-EPr-CZ03-2020-17.5IEER | CZ03 | EPr | 2020 | 135to240 | 12 | 17.5 | 108.6421 | 1511.9642 | 0.018699 | 1622.0619 | 0.01914 | 110.0978 | 0.00044099
1996 | MCLU-135to240-ERC-CZ03-2003-17.5IEER | CZ03 | ERC | 2003 | 135to240 | 12 | 17.5 | 5.7096 | 1310.4816 | 0.028972 | 1425.0799 | 0.031427 | 114.5983 | 0.0024553
1997 | MCLU-135to240-ERC-CZ03-2007-17.5IEER | CZ03 | ERC | 2007 | 135to240 | 12 | 17.5 | 5.7065 | 1311.6084 | 0.028947 | 1426.5187 | 0.031381 | 114.9103 | 0.0024346
1998 | MCLU-135to240-ERC-CZ03-2011-17.5IEER | CZ03 | ERC | 2011 | 135to240 | 12 | 17.5 | 5.7031 | 1349.3583 | 0.030017 | 1428.2578 | 0.031344 | 78.8995 | 0.0013273
1999 | MCLU-135to240-ERC-CZ03-2015-17.5IEER | CZ03 | ERC | 2015 | 135to240 | 12 | 17.5 | 5.3037 | 1370.9261 | 0.026173 | 1442.86 | 0.026173 | 71.9339 | 0
2000 | MCLU-135to240-ERC-CZ03-2020-17.5IEER | CZ03 | ERC | 2020 | 135to240 | 12 | 17.5 | 5.0897 | 1176.5394 | 0.017481 | 1270.6634 | 0.017481 | 94.124 | 0
2001 | MCLU-135to240-ESe-CZ03-2003-17.5IEER | CZ03 | ESe | 2003 | 135to240 | 12 | 17.5 | 433.0045 | 1558.3464 | 0.078842 | 1669.0654 | 0.090087 | 110.719 | 0.011245
2002 | MCLU-135to240-ESe-CZ03-2007-17.5IEER | CZ03 | ESe | 2007 | 135to240 | 12 | 17.5 | 432.0516 | 1561.6369 | 0.078946 | 1672.3185 | 0.090175 | 110.6816 | 0.011229
2003 | MCLU-135to240-ESe-CZ03-2011-17.5IEER | CZ03 | ESe | 2011 | 135to240 | 12 | 17.5 | 431.0493 | 1588.9404 | 0.083713 | 1674.8921 | 0.090207 | 85.9517 | 0.0064935
2004 | MCLU-135to240-ESe-CZ03-2015-17.5IEER | CZ03 | ESe | 2015 | 135to240 | 12 | 17.5 | 368.3474 | 1802.146 | 0.076635 | 1890.9245 | 0.079052 | 88.7786 | 0.0024172
2005 | MCLU-135to240-ESe-CZ03-2020-17.5IEER | CZ03 | ESe | 2020 | 135to240 | 12 | 17.5 | 349.8094 | 1551.8058 | 0.056454 | 1665.6413 | 0.059213 | 113.8355 | 0.0027588
2006 | MCLU-135to240-EUn-CZ03-2003-17.5IEER | CZ03 | EUn | 2003 | 135to240 | 12 | 17.5 | 2543.6608 | 2311.0452 | 0.46289 | 2465.6556 | 0.56841 | 154.6104 | 0.10552
2007 | MCLU-135to240-EUn-CZ03-2007-17.5IEER | CZ03 | EUn | 2007 | 135to240 | 12 | 17.5 | 2538.4532 | 2305.1267 | 0.45833 | 2459.5742 | 0.56366 | 154.4476 | 0.10534
2008 | MCLU-135to240-EUn-CZ03-2011-17.5IEER | CZ03 | EUn | 2011 | 135to240 | 12 | 17.5 | 2518.1183 | 2347.1082 | 0.49071 | 2467.1873 | 0.56574 | 120.0791 | 0.075027
2009 | MCLU-135to240-EUn-CZ03-2015-17.5IEER | CZ03 | EUn | 2015 | 135to240 | 12 | 17.5 | 2204.0414 | 2625.8739 | 0.52332 | 2743.1814 | 0.59906 | 117.3075 | 0.075745
2010 | MCLU-135to240-EUn-CZ03-2020-17.5IEER | CZ03 | EUn | 2020 | 135to240 | 12 | 17.5 | 2105.5784 | 2346.4126 | 0.46312 | 2501.6478 | 0.56814 | 155.2352 | 0.10502
2011 | MCLU-135to240-Gro-CZ03-2003-17.5IEER | CZ03 | Gro | 2003 | 135to240 | 12 | 17.5 | 90.543 | 17777.7402 | 2.4585 | 18176.9764 | 2.5537 | 399.2362 | 0.095147
2012 | MCLU-135to240-Gro-CZ03-2007-17.5IEER | CZ03 | Gro | 2007 | 135to240 | 12 | 17.5 | 89.5985 | 16214.1818 | 2.3586 | 16534.1917 | 2.4548 | 320.0099 | 0.096163
2013 | MCLU-135to240-Gro-CZ03-2011-17.5IEER | CZ03 | Gro | 2011 | 135to240 | 12 | 17.5 | 88.6418 | 16388.8999 | 2.3816 | 16707.5631 | 2.4775 | 318.6632 | 0.095886
2014 | MCLU-135to240-Gro-CZ03-2015-17.5IEER | CZ03 | Gro | 2015 | 135to240 | 12 | 17.5 | 82.8814 | 16771.239 | 2.4198 | 17084.352 | 2.5101 | 313.113 | 0.090338
2015 | MCLU-135to240-Gro-CZ03-2020-17.5IEER | CZ03 | Gro | 2020 | 135to240 | 12 | 17.5 | 80.2484 | 16783.3006 | 2.4121 | 17093.6418 | 2.4981 | 310.3412 | 0.086025
2016 | MCLU-135to240-Hsp-CZ03-2003-17.5IEER | CZ03 | Hsp | 2003 | 135to240 | 12 | 17.5 | 680.9706 | 3953.8593 | 0.65266 | 4270.7524 | 0.77065 | 316.8932 | 0.11799
2017 | MCLU-135to240-Hsp-CZ03-2007-17.5IEER | CZ03 | Hsp | 2007 | 135to240 | 12 | 17.5 | 680.9706 | 3953.8147 | 0.65234 | 4270.6513 | 0.77017 | 316.8366 | 0.11783
2018 | MCLU-135to240-Hsp-CZ03-2011-17.5IEER | CZ03 | Hsp | 2011 | 135to240 | 12 | 17.5 | 680.9706 | 3987.3175 | 0.6851 | 4270.5509 | 0.76966 | 283.2334 | 0.084566
2019 | MCLU-135to240-Hsp-CZ03-2015-17.5IEER | CZ03 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 3946.0512 | 0.6709 | 4232.3291 | 0.7549 | 286.2779 | 0.084005
2020 | MCLU-135to240-Hsp-CZ03-2020-17.5IEER | CZ03 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3416.5953 | 0.56906 | 3740.048 | 0.67934 | 323.4527 | 0.11028
2021 | MCLU-135to240-Htl-CZ03-2003-17.5IEER | CZ03 | Htl | 2003 | 135to240 | 12 | 17.5 | 269.0776 | 2734.3771 | 0.60746 | 2805.3917 | 0.63973 | 71.0146 | 0.032268
2022 | MCLU-135to240-Htl-CZ03-2007-17.5IEER | CZ03 | Htl | 2007 | 135to240 | 12 | 17.5 | 269.0526 | 2652.0288 | 0.57312 | 2723.3349 | 0.6053 | 71.3061 | 0.032177
2023 | MCLU-135to240-Htl-CZ03-2011-17.5IEER | CZ03 | Htl | 2011 | 135to240 | 12 | 17.5 | 262.8066 | 2678.318 | 0.589 | 2742.4192 | 0.61221 | 64.1012 | 0.023211
2024 | MCLU-135to240-Htl-CZ03-2015-17.5IEER | CZ03 | Htl | 2015 | 135to240 | 12 | 17.5 | 227.8884 | 2862.8024 | 0.59989 | 2929.8864 | 0.62418 | 67.084 | 0.02429
2025 | MCLU-135to240-Htl-CZ03-2020-17.5IEER | CZ03 | Htl | 2020 | 135to240 | 12 | 17.5 | 226.5477 | 2752.796 | 0.57616 | 2825.5254 | 0.60931 | 72.7294 | 0.03315
2026 | MCLU-135to240-MBT-CZ03-2003-17.5IEER | CZ03 | MBT | 2003 | 135to240 | 12 | 17.5 | 348.9089 | 3969.7924 | 0.51004 | 4122.8874 | 0.60621 | 153.0949 | 0.096172
2027 | MCLU-135to240-MBT-CZ03-2007-17.5IEER | CZ03 | MBT | 2007 | 135to240 | 12 | 17.5 | 345.4511 | 4013.3183 | 0.51397 | 4165.9112 | 0.60977 | 152.5929 | 0.095803
2028 | MCLU-135to240-MBT-CZ03-2011-17.5IEER | CZ03 | MBT | 2011 | 135to240 | 12 | 17.5 | 335.3449 | 4133.1317 | 0.54739 | 4237.0961 | 0.61549 | 103.9644 | 0.068099
2029 | MCLU-135to240-MBT-CZ03-2015-17.5IEER | CZ03 | MBT | 2015 | 135to240 | 12 | 17.5 | 311.1371 | 4394.9514 | 0.57015 | 4498.4817 | 0.63761 | 103.5302 | 0.067465
2030 | MCLU-135to240-MBT-CZ03-2020-17.5IEER | CZ03 | MBT | 2020 | 135to240 | 12 | 17.5 | 290.9697 | 4153.4224 | 0.51987 | 4303.8441 | 0.61236 | 150.4217 | 0.092482
2031 | MCLU-135to240-MLI-CZ03-2003-17.5IEER | CZ03 | MLI | 2003 | 135to240 | 12 | 17.5 | 198.3144 | 3132.743 | 0.39188 | 3285.4723 | 0.45832 | 152.7292 | 0.066443
2032 | MCLU-135to240-MLI-CZ03-2007-17.5IEER | CZ03 | MLI | 2007 | 135to240 | 12 | 17.5 | 194.7769 | 3188.3603 | 0.39744 | 3340.9049 | 0.46353 | 152.5447 | 0.066087
2033 | MCLU-135to240-MLI-CZ03-2011-17.5IEER | CZ03 | MLI | 2011 | 135to240 | 12 | 17.5 | 191.1828 | 3263.5966 | 0.42271 | 3399.5557 | 0.46917 | 135.9591 | 0.046453
2034 | MCLU-135to240-MLI-CZ03-2015-17.5IEER | CZ03 | MLI | 2015 | 135to240 | 12 | 17.5 | 188.0204 | 3293.1743 | 0.42491 | 3430.0907 | 0.47119 | 136.9164 | 0.046285
2035 | MCLU-135to240-MLI-CZ03-2020-17.5IEER | CZ03 | MLI | 2020 | 135to240 | 12 | 17.5 | 181.959 | 2826.0597 | 0.35252 | 2977.5308 | 0.41505 | 151.4711 | 0.062535
2036 | MCLU-135to240-Mtl-CZ03-2003-17.5IEER | CZ03 | Mtl | 2003 | 135to240 | 12 | 17.5 | 51.1232 | 2541.0212 | 0.51977 | 2605.2857 | 0.54287 | 64.2645 | 0.023094
2037 | MCLU-135to240-Mtl-CZ03-2007-17.5IEER | CZ03 | Mtl | 2007 | 135to240 | 12 | 17.5 | 51.1232 | 2463.495 | 0.48784 | 2527.7787 | 0.51094 | 64.2837 | 0.023095
2038 | MCLU-135to240-Mtl-CZ03-2011-17.5IEER | CZ03 | Mtl | 2011 | 135to240 | 12 | 17.5 | 49.9911 | 2475.0708 | 0.49793 | 2531.7801 | 0.51441 | 56.7093 | 0.016481
2039 | MCLU-135to240-Mtl-CZ03-2015-17.5IEER | CZ03 | Mtl | 2015 | 135to240 | 12 | 17.5 | 42.4973 | 2678.0961 | 0.51564 | 2736.8035 | 0.53355 | 58.7073 | 0.017914
2040 | MCLU-135to240-Mtl-CZ03-2020-17.5IEER | CZ03 | Mtl | 2020 | 135to240 | 12 | 17.5 | 42.1202 | 2597.6398 | 0.49657 | 2664.0811 | 0.52116 | 66.4413 | 0.024588
2041 | MCLU-135to240-Nrs-CZ03-2003-17.5IEER | CZ03 | Nrs | 2003 | 135to240 | 12 | 17.5 | 185.6806 | 4117.5483 | 0.74608 | 4278.5544 | 0.80432 | 161.0061 | 0.058238
2042 | MCLU-135to240-Nrs-CZ03-2007-17.5IEER | CZ03 | Nrs | 2007 | 135to240 | 12 | 17.5 | 185.676 | 4048.8696 | 0.72224 | 4210.2122 | 0.78028 | 161.3426 | 0.05804
2043 | MCLU-135to240-Nrs-CZ03-2011-17.5IEER | CZ03 | Nrs | 2011 | 135to240 | 12 | 17.5 | 185.6713 | 4067.5363 | 0.73824 | 4212.2167 | 0.7796 | 144.6805 | 0.041358
2044 | MCLU-135to240-Nrs-CZ03-2015-17.5IEER | CZ03 | Nrs | 2015 | 135to240 | 12 | 17.5 | 181.6163 | 3988.5128 | 0.68734 | 4130.8753 | 0.72637 | 142.3624 | 0.039032
2045 | MCLU-135to240-Nrs-CZ03-2020-17.5IEER | CZ03 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.607 | 3609.9495 | 0.61619 | 3767.8115 | 0.6679 | 157.862 | 0.051713
2046 | MCLU-135to240-OfL-CZ03-2003-17.5IEER | CZ03 | OfL | 2003 | 135to240 | 12 | 17.5 | 516.5182 | 2840.556 | 0.4313 | 2981.0515 | 0.48894 | 140.4955 | 0.057641
2047 | MCLU-135to240-OfL-CZ03-2007-17.5IEER | CZ03 | OfL | 2007 | 135to240 | 12 | 17.5 | 516.0978 | 2842.9007 | 0.43155 | 2983.3641 | 0.48918 | 140.4634 | 0.057632
2048 | MCLU-135to240-OfL-CZ03-2011-17.5IEER | CZ03 | OfL | 2011 | 135to240 | 12 | 17.5 | 507.5668 | 2899.1852 | 0.44828 | 2995.7848 | 0.4887 | 96.5995 | 0.040419
2049 | MCLU-135to240-OfL-CZ03-2015-17.5IEER | CZ03 | OfL | 2015 | 135to240 | 12 | 17.5 | 471.9134 | 3058.4916 | 0.46735 | 3154.7903 | 0.50648 | 96.2987 | 0.039123
2050 | MCLU-135to240-OfL-CZ03-2020-17.5IEER | CZ03 | OfL | 2020 | 135to240 | 12 | 17.5 | 457.2714 | 2874.6091 | 0.43474 | 3011.9444 | 0.4902 | 137.3353 | 0.05546
2051 | MCLU-135to240-OfS-CZ03-2003-17.5IEER | CZ03 | OfS | 2003 | 135to240 | 12 | 17.5 | 34.0588 | 2120.9318 | 0.31697 | 2268.6603 | 0.3731 | 147.7284 | 0.056126
2052 | MCLU-135to240-OfS-CZ03-2007-17.5IEER | CZ03 | OfS | 2007 | 135to240 | 12 | 17.5 | 34.0522 | 2121.4167 | 0.31677 | 2269.0946 | 0.37279 | 147.6779 | 0.056016
2053 | MCLU-135to240-OfS-CZ03-2011-17.5IEER | CZ03 | OfS | 2011 | 135to240 | 12 | 17.5 | 33.9373 | 2137.0046 | 0.33084 | 2251.948 | 0.37013 | 114.9434 | 0.039288
2054 | MCLU-135to240-OfS-CZ03-2015-17.5IEER | CZ03 | OfS | 2015 | 135to240 | 12 | 17.5 | 27.5235 | 2567.4604 | 0.37945 | 2679.5442 | 0.41797 | 112.0838 | 0.038518
2055 | MCLU-135to240-OfS-CZ03-2020-17.5IEER | CZ03 | OfS | 2020 | 135to240 | 12 | 17.5 | 26.7523 | 2383.1504 | 0.34271 | 2529.5859 | 0.39703 | 146.4355 | 0.05432
2056 | MCLU-135to240-RFF-CZ03-2003-17.5IEER | CZ03 | RFF | 2003 | 135to240 | 12 | 17.5 | 7.7282 | 4846.9815 | 0.93757 | 5105.2127 | 1.0847 | 258.2312 | 0.14709
2057 | MCLU-135to240-RFF-CZ03-2007-17.5IEER | CZ03 | RFF | 2007 | 135to240 | 12 | 17.5 | 7.6671 | 4885.1864 | 0.94327 | 5145.6564 | 1.0908 | 260.47 | 0.14753
2058 | MCLU-135to240-RFF-CZ03-2011-17.5IEER | CZ03 | RFF | 2011 | 135to240 | 12 | 17.5 | 7.6175 | 4964.6766 | 0.99674 | 5179.11 | 1.0953 | 214.4334 | 0.098561
2059 | MCLU-135to240-RFF-CZ03-2015-17.5IEER | CZ03 | RFF | 2015 | 135to240 | 12 | 17.5 | 7.1594 | 5009.5942 | 0.99956 | 5233.595 | 1.1008 | 224.0008 | 0.1012
2060 | MCLU-135to240-RFF-CZ03-2020-17.5IEER | CZ03 | RFF | 2020 | 135to240 | 12 | 17.5 | 6.7212 | 4598.222 | 0.89258 | 4869.858 | 1.0445 | 271.636 | 0.15189
2061 | MCLU-135to240-RSD-CZ03-2003-17.5IEER | CZ03 | RSD | 2003 | 135to240 | 12 | 17.5 | 13.4698 | 5071.6407 | 1.0051 | 5341.6408 | 1.1626 | 270.0001 | 0.15752
2062 | MCLU-135to240-RSD-CZ03-2007-17.5IEER | CZ03 | RSD | 2007 | 135to240 | 12 | 17.5 | 13.3341 | 5123.9011 | 1.0138 | 5395.8198 | 1.1714 | 271.9187 | 0.15759
2063 | MCLU-135to240-RSD-CZ03-2011-17.5IEER | CZ03 | RSD | 2011 | 135to240 | 12 | 17.5 | 13.1976 | 5233.9022 | 1.0712 | 5451.6907 | 1.1805 | 217.7885 | 0.10935
2064 | MCLU-135to240-RSD-CZ03-2015-17.5IEER | CZ03 | RSD | 2015 | 135to240 | 12 | 17.5 | 12.0348 | 5409.8824 | 1.0942 | 5621.2961 | 1.2029 | 211.4136 | 0.10874
2065 | MCLU-135to240-RSD-CZ03-2020-17.5IEER | CZ03 | RSD | 2020 | 135to240 | 12 | 17.5 | 10.984 | 4907.0998 | 0.96558 | 5149.5959 | 1.1191 | 242.4961 | 0.15356
2066 | MCLU-135to240-Rt3-CZ03-2003-17.5IEER | CZ03 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 215.9149 | 5965.341 | 1.1458 | 6165.3316 | 1.2898 | 199.9906 | 0.14404
2067 | MCLU-135to240-Rt3-CZ03-2007-17.5IEER | CZ03 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 215.8659 | 5967.0213 | 1.1451 | 6166.8206 | 1.289 | 199.7993 | 0.14394
2068 | MCLU-135to240-Rt3-CZ03-2011-17.5IEER | CZ03 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 215.8146 | 6045.0956 | 1.1923 | 6168.382 | 1.2881 | 123.2863 | 0.095841
2069 | MCLU-135to240-Rt3-CZ03-2015-17.5IEER | CZ03 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 203.1709 | 5761.4056 | 1.151 | 5894.9964 | 1.2468 | 133.5908 | 0.095795
2070 | MCLU-135to240-Rt3-CZ03-2020-17.5IEER | CZ03 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 193.3551 | 5270.4672 | 1.0384 | 5479.9894 | 1.181 | 209.5222 | 0.14265
2071 | MCLU-135to240-RtL-CZ03-2003-17.5IEER | CZ03 | RtL | 2003 | 135to240 | 12 | 17.5 | 184.0179 | 6683.3206 | 1.2576 | 6966.5035 | 1.3998 | 283.1828 | 0.14221
2072 | MCLU-135to240-RtL-CZ03-2007-17.5IEER | CZ03 | RtL | 2007 | 135to240 | 12 | 17.5 | 182.8866 | 6729.2436 | 1.2645 | 7013.1362 | 1.4062 | 283.8926 | 0.14167
2073 | MCLU-135to240-RtL-CZ03-2011-17.5IEER | CZ03 | RtL | 2011 | 135to240 | 12 | 17.5 | 181.7357 | 6865.9474 | 1.316 | 7061.938 | 1.4129 | 195.9905 | 0.096933
2074 | MCLU-135to240-RtL-CZ03-2015-17.5IEER | CZ03 | RtL | 2015 | 135to240 | 12 | 17.5 | 172.5479 | 6710.8239 | 1.3081 | 6926.816 | 1.4072 | 215.9921 | 0.099154
2075 | MCLU-135to240-RtL-CZ03-2020-17.5IEER | CZ03 | RtL | 2020 | 135to240 | 12 | 17.5 | 161.7381 | 6375.9781 | 1.2528 | 6689.2814 | 1.3961 | 313.3033 | 0.14333
2076 | MCLU-135to240-RtS-CZ03-2003-17.5IEER | CZ03 | RtS | 2003 | 135to240 | 12 | 17.5 | 14.1773 | 3831.2128 | 0.73423 | 4134.6147 | 0.86172 | 303.4018 | 0.12749
2077 | MCLU-135to240-RtS-CZ03-2007-17.5IEER | CZ03 | RtS | 2007 | 135to240 | 12 | 17.5 | 14.1688 | 3834.5433 | 0.73247 | 4138.6894 | 0.85961 | 304.146 | 0.12715
2078 | MCLU-135to240-RtS-CZ03-2011-17.5IEER | CZ03 | RtS | 2011 | 135to240 | 12 | 17.5 | 14.1604 | 3924.9547 | 0.77015 | 4143.1807 | 0.85737 | 218.226 | 0.08722
2079 | MCLU-135to240-RtS-CZ03-2015-17.5IEER | CZ03 | RtS | 2015 | 135to240 | 12 | 17.5 | 13.0947 | 3746.0923 | 0.7578 | 3908.1583 | 0.84216 | 162.066 | 0.084354
2080 | MCLU-135to240-RtS-CZ03-2020-17.5IEER | CZ03 | RtS | 2020 | 135to240 | 12 | 17.5 | 12.7272 | 3434.9072 | 0.67808 | 3639.7558 | 0.79834 | 204.8486 | 0.12025
2081 | MCLU-135to240-SCn-CZ03-2003-17.5IEER | CZ03 | SCn | 2003 | 135to240 | 12 | 17.5 | 323.1707 | 2209.3011 | 0.20811 | 2402.102 | 0.24674 | 192.8009 | 0.038631
2082 | MCLU-135to240-SCn-CZ03-2007-17.5IEER | CZ03 | SCn | 2007 | 135to240 | 12 | 17.5 | 321.3819 | 2218.3408 | 0.20688 | 2407.7314 | 0.24429 | 189.3906 | 0.037411
2083 | MCLU-135to240-SCn-CZ03-2011-17.5IEER | CZ03 | SCn | 2011 | 135to240 | 12 | 17.5 | 319.6994 | 2241.3395 | 0.21265 | 2416.4754 | 0.2416 | 175.1359 | 0.028949
2084 | MCLU-135to240-SCn-CZ03-2015-17.5IEER | CZ03 | SCn | 2015 | 135to240 | 12 | 17.5 | 319.2649 | 2222.8842 | 0.21105 | 2404.4551 | 0.23959 | 181.5709 | 0.028538
2085 | MCLU-135to240-SCn-CZ03-2020-17.5IEER | CZ03 | SCn | 2020 | 135to240 | 12 | 17.5 | 317.1333 | 1937.3345 | 0.17026 | 2123.4209 | 0.20162 | 186.0863 | 0.031356
2086 | MCLU-135to240-WRf-CZ03-2003-17.5IEER | CZ03 | WRf | 2003 | 135to240 | 12 | 17.5 | 12.628 | 296630.7584 | 38.4909 | 296948.3856 | 38.5404 | 317.6272 | 0.049445
2087 | MCLU-135to240-WRf-CZ03-2007-17.5IEER | CZ03 | WRf | 2007 | 135to240 | 12 | 17.5 | 11.7663 | 308802.3952 | 38.991 | 309139.2782 | 39.0386 | 336.883 | 0.047541
2088 | MCLU-135to240-WRf-CZ03-2011-17.5IEER | CZ03 | WRf | 2011 | 135to240 | 12 | 17.5 | 11.84 | 300049.94 | 37.3821 | 300405.4279 | 37.4306 | 355.4878 | 0.048461
2089 | MCLU-135to240-WRf-CZ03-2015-17.5IEER | CZ03 | WRf | 2015 | 135to240 | 12 | 17.5 | 11.1758 | 317319.6489 | 39.5855 | 317521.3605 | 39.6297 | 201.7116 | 0.044232
2090 | MCLU-135to240-WRf-CZ03-2020-17.5IEER | CZ03 | WRf | 2020 | 135to240 | 12 | 17.5 | 9.8962 | 338845.2184 | 42.131 | 339046.9092 | 42.1707 | 201.6908 | 0.039684
2091 | MCLU-135to240-Asm-CZ04-2003-17.5IEER | CZ04 | Asm | 2003 | 135to240 | 12 | 17.5 | 311.1205 | 2328.768 | 0.76548 | 2646.8156 | 0.93002 | 318.0476 | 0.16454
2092 | MCLU-135to240-Asm-CZ04-2007-17.5IEER | CZ04 | Asm | 2007 | 135to240 | 12 | 17.5 | 308.9667 | 2341.9094 | 0.76967 | 2660.2995 | 0.93401 | 318.3901 | 0.16434
2093 | MCLU-135to240-Asm-CZ04-2011-17.5IEER | CZ04 | Asm | 2011 | 135to240 | 12 | 17.5 | 306.7521 | 2438.8696 | 0.81883 | 2674.5889 | 0.93816 | 235.7193 | 0.11933
2094 | MCLU-135to240-Asm-CZ04-2015-17.5IEER | CZ04 | Asm | 2015 | 135to240 | 12 | 17.5 | 277.0757 | 2672.5152 | 0.86043 | 2877.5508 | 0.97891 | 205.0357 | 0.11848
2095 | MCLU-135to240-Asm-CZ04-2020-17.5IEER | CZ04 | Asm | 2020 | 135to240 | 12 | 17.5 | 269.3363 | 2469.8441 | 0.78902 | 2748.7442 | 0.95273 | 278.9001 | 0.16371
2096 | MCLU-135to240-ECC-CZ04-2003-17.5IEER | CZ04 | ECC | 2003 | 135to240 | 12 | 17.5 | 750.8191 | 2622.4838 | 0.80691 | 2870.2819 | 0.98493 | 247.7982 | 0.17803
2097 | MCLU-135to240-ECC-CZ04-2007-17.5IEER | CZ04 | ECC | 2007 | 135to240 | 12 | 17.5 | 749.5865 | 2626.2794 | 0.80724 | 2874.1616 | 0.98506 | 247.8822 | 0.17782
2098 | MCLU-135to240-ECC-CZ04-2011-17.5IEER | CZ04 | ECC | 2011 | 135to240 | 12 | 17.5 | 748.1813 | 2698.2835 | 0.85797 | 2876.5773 | 0.98488 | 178.2937 | 0.12691
2099 | MCLU-135to240-ECC-CZ04-2015-17.5IEER | CZ04 | ECC | 2015 | 135to240 | 12 | 17.5 | 690.8965 | 2864.1897 | 0.89137 | 3044.8623 | 1.0199 | 180.6726 | 0.1285
2100 | MCLU-135to240-ECC-CZ04-2020-17.5IEER | CZ04 | ECC | 2020 | 135to240 | 12 | 17.5 | 659.9752 | 2458.51 | 0.79055 | 2705.3773 | 0.97025 | 246.8673 | 0.1797
2101 | MCLU-135to240-EPr-CZ04-2003-17.5IEER | CZ04 | EPr | 2003 | 135to240 | 12 | 17.5 | 120.8942 | 1772.8174 | 0.41657 | 1934.4513 | 0.51443 | 161.6339 | 0.097865
2102 | MCLU-135to240-EPr-CZ04-2007-17.5IEER | CZ04 | EPr | 2007 | 135to240 | 12 | 17.5 | 119.8719 | 1786.4694 | 0.41887 | 1948.7322 | 0.51643 | 162.2628 | 0.097554
2103 | MCLU-135to240-EPr-CZ04-2011-17.5IEER | CZ04 | EPr | 2011 | 135to240 | 12 | 17.5 | 116.6146 | 1878.2784 | 0.45742 | 2001.656 | 0.52464 | 123.3776 | 0.067221
2104 | MCLU-135to240-EPr-CZ04-2015-17.5IEER | CZ04 | EPr | 2015 | 135to240 | 12 | 17.5 | 104.8733 | 2027.47 | 0.48167 | 2154.6626 | 0.5484 | 127.1927 | 0.066722
2105 | MCLU-135to240-EPr-CZ04-2020-17.5IEER | CZ04 | EPr | 2020 | 135to240 | 12 | 17.5 | 99.6429 | 1763.0951 | 0.41695 | 1929.706 | 0.51168 | 166.6109 | 0.094729
2106 | MCLU-135to240-ERC-CZ04-2003-17.5IEER | CZ04 | ERC | 2003 | 135to240 | 12 | 17.5 | 5.6884 | 1408.8357 | 0.25157 | 1565.9967 | 0.30093 | 157.161 | 0.049359
2107 | MCLU-135to240-ERC-CZ04-2007-17.5IEER | CZ04 | ERC | 2007 | 135to240 | 12 | 17.5 | 5.6747 | 1412.0135 | 0.25163 | 1569.683 | 0.30084 | 157.6695 | 0.049205
2108 | MCLU-135to240-ERC-CZ04-2011-17.5IEER | CZ04 | ERC | 2011 | 135to240 | 12 | 17.5 | 5.4734 | 1507.1748 | 0.27037 | 1618.6877 | 0.29993 | 111.5129 | 0.029563
2109 | MCLU-135to240-ERC-CZ04-2015-17.5IEER | CZ04 | ERC | 2015 | 135to240 | 12 | 17.5 | 5.1528 | 1516.6934 | 0.26535 | 1615.3358 | 0.29227 | 98.6424 | 0.026916
2110 | MCLU-135to240-ERC-CZ04-2020-17.5IEER | CZ04 | ERC | 2020 | 135to240 | 12 | 17.5 | 4.9862 | 1289.7583 | 0.21843 | 1423.0825 | 0.25838 | 133.3242 | 0.039943
2111 | MCLU-135to240-ESe-CZ04-2003-17.5IEER | CZ04 | ESe | 2003 | 135to240 | 12 | 17.5 | 387.7181 | 1865.3044 | 0.37945 | 2042.5215 | 0.47707 | 177.2171 | 0.097623
2112 | MCLU-135to240-ESe-CZ04-2007-17.5IEER | CZ04 | ESe | 2007 | 135to240 | 12 | 17.5 | 386.4765 | 1870.8112 | 0.38018 | 2048.2417 | 0.47762 | 177.4305 | 0.097438
2113 | MCLU-135to240-ESe-CZ04-2011-17.5IEER | CZ04 | ESe | 2011 | 135to240 | 12 | 17.5 | 385.1823 | 1924.3503 | 0.41028 | 2053.2208 | 0.4781 | 128.8706 | 0.067822
2114 | MCLU-135to240-ESe-CZ04-2015-17.5IEER | CZ04 | ESe | 2015 | 135to240 | 12 | 17.5 | 347.9959 | 2040.7147 | 0.41109 | 2169.0398 | 0.47949 | 128.3251 | 0.068404
2115 | MCLU-135to240-ESe-CZ04-2020-17.5IEER | CZ04 | ESe | 2020 | 135to240 | 12 | 17.5 | 332.5531 | 1744.3943 | 0.3664 | 1915.6803 | 0.46423 | 171.286 | 0.097829
2116 | MCLU-135to240-EUn-CZ04-2003-17.5IEER | CZ04 | EUn | 2003 | 135to240 | 12 | 17.5 | 2279.0888 | 2800.1933 | 0.96607 | 3051.3494 | 1.1194 | 251.1561 | 0.15335
2117 | MCLU-135to240-EUn-CZ04-2007-17.5IEER | CZ04 | EUn | 2007 | 135to240 | 12 | 17.5 | 2268.9642 | 2794.8779 | 0.9602 | 3046.1144 | 1.1132 | 251.2365 | 0.15304
2118 | MCLU-135to240-EUn-CZ04-2011-17.5IEER | CZ04 | EUn | 2011 | 135to240 | 12 | 17.5 | 2240.3191 | 2883.4144 | 1.0126 | 3067.6098 | 1.1219 | 184.1954 | 0.10933
2119 | MCLU-135to240-EUn-CZ04-2015-17.5IEER | CZ04 | EUn | 2015 | 135to240 | 12 | 17.5 | 2030.3984 | 3084.3688 | 1.0624 | 3269.4983 | 1.1726 | 185.1295 | 0.1102
2120 | MCLU-135to240-EUn-CZ04-2020-17.5IEER | CZ04 | EUn | 2020 | 135to240 | 12 | 17.5 | 1939.253 | 2751.8526 | 0.96576 | 3003.2347 | 1.1199 | 251.382 | 0.15418
2121 | MCLU-135to240-Gro-CZ04-2003-17.5IEER | CZ04 | Gro | 2003 | 135to240 | 12 | 17.5 | 114.047 | 14370.2252 | 2.1758 | 14721.8847 | 2.2942 | 351.6595 | 0.11844
2122 | MCLU-135to240-Gro-CZ04-2007-17.5IEER | CZ04 | Gro | 2007 | 135to240 | 12 | 17.5 | 111.6767 | 13322.4097 | 2.1042 | 13627.2603 | 2.2231 | 304.8506 | 0.11893
2123 | MCLU-135to240-Gro-CZ04-2011-17.5IEER | CZ04 | Gro | 2011 | 135to240 | 12 | 17.5 | 110.0105 | 13519.0778 | 2.1321 | 13821.8247 | 2.251 | 302.7469 | 0.11884
2124 | MCLU-135to240-Gro-CZ04-2015-17.5IEER | CZ04 | Gro | 2015 | 135to240 | 12 | 17.5 | 103.6675 | 13720.3875 | 2.1542 | 14019.9275 | 2.2704 | 299.54 | 0.1162
2125 | MCLU-135to240-Gro-CZ04-2020-17.5IEER | CZ04 | Gro | 2020 | 135to240 | 12 | 17.5 | 100.6974 | 13682.1688 | 2.1414 | 13978.2296 | 2.2583 | 296.0609 | 0.11684
2126 | MCLU-135to240-Hsp-CZ04-2003-17.5IEER | CZ04 | Hsp | 2003 | 135to240 | 12 | 17.5 | 682.5957 | 4100.1363 | 0.72383 | 4514.5941 | 0.88546 | 414.4578 | 0.16162
2127 | MCLU-135to240-Hsp-CZ04-2007-17.5IEER | CZ04 | Hsp | 2007 | 135to240 | 12 | 17.5 | 682.5953 | 4099.8028 | 0.72341 | 4514.0508 | 0.88478 | 414.2479 | 0.16137
2128 | MCLU-135to240-Hsp-CZ04-2011-17.5IEER | CZ04 | Hsp | 2011 | 135to240 | 12 | 17.5 | 682.595 | 4167.71 | 0.76704 | 4513.496 | 0.88409 | 345.786 | 0.11705
2129 | MCLU-135to240-Hsp-CZ04-2015-17.5IEER | CZ04 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 4127.4258 | 0.74857 | 4473.7264 | 0.86564 | 346.3007 | 0.11707
2130 | MCLU-135to240-Hsp-CZ04-2020-17.5IEER | CZ04 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3554.5849 | 0.63057 | 3963.7874 | 0.7884 | 409.2024 | 0.15783
2131 | MCLU-135to240-Htl-CZ04-2003-17.5IEER | CZ04 | Htl | 2003 | 135to240 | 12 | 17.5 | 239.8328 | 3523.2382 | 0.87491 | 3622.3233 | 0.91575 | 99.0851 | 0.040839
2132 | MCLU-135to240-Htl-CZ04-2007-17.5IEER | CZ04 | Htl | 2007 | 135to240 | 12 | 17.5 | 239.4852 | 3400.7942 | 0.82039 | 3499.9191 | 0.86119 | 99.1249 | 0.040801
2133 | MCLU-135to240-Htl-CZ04-2011-17.5IEER | CZ04 | Htl | 2011 | 135to240 | 12 | 17.5 | 230.3412 | 3482.0854 | 0.8478 | 3563.4927 | 0.8774 | 81.4073 | 0.0296
2134 | MCLU-135to240-Htl-CZ04-2015-17.5IEER | CZ04 | Htl | 2015 | 135to240 | 12 | 17.5 | 203.4605 | 3632.4449 | 0.8515 | 3716.0889 | 0.88176 | 83.644 | 0.030255
2135 | MCLU-135to240-Htl-CZ04-2020-17.5IEER | CZ04 | Htl | 2020 | 135to240 | 12 | 17.5 | 201.6061 | 3512.0059 | 0.82707 | 3611.237 | 0.86869 | 99.2311 | 0.041615
2136 | MCLU-135to240-MBT-CZ04-2003-17.5IEER | CZ04 | MBT | 2003 | 135to240 | 12 | 17.5 | 336.612 | 4283.2395 | 0.61079 | 4510.0061 | 0.73787 | 226.7666 | 0.12708
2137 | MCLU-135to240-MBT-CZ04-2007-17.5IEER | CZ04 | MBT | 2007 | 135to240 | 12 | 17.5 | 331.2456 | 4354.4185 | 0.61909 | 4581.8728 | 0.74594 | 227.4543 | 0.12685
2138 | MCLU-135to240-MBT-CZ04-2011-17.5IEER | CZ04 | MBT | 2011 | 135to240 | 12 | 17.5 | 312.8939 | 4628.7334 | 0.67698 | 4781.5651 | 0.76676 | 152.8317 | 0.08978
2139 | MCLU-135to240-MBT-CZ04-2015-17.5IEER | CZ04 | MBT | 2015 | 135to240 | 12 | 17.5 | 290.1552 | 4910.5393 | 0.70433 | 5061.8734 | 0.79505 | 151.3341 | 0.090722
2140 | MCLU-135to240-MBT-CZ04-2020-17.5IEER | CZ04 | MBT | 2020 | 135to240 | 12 | 17.5 | 268.5781 | 4672.0621 | 0.65269 | 4897.8666 | 0.77989 | 225.8045 | 0.1272
2141 | MCLU-135to240-MLI-CZ04-2003-17.5IEER | CZ04 | MLI | 2003 | 135to240 | 12 | 17.5 | 202.2653 | 3198.9303 | 0.45533 | 3405.8643 | 0.55036 | 206.9341 | 0.095027
2142 | MCLU-135to240-MLI-CZ04-2007-17.5IEER | CZ04 | MLI | 2007 | 135to240 | 12 | 17.5 | 197.6802 | 3269.2912 | 0.46378 | 3476.0514 | 0.55896 | 206.7602 | 0.095186
2143 | MCLU-135to240-MLI-CZ04-2011-17.5IEER | CZ04 | MLI | 2011 | 135to240 | 12 | 17.5 | 193.1094 | 3384.1588 | 0.50172 | 3549.4997 | 0.56785 | 165.3409 | 0.06613
2144 | MCLU-135to240-MLI-CZ04-2015-17.5IEER | CZ04 | MLI | 2015 | 135to240 | 12 | 17.5 | 190.2141 | 3408.1482 | 0.50356 | 3573.6255 | 0.56998 | 165.4773 | 0.066413
2145 | MCLU-135to240-MLI-CZ04-2020-17.5IEER | CZ04 | MLI | 2020 | 135to240 | 12 | 17.5 | 176.5114 | 3033.3954 | 0.44059 | 3237.0687 | 0.53583 | 203.6733 | 0.095246
2146 | MCLU-135to240-Mtl-CZ04-2003-17.5IEER | CZ04 | Mtl | 2003 | 135to240 | 12 | 17.5 | 44.213 | 3405.5465 | 0.79793 | 3482.7757 | 0.82587 | 77.2292 | 0.027937
2147 | MCLU-135to240-Mtl-CZ04-2007-17.5IEER | CZ04 | Mtl | 2007 | 135to240 | 12 | 17.5 | 44.213 | 3277.7648 | 0.74148 | 3354.9759 | 0.7694 | 77.211 | 0.027922
2148 | MCLU-135to240-Mtl-CZ04-2011-17.5IEER | CZ04 | Mtl | 2011 | 135to240 | 12 | 17.5 | 42.2098 | 3342.2367 | 0.7618 | 3404.6177 | 0.78138 | 62.381 | 0.019584
2149 | MCLU-135to240-Mtl-CZ04-2015-17.5IEER | CZ04 | Mtl | 2015 | 135to240 | 12 | 17.5 | 35.7266 | 3569.1982 | 0.77586 | 3634.6834 | 0.7967 | 65.4852 | 0.020832
2150 | MCLU-135to240-Mtl-CZ04-2020-17.5IEER | CZ04 | Mtl | 2020 | 135to240 | 12 | 17.5 | 35.5907 | 3467.6113 | 0.75627 | 3548.8173 | 0.78527 | 81.2061 | 0.029004
2151 | MCLU-135to240-Nrs-CZ04-2003-17.5IEER | CZ04 | Nrs | 2003 | 135to240 | 12 | 17.5 | 187.2534 | 4312.4453 | 0.85884 | 4524.9383 | 0.94196 | 212.493 | 0.083118
2152 | MCLU-135to240-Nrs-CZ04-2007-17.5IEER | CZ04 | Nrs | 2007 | 135to240 | 12 | 17.5 | 187.19 | 4228.422 | 0.82674 | 4441.1104 | 0.90961 | 212.6884 | 0.082875
2153 | MCLU-135to240-Nrs-CZ04-2011-17.5IEER | CZ04 | Nrs | 2011 | 135to240 | 12 | 17.5 | 186.2432 | 4308.2164 | 0.84715 | 4485.0259 | 0.90606 | 176.8094 | 0.058907
2154 | MCLU-135to240-Nrs-CZ04-2015-17.5IEER | CZ04 | Nrs | 2015 | 135to240 | 12 | 17.5 | 181.6379 | 4199.499 | 0.78209 | 4369.9438 | 0.83923 | 170.4448 | 0.057141
2155 | MCLU-135to240-Nrs-CZ04-2020-17.5IEER | CZ04 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.607 | 3797.1313 | 0.70146 | 3996.8606 | 0.77844 | 199.7293 | 0.076982
2156 | MCLU-135to240-OfL-CZ04-2003-17.5IEER | CZ04 | OfL | 2003 | 135to240 | 12 | 17.5 | 446.5775 | 3445.8455 | 0.55551 | 3677.8856 | 0.62074 | 232.0401 | 0.06523
2157 | MCLU-135to240-OfL-CZ04-2007-17.5IEER | CZ04 | OfL | 2007 | 135to240 | 12 | 17.5 | 446.1193 | 3449.2284 | 0.55595 | 3681.3421 | 0.62115 | 232.1137 | 0.065199
2158 | MCLU-135to240-OfL-CZ04-2011-17.5IEER | CZ04 | OfL | 2011 | 135to240 | 12 | 17.5 | 428.7737 | 3623.9591 | 0.5833 | 3780.3598 | 0.62843 | 156.4008 | 0.045133
2159 | MCLU-135to240-OfL-CZ04-2015-17.5IEER | CZ04 | OfL | 2015 | 135to240 | 12 | 17.5 | 402.0262 | 3781.7902 | 0.60295 | 3935.5128 | 0.64725 | 153.7226 | 0.044299
2160 | MCLU-135to240-OfL-CZ04-2020-17.5IEER | CZ04 | OfL | 2020 | 135to240 | 12 | 17.5 | 389.7832 | 3535.1911 | 0.56545 | 3763.1001 | 0.6291 | 227.909 | 0.063643
2161 | MCLU-135to240-OfS-CZ04-2003-17.5IEER | CZ04 | OfS | 2003 | 135to240 | 12 | 17.5 | 30.9656 | 2483.6951 | 0.40521 | 2711.9789 | 0.47106 | 228.2838 | 0.06585
2162 | MCLU-135to240-OfS-CZ04-2007-17.5IEER | CZ04 | OfS | 2007 | 135to240 | 12 | 17.5 | 30.8948 | 2489.0287 | 0.4057 | 2717.3628 | 0.4715 | 228.334 | 0.065805
2163 | MCLU-135to240-OfS-CZ04-2011-17.5IEER | CZ04 | OfS | 2011 | 135to240 | 12 | 17.5 | 30.2301 | 2582.9425 | 0.42787 | 2747.5537 | 0.4728 | 164.6112 | 0.044927
2164 | MCLU-135to240-OfS-CZ04-2015-17.5IEER | CZ04 | OfS | 2015 | 135to240 | 12 | 17.5 | 25.0357 | 3007.466 | 0.47337 | 3165.6728 | 0.51752 | 158.2068 | 0.04415
2165 | MCLU-135to240-OfS-CZ04-2020-17.5IEER | CZ04 | OfS | 2020 | 135to240 | 12 | 17.5 | 24.2892 | 2780.5078 | 0.43209 | 3003.5812 | 0.49575 | 223.0734 | 0.063651
2166 | MCLU-135to240-RFF-CZ04-2003-17.5IEER | CZ04 | RFF | 2003 | 135to240 | 12 | 17.5 | 6.7097 | 5897.474 | 1.3226 | 6329.5832 | 1.4931 | 432.1093 | 0.1705
2167 | MCLU-135to240-RFF-CZ04-2007-17.5IEER | CZ04 | RFF | 2007 | 135to240 | 12 | 17.5 | 6.65 | 5947.714 | 1.3323 | 6381.3871 | 1.5023 | 433.6731 | 0.17002
2168 | MCLU-135to240-RFF-CZ04-2011-17.5IEER | CZ04 | RFF | 2011 | 135to240 | 12 | 17.5 | 6.5857 | 6109.4899 | 1.3887 | 6438.6052 | 1.5127 | 329.1153 | 0.12397
2169 | MCLU-135to240-RFF-CZ04-2015-17.5IEER | CZ04 | RFF | 2015 | 135to240 | 12 | 17.5 | 6.285 | 6066.3475 | 1.3847 | 6397.25 | 1.5101 | 330.9025 | 0.12536
2170 | MCLU-135to240-RFF-CZ04-2020-17.5IEER | CZ04 | RFF | 2020 | 135to240 | 12 | 17.5 | 5.9577 | 5488.6011 | 1.2708 | 5918.7179 | 1.4434 | 430.1168 | 0.17255
2171 | MCLU-135to240-RSD-CZ04-2003-17.5IEER | CZ04 | RSD | 2003 | 135to240 | 12 | 17.5 | 12.5268 | 5747.7638 | 1.2971 | 6149.3188 | 1.4748 | 401.5551 | 0.17768
2172 | MCLU-135to240-RSD-CZ04-2007-17.5IEER | CZ04 | RSD | 2007 | 135to240 | 12 | 17.5 | 12.4144 | 5778.6093 | 1.3068 | 6192.0973 | 1.4842 | 413.488 | 0.17734
2173 | MCLU-135to240-RSD-CZ04-2011-17.5IEER | CZ04 | RSD | 2011 | 135to240 | 12 | 17.5 | 12.1218 | 6032.7255 | 1.3838 | 6345.6588 | 1.5109 | 312.9332 | 0.12708
2174 | MCLU-135to240-RSD-CZ04-2015-17.5IEER | CZ04 | RSD | 2015 | 135to240 | 12 | 17.5 | 11.3072 | 6084.6075 | 1.396 | 6396.692 | 1.5232 | 312.0845 | 0.12721
2175 | MCLU-135to240-RSD-CZ04-2020-17.5IEER | CZ04 | RSD | 2020 | 135to240 | 12 | 17.5 | 10.5303 | 5401.7058 | 1.2562 | 5788.2294 | 1.4319 | 386.5236 | 0.17576
2176 | MCLU-135to240-Rt3-CZ04-2003-17.5IEER | CZ04 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 236.3645 | 5703.2946 | 1.2009 | 6025.8644 | 1.3836 | 322.5698 | 0.18272
2177 | MCLU-135to240-Rt3-CZ04-2007-17.5IEER | CZ04 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 235.5933 | 5721.4906 | 1.2039 | 6044.2096 | 1.3862 | 322.719 | 0.18238
2178 | MCLU-135to240-Rt3-CZ04-2011-17.5IEER | CZ04 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 234.8331 | 5851.2561 | 1.2608 | 6062.4568 | 1.3888 | 211.2006 | 0.12804
2179 | MCLU-135to240-Rt3-CZ04-2015-17.5IEER | CZ04 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 224.2182 | 5519.8259 | 1.2107 | 5735.2268 | 1.3398 | 215.4009 | 0.12913
2180 | MCLU-135to240-Rt3-CZ04-2020-17.5IEER | CZ04 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 214.2609 | 5012.7028 | 1.0961 | 5336.7914 | 1.281 | 324.0886 | 0.1849
2181 | MCLU-135to240-RtL-CZ04-2003-17.5IEER | CZ04 | RtL | 2003 | 135to240 | 12 | 17.5 | 201.6115 | 6377.5932 | 1.3036 | 6736.607 | 1.4851 | 359.0138 | 0.18147
2182 | MCLU-135to240-RtL-CZ04-2007-17.5IEER | CZ04 | RtL | 2007 | 135to240 | 12 | 17.5 | 198.8912 | 6464.8092 | 1.3195 | 6825.5549 | 1.5004 | 360.7457 | 0.18087
2183 | MCLU-135to240-RtL-CZ04-2011-17.5IEER | CZ04 | RtL | 2011 | 135to240 | 12 | 17.5 | 196.1114 | 6681.4379 | 1.3879 | 6919.5854 | 1.5168 | 238.1475 | 0.1289
2184 | MCLU-135to240-RtL-CZ04-2015-17.5IEER | CZ04 | RtL | 2015 | 135to240 | 12 | 17.5 | 188.0552 | 6480.5177 | 1.3748 | 6730.1548 | 1.5051 | 249.6371 | 0.13023
2185 | MCLU-135to240-RtL-CZ04-2020-17.5IEER | CZ04 | RtL | 2020 | 135to240 | 12 | 17.5 | 176.4467 | 6125.5189 | 1.321 | 6502.7378 | 1.5022 | 377.219 | 0.18113
2186 | MCLU-135to240-RtS-CZ04-2003-17.5IEER | CZ04 | RtS | 2003 | 135to240 | 12 | 17.5 | 15.7271 | 3671.3302 | 0.78978 | 4075.2026 | 0.95203 | 403.8724 | 0.16225
2187 | MCLU-135to240-RtS-CZ04-2007-17.5IEER | CZ04 | RtS | 2007 | 135to240 | 12 | 17.5 | 15.5167 | 3719.0712 | 0.7978 | 4124.3919 | 0.95974 | 405.3207 | 0.16194
2188 | MCLU-135to240-RtS-CZ04-2011-17.5IEER | CZ04 | RtS | 2011 | 135to240 | 12 | 17.5 | 15.2637 | 3898.1092 | 0.85563 | 4185.8199 | 0.97029 | 287.7107 | 0.11465
2189 | MCLU-135to240-RtS-CZ04-2015-17.5IEER | CZ04 | RtS | 2015 | 135to240 | 12 | 17.5 | 14.3897 | 3692.7697 | 0.83551 | 3923.5402 | 0.95092 | 230.7704 | 0.11541
2190 | MCLU-135to240-RtS-CZ04-2020-17.5IEER | CZ04 | RtS | 2020 | 135to240 | 12 | 17.5 | 13.7982 | 3404.2371 | 0.76075 | 3719.9552 | 0.92373 | 315.7181 | 0.16298
2191 | MCLU-135to240-SCn-CZ04-2003-17.5IEER | CZ04 | SCn | 2003 | 135to240 | 12 | 17.5 | 228.1443 | 3181.8137 | 0.39918 | 3439.3988 | 0.49814 | 257.5851 | 0.098965
2192 | MCLU-135to240-SCn-CZ04-2007-17.5IEER | CZ04 | SCn | 2007 | 135to240 | 12 | 17.5 | 218.7508 | 3308.5653 | 0.4123 | 3565.4251 | 0.50958 | 256.8598 | 0.097285
2193 | MCLU-135to240-SCn-CZ04-2011-17.5IEER | CZ04 | SCn | 2011 | 135to240 | 12 | 17.5 | 209.3148 | 3481.1281 | 0.45668 | 3701.4704 | 0.52412 | 220.3423 | 0.067441
2194 | MCLU-135to240-SCn-CZ04-2015-17.5IEER | CZ04 | SCn | 2015 | 135to240 | 12 | 17.5 | 208.5037 | 3463.4609 | 0.45372 | 3674.6024 | 0.52155 | 211.1414 | 0.067836
2195 | MCLU-135to240-SCn-CZ04-2020-17.5IEER | CZ04 | SCn | 2020 | 135to240 | 12 | 17.5 | 189.5206 | 3266.3985 | 0.40838 | 3499.0655 | 0.50589 | 232.667 | 0.097512
2196 | MCLU-135to240-WRf-CZ04-2003-17.5IEER | CZ04 | WRf | 2003 | 135to240 | 12 | 17.5 | 14.0953 | 270073.5475 | 36.589 | 270409.7599 | 36.6451 | 336.2123 | 0.056047
2197 | MCLU-135to240-WRf-CZ04-2007-17.5IEER | CZ04 | WRf | 2007 | 135to240 | 12 | 17.5 | 13.8277 | 265211.8089 | 34.8355 | 265550.3454 | 34.889 | 338.5365 | 0.053467
2198 | MCLU-135to240-WRf-CZ04-2011-17.5IEER | CZ04 | WRf | 2011 | 135to240 | 12 | 17.5 | 12.8828 | 275923.595 | 35.3572 | 276281.5161 | 35.4058 | 357.9211 | 0.048656
2199 | MCLU-135to240-WRf-CZ04-2015-17.5IEER | CZ04 | WRf | 2015 | 135to240 | 12 | 17.5 | 12.1368 | 292420.5146 | 37.5074 | 292654.7915 | 37.5557 | 234.2769 | 0.048315
2200 | MCLU-135to240-WRf-CZ04-2020-17.5IEER | CZ04 | WRf | 2020 | 135to240 | 12 | 17.5 | 11.411 | 293839.5914 | 37.6318 | 294066.3721 | 37.6735 | 226.7807 | 0.041704
2201 | MCLU-135to240-Asm-CZ05-2003-17.5IEER | CZ05 | Asm | 2003 | 135to240 | 12 | 17.5 | 344.6927 | 1796.3277 | 0.38669 | 2018.9933 | 0.48358 | 222.6657 | 0.096891
2202 | MCLU-135to240-Asm-CZ05-2007-17.5IEER | CZ05 | Asm | 2007 | 135to240 | 12 | 17.5 | 341.3281 | 1811.9602 | 0.39014 | 2034.6948 | 0.48748 | 222.7346 | 0.097347
2203 | MCLU-135to240-Asm-CZ05-2011-17.5IEER | CZ05 | Asm | 2011 | 135to240 | 12 | 17.5 | 341.3281 | 1848.3444 | 0.41641 | 2034.6948 | 0.48748 | 186.3504 | 0.071073
2204 | MCLU-135to240-Asm-CZ05-2015-17.5IEER | CZ05 | Asm | 2015 | 135to240 | 12 | 17.5 | 297.8755 | 2028.068 | 0.45066 | 2209.4729 | 0.52118 | 181.405 | 0.070524
2205 | MCLU-135to240-Asm-CZ05-2020-17.5IEER | CZ05 | Asm | 2020 | 135to240 | 12 | 17.5 | 286.4664 | 1996.4199 | 0.4244 | 2172.399 | 0.51466 | 175.979 | 0.090259
2206 | MCLU-135to240-ECC-CZ05-2003-17.5IEER | CZ05 | ECC | 2003 | 135to240 | 12 | 17.5 | 832.3385 | 2224.9885 | 0.51105 | 2368.9095 | 0.60694 | 143.921 | 0.09589
2207 | MCLU-135to240-ECC-CZ05-2007-17.5IEER | CZ05 | ECC | 2007 | 135to240 | 12 | 17.5 | 831.9618 | 2226.0985 | 0.5111 | 2370.0168 | 0.60697 | 143.9183 | 0.09587
2208 | MCLU-135to240-ECC-CZ05-2011-17.5IEER | CZ05 | ECC | 2011 | 135to240 | 12 | 17.5 | 831.929 | 2259.6318 | 0.54033 | 2368.3331 | 0.60661 | 108.7013 | 0.066279
2209 | MCLU-135to240-ECC-CZ05-2015-17.5IEER | CZ05 | ECC | 2015 | 135to240 | 12 | 17.5 | 735.9959 | 2517.6659 | 0.59655 | 2629.7894 | 0.66476 | 112.1235 | 0.068202
2210 | MCLU-135to240-ECC-CZ05-2020-17.5IEER | CZ05 | ECC | 2020 | 135to240 | 12 | 17.5 | 693.7133 | 2190.903 | 0.52143 | 2339.9661 | 0.61998 | 149.0631 | 0.098551
2211 | MCLU-135to240-EPr-CZ05-2003-17.5IEER | CZ05 | EPr | 2003 | 135to240 | 12 | 17.5 | 125.9736 | 1619.6874 | 0.2856 | 1721.4917 | 0.33599 | 101.8043 | 0.050388
2212 | MCLU-135to240-EPr-CZ05-2007-17.5IEER | CZ05 | EPr | 2007 | 135to240 | 12 | 17.5 | 125.6621 | 1623.5513 | 0.2861 | 1725.3678 | 0.33645 | 101.8165 | 0.050349
2213 | MCLU-135to240-EPr-CZ05-2011-17.5IEER | CZ05 | EPr | 2011 | 135to240 | 12 | 17.5 | 125.6621 | 1646.0201 | 0.3006 | 1725.3678 | 0.33645 | 79.3477 | 0.03585
2214 | MCLU-135to240-EPr-CZ05-2015-17.5IEER | CZ05 | EPr | 2015 | 135to240 | 12 | 17.5 | 110.2821 | 1829.3727 | 0.32746 | 1917.0772 | 0.36463 | 87.7044 | 0.037167
2215 | MCLU-135to240-EPr-CZ05-2020-17.5IEER | CZ05 | EPr | 2020 | 135to240 | 12 | 17.5 | 105.356 | 1608.3245 | 0.27909 | 1711.5407 | 0.32812 | 103.2162 | 0.049023
2216 | MCLU-135to240-ERC-CZ05-2003-17.5IEER | CZ05 | ERC | 2003 | 135to240 | 12 | 17.5 | 5.3785 | 1406.2873 | 0.1984 | 1543.3179 | 0.21037 | 137.0306 | 0.011973
2217 | MCLU-135to240-ERC-CZ05-2007-17.5IEER | CZ05 | ERC | 2007 | 135to240 | 12 | 17.5 | 5.3776 | 1407.031 | 0.19838 | 1544.5587 | 0.21033 | 137.5277 | 0.011952
2218 | MCLU-135to240-ERC-CZ05-2011-17.5IEER | CZ05 | ERC | 2011 | 135to240 | 12 | 17.5 | 5.3776 | 1448.3319 | 0.20288 | 1544.5587 | 0.21033 | 96.2268 | 0.0074494
2219 | MCLU-135to240-ERC-CZ05-2015-17.5IEER | CZ05 | ERC | 2015 | 135to240 | 12 | 17.5 | 4.9713 | 1491.9549 | 0.20929 | 1578.5419 | 0.21486 | 86.5869 | 0.0055698
2220 | MCLU-135to240-ERC-CZ05-2020-17.5IEER | CZ05 | ERC | 2020 | 135to240 | 12 | 17.5 | 4.763 | 1281.3367 | 0.17729 | 1395.6192 | 0.18375 | 114.2825 | 0.0064578
2221 | MCLU-135to240-ESe-CZ05-2003-17.5IEER | CZ05 | ESe | 2003 | 135to240 | 12 | 17.5 | 419.7022 | 1622.1088 | 0.2434 | 1737.2174 | 0.30071 | 115.1086 | 0.057306
2222 | MCLU-135to240-ESe-CZ05-2007-17.5IEER | CZ05 | ESe | 2007 | 135to240 | 12 | 17.5 | 418.8941 | 1625.2878 | 0.24378 | 1740.3939 | 0.30111 | 115.1061 | 0.057323
2223 | MCLU-135to240-ESe-CZ05-2011-17.5IEER | CZ05 | ESe | 2011 | 135to240 | 12 | 17.5 | 418.8623 | 1652.0098 | 0.26079 | 1739.5687 | 0.30106 | 87.5588 | 0.040271
2224 | MCLU-135to240-ESe-CZ05-2015-17.5IEER | CZ05 | ESe | 2015 | 135to240 | 12 | 17.5 | 356.5789 | 1876.2141 | 0.28043 | 1967.6306 | 0.32003 | 91.4165 | 0.039606
2225 | MCLU-135to240-ESe-CZ05-2020-17.5IEER | CZ05 | ESe | 2020 | 135to240 | 12 | 17.5 | 336.0292 | 1627.4919 | 0.24926 | 1745.1749 | 0.30469 | 117.683 | 0.055433
2226 | MCLU-135to240-EUn-CZ05-2003-17.5IEER | CZ05 | EUn | 2003 | 135to240 | 12 | 17.5 | 2479.7395 | 2398.6376 | 0.62437 | 2550.6872 | 0.71021 | 152.0496 | 0.085844
2227 | MCLU-135to240-EUn-CZ05-2007-17.5IEER | CZ05 | EUn | 2007 | 135to240 | 12 | 17.5 | 2476.5867 | 2390.6358 | 0.62125 | 2542.5249 | 0.7071 | 151.8891 | 0.085847
2228 | MCLU-135to240-EUn-CZ05-2011-17.5IEER | CZ05 | EUn | 2011 | 135to240 | 12 | 17.5 | 2461.8198 | 2427.1886 | 0.65195 | 2543.7723 | 0.71083 | 116.5837 | 0.058879
2229 | MCLU-135to240-EUn-CZ05-2015-17.5IEER | CZ05 | EUn | 2015 | 135to240 | 12 | 17.5 | 2156.9185 | 2711.1173 | 0.72304 | 2825.7309 | 0.78281 | 114.6136 | 0.059768
2230 | MCLU-135to240-EUn-CZ05-2020-17.5IEER | CZ05 | EUn | 2020 | 135to240 | 12 | 17.5 | 2058.1872 | 2433.7688 | 0.64263 | 2583.4527 | 0.72943 | 149.6839 | 0.086802
2231 | MCLU-135to240-Gro-CZ05-2003-17.5IEER | CZ05 | Gro | 2003 | 135to240 | 12 | 17.5 | 82.6915 | 19402.3274 | 2.4924 | 19813.8792 | 2.5621 | 411.5518 | 0.069726
2232 | MCLU-135to240-Gro-CZ05-2007-17.5IEER | CZ05 | Gro | 2007 | 135to240 | 12 | 17.5 | 81.7901 | 17689.2208 | 2.3722 | 18013.4783 | 2.4299 | 324.2575 | 0.057731
2233 | MCLU-135to240-Gro-CZ05-2011-17.5IEER | CZ05 | Gro | 2011 | 135to240 | 12 | 17.5 | 81.7901 | 17689.2208 | 2.3722 | 18013.4783 | 2.4299 | 324.2575 | 0.057731
2234 | MCLU-135to240-Gro-CZ05-2015-17.5IEER | CZ05 | Gro | 2015 | 135to240 | 12 | 17.5 | 76.3661 | 18127.2068 | 2.4071 | 18446.3577 | 2.4606 | 319.1509 | 0.053525
2235 | MCLU-135to240-Gro-CZ05-2020-17.5IEER | CZ05 | Gro | 2020 | 135to240 | 12 | 17.5 | 73.7338 | 18198.366 | 2.4011 | 18498.1907 | 2.4496 | 299.8247 | 0.048459
2236 | MCLU-135to240-Hsp-CZ05-2003-17.5IEER | CZ05 | Hsp | 2003 | 135to240 | 12 | 17.5 | 681.4537 | 3959.7656 | 0.6081 | 4272.3716 | 0.68536 | 312.606 | 0.077263
2237 | MCLU-135to240-Hsp-CZ05-2007-17.5IEER | CZ05 | Hsp | 2007 | 135to240 | 12 | 17.5 | 681.4537 | 3959.8196 | 0.60803 | 4272.3874 | 0.68524 | 312.5679 | 0.07721
2238 | MCLU-135to240-Hsp-CZ05-2011-17.5IEER | CZ05 | Hsp | 2011 | 135to240 | 12 | 17.5 | 681.4537 | 3992.3152 | 0.62987 | 4272.3874 | 0.68524 | 280.0722 | 0.05537
2239 | MCLU-135to240-Hsp-CZ05-2015-17.5IEER | CZ05 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4567 | 3952.517 | 0.61999 | 4235.5158 | 0.67417 | 282.9988 | 0.054174
2240 | MCLU-135to240-Hsp-CZ05-2020-17.5IEER | CZ05 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4567 | 3425.6748 | 0.5306 | 3741.8896 | 0.6013 | 316.2148 | 0.070697
2241 | MCLU-135to240-Htl-CZ05-2003-17.5IEER | CZ05 | Htl | 2003 | 135to240 | 12 | 17.5 | 266.3106 | 2854.8755 | 0.4819 | 2917.8394 | 0.50139 | 62.9638 | 0.019495
2242 | MCLU-135to240-Htl-CZ05-2007-17.5IEER | CZ05 | Htl | 2007 | 135to240 | 12 | 17.5 | 266.2825 | 2769.1584 | 0.46051 | 2832.3949 | 0.47999 | 63.2365 | 0.019481
2243 | MCLU-135to240-Htl-CZ05-2011-17.5IEER | CZ05 | Htl | 2011 | 135to240 | 12 | 17.5 | 260.115 | 2789.3255 | 0.47586 | 2844.5858 | 0.48975 | 55.2604 | 0.013895
2244 | MCLU-135to240-Htl-CZ05-2015-17.5IEER | CZ05 | Htl | 2015 | 135to240 | 12 | 17.5 | 225.6487 | 2973.4941 | 0.49787 | 3030.3043 | 0.51209 | 56.8102 | 0.014223
2245 | MCLU-135to240-Htl-CZ05-2020-17.5IEER | CZ05 | Htl | 2020 | 135to240 | 12 | 17.5 | 224.2546 | 2861.9981 | 0.47862 | 2924.128 | 0.49797 | 62.1299 | 0.019353
2246 | MCLU-135to240-MBT-CZ05-2003-17.5IEER | CZ05 | MBT | 2003 | 135to240 | 12 | 17.5 | 347.869 | 4015.0271 | 0.47942 | 4168.8737 | 0.54824 | 153.8466 | 0.068823
2247 | MCLU-135to240-MBT-CZ05-2007-17.5IEER | CZ05 | MBT | 2007 | 135to240 | 12 | 17.5 | 344.3197 | 4060.2611 | 0.48461 | 4214.0746 | 0.55393 | 153.8134 | 0.069322
2248 | MCLU-135to240-MBT-CZ05-2011-17.5IEER | CZ05 | MBT | 2011 | 135to240 | 12 | 17.5 | 336.5017 | 4152.4433 | 0.50983 | 4257.1481 | 0.55958 | 104.7048 | 0.049752
2249 | MCLU-135to240-MBT-CZ05-2015-17.5IEER | CZ05 | MBT | 2015 | 135to240 | 12 | 17.5 | 311.5407 | 4423.1664 | 0.53451 | 4527.5987 | 0.584 | 104.4323 | 0.049483
2250 | MCLU-135to240-MBT-CZ05-2020-17.5IEER | CZ05 | MBT | 2020 | 135to240 | 12 | 17.5 | 287.3271 | 4245.4136 | 0.49984 | 4396.7927 | 0.56816 | 151.3791 | 0.068325
2251 | MCLU-135to240-MLI-CZ05-2003-17.5IEER | CZ05 | MLI | 2003 | 135to240 | 12 | 17.5 | 196.0452 | 3171.8951 | 0.35794 | 3326.1705 | 0.40302 | 154.2754 | 0.045085
2252 | MCLU-135to240-MLI-CZ05-2007-17.5IEER | CZ05 | MLI | 2007 | 135to240 | 12 | 17.5 | 192.3872 | 3230.7029 | 0.36432 | 3384.5841 | 0.40949 | 153.8812 | 0.045168
2253 | MCLU-135to240-MLI-CZ05-2011-17.5IEER | CZ05 | MLI | 2011 | 135to240 | 12 | 17.5 | 192.3872 | 3247.2281 | 0.37551 | 3384.5841 | 0.40949 | 137.356 | 0.033977
2254 | MCLU-135to240-MLI-CZ05-2015-17.5IEER | CZ05 | MLI | 2015 | 135to240 | 12 | 17.5 | 189.0615 | 3278.7534 | 0.37797 | 3417.027 | 0.41188 | 138.2736 | 0.033915
2255 | MCLU-135to240-MLI-CZ05-2020-17.5IEER | CZ05 | MLI | 2020 | 135to240 | 12 | 17.5 | 179.1424 | 2871.9066 | 0.32365 | 3024.0761 | 0.36612 | 152.1694 | 0.042471
2256 | MCLU-135to240-Mtl-CZ05-2003-17.5IEER | CZ05 | Mtl | 2003 | 135to240 | 12 | 17.5 | 50.6895 | 2614.8271 | 0.38124 | 2680.5319 | 0.39535 | 65.7048 | 0.014111
2257 | MCLU-135to240-Mtl-CZ05-2007-17.5IEER | CZ05 | Mtl | 2007 | 135to240 | 12 | 17.5 | 50.6895 | 2535.0023 | 0.36343 | 2600.6621 | 0.3776 | 65.6598 | 0.014171
2258 | MCLU-135to240-Mtl-CZ05-2011-17.5IEER | CZ05 | Mtl | 2011 | 135to240 | 12 | 17.5 | 49.494 | 2538.6434 | 0.37447 | 2596.6721 | 0.38456 | 58.0287 | 0.010093
2259 | MCLU-135to240-Mtl-CZ05-2015-17.5IEER | CZ05 | Mtl | 2015 | 135to240 | 12 | 17.5 | 42.1277 | 2724.1857 | 0.41077 | 2783.885 | 0.42141 | 59.6993 | 0.010633
2260 | MCLU-135to240-Mtl-CZ05-2020-17.5IEER | CZ05 | Mtl | 2020 | 135to240 | 12 | 17.5 | 41.6837 | 2643.6693 | 0.39811 | 2710.7189 | 0.4129 | 67.0496 | 0.014786
2261 | MCLU-135to240-Nrs-CZ05-2003-17.5IEER | CZ05 | Nrs | 2003 | 135to240 | 12 | 17.5 | 185.4878 | 4170.3867 | 0.66885 | 4316.9583 | 0.70604 | 146.5716 | 0.037192
2262 | MCLU-135to240-Nrs-CZ05-2007-17.5IEER | CZ05 | Nrs | 2007 | 135to240 | 12 | 17.5 | 185.4822 | 4102.3025 | 0.65173 | 4249.2823 | 0.68887 | 146.9798 | 0.037135
2263 | MCLU-135to240-Nrs-CZ05-2011-17.5IEER | CZ05 | Nrs | 2011 | 135to240 | 12 | 17.5 | 185.4822 | 4119.7159 | 0.66211 | 4249.2823 | 0.68887 | 129.5664 | 0.026758
2264 | MCLU-135to240-Nrs-CZ05-2015-17.5IEER | CZ05 | Nrs | 2015 | 135to240 | 12 | 17.5 | 181.607 | 4028.3706 | 0.62817 | 4154.837 | 0.65332 | 126.4664 | 0.025155
2265 | MCLU-135to240-Nrs-CZ05-2020-17.5IEER | CZ05 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.607 | 3651.2896 | 0.56567 | 3793.0234 | 0.59885 | 141.7338 | 0.033186
2266 | MCLU-135to240-OfL-CZ05-2003-17.5IEER | CZ05 | OfL | 2003 | 135to240 | 12 | 17.5 | 513.2571 | 2878.0075 | 0.41555 | 3028.3489 | 0.46391 | 150.3414 | 0.048364
2267 | MCLU-135to240-OfL-CZ05-2007-17.5IEER | CZ05 | OfL | 2007 | 135to240 | 12 | 17.5 | 512.77 | 2880.8227 | 0.41591 | 3031.1845 | 0.46429 | 150.3618 | 0.048374
2268 | MCLU-135to240-OfL-CZ05-2011-17.5IEER | CZ05 | OfL | 2011 | 135to240 | 12 | 17.5 | 503.072 | 2955.6774 | 0.43363 | 3057.7034 | 0.4673 | 102.0259 | 0.033667
2269 | MCLU-135to240-OfL-CZ05-2015-17.5IEER | CZ05 | OfL | 2015 | 135to240 | 12 | 17.5 | 467.3343 | 3117.8965 | 0.45524 | 3219.3738 | 0.48868 | 101.4773 | 0.033441
2270 | MCLU-135to240-OfL-CZ05-2020-17.5IEER | CZ05 | OfL | 2020 | 135to240 | 12 | 17.5 | 451.7057 | 2933.576 | 0.42578 | 3080.2341 | 0.47385 | 146.6581 | 0.048062
2271 | MCLU-135to240-OfS-CZ05-2003-17.5IEER | CZ05 | OfS | 2003 | 135to240 | 12 | 17.5 | 33.6428 | 2164.4613 | 0.29773 | 2319.0696 | 0.34289 | 154.6083 | 0.04516
2272 | MCLU-135to240-OfS-CZ05-2007-17.5IEER | CZ05 | OfS | 2007 | 135to240 | 12 | 17.5 | 33.6348 | 2165.1631 | 0.29775 | 2319.7825 | 0.3429 | 154.6194 | 0.045149
2273 | MCLU-135to240-OfS-CZ05-2011-17.5IEER | CZ05 | OfS | 2011 | 135to240 | 12 | 17.5 | 33.5281 | 2183.2812 | 0.30893 | 2301.7297 | 0.34052 | 118.4485 | 0.03159
2274 | MCLU-135to240-OfS-CZ05-2015-17.5IEER | CZ05 | OfS | 2015 | 135to240 | 12 | 17.5 | 27.1741 | 2619.5035 | 0.36201 | 2735.5588 | 0.39372 | 116.0554 | 0.031712
2275 | MCLU-135to240-OfS-CZ05-2020-17.5IEER | CZ05 | OfS | 2020 | 135to240 | 12 | 17.5 | 26.3972 | 2430.2813 | 0.32823 | 2583.4813 | 0.37314 | 153.2 | 0.044917
2276 | MCLU-135to240-RFF-CZ05-2003-17.5IEER | CZ05 | RFF | 2003 | 135to240 | 12 | 17.5 | 7.3498 | 5073.8102 | 0.88127 | 5338.7065 | 0.98355 | 264.8963 | 0.10228
2277 | MCLU-135to240-RFF-CZ05-2007-17.5IEER | CZ05 | RFF | 2007 | 135to240 | 12 | 17.5 | 7.2743 | 5125.7194 | 0.89004 | 5393.6263 | 0.99348 | 267.9069 | 0.10344
2278 | MCLU-135to240-RFF-CZ05-2011-17.5IEER | CZ05 | RFF | 2011 | 135to240 | 12 | 17.5 | 7.2743 | 5171.8364 | 0.92241 | 5393.6263 | 0.99348 | 221.7899 | 0.071071
2279 | MCLU-135to240-RFF-CZ05-2015-17.5IEER | CZ05 | RFF | 2015 | 135to240 | 12 | 17.5 | 6.8118 | 5234.2744 | 0.93148 | 5466.034 | 1.0055 | 231.7597 | 0.074031
2280 | MCLU-135to240-RFF-CZ05-2020-17.5IEER | CZ05 | RFF | 2020 | 135to240 | 12 | 17.5 | 6.2775 | 4892.0463 | 0.85541 | 5168.7093 | 0.96253 | 276.6631 | 0.10712
2281 | MCLU-135to240-RSD-CZ05-2003-17.5IEER | CZ05 | RSD | 2003 | 135to240 | 12 | 17.5 | 13.2695 | 5138.6615 | 0.92202 | 5411.1461 | 1.0353 | 272.4846 | 0.11323
2282 | MCLU-135to240-RSD-CZ05-2007-17.5IEER | CZ05 | RSD | 2007 | 135to240 | 12 | 17.5 | 13.1022 | 5204.8477 | 0.93378 | 5479.6034 | 1.0478 | 274.7557 | 0.11405
2283 | MCLU-135to240-RSD-CZ05-2011-17.5IEER | CZ05 | RSD | 2011 | 135to240 | 12 | 17.5 | 13.1022 | 5259.631 | 0.96627 | 5479.6034 | 1.0478 | 219.9724 | 0.08156
2284 | MCLU-135to240-RSD-CZ05-2015-17.5IEER | CZ05 | RSD | 2015 | 135to240 | 12 | 17.5 | 11.9595 | 5424.1412 | 0.98873 | 5633.373 | 1.0688 | 209.2318 | 0.080055
2285 | MCLU-135to240-RSD-CZ05-2020-17.5IEER | CZ05 | RSD | 2020 | 135to240 | 12 | 17.5 | 10.7027 | 5013.5307 | 0.89456 | 5246.9398 | 0.9982 | 233.409 | 0.10364
2286 | MCLU-135to240-Rt3-CZ05-2003-17.5IEER | CZ05 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 215.6131 | 5980.1526 | 1.0445 | 6183.1112 | 1.1436 | 202.9586 | 0.099053
2287 | MCLU-135to240-Rt3-CZ05-2007-17.5IEER | CZ05 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 215.5601 | 5982.2053 | 1.0446 | 6185.0987 | 1.1437 | 202.8934 | 0.09902
2288 | MCLU-135to240-Rt3-CZ05-2011-17.5IEER | CZ05 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 215.5601 | 6061.1417 | 1.082 | 6185.0987 | 1.1437 | 123.957 | 0.061634
2289 | MCLU-135to240-Rt3-CZ05-2015-17.5IEER | CZ05 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 202.6492 | 5781.455 | 1.0402 | 5914.0099 | 1.1017 | 132.5548 | 0.061526
2290 | MCLU-135to240-Rt3-CZ05-2020-17.5IEER | CZ05 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 192.8015 | 5286.3233 | 0.93864 | 5494.8081 | 1.0362 | 208.4848 | 0.097552
2291 | MCLU-135to240-RtL-CZ05-2003-17.5IEER | CZ05 | RtL | 2003 | 135to240 | 12 | 17.5 | 183.5318 | 6700.7432 | 1.1458 | 6989.4453 | 1.2514 | 288.7021 | 0.10565
2292 | MCLU-135to240-RtL-CZ05-2007-17.5IEER | CZ05 | RtL | 2007 | 135to240 | 12 | 17.5 | 182.3799 | 6747.7899 | 1.1539 | 7037.4519 | 1.2601 | 289.662 | 0.10614
2293 | MCLU-135to240-RtL-CZ05-2011-17.5IEER | CZ05 | RtL | 2011 | 135to240 | 12 | 17.5 | 182.3799 | 6836.0738 | 1.1892 | 7037.4519 | 1.2601 | 201.3781 | 0.070904
2294 | MCLU-135to240-RtL-CZ05-2015-17.5IEER | CZ05 | RtL | 2015 | 135to240 | 12 | 17.5 | 172.945 | 6688.2256 | 1.1816 | 6909.9173 | 1.2561 | 221.6917 | 0.074454
2295 | MCLU-135to240-RtL-CZ05-2020-17.5IEER | CZ05 | RtL | 2020 | 135to240 | 12 | 17.5 | 161.001 | 6402.2848 | 1.1448 | 6721.213 | 1.2563 | 318.9282 | 0.1115
2296 | MCLU-135to240-RtS-CZ05-2003-17.5IEER | CZ05 | RtS | 2003 | 135to240 | 12 | 17.5 | 13.9895 | 3879.7516 | 0.65253 | 4179.8662 | 0.74899 | 300.1146 | 0.096453
2297 | MCLU-135to240-RtS-CZ05-2007-17.5IEER | CZ05 | RtS | 2007 | 135to240 | 12 | 17.5 | 13.9808 | 3883.549 | 0.65286 | 4184.7644 | 0.74936 | 301.2154 | 0.096506
2298 | MCLU-135to240-RtS-CZ05-2011-17.5IEER | CZ05 | RtS | 2011 | 135to240 | 12 | 17.5 | 13.9808 | 3971.2754 | 0.68305 | 4184.7644 | 0.74936 | 213.489 | 0.066313
2299 | MCLU-135to240-RtS-CZ05-2015-17.5IEER | CZ05 | RtS | 2015 | 135to240 | 12 | 17.5 | 12.9214 | 3795.877 | 0.66734 | 3954.3062 | 0.72433 | 158.4292 | 0.056996
2300 | MCLU-135to240-RtS-CZ05-2020-17.5IEER | CZ05 | RtS | 2020 | 135to240 | 12 | 17.5 | 12.5376 | 3484.2562 | 0.60216 | 3686.1651 | 0.68359 | 201.9089 | 0.081429
2301 | MCLU-135to240-SCn-CZ05-2003-17.5IEER | CZ05 | SCn | 2003 | 135to240 | 12 | 17.5 | 318.6951 | 2240.2782 | 0.18481 | 2423.77 | 0.21131 | 183.4918 | 0.026492
2302 | MCLU-135to240-SCn-CZ05-2007-17.5IEER | CZ05 | SCn | 2007 | 135to240 | 12 | 17.5 | 317.0803 | 2247.0029 | 0.18519 | 2430.4194 | 0.2111 | 183.4164 | 0.025902
2303 | MCLU-135to240-SCn-CZ05-2011-17.5IEER | CZ05 | SCn | 2011 | 135to240 | 12 | 17.5 | 317.0803 | 2256.6344 | 0.18727 | 2430.4194 | 0.2111 | 173.785 | 0.023825
2304 | MCLU-135to240-SCn-CZ05-2015-17.5IEER | CZ05 | SCn | 2015 | 135to240 | 12 | 17.5 | 316.6376 | 2242.7785 | 0.18657 | 2415.2648 | 0.20987 | 172.4864 | 0.023295
2305 | MCLU-135to240-SCn-CZ05-2020-17.5IEER | CZ05 | SCn | 2020 | 135to240 | 12 | 17.5 | 313.1034 | 1950.0995 | 0.15336 | 2083.5862 | 0.16336 | 133.4867 | 0.010002
2306 | MCLU-135to240-WRf-CZ05-2003-17.5IEER | CZ05 | WRf | 2003 | 135to240 | 12 | 17.5 | 11.5225 | 323544.9205 | 39.2878 | 323875.3819 | 39.3316 | 330.4614 | 0.043808
2307 | MCLU-135to240-WRf-CZ05-2007-17.5IEER | CZ05 | WRf | 2007 | 135to240 | 12 | 17.5 | 11.3384 | 318538.1444 | 38.1929 | 318874.7818 | 38.237 | 336.6374 | 0.044108
2308 | MCLU-135to240-WRf-CZ05-2011-17.5IEER | CZ05 | WRf | 2011 | 135to240 | 12 | 17.5 | 10.7924 | 327971.159 | 39.1507 | 328335.4438 | 39.1953 | 364.2848 | 0.044646
2309 | MCLU-135to240-WRf-CZ05-2015-17.5IEER | CZ05 | WRf | 2015 | 135to240 | 12 | 17.5 | 10.1357 | 348633.9229 | 41.6707 | 348856.2458 | 41.7145 | 222.3229 | 0.043789
2310 | MCLU-135to240-WRf-CZ05-2020-17.5IEER | CZ05 | WRf | 2020 | 135to240 | 12 | 17.5 | 9.3229 | 355651.0724 | 42.5685 | 355867.693 | 42.6113 | 216.6206 | 0.04275
2311 | MCLU-135to240-Asm-CZ06-2003-17.5IEER | CZ06 | Asm | 2003 | 135to240 | 12 | 17.5 | 383.7436 | 1823.9204 | 0.52268 | 2163.6473 | 0.68772 | 339.7269 | 0.16505
2312 | MCLU-135to240-Asm-CZ06-2007-17.5IEER | CZ06 | Asm | 2007 | 135to240 | 12 | 17.5 | 383.7436 | 1823.9204 | 0.52268 | 2163.6473 | 0.68772 | 339.7269 | 0.16505
2313 | MCLU-135to240-Asm-CZ06-2011-17.5IEER | CZ06 | Asm | 2011 | 135to240 | 12 | 17.5 | 383.7436 | 1904.3058 | 0.57122 | 2163.6473 | 0.68772 | 259.3415 | 0.1165
2314 | MCLU-135to240-Asm-CZ06-2015-17.5IEER | CZ06 | Asm | 2015 | 135to240 | 12 | 17.5 | 334.5387 | 2060.0687 | 0.6237 | 2319.443 | 0.74137 | 259.3743 | 0.11767
2315 | MCLU-135to240-Asm-CZ06-2020-17.5IEER | CZ06 | Asm | 2020 | 135to240 | 12 | 17.5 | 317.4399 | 1898.472 | 0.56849 | 2230.2726 | 0.73529 | 331.8006 | 0.1668
2316 | MCLU-135to240-ECC-CZ06-2003-17.5IEER | CZ06 | ECC | 2003 | 135to240 | 12 | 17.5 | 907.8463 | 2206.2269 | 0.61169 | 2447.0102 | 0.78074 | 240.7833 | 0.16905
2317 | MCLU-135to240-ECC-CZ06-2007-17.5IEER | CZ06 | ECC | 2007 | 135to240 | 12 | 17.5 | 907.8463 | 2206.2269 | 0.61169 | 2447.0102 | 0.78074 | 240.7833 | 0.16905
2318 | MCLU-135to240-ECC-CZ06-2011-17.5IEER | CZ06 | ECC | 2011 | 135to240 | 12 | 17.5 | 907.7332 | 2277.1111 | 0.66053 | 2445.561 | 0.78042 | 168.4499 | 0.11989
2319 | MCLU-135to240-ECC-CZ06-2015-17.5IEER | CZ06 | ECC | 2015 | 135to240 | 12 | 17.5 | 805.349 | 2522.0438 | 0.72138 | 2692.8447 | 0.84399 | 170.8009 | 0.12261
2320 | MCLU-135to240-ECC-CZ06-2020-17.5IEER | CZ06 | ECC | 2020 | 135to240 | 12 | 17.5 | 761.6468 | 2170.4992 | 0.63383 | 2415.0924 | 0.80547 | 244.5932 | 0.17164
2321 | MCLU-135to240-EPr-CZ06-2003-17.5IEER | CZ06 | EPr | 2003 | 135to240 | 12 | 17.5 | 143.1541 | 1528.5229 | 0.32941 | 1675.3796 | 0.41983 | 146.8567 | 0.090417
2322 | MCLU-135to240-EPr-CZ06-2007-17.5IEER | CZ06 | EPr | 2007 | 135to240 | 12 | 17.5 | 143.1541 | 1528.5229 | 0.32941 | 1675.3796 | 0.41983 | 146.8567 | 0.090417
2323 | MCLU-135to240-EPr-CZ06-2011-17.5IEER | CZ06 | EPr | 2011 | 135to240 | 12 | 17.5 | 143.1541 | 1570.7158 | 0.3549 | 1675.3796 | 0.41983 | 104.6638 | 0.064928
2324 | MCLU-135to240-EPr-CZ06-2015-17.5IEER | CZ06 | EPr | 2015 | 135to240 | 12 | 17.5 | 126.2469 | 1728.8151 | 0.38365 | 1840.0785 | 0.4492 | 111.2634 | 0.065547
2325 | MCLU-135to240-EPr-CZ06-2020-17.5IEER | CZ06 | EPr | 2020 | 135to240 | 12 | 17.5 | 119.6389 | 1502.9115 | 0.32724 | 1652.9152 | 0.41661 | 150.0037 | 0.08937
2326 | MCLU-135to240-ERC-CZ06-2003-17.5IEER | CZ06 | ERC | 2003 | 135to240 | 12 | 17.5 | 6.1962 | 1326.5438 | 0.21645 | 1492.7178 | 0.24807 | 166.174 | 0.031627
2327 | MCLU-135to240-ERC-CZ06-2007-17.5IEER | CZ06 | ERC | 2007 | 135to240 | 12 | 17.5 | 6.1965 | 1326.4458 | 0.21642 | 1492.5795 | 0.24803 | 166.1336 | 0.031612
2328 | MCLU-135to240-ERC-CZ06-2011-17.5IEER | CZ06 | ERC | 2011 | 135to240 | 12 | 17.5 | 6.1965 | 1384.3411 | 0.23028 | 1492.5795 | 0.24803 | 108.2384 | 0.017744
2329 | MCLU-135to240-ERC-CZ06-2015-17.5IEER | CZ06 | ERC | 2015 | 135to240 | 12 | 17.5 | 5.82 | 1397.5311 | 0.22435 | 1489.1908 | 0.2403 | 91.6597 | 0.01595
2330 | MCLU-135to240-ERC-CZ06-2020-17.5IEER | CZ06 | ERC | 2020 | 135to240 | 12 | 17.5 | 5.5987 | 1189.6586 | 0.18573 | 1324.03 | 0.21105 | 134.3714 | 0.025324
2331 | MCLU-135to240-ESe-CZ06-2003-17.5IEER | CZ06 | ESe | 2003 | 135to240 | 12 | 17.5 | 471.416 | 1561.7723 | 0.28413 | 1730.8545 | 0.37534 | 169.0822 | 0.091209
2332 | MCLU-135to240-ESe-CZ06-2007-17.5IEER | CZ06 | ESe | 2007 | 135to240 | 12 | 17.5 | 471.416 | 1561.7723 | 0.28413 | 1730.8545 | 0.37534 | 169.0822 | 0.091209
2333 | MCLU-135to240-ESe-CZ06-2011-17.5IEER | CZ06 | ESe | 2011 | 135to240 | 12 | 17.5 | 471.3782 | 1611.695 | 0.31043 | 1730.0932 | 0.3753 | 118.3981 | 0.064871
2334 | MCLU-135to240-ESe-CZ06-2015-17.5IEER | CZ06 | ESe | 2015 | 135to240 | 12 | 17.5 | 403.3384 | 1793.6903 | 0.33054 | 1909.6859 | 0.39725 | 115.9955 | 0.066711
2335 | MCLU-135to240-ESe-CZ06-2020-17.5IEER | CZ06 | ESe | 2020 | 135to240 | 12 | 17.5 | 380.5481 | 1542.6663 | 0.29332 | 1704.9708 | 0.3864 | 162.3045 | 0.093082
2336 | MCLU-135to240-EUn-CZ06-2003-17.5IEER | CZ06 | EUn | 2003 | 135to240 | 12 | 17.5 | 2688.267 | 2356.1379 | 0.744 | 2607.3101 | 0.89631 | 251.1723 | 0.15231
2337 | MCLU-135to240-EUn-CZ06-2007-17.5IEER | CZ06 | EUn | 2007 | 135to240 | 12 | 17.5 | 2688.267 | 2344.1043 | 0.73693 | 2595.2515 | 0.88921 | 251.1473 | 0.15228
2338 | MCLU-135to240-EUn-CZ06-2011-17.5IEER | CZ06 | EUn | 2011 | 135to240 | 12 | 17.5 | 2673.075 | 2422.3193 | 0.78374 | 2604.7514 | 0.89173 | 182.4321 | 0.10799
2339 | MCLU-135to240-EUn-CZ06-2015-17.5IEER | CZ06 | EUn | 2015 | 135to240 | 12 | 17.5 | 2339.0802 | 2693.3796 | 0.86064 | 2874.7279 | 0.9697 | 181.3483 | 0.10906
2340 | MCLU-135to240-EUn-CZ06-2020-17.5IEER | CZ06 | EUn | 2020 | 135to240 | 12 | 17.5 | 2219.6215 | 2401.3944 | 0.77274 | 2650.2953 | 0.92646 | 248.901 | 0.15373
2341 | MCLU-135to240-Gro-CZ06-2003-17.5IEER | CZ06 | Gro | 2003 | 135to240 | 12 | 17.5 | 118.8842 | 13970.4005 | 2.0165 | 14385.7944 | 2.1261 | 415.3939 | 0.10959
2342 | MCLU-135to240-Gro-CZ06-2007-17.5IEER | CZ06 | Gro | 2007 | 135to240 | 12 | 17.5 | 118.8842 | 12797.1891 | 1.9086 | 13173.082 | 2.0283 | 375.8928 | 0.11967
2343 | MCLU-135to240-Gro-CZ06-2011-17.5IEER | CZ06 | Gro | 2011 | 135to240 | 12 | 17.5 | 118.8842 | 12797.1891 | 1.9086 | 13173.082 | 2.0283 | 375.8928 | 0.11967
2344 | MCLU-135to240-Gro-CZ06-2015-17.5IEER | CZ06 | Gro | 2015 | 135to240 | 12 | 17.5 | 112.8272 | 12916.4953 | 1.9206 | 13285.913 | 2.0343 | 369.4177 | 0.11378
2345 | MCLU-135to240-Gro-CZ06-2020-17.5IEER | CZ06 | Gro | 2020 | 135to240 | 12 | 17.5 | 106.4016 | 13275.4291 | 1.9665 | 13634.1651 | 2.076 | 358.736 | 0.10949
2346 | MCLU-135to240-Hsp-CZ06-2003-17.5IEER | CZ06 | Hsp | 2003 | 135to240 | 12 | 17.5 | 683.7961 | 4148.7201 | 0.70197 | 4581.6285 | 0.86001 | 432.9084 | 0.15804
2347 | MCLU-135to240-Hsp-CZ06-2007-17.5IEER | CZ06 | Hsp | 2007 | 135to240 | 12 | 17.5 | 683.7961 | 4148.7201 | 0.70197 | 4581.6285 | 0.86001 | 432.9084 | 0.15804
2348 | MCLU-135to240-Hsp-CZ06-2011-17.5IEER | CZ06 | Hsp | 2011 | 135to240 | 12 | 17.5 | 683.7961 | 4233.1348 | 0.74321 | 4581.6285 | 0.86001 | 348.4937 | 0.11681
2349 | MCLU-135to240-Hsp-CZ06-2015-17.5IEER | CZ06 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 4195.157 | 0.72792 | 4542.9496 | 0.84469 | 347.7926 | 0.11677
2350 | MCLU-135to240-Hsp-CZ06-2020-17.5IEER | CZ06 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3597.6313 | 0.61347 | 4018.4758 | 0.76679 | 420.8445 | 0.15332
2351 | MCLU-135to240-Htl-CZ06-2003-17.5IEER | CZ06 | Htl | 2003 | 135to240 | 12 | 17.5 | 280.9949 | 2899.7499 | 0.68638 | 2997.5135 | 0.72849 | 97.7636 | 0.042106
2352 | MCLU-135to240-Htl-CZ06-2007-17.5IEER | CZ06 | Htl | 2007 | 135to240 | 12 | 17.5 | 280.9949 | 2794.5171 | 0.64525 | 2892.3135 | 0.68725 | 97.7964 | 0.041994
2353 | MCLU-135to240-Htl-CZ06-2011-17.5IEER | CZ06 | Htl | 2011 | 135to240 | 12 | 17.5 | 273.5958 | 2864.5207 | 0.66389 | 2942.6957 | 0.69475 | 78.175 | 0.03086
2354 | MCLU-135to240-Htl-CZ06-2015-17.5IEER | CZ06 | Htl | 2015 | 135to240 | 12 | 17.5 | 236.6265 | 3025.2196 | 0.67528 | 3102.2708 | 0.70657 | 77.0512 | 0.03129
2355 | MCLU-135to240-Htl-CZ06-2020-17.5IEER | CZ06 | Htl | 2020 | 135to240 | 12 | 17.5 | 235.2 | 2900.0216 | 0.64876 | 2994.1803 | 0.69117 | 94.1587 | 0.042415
2356 | MCLU-135to240-MBT-CZ06-2003-17.5IEER | CZ06 | MBT | 2003 | 135to240 | 12 | 17.5 | 376.7514 | 3877.7505 | 0.52428 | 4128.7044 | 0.64278 | 250.9539 | 0.1185
2357 | MCLU-135to240-MBT-CZ06-2007-17.5IEER | CZ06 | MBT | 2007 | 135to240 | 12 | 17.5 | 376.7514 | 3877.7505 | 0.52428 | 4128.7044 | 0.64278 | 250.9539 | 0.1185
2358 | MCLU-135to240-MBT-CZ06-2011-17.5IEER | CZ06 | MBT | 2011 | 135to240 | 12 | 17.5 | 370.3897 | 3968.9507 | 0.55566 | 4142.2121 | 0.64294 | 173.2614 | 0.087271
2359 | MCLU-135to240-MBT-CZ06-2015-17.5IEER | CZ06 | MBT | 2015 | 135to240 | 12 | 17.5 | 342.9677 | 4214.3386 | 0.58083 | 4387.1423 | 0.66871 | 172.8038 | 0.087889
2360 | MCLU-135to240-MBT-CZ06-2020-17.5IEER | CZ06 | MBT | 2020 | 135to240 | 12 | 17.5 | 311.2862 | 4083.5464 | 0.54142 | 4329.6421 | 0.65891 | 246.0958 | 0.11749
2361 | MCLU-135to240-MLI-CZ06-2003-17.5IEER | CZ06 | MLI | 2003 | 135to240 | 12 | 17.5 | 227.0838 | 2866.992 | 0.38492 | 3085.9502 | 0.47097 | 218.9582 | 0.08605
2362 | MCLU-135to240-MLI-CZ06-2007-17.5IEER | CZ06 | MLI | 2007 | 135to240 | 12 | 17.5 | 227.0838 | 2866.992 | 0.38492 | 3085.9502 | 0.47097 | 218.9582 | 0.08605
2363 | MCLU-135to240-MLI-CZ06-2011-17.5IEER | CZ06 | MLI | 2011 | 135to240 | 12 | 17.5 | 227.0838 | 2909.8001 | 0.40847 | 3085.9502 | 0.47097 | 176.1501 | 0.062502
2364 | MCLU-135to240-MLI-CZ06-2015-17.5IEER | CZ06 | MLI | 2015 | 135to240 | 12 | 17.5 | 223.869 | 2927.5033 | 0.41026 | 3103.8995 | 0.47268 | 176.3962 | 0.062415
2365 | MCLU-135to240-MLI-CZ06-2020-17.5IEER | CZ06 | MLI | 2020 | 135to240 | 12 | 17.5 | 203.4677 | 2648.3432 | 0.36246 | 2860.3473 | 0.44743 | 212.0041 | 0.084975
2366 | MCLU-135to240-Mtl-CZ06-2003-17.5IEER | CZ06 | Mtl | 2003 | 135to240 | 12 | 17.5 | 52.8994 | 2676.9961 | 0.58743 | 2762.1816 | 0.6182 | 85.1855 | 0.030766
2367 | MCLU-135to240-Mtl-CZ06-2007-17.5IEER | CZ06 | Mtl | 2007 | 135to240 | 12 | 17.5 | 52.8994 | 2570.8318 | 0.54794 | 2656.2862 | 0.57866 | 85.4544 | 0.030714
2368 | MCLU-135to240-Mtl-CZ06-2011-17.5IEER | CZ06 | Mtl | 2011 | 135to240 | 12 | 17.5 | 51.3843 | 2649.4835 | 0.56134 | 2716.8396 | 0.5843 | 67.3562 | 0.022965
2369 | MCLU-135to240-Mtl-CZ06-2015-17.5IEER | CZ06 | Mtl | 2015 | 135to240 | 12 | 17.5 | 44.1084 | 2793.0849 | 0.56631 | 2864.9383 | 0.59124 | 71.8535 | 0.024925
2370 | MCLU-135to240-Mtl-CZ06-2020-17.5IEER | CZ06 | Mtl | 2020 | 135to240 | 12 | 17.5 | 43.6379 | 2714.059 | 0.54717 | 2803.4489 | 0.58022 | 89.3898 | 0.033049
2371 | MCLU-135to240-Nrs-CZ06-2003-17.5IEER | CZ06 | Nrs | 2003 | 135to240 | 12 | 17.5 | 188.1175 | 4442.7457 | 0.81926 | 4651.1199 | 0.89691 | 208.3742 | 0.077643
2372 | MCLU-135to240-Nrs-CZ06-2007-17.5IEER | CZ06 | Nrs | 2007 | 135to240 | 12 | 17.5 | 188.1175 | 4347.1965 | 0.79077 | 4555.6986 | 0.86838 | 208.502 | 0.077605
2373 | MCLU-135to240-Nrs-CZ06-2011-17.5IEER | CZ06 | Nrs | 2011 | 135to240 | 12 | 17.5 | 188.1175 | 4387.8869 | 0.81231 | 4555.6986 | 0.86838 | 167.8117 | 0.056068
2374 | MCLU-135to240-Nrs-CZ06-2015-17.5IEER | CZ06 | Nrs | 2015 | 135to240 | 12 | 17.5 | 181.6971 | 4296.8232 | 0.7619 | 4456.2846 | 0.81592 | 159.4614 | 0.054017
2375 | MCLU-135to240-Nrs-CZ06-2020-17.5IEER | CZ06 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.607 | 3886.3757 | 0.68273 | 4077.8855 | 0.7538 | 191.5098 | 0.071073
2376 | MCLU-135to240-OfL-CZ06-2003-17.5IEER | CZ06 | OfL | 2003 | 135to240 | 12 | 17.5 | 549.3413 | 2836.0059 | 0.41972 | 3084.833 | 0.48212 | 248.8271 | 0.0624
2377 | MCLU-135to240-OfL-CZ06-2007-17.5IEER | CZ06 | OfL | 2007 | 135to240 | 12 | 17.5 | 549.3413 | 2836.0059 | 0.41972 | 3084.833 | 0.48212 | 248.8271 | 0.0624
2378 | MCLU-135to240-OfL-CZ06-2011-17.5IEER | CZ06 | OfL | 2011 | 135to240 | 12 | 17.5 | 540.669 | 2921.9396 | 0.43728 | 3094.0589 | 0.48176 | 172.1193 | 0.044482
2379 | MCLU-135to240-OfL-CZ06-2015-17.5IEER | CZ06 | OfL | 2015 | 135to240 | 12 | 17.5 | 508.3345 | 3039.6936 | 0.45323 | 3209.7021 | 0.49756 | 170.0086 | 0.044332
2380 | MCLU-135to240-OfL-CZ06-2020-17.5IEER | CZ06 | OfL | 2020 | 135to240 | 12 | 17.5 | 488.9436 | 2852.4331 | 0.42187 | 3097.0009 | 0.48362 | 244.5678 | 0.061751
2381 | MCLU-135to240-OfS-CZ06-2003-17.5IEER | CZ06 | OfS | 2003 | 135to240 | 12 | 17.5 | 36.211 | 2146.4261 | 0.31672 | 2390.0596 | 0.3785 | 243.6335 | 0.061776
2382 | MCLU-135to240-OfS-CZ06-2007-17.5IEER | CZ06 | OfS | 2007 | 135to240 | 12 | 17.5 | 36.211 | 2146.4261 | 0.31672 | 2390.0596 | 0.3785 | 243.6335 | 0.061776
2383 | MCLU-135to240-OfS-CZ06-2011-17.5IEER | CZ06 | OfS | 2011 | 135to240 | 12 | 17.5 | 36.1058 | 2194.5731 | 0.33193 | 2372.4601 | 0.37627 | 177.887 | 0.044346
2384 | MCLU-135to240-OfS-CZ06-2015-17.5IEER | CZ06 | OfS | 2015 | 135to240 | 12 | 17.5 | 29.3997 | 2600.6745 | 0.38015 | 2776.1557 | 0.42414 | 175.4812 | 0.043988
2385 | MCLU-135to240-OfS-CZ06-2020-17.5IEER | CZ06 | OfS | 2020 | 135to240 | 12 | 17.5 | 28.6007 | 2385.1239 | 0.34283 | 2627.993 | 0.40393 | 242.8691 | 0.061094
2386 | MCLU-135to240-RFF-CZ06-2003-17.5IEER | CZ06 | RFF | 2003 | 135to240 | 12 | 17.5 | 8.5564 | 4665.6684 | 0.94929 | 5050.3774 | 1.1205 | 384.709 | 0.17124
2387 | MCLU-135to240-RFF-CZ06-2007-17.5IEER | CZ06 | RFF | 2007 | 135to240 | 12 | 17.5 | 8.5564 | 4665.6684 | 0.94929 | 5050.3774 | 1.1205 | 384.709 | 0.17124
2388 | MCLU-135to240-RFF-CZ06-2011-17.5IEER | CZ06 | RFF | 2011 | 135to240 | 12 | 17.5 | 8.5564 | 4774.3313 | 1.0049 | 5050.3774 | 1.1205 | 276.0461 | 0.11566
2389 | MCLU-135to240-RFF-CZ06-2015-17.5IEER | CZ06 | RFF | 2015 | 135to240 | 12 | 17.5 | 8.1088 | 4766.1135 | 1.0112 | 5052.2486 | 1.1285 | 286.1351 | 0.11732
2390 | MCLU-135to240-RFF-CZ06-2020-17.5IEER | CZ06 | RFF | 2020 | 135to240 | 12 | 17.5 | 7.484 | 4398.1372 | 0.92367 | 4798.3458 | 1.099 | 400.2085 | 0.17537
2391 | MCLU-135to240-RSD-CZ06-2003-17.5IEER | CZ06 | RSD | 2003 | 135to240 | 12 | 17.5 | 14.8377 | 4893.1317 | 1.02 | 5300.742 | 1.1959 | 407.6104 | 0.17585
2392 | MCLU-135to240-RSD-CZ06-2007-17.5IEER | CZ06 | RSD | 2007 | 135to240 | 12 | 17.5 | 14.8377 | 4893.1317 | 1.02 | 5300.742 | 1.1959 | 407.6104 | 0.17585
2393 | MCLU-135to240-RSD-CZ06-2011-17.5IEER | CZ06 | RSD | 2011 | 135to240 | 12 | 17.5 | 14.8377 | 5005.74 | 1.0734 | 5300.742 | 1.1959 | 295.002 | 0.12242
2394 | MCLU-135to240-RSD-CZ06-2015-17.5IEER | CZ06 | RSD | 2015 | 135to240 | 12 | 17.5 | 13.5943 | 5119.6119 | 1.1062 | 5434.574 | 1.2277 | 314.9621 | 0.12148
2395 | MCLU-135to240-RSD-CZ06-2020-17.5IEER | CZ06 | RSD | 2020 | 135to240 | 12 | 17.5 | 12.1402 | 4706 | 1.0216 | 5102.7683 | 1.195 | 396.7683 | 0.17336
2396 | MCLU-135to240-Rt3-CZ06-2003-17.5IEER | CZ06 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 232.7037 | 5873.8528 | 1.1851 | 6234.6257 | 1.3665 | 360.7729 | 0.18138
2397 | MCLU-135to240-Rt3-CZ06-2007-17.5IEER | CZ06 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 232.7037 | 5873.8528 | 1.1851 | 6234.6257 | 1.3665 | 360.7729 | 0.18138
2398 | MCLU-135to240-Rt3-CZ06-2011-17.5IEER | CZ06 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 232.7037 | 6008.3096 | 1.2363 | 6234.6257 | 1.3665 | 226.3162 | 0.13026
2399 | MCLU-135to240-Rt3-CZ06-2015-17.5IEER | CZ06 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 219.902 | 5726.4475 | 1.2013 | 5953.6675 | 1.3326 | 227.22 | 0.13129
2400 | MCLU-135to240-Rt3-CZ06-2020-17.5IEER | CZ06 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 210.0859 | 5182.0633 | 1.0876 | 5536.0049 | 1.2706 | 353.9416 | 0.18304
2401 | MCLU-135to240-RtL-CZ06-2003-17.5IEER | CZ06 | RtL | 2003 | 135to240 | 12 | 17.5 | 195.142 | 6677.3663 | 1.3313 | 7116.6043 | 1.5005 | 439.238 | 0.16918
2402 | MCLU-135to240-RtL-CZ06-2007-17.5IEER | CZ06 | RtL | 2007 | 135to240 | 12 | 17.5 | 195.142 | 6677.3663 | 1.3313 | 7116.6043 | 1.5005 | 439.238 | 0.16918
2403 | MCLU-135to240-RtL-CZ06-2011-17.5IEER | CZ06 | RtL | 2011 | 135to240 | 12 | 17.5 | 195.142 | 6816.1622 | 1.3747 | 7116.6043 | 1.5005 | 300.4421 | 0.12574
2404 | MCLU-135to240-RtL-CZ06-2015-17.5IEER | CZ06 | RtL | 2015 | 135to240 | 12 | 17.5 | 186.0847 | 6649.3891 | 1.3729 | 6962.0122 | 1.4982 | 312.6231 | 0.12529
2405 | MCLU-135to240-RtL-CZ06-2020-17.5IEER | CZ06 | RtL | 2020 | 135to240 | 12 | 17.5 | 172.1078 | 6369.1432 | 1.3433 | 6825.3143 | 1.5084 | 456.171 | 0.16514
2406 | MCLU-135to240-RtS-CZ06-2003-17.5IEER | CZ06 | RtS | 2003 | 135to240 | 12 | 17.5 | 15.5369 | 3764.3148 | 0.76878 | 4194.3767 | 0.92715 | 430.062 | 0.15837
2407 | MCLU-135to240-RtS-CZ06-2007-17.5IEER | CZ06 | RtS | 2007 | 135to240 | 12 | 17.5 | 15.5369 | 3764.3148 | 0.76878 | 4194.3767 | 0.92715 | 430.062 | 0.15837
2408 | MCLU-135to240-RtS-CZ06-2011-17.5IEER | CZ06 | RtS | 2011 | 135to240 | 12 | 17.5 | 15.5369 | 3895.7874 | 0.81233 | 4194.3767 | 0.92715 | 298.5893 | 0.11482
2409 | MCLU-135to240-RtS-CZ06-2015-17.5IEER | CZ06 | RtS | 2015 | 135to240 | 12 | 17.5 | 14.3505 | 3750.5107 | 0.81343 | 3986.9516 | 0.92911 | 236.441 | 0.11568
2410 | MCLU-135to240-RtS-CZ06-2020-17.5IEER | CZ06 | RtS | 2020 | 135to240 | 12 | 17.5 | 13.7283 | 3449.4887 | 0.73583 | 3778.1924 | 0.89497 | 328.7037 | 0.15914
2411 | MCLU-135to240-SCn-CZ06-2003-17.5IEER | CZ06 | SCn | 2003 | 135to240 | 12 | 17.5 | 320.9938 | 2299.2588 | 0.27634 | 2525.7968 | 0.36341 | 226.5381 | 0.087067
2412 | MCLU-135to240-SCn-CZ06-2007-17.5IEER | CZ06 | SCn | 2007 | 135to240 | 12 | 17.5 | 320.9938 | 2299.2588 | 0.27634 | 2525.7968 | 0.36341 | 226.5381 | 0.087067
2413 | MCLU-135to240-SCn-CZ06-2011-17.5IEER | CZ06 | SCn | 2011 | 135to240 | 12 | 17.5 | 320.9938 | 2327.165 | 0.29929 | 2525.7968 | 0.36341 | 198.6319 | 0.064114
2414 | MCLU-135to240-SCn-CZ06-2015-17.5IEER | CZ06 | SCn | 2015 | 135to240 | 12 | 17.5 | 319.5757 | 2319.3442 | 0.29884 | 2518.5231 | 0.3628 | 199.1788 | 0.063956
2415 | MCLU-135to240-SCn-CZ06-2020-17.5IEER | CZ06 | SCn | 2020 | 135to240 | 12 | 17.5 | 313.7254 | 2020.3829 | 0.24204 | 2226.1728 | 0.32227 | 205.79 | 0.080234
2416 | MCLU-135to240-WRf-CZ06-2003-17.5IEER | CZ06 | WRf | 2003 | 135to240 | 12 | 17.5 | 14.7832 | 270630.0421 | 35.4661 | 270975.5547 | 35.52 | 345.5126 | 0.053898
2417 | MCLU-135to240-WRf-CZ06-2007-17.5IEER | CZ06 | WRf | 2007 | 135to240 | 12 | 17.5 | 14.7832 | 263699.9287 | 33.7673 | 264045.5071 | 33.8212 | 345.5784 | 0.05383
2418 | MCLU-135to240-WRf-CZ06-2011-17.5IEER | CZ06 | WRf | 2011 | 135to240 | 12 | 17.5 | 14.4848 | 263366.2933 | 33.7329 | 263718.477 | 33.7863 | 352.1837 | 0.05337
2419 | MCLU-135to240-WRf-CZ06-2015-17.5IEER | CZ06 | WRf | 2015 | 135to240 | 12 | 17.5 | 13.753 | 277101.9847 | 35.5135 | 277352.994 | 35.5655 | 251.0094 | 0.052001
2420 | MCLU-135to240-WRf-CZ06-2020-17.5IEER | CZ06 | WRf | 2020 | 135to240 | 12 | 17.5 | 12.4436 | 277842.4686 | 34.4225 | 278096.3074 | 34.4686 | 253.8388 | 0.046039
2421 | MCLU-135to240-Asm-CZ07-2003-17.5IEER | CZ07 | Asm | 2003 | 135to240 | 12 | 17.5 | 373.0817 | 1818.674 | 0.45427 | 2117.6378 | 0.59901 | 298.9638 | 0.14474
2422 | MCLU-135to240-Asm-CZ07-2007-17.5IEER | CZ07 | Asm | 2007 | 135to240 | 12 | 17.5 | 373.0817 | 1818.674 | 0.45427 | 2117.6378 | 0.59901 | 298.9638 | 0.14474
2423 | MCLU-135to240-Asm-CZ07-2011-17.5IEER | CZ07 | Asm | 2011 | 135to240 | 12 | 17.5 | 368.8342 | 1900.1725 | 0.50194 | 2133.8716 | 0.6045 | 233.6991 | 0.10256
2424 | MCLU-135to240-Asm-CZ07-2015-17.5IEER | CZ07 | Asm | 2015 | 135to240 | 12 | 17.5 | 321.5465 | 2054.681 | 0.54549 | 2283.7187 | 0.64787 | 229.0376 | 0.10238
2425 | MCLU-135to240-Asm-CZ07-2020-17.5IEER | CZ07 | Asm | 2020 | 135to240 | 12 | 17.5 | 308.0252 | 1884.7677 | 0.48399 | 2172.7936 | 0.62992 | 288.0259 | 0.14593
2426 | MCLU-135to240-ECC-CZ07-2003-17.5IEER | CZ07 | ECC | 2003 | 135to240 | 12 | 17.5 | 898.0293 | 2201.6831 | 0.56382 | 2406.9852 | 0.71412 | 205.3021 | 0.1503
2427 | MCLU-135to240-ECC-CZ07-2007-17.5IEER | CZ07 | ECC | 2007 | 135to240 | 12 | 17.5 | 898.0293 | 2201.6831 | 0.56382 | 2406.9852 | 0.71412 | 205.3021 | 0.1503
2428 | MCLU-135to240-ECC-CZ07-2011-17.5IEER | CZ07 | ECC | 2011 | 135to240 | 12 | 17.5 | 897.353 | 2267.3224 | 0.60746 | 2406.3203 | 0.71308 | 138.9979 | 0.10562
2429 | MCLU-135to240-ECC-CZ07-2015-17.5IEER | CZ07 | ECC | 2015 | 135to240 | 12 | 17.5 | 796.9751 | 2513.8497 | 0.66776 | 2656.005 | 0.77449 | 142.1553 | 0.10673
2430 | MCLU-135to240-ECC-CZ07-2020-17.5IEER | CZ07 | ECC | 2020 | 135to240 | 12 | 17.5 | 753.2452 | 2162.7033 | 0.58178 | 2374.8891 | 0.73376 | 212.1857 | 0.15199
2431 | MCLU-135to240-EPr-CZ07-2003-17.5IEER | CZ07 | EPr | 2003 | 135to240 | 12 | 17.5 | 140.8699 | 1508.3305 | 0.29535 | 1638.1115 | 0.37105 | 129.781 | 0.075703
2432 | MCLU-135to240-EPr-CZ07-2007-17.5IEER | CZ07 | EPr | 2007 | 135to240 | 12 | 17.5 | 140.8699 | 1508.3305 | 0.29535 | 1638.1115 | 0.37105 | 129.781 | 0.075703
2433 | MCLU-135to240-EPr-CZ07-2011-17.5IEER | CZ07 | EPr | 2011 | 135to240 | 12 | 17.5 | 140.4499 | 1549.8006 | 0.31714 | 1642.1397 | 0.37076 | 92.3391 | 0.05362
2434 | MCLU-135to240-EPr-CZ07-2015-17.5IEER | CZ07 | EPr | 2015 | 135to240 | 12 | 17.5 | 123.9448 | 1706.5654 | 0.34256 | 1807.5116 | 0.39721 | 100.9462 | 0.054651
2435 | MCLU-135to240-EPr-CZ07-2020-17.5IEER | CZ07 | EPr | 2020 | 135to240 | 12 | 17.5 | 117.6096 | 1477.6042 | 0.28806 | 1613.7639 | 0.36276 | 136.1597 | 0.0747
2436 | MCLU-135to240-ERC-CZ07-2003-17.5IEER | CZ07 | ERC | 2003 | 135to240 | 12 | 17.5 | 5.9711 | 1349.9893 | 0.19811 | 1509.9667 | 0.2192 | 159.9774 | 0.021089
2437 | MCLU-135to240-ERC-CZ07-2007-17.5IEER | CZ07 | ERC | 2007 | 135to240 | 12 | 17.5 | 5.9714 | 1349.8797 | 0.19808 | 1509.8472 | 0.21916 | 159.9675 | 0.021075
2438 | MCLU-135to240-ERC-CZ07-2011-17.5IEER | CZ07 | ERC | 2011 | 135to240 | 12 | 17.5 | 5.9666 | 1408.2059 | 0.20658 | 1511.1641 | 0.21899 | 102.9582 | 0.012419
2439 | MCLU-135to240-ERC-CZ07-2015-17.5IEER | CZ07 | ERC | 2015 | 135to240 | 12 | 17.5 | 5.5952 | 1410.7843 | 0.20645 | 1489.4656 | 0.21704 | 78.6813 | 0.010591
2440 | MCLU-135to240-ERC-CZ07-2020-17.5IEER | CZ07 | ERC | 2020 | 135to240 | 12 | 17.5 | 5.3784 | 1201.2817 | 0.17155 | 1318.3422 | 0.18613 | 117.0605 | 0.014584
2441 | MCLU-135to240-ESe-CZ07-2003-17.5IEER | CZ07 | ESe | 2003 | 135to240 | 12 | 17.5 | 464.9847 | 1562.5289 | 0.25825 | 1709.9285 | 0.33726 | 147.3997 | 0.079012
2442 | MCLU-135to240-ESe-CZ07-2007-17.5IEER | CZ07 | ESe | 2007 | 135to240 | 12 | 17.5 | 464.9847 | 1562.5289 | 0.25825 | 1709.9285 | 0.33726 | 147.3997 | 0.079012
2443 | MCLU-135to240-ESe-CZ07-2011-17.5IEER | CZ07 | ESe | 2011 | 135to240 | 12 | 17.5 | 463.8007 | 1612.648 | 0.28161 | 1712.7974 | 0.33742 | 100.1494 | 0.055819
2444 | MCLU-135to240-ESe-CZ07-2015-17.5IEER | CZ07 | ESe | 2015 | 135to240 | 12 | 17.5 | 395.7519 | 1803.4749 | 0.30317 | 1902.3586 | 0.35939 | 98.8837 | 0.056221
2445 | MCLU-135to240-ESe-CZ07-2020-17.5IEER | CZ07 | ESe | 2020 | 135to240 | 12 | 17.5 | 373.8582 | 1548.9597 | 0.26704 | 1692.4375 | 0.34668 | 143.4778 | 0.07964
2446 | MCLU-135to240-EUn-CZ07-2003-17.5IEER | CZ07 | EUn | 2003 | 135to240 | 12 | 17.5 | 2642.8897 | 2342.5703 | 0.68402 | 2557.6882 | 0.82296 | 215.1178 | 0.13894
2447 | MCLU-135to240-EUn-CZ07-2007-17.5IEER | CZ07 | EUn | 2007 | 135to240 | 12 | 17.5 | 2642.8897 | 2331.6241 | 0.67832 | 2546.7321 | 0.81724 | 215.1079 | 0.13891
2448 | MCLU-135to240-EUn-CZ07-2011-17.5IEER | CZ07 | EUn | 2011 | 135to240 | 12 | 17.5 | 2621.9162 | 2411.6499 | 0.72315 | 2564.4032 | 0.82143 | 152.7533 | 0.098287
2449 | MCLU-135to240-EUn-CZ07-2015-17.5IEER | CZ07 | EUn | 2015 | 135to240 | 12 | 17.5 | 2298.4284 | 2684.8839 | 0.79881 | 2836.4649 | 0.89775 | 151.581 | 0.098941
2450 | MCLU-135to240-EUn-CZ07-2020-17.5IEER | CZ07 | EUn | 2020 | 135to240 | 12 | 17.5 | 2186.3237 | 2389.7835 | 0.70971 | 2603.308 | 0.84964 | 213.5245 | 0.13993
2451 | MCLU-135to240-Gro-CZ07-2003-17.5IEER | CZ07 | Gro | 2003 | 135to240 | 12 | 17.5 | 88.0018 | 18811.5297 | 2.6007 | 19331.483 | 2.7306 | 519.9533 | 0.12994
2452 | MCLU-135to240-Gro-CZ07-2007-17.5IEER | CZ07 | Gro | 2007 | 135to240 | 12 | 17.5 | 88.0018 | 17206.4497 | 2.4472 | 17662.7152 | 2.5926 | 456.2655 | 0.14543
2453 | MCLU-135to240-Gro-CZ07-2011-17.5IEER | CZ07 | Gro | 2011 | 135to240 | 12 | 17.5 | 87.0093 | 17399.6148 | 2.4733 | 17855.6701 | 2.6197 | 456.0553 | 0.14638
2454 | MCLU-135to240-Gro-CZ07-2015-17.5IEER | CZ07 | Gro | 2015 | 135to240 | 12 | 17.5 | 92.561 | 15675.7052 | 2.2261 | 16074.1147 | 2.3466 | 398.4095 | 0.12052
2455 | MCLU-135to240-Gro-CZ07-2020-17.5IEER | CZ07 | Gro | 2020 | 135to240 | 12 | 17.5 | 76.9144 | 18289.3014 | 2.5963 | 18738.6524 | 2.725 | 449.351 | 0.12872
2456 | MCLU-135to240-Hsp-CZ07-2003-17.5IEER | CZ07 | Hsp | 2003 | 135to240 | 12 | 17.5 | 682.8223 | 4129.3576 | 0.66876 | 4525.1396 | 0.80494 | 395.782 | 0.13619
2457 | MCLU-135to240-Hsp-CZ07-2007-17.5IEER | CZ07 | Hsp | 2007 | 135to240 | 12 | 17.5 | 682.8223 | 4129.3576 | 0.66876 | 4525.1396 | 0.80494 | 395.782 | 0.13619
2458 | MCLU-135to240-Hsp-CZ07-2011-17.5IEER | CZ07 | Hsp | 2011 | 135to240 | 12 | 17.5 | 682.8205 | 4208.5262 | 0.70505 | 4524.6085 | 0.80439 | 316.0823 | 0.099342
2459 | MCLU-135to240-Hsp-CZ07-2015-17.5IEER | CZ07 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 4162.5885 | 0.69255 | 4478.2579 | 0.79205 | 315.6695 | 0.0995
2460 | MCLU-135to240-Hsp-CZ07-2020-17.5IEER | CZ07 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3567.3567 | 0.58547 | 3953.9289 | 0.71632 | 386.5721 | 0.13085
2461 | MCLU-135to240-Htl-CZ07-2003-17.5IEER | CZ07 | Htl | 2003 | 135to240 | 12 | 17.5 | 275.0419 | 2834.5037 | 0.59102 | 2926.4215 | 0.62711 | 91.9178 | 0.036088
2462 | MCLU-135to240-Htl-CZ07-2007-17.5IEER | CZ07 | Htl | 2007 | 135to240 | 12 | 17.5 | 275.0419 | 2732.4322 | 0.55861 | 2824.5368 | 0.59459 | 92.1046 | 0.035983
2463 | MCLU-135to240-Htl-CZ07-2011-17.5IEER | CZ07 | Htl | 2011 | 135to240 | 12 | 17.5 | 268.0454 | 2815.5211 | 0.57667 | 2890.5749 | 0.60317 | 75.0537 | 0.026496
2464 | MCLU-135to240-Htl-CZ07-2015-17.5IEER | CZ07 | Htl | 2015 | 135to240 | 12 | 17.5 | 233.084 | 2969.4758 | 0.58931 | 3046.7476 | 0.61689 | 77.2718 | 0.027571
2465 | MCLU-135to240-Htl-CZ07-2020-17.5IEER | CZ07 | Htl | 2020 | 135to240 | 12 | 17.5 | 231.6947 | 2846.3533 | 0.56475 | 2937.8445 | 0.6017 | 91.4912 | 0.036943
2466 | MCLU-135to240-MBT-CZ07-2003-17.5IEER | CZ07 | MBT | 2003 | 135to240 | 12 | 17.5 | 369.9756 | 3888.3648 | 0.49267 | 4114.0513 | 0.59193 | 225.6865 | 0.09926
2467 | MCLU-135to240-MBT-CZ07-2007-17.5IEER | CZ07 | MBT | 2007 | 135to240 | 12 | 17.5 | 369.9756 | 3888.3648 | 0.49267 | 4114.0513 | 0.59193 | 225.6865 | 0.09926
2468 | MCLU-135to240-MBT-CZ07-2011-17.5IEER | CZ07 | MBT | 2011 | 135to240 | 12 | 17.5 | 360.5115 | 4011.7261 | 0.5236 | 4165.244 | 0.59544 | 153.5178 | 0.07184
2469 | MCLU-135to240-MBT-CZ07-2015-17.5IEER | CZ07 | MBT | 2015 | 135to240 | 12 | 17.5 | 333.9731 | 4258.8046 | 0.54844 | 4412.9636 | 0.62028 | 154.159 | 0.071832
2470 | MCLU-135to240-MBT-CZ07-2020-17.5IEER | CZ07 | MBT | 2020 | 135to240 | 12 | 17.5 | 306.9222 | 4076.559 | 0.50692 | 4300.5208 | 0.60411 | 223.9618 | 0.097197
2471 | MCLU-135to240-MLI-CZ07-2003-17.5IEER | CZ07 | MLI | 2003 | 135to240 | 12 | 17.5 | 214.589 | 2984.8778 | 0.37439 | 3176.5052 | 0.44404 | 191.6274 | 0.069649
2472 | MCLU-135to240-MLI-CZ07-2007-17.5IEER | CZ07 | MLI | 2007 | 135to240 | 12 | 17.5 | 214.589 | 2984.8778 | 0.37439 | 3176.5052 | 0.44404 | 191.6274 | 0.069649
2473 | MCLU-135to240-MLI-CZ07-2011-17.5IEER | CZ07 | MLI | 2011 | 135to240 | 12 | 17.5 | 211.0979 | 3069.2931 | 0.39921 | 3224.2826 | 0.4491 | 154.9895 | 0.049894
2474 | MCLU-135to240-MLI-CZ07-2015-17.5IEER | CZ07 | MLI | 2015 | 135to240 | 12 | 17.5 | 208.0124 | 3088.8362 | 0.40115 | 3244.7485 | 0.45102 | 155.9124 | 0.049874
2475 | MCLU-135to240-MLI-CZ07-2020-17.5IEER | CZ07 | MLI | 2020 | 135to240 | 12 | 17.5 | 192.1136 | 2757.8837 | 0.35014 | 2944.4197 | 0.41768 | 186.5359 | 0.067535
2476 | MCLU-135to240-Mtl-CZ07-2003-17.5IEER | CZ07 | Mtl | 2003 | 135to240 | 12 | 17.5 | 52.0049 | 2655.495 | 0.50552 | 2731.3974 | 0.53183 | 75.9024 | 0.026312
2477 | MCLU-135to240-Mtl-CZ07-2007-17.5IEER | CZ07 | Mtl | 2007 | 135to240 | 12 | 17.5 | 52.0049 | 2551.0817 | 0.47481 | 2627.4136 | 0.50108 | 76.3319 | 0.026275
2478 | MCLU-135to240-Mtl-CZ07-2011-17.5IEER | CZ07 | Mtl | 2011 | 135to240 | 12 | 17.5 | 50.7262 | 2636.7757 | 0.48745 | 2695.8417 | 0.50675 | 59.0659 | 0.0193
2479 | MCLU-135to240-Mtl-CZ07-2015-17.5IEER | CZ07 | Mtl | 2015 | 135to240 | 12 | 17.5 | 43.5482 | 2788.0399 | 0.49864 | 2851.0566 | 0.51948 | 63.0167 | 0.02084
2480 | MCLU-135to240-Mtl-CZ07-2020-17.5IEER | CZ07 | Mtl | 2020 | 135to240 | 12 | 17.5 | 43.4163 | 2696.3976 | 0.48175 | 2775.9989 | 0.50958 | 79.6012 | 0.027826
2481 | MCLU-135to240-Nrs-CZ07-2003-17.5IEER | CZ07 | Nrs | 2003 | 135to240 | 12 | 17.5 | 187.1945 | 4462.3184 | 0.76072 | 4648.7153 | 0.82568 | 186.3969 | 0.064955
2482 | MCLU-135to240-Nrs-CZ07-2007-17.5IEER | CZ07 | Nrs | 2007 | 135to240 | 12 | 17.5 | 187.1945 | 4364.1094 | 0.73659 | 4550.5387 | 0.8015 | 186.4292 | 0.064914
2483 | MCLU-135to240-Nrs-CZ07-2011-17.5IEER | CZ07 | Nrs | 2011 | 135to240 | 12 | 17.5 | 187.1863 | 4400.4095 | 0.75412 | 4551.2835 | 0.80077 | 150.874 | 0.046649
2484 | MCLU-135to240-Nrs-CZ07-2015-17.5IEER | CZ07 | Nrs | 2015 | 135to240 | 12 | 17.5 | 181.6787 | 4282.216 | 0.7122 | 4426.0929 | 0.75645 | 143.8769 | 0.044244
2485 | MCLU-135to240-Nrs-CZ07-2020-17.5IEER | CZ07 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.607 | 3876.0902 | 0.63856 | 4048.5482 | 0.69657 | 172.458 | 0.058004
2486 | MCLU-135to240-OfL-CZ07-2003-17.5IEER | CZ07 | OfL | 2003 | 135to240 | 12 | 17.5 | 537.8125 | 2862.5765 | 0.41241 | 3071.6731 | 0.46876 | 209.0967 | 0.056354
2487 | MCLU-135to240-OfL-CZ07-2007-17.5IEER | CZ07 | OfL | 2007 | 135to240 | 12 | 17.5 | 537.8125 | 2862.5765 | 0.41241 | 3071.6731 | 0.46876 | 209.0967 | 0.056354
2488 | MCLU-135to240-OfL-CZ07-2011-17.5IEER | CZ07 | OfL | 2011 | 135to240 | 12 | 17.5 | 529.3428 | 2942.0257 | 0.42884 | 3080.7736 | 0.46885 | 138.7479 | 0.040009
2489 | MCLU-135to240-OfL-CZ07-2015-17.5IEER | CZ07 | OfL | 2015 | 135to240 | 12 | 17.5 | 496.6136 | 3068.9522 | 0.44673 | 3205.2672 | 0.48647 | 136.315 | 0.039742
2490 | MCLU-135to240-OfL-CZ07-2020-17.5IEER | CZ07 | OfL | 2020 | 135to240 | 12 | 17.5 | 478.1077 | 2883.3845 | 0.41735 | 3087.244 | 0.47338 | 203.8595 | 0.056029
2491 | MCLU-135to240-OfS-CZ07-2003-17.5IEER | CZ07 | OfS | 2003 | 135to240 | 12 | 17.5 | 35.3344 | 2161.7715 | 0.30498 | 2369.049 | 0.35999 | 207.2775 | 0.055002
2492 | MCLU-135to240-OfS-CZ07-2007-17.5IEER | CZ07 | OfS | 2007 | 135to240 | 12 | 17.5 | 35.3344 | 2161.7715 | 0.30498 | 2369.049 | 0.35999 | 207.2775 | 0.055002
2493 | MCLU-135to240-OfS-CZ07-2011-17.5IEER | CZ07 | OfS | 2011 | 135to240 | 12 | 17.5 | 35.2214 | 2202.7053 | 0.31805 | 2351.2776 | 0.35744 | 148.5723 | 0.039388
2494 | MCLU-135to240-OfS-CZ07-2015-17.5IEER | CZ07 | OfS | 2015 | 135to240 | 12 | 17.5 | 28.7107 | 2618.2786 | 0.36901 | 2763.2077 | 0.4084 | 144.9291 | 0.039386
2495 | MCLU-135to240-OfS-CZ07-2020-17.5IEER | CZ07 | OfS | 2020 | 135to240 | 12 | 17.5 | 27.9285 | 2406.5738 | 0.33339 | 2612.317 | 0.38847 | 205.7433 | 0.055084
2496 | MCLU-135to240-RFF-CZ07-2003-17.5IEER | CZ07 | RFF | 2003 | 135to240 | 12 | 17.5 | 8.2758 | 4789.613 | 0.90837 | 5144.5784 | 1.0652 | 354.9654 | 0.15679
2497 | MCLU-135to240-RFF-CZ07-2007-17.5IEER | CZ07 | RFF | 2007 | 135to240 | 12 | 17.5 | 8.2758 | 4789.613 | 0.90837 | 5144.5784 | 1.0652 | 354.9654 | 0.15679
2498 | MCLU-135to240-RFF-CZ07-2011-17.5IEER | CZ07 | RFF | 2011 | 135to240 | 12 | 17.5 | 8.2164 | 4929.2813 | 0.96627 | 5182.1595 | 1.0708 | 252.8782 | 0.10452
2499 | MCLU-135to240-RFF-CZ07-2015-17.5IEER | CZ07 | RFF | 2015 | 135to240 | 12 | 17.5 | 7.7636 | 4929.5623 | 0.97343 | 5195.8829 | 1.0798 | 266.3206 | 0.10635
2500 | MCLU-135to240-RFF-CZ07-2020-17.5IEER | CZ07 | RFF | 2020 | 135to240 | 12 | 17.5 | 7.2502 | 4499.9023 | 0.87472 | 4874.9216 | 1.0351 | 375.0193 | 0.16041
2501 | MCLU-135to240-RSD-CZ07-2003-17.5IEER | CZ07 | RSD | 2003 | 135to240 | 12 | 17.5 | 14.3852 | 5002.0048 | 0.97752 | 5391.1563 | 1.1418 | 389.1515 | 0.16432
2502 | MCLU-135to240-RSD-CZ07-2007-17.5IEER | CZ07 | RSD | 2007 | 135to240 | 12 | 17.5 | 14.3852 | 5002.0048 | 0.97752 | 5391.1563 | 1.1418 | 389.1515 | 0.16432
2503 | MCLU-135to240-RSD-CZ07-2011-17.5IEER | CZ07 | RSD | 2011 | 135to240 | 12 | 17.5 | 14.2134 | 5169.6679 | 1.0388 | 5459.8847 | 1.1532 | 290.2168 | 0.11433
2504 | MCLU-135to240-RSD-CZ07-2015-17.5IEER | CZ07 | RSD | 2015 | 135to240 | 12 | 17.5 | 13.0039 | 5284.0827 | 1.065 | 5582.2798 | 1.1806 | 298.1971 | 0.11559
2505 | MCLU-135to240-RSD-CZ07-2020-17.5IEER | CZ07 | RSD | 2020 | 135to240 | 12 | 17.5 | 11.8119 | 4775.8381 | 0.94912 | 5137.0498 | 1.113 | 361.2117 | 0.16384
2506 | MCLU-135to240-Rt3-CZ07-2003-17.5IEER | CZ07 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 226.595 | 6009.8712 | 1.1483 | 6325.7061 | 1.3114 | 315.8349 | 0.16307
2507 | MCLU-135to240-Rt3-CZ07-2007-17.5IEER | CZ07 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 226.595 | 6009.8712 | 1.1483 | 6325.7061 | 1.3114 | 315.8349 | 0.16307
2508 | MCLU-135to240-Rt3-CZ07-2011-17.5IEER | CZ07 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 226.5343 | 6141.6511 | 1.1973 | 6326.7265 | 1.3104 | 185.0753 | 0.11311
2509 | MCLU-135to240-Rt3-CZ07-2015-17.5IEER | CZ07 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 213.6623 | 5861.9053 | 1.1619 | 6047.0019 | 1.2748 | 185.0966 | 0.11297
2510 | MCLU-135to240-Rt3-CZ07-2020-17.5IEER | CZ07 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 203.913 | 5315.1399 | 1.0501 | 5621.9163 | 1.2124 | 306.7765 | 0.1623
2511 | MCLU-135to240-RtL-CZ07-2003-17.5IEER | CZ07 | RtL | 2003 | 135to240 | 12 | 17.5 | 191.3123 | 6761.5457 | 1.2677 | 7170.9659 | 1.4234 | 409.4202 | 0.15565
2512 | MCLU-135to240-RtL-CZ07-2007-17.5IEER | CZ07 | RtL | 2007 | 135to240 | 12 | 17.5 | 191.3123 | 6761.5457 | 1.2677 | 7170.9659 | 1.4234 | 409.4202 | 0.15565
2513 | MCLU-135to240-RtL-CZ07-2011-17.5IEER | CZ07 | RtL | 2011 | 135to240 | 12 | 17.5 | 190.0981 | 6942.6008 | 1.3188 | 7217.2011 | 1.4299 | 274.6003 | 0.11106
2514 | MCLU-135to240-RtL-CZ07-2015-17.5IEER | CZ07 | RtL | 2015 | 135to240 | 12 | 17.5 | 181.3293 | 6769.1679 | 1.3121 | 7054.9951 | 1.4239 | 285.8272 | 0.11176
2515 | MCLU-135to240-RtL-CZ07-2020-17.5IEER | CZ07 | RtL | 2020 | 135to240 | 12 | 17.5 | 168.6678 | 6452.0283 | 1.2731 | 6880.8056 | 1.4265 | 428.7773 | 0.15335
2516 | MCLU-135to240-RtS-CZ07-2003-17.5IEER | CZ07 | RtS | 2003 | 135to240 | 12 | 17.5 | 15.0239 | 3880.8247 | 0.72457 | 4309.1809 | 0.86009 | 428.3561 | 0.13552
2517 | MCLU-135to240-RtS-CZ07-2007-17.5IEER | CZ07 | RtS | 2007 | 135to240 | 12 | 17.5 | 15.0239 | 3880.8247 | 0.72457 | 4309.1809 | 0.86009 | 428.3561 | 0.13552
2518 | MCLU-135to240-RtS-CZ07-2011-17.5IEER | CZ07 | RtS | 2011 | 135to240 | 12 | 17.5 | 14.8672 | 4058.7265 | 0.77159 | 4350.8486 | 0.86597 | 292.1221 | 0.094388
2519 | MCLU-135to240-RtS-CZ07-2015-17.5IEER | CZ07 | RtS | 2015 | 135to240 | 12 | 17.5 | 13.8033 | 3843.4828 | 0.7653 | 4037.9514 | 0.8597 | 194.4686 | 0.094403
2520 | MCLU-135to240-RtS-CZ07-2020-17.5IEER | CZ07 | RtS | 2020 | 135to240 | 12 | 17.5 | 13.4252 | 3487.7533 | 0.68238 | 3767.7875 | 0.81712 | 280.0342 | 0.13474
2521 | MCLU-135to240-SCn-CZ07-2003-17.5IEER | CZ07 | SCn | 2003 | 135to240 | 12 | 17.5 | 311.0352 | 2341.9092 | 0.25066 | 2556.0543 | 0.30972 | 214.1451 | 0.059059
2522 | MCLU-135to240-SCn-CZ07-2007-17.5IEER | CZ07 | SCn | 2007 | 135to240 | 12 | 17.5 | 311.0352 | 2341.9092 | 0.25066 | 2556.0543 | 0.30972 | 214.1451 | 0.059059
2523 | MCLU-135to240-SCn-CZ07-2011-17.5IEER | CZ07 | SCn | 2011 | 135to240 | 12 | 17.5 | 309.8218 | 2372.4197 | 0.26664 | 2561.8324 | 0.30806 | 189.4127 | 0.041422
2524 | MCLU-135to240-SCn-CZ07-2015-17.5IEER | CZ07 | SCn | 2015 | 135to240 | 12 | 17.5 | 308.5402 | 2359.7196 | 0.26613 | 2545.1387 | 0.30719 | 185.419 | 0.041058
2525 | MCLU-135to240-SCn-CZ07-2020-17.5IEER | CZ07 | SCn | 2020 | 135to240 | 12 | 17.5 | 304.2074 | 2054.8248 | 0.21722 | 2250.8229 | 0.26904 | 195.9982 | 0.051817
2526 | MCLU-135to240-WRf-CZ07-2003-17.5IEER | CZ07 | WRf | 2003 | 135to240 | 12 | 17.5 | 12.7659 | 314803.9921 | 40.0823 | 315183.0909 | 40.1301 | 379.0987 | 0.047757
2527 | MCLU-135to240-WRf-CZ07-2007-17.5IEER | CZ07 | WRf | 2007 | 135to240 | 12 | 17.5 | 12.7659 | 306047.062 | 38.1014 | 306428.0926 | 38.1492 | 381.0307 | 0.04781
2528 | MCLU-135to240-WRf-CZ07-2011-17.5IEER | CZ07 | WRf | 2011 | 135to240 | 12 | 17.5 | 12.3247 | 304193.0863 | 37.8332 | 304585.8349 | 37.8784 | 392.7486 | 0.045216
2529 | MCLU-135to240-WRf-CZ07-2015-17.5IEER | CZ07 | WRf | 2015 | 135to240 | 12 | 17.5 | 11.6483 | 321465.3696 | 40.0175 | 321721.1492 | 40.061 | 255.7796 | 0.043487
2530 | MCLU-135to240-WRf-CZ07-2020-17.5IEER | CZ07 | WRf | 2020 | 135to240 | 12 | 17.5 | 10.66 | 325481.2018 | 39.6127 | 325734.1317 | 39.6531 | 252.9299 | 0.040364
2531 | MCLU-135to240-Asm-CZ08-2003-17.5IEER | CZ08 | Asm | 2003 | 135to240 | 12 | 17.5 | 348.2393 | 2128.0705 | 0.59366 | 2535.5541 | 0.75882 | 407.4836 | 0.16515
2532 | MCLU-135to240-Asm-CZ08-2007-17.5IEER | CZ08 | Asm | 2007 | 135to240 | 12 | 17.5 | 348.2393 | 2128.0705 | 0.59366 | 2535.5541 | 0.75882 | 407.4836 | 0.16515
2533 | MCLU-135to240-Asm-CZ08-2011-17.5IEER | CZ08 | Asm | 2011 | 135to240 | 12 | 17.5 | 345.7387 | 2245.1762 | 0.64671 | 2547.8368 | 0.76272 | 302.6606 | 0.11601
2534 | MCLU-135to240-Asm-CZ08-2015-17.5IEER | CZ08 | Asm | 2015 | 135to240 | 12 | 17.5 | 313.244 | 2348.1908 | 0.67702 | 2643.7063 | 0.79352 | 295.5155 | 0.1165
2535 | MCLU-135to240-Asm-CZ08-2020-17.5IEER | CZ08 | Asm | 2020 | 135to240 | 12 | 17.5 | 302.4059 | 2127.3798 | 0.60808 | 2519.304 | 0.77409 | 391.9243 | 0.16601
2536 | MCLU-135to240-ECC-CZ08-2003-17.5IEER | CZ08 | ECC | 2003 | 135to240 | 12 | 17.5 | 828.4617 | 2502.6424 | 0.68752 | 2796.6543 | 0.85903 | 294.0119 | 0.17151
2537 | MCLU-135to240-ECC-CZ08-2007-17.5IEER | CZ08 | ECC | 2007 | 135to240 | 12 | 17.5 | 828.4617 | 2502.6424 | 0.68752 | 2796.6543 | 0.85903 | 294.0119 | 0.17151
2538 | MCLU-135to240-ECC-CZ08-2011-17.5IEER | CZ08 | ECC | 2011 | 135to240 | 12 | 17.5 | 826.7623 | 2596.7515 | 0.73865 | 2799.0849 | 0.85869 | 202.3334 | 0.12003
2539 | MCLU-135to240-ECC-CZ08-2015-17.5IEER | CZ08 | ECC | 2015 | 135to240 | 12 | 17.5 | 769.6883 | 2731.5156 | 0.76768 | 2934.0828 | 0.8893 | 202.5672 | 0.12162
2540 | MCLU-135to240-ECC-CZ08-2020-17.5IEER | CZ08 | ECC | 2020 | 135to240 | 12 | 17.5 | 737.4397 | 2320.2454 | 0.66633 | 2610.7686 | 0.83975 | 290.5232 | 0.17343
2541 | MCLU-135to240-EPr-CZ08-2003-17.5IEER | CZ08 | EPr | 2003 | 135to240 | 12 | 17.5 | 140.1088 | 1615.5835 | 0.33653 | 1792.4052 | 0.4285 | 176.8217 | 0.091971
2542 | MCLU-135to240-EPr-CZ08-2007-17.5IEER | CZ08 | EPr | 2007 | 135to240 | 12 | 17.5 | 140.1088 | 1615.5835 | 0.33653 | 1792.4052 | 0.4285 | 176.8217 | 0.091971
2543 | MCLU-135to240-EPr-CZ08-2011-17.5IEER | CZ08 | EPr | 2011 | 135to240 | 12 | 17.5 | 138.8209 | 1681.0555 | 0.36575 | 1805.9033 | 0.42992 | 124.8478 | 0.064178
2544 | MCLU-135to240-EPr-CZ08-2015-17.5IEER | CZ08 | EPr | 2015 | 135to240 | 12 | 17.5 | 126.5385 | 1782.1193 | 0.38096 | 1911.4973 | 0.44584 | 129.378 | 0.06488
2545 | MCLU-135to240-EPr-CZ08-2020-17.5IEER | CZ08 | EPr | 2020 | 135to240 | 12 | 17.5 | 119.55 | 1548.7978 | 0.32233 | 1728.9599 | 0.41443 | 180.1621 | 0.092102
2546 | MCLU-135to240-ERC-CZ08-2003-17.5IEER | CZ08 | ERC | 2003 | 135to240 | 12 | 17.5 | 6.1597 | 1381.6436 | 0.22152 | 1569.5237 | 0.25681 | 187.8801 | 0.035286
2547 | MCLU-135to240-ERC-CZ08-2007-17.5IEER | CZ08 | ERC | 2007 | 135to240 | 12 | 17.5 | 6.1601 | 1381.5019 | 0.2215 | 1569.346 | 0.25677 | 187.8441 | 0.035273
2548 | MCLU-135to240-ERC-CZ08-2011-17.5IEER | CZ08 | ERC | 2011 | 135to240 | 12 | 17.5 | 6.1345 | 1450.772 | 0.23686 | 1574.9157 | 0.25708 | 124.1437 | 0.020221
2549 | MCLU-135to240-ERC-CZ08-2015-17.5IEER | CZ08 | ERC | 2015 | 135to240 | 12 | 17.5 | 5.9194 | 1422.352 | 0.23118 | 1524.8111 | 0.24979 | 102.4591 | 0.01861
2550 | MCLU-135to240-ERC-CZ08-2020-17.5IEER | CZ08 | ERC | 2020 | 135to240 | 12 | 17.5 | 5.7162 | 1208.2535 | 0.19044 | 1357.1255 | 0.22031 | 148.8719 | 0.029872
2551 | MCLU-135to240-ESe-CZ08-2003-17.5IEER | CZ08 | ESe | 2003 | 135to240 | 12 | 17.5 | 435.1597 | 1767.5633 | 0.31483 | 1975.3385 | 0.40745 | 207.7752 | 0.092621
2552 | MCLU-135to240-ESe-CZ08-2007-17.5IEER | CZ08 | ESe | 2007 | 135to240 | 12 | 17.5 | 435.1597 | 1767.5633 | 0.31483 | 1975.3385 | 0.40745 | 207.7752 | 0.092621
2553 | MCLU-135to240-ESe-CZ08-2011-17.5IEER | CZ08 | ESe | 2011 | 135to240 | 12 | 17.5 | 433.6243 | 1837.9278 | 0.34367 | 1980.118 | 0.4078 | 142.1902 | 0.064129
2554 | MCLU-135to240-ESe-CZ08-2015-17.5IEER | CZ08 | ESe | 2015 | 135to240 | 12 | 17.5 | 395.6503 | 1903.6697 | 0.34273 | 2040.7306 | 0.40856 | 137.0609 | 0.065825
2555 | MCLU-135to240-ESe-CZ08-2020-17.5IEER | CZ08 | ESe | 2020 | 135to240 | 12 | 17.5 | 378.5705 | 1614.4503 | 0.29911 | 1807.6883 | 0.39332 | 193.2379 | 0.094216
2556 | MCLU-135to240-EUn-CZ08-2003-17.5IEER | CZ08 | EUn | 2003 | 135to240 | 12 | 17.5 | 2455.7822 | 2683.2541 | 0.83419 | 2981.7716 | 0.98523 | 298.5174 | 0.15103
2557 | MCLU-135to240-EUn-CZ08-2007-17.5IEER | CZ08 | EUn | 2007 | 135to240 | 12 | 17.5 | 2455.7822 | 2667.9168 | 0.82623 | 2966.4017 | 0.97724 | 298.4849 | 0.15101
2558 | MCLU-135to240-EUn-CZ08-2011-17.5IEER | CZ08 | EUn | 2011 | 135to240 | 12 | 17.5 | 2427.1301 | 2780.3514 | 0.87851 | 2992.1047 | 0.98403 | 211.7533 | 0.10553
2559 | MCLU-135to240-EUn-CZ08-2015-17.5IEER | CZ08 | EUn | 2015 | 135to240 | 12 | 17.5 | 2204.8675 | 2965.8358 | 0.92875 | 3178.9135 | 1.0355 | 213.0778 | 0.10679
2560 | MCLU-135to240-EUn-CZ08-2020-17.5IEER | CZ08 | EUn | 2020 | 135to240 | 12 | 17.5 | 2100.9026 | 2631.6732 | 0.83333 | 2930.9044 | 0.98715 | 299.2311 | 0.15382
2561 | MCLU-135to240-Gro-CZ08-2003-17.5IEER | CZ08 | Gro | 2003 | 135to240 | 12 | 17.5 | 125.086 | 13388.5608 | 1.9281 | 13795.7401 | 2.0332 | 407.1793 | 0.10513
2562 | MCLU-135to240-Gro-CZ08-2007-17.5IEER | CZ08 | Gro | 2007 | 135to240 | 12 | 17.5 | 125.086 | 12264.656 | 1.8297 | 12640.6721 | 1.9401 | 376.0161 | 0.11044
2563 | MCLU-135to240-Gro-CZ08-2011-17.5IEER | CZ08 | Gro | 2011 | 135to240 | 12 | 17.5 | 117.091 | 13090.6672 | 1.9536 | 13468.0091 | 2.0626 | 377.3419 | 0.10892
2564 | MCLU-135to240-Gro-CZ08-2015-17.5IEER | CZ08 | Gro | 2015 | 135to240 | 12 | 17.5 | 110.9903 | 13223.3339 | 1.9649 | 13596.0928 | 2.0693 | 372.7589 | 0.10438
2565 | MCLU-135to240-Gro-CZ08-2020-17.5IEER | CZ08 | Gro | 2020 | 135to240 | 12 | 17.5 | 105.4126 | 13488.3874 | 1.9957 | 13856.114 | 2.0999 | 367.7265 | 0.10421
2566 | MCLU-135to240-Hsp-CZ08-2003-17.5IEER | CZ08 | Hsp | 2003 | 135to240 | 12 | 17.5 | 685.4619 | 4216.2087 | 0.70836 | 4692.9449 | 0.86062 | 476.7362 | 0.15226
2567 | MCLU-135to240-Hsp-CZ08-2007-17.5IEER | CZ08 | Hsp | 2007 | 135to240 | 12 | 17.5 | 685.4619 | 4216.2087 | 0.70836 | 4692.9449 | 0.86062 | 476.7362 | 0.15226
2568 | MCLU-135to240-Hsp-CZ08-2011-17.5IEER | CZ08 | Hsp | 2011 | 135to240 | 12 | 17.5 | 685.4589 | 4315.7118 | 0.74968 | 4692.0449 | 0.85988 | 376.3331 | 0.11021
2569 | MCLU-135to240-Hsp-CZ08-2015-17.5IEER | CZ08 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 4283.8852 | 0.73677 | 4658.9133 | 0.84707 | 375.028 | 0.1103
2570 | MCLU-135to240-Hsp-CZ08-2020-17.5IEER | CZ08 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3666.0892 | 0.62144 | 4128.4166 | 0.76988 | 462.3274 | 0.14844
2571 | MCLU-135to240-Htl-CZ08-2003-17.5IEER | CZ08 | Htl | 2003 | 135to240 | 12 | 17.5 | 253.927 | 3314.0847 | 0.75891 | 3432.7374 | 0.79944 | 118.6528 | 0.040532
2572 | MCLU-135to240-Htl-CZ08-2007-17.5IEER | CZ08 | Htl | 2007 | 135to240 | 12 | 17.5 | 253.927 | 3184.9245 | 0.713 | 3303.4219 | 0.75348 | 118.4974 | 0.040479
2573 | MCLU-135to240-Htl-CZ08-2011-17.5IEER | CZ08 | Htl | 2011 | 135to240 | 12 | 17.5 | 245.4511 | 3288.6118 | 0.73636 | 3382.3325 | 0.76539 | 93.7206 | 0.029034
2574 | MCLU-135to240-Htl-CZ08-2015-17.5IEER | CZ08 | Htl | 2015 | 135to240 | 12 | 17.5 | 210.9117 | 3490.6016 | 0.75559 | 3590.0623 | 0.78644 | 99.4607 | 0.030849
2575 | MCLU-135to240-Htl-CZ08-2020-17.5IEER | CZ08 | Htl | 2020 | 135to240 | 12 | 17.5 | 208.9003 | 3354.2571 | 0.72958 | 3478.8711 | 0.7727 | 124.6141 | 0.043121
2576 | MCLU-135to240-MBT-CZ08-2003-17.5IEER | CZ08 | MBT | 2003 | 135to240 | 12 | 17.5 | 375.1964 | 3943.4286 | 0.53002 | 4228.6317 | 0.64832 | 285.2031 | 0.11829
2577 | MCLU-135to240-MBT-CZ08-2007-17.5IEER | CZ08 | MBT | 2007 | 135to240 | 12 | 17.5 | 375.1964 | 3943.4286 | 0.53002 | 4228.6317 | 0.64832 | 285.2031 | 0.11829
2578 | MCLU-135to240-MBT-CZ08-2011-17.5IEER | CZ08 | MBT | 2011 | 135to240 | 12 | 17.5 | 358.3028 | 4164.4828 | 0.5743 | 4361.0534 | 0.65882 | 196.5707 | 0.084517
2579 | MCLU-135to240-MBT-CZ08-2015-17.5IEER | CZ08 | MBT | 2015 | 135to240 | 12 | 17.5 | 333.9802 | 4386.6587 | 0.5956 | 4582.2084 | 0.6812 | 195.5498 | 0.085596
2580 | MCLU-135to240-MBT-CZ08-2020-17.5IEER | CZ08 | MBT | 2020 | 135to240 | 12 | 17.5 | 307.5742 | 4198.1792 | 0.55221 | 4474.5316 | 0.66969 | 276.3524 | 0.11748
2581 | MCLU-135to240-MLI-CZ08-2003-17.5IEER | CZ08 | MLI | 2003 | 135to240 | 12 | 17.5 | 223.6543 | 2984.6237 | 0.40666 | 3229.0875 | 0.49271 | 244.4639 | 0.086048
2582 | MCLU-135to240-MLI-CZ08-2007-17.5IEER | CZ08 | MLI | 2007 | 135to240 | 12 | 17.5 | 223.6543 | 2984.6237 | 0.40666 | 3229.0875 | 0.49271 | 244.4639 | 0.086048
2583 | MCLU-135to240-MLI-CZ08-2011-17.5IEER | CZ08 | MLI | 2011 | 135to240 | 12 | 17.5 | 219.801 | 3089.907 | 0.43782 | 3276.5507 | 0.49789 | 186.6437 | 0.060071
2584 | MCLU-135to240-MLI-CZ08-2015-17.5IEER | CZ08 | MLI | 2015 | 135to240 | 12 | 17.5 | 215.9757 | 3119.055 | 0.44136 | 3305.5063 | 0.50164 | 186.4513 | 0.060279
2585 | MCLU-135to240-MLI-CZ08-2020-17.5IEER | CZ08 | MLI | 2020 | 135to240 | 12 | 17.5 | 198.9678 | 2780.0234 | 0.38643 | 3019.2304 | 0.4726 | 239.207 | 0.086169
2586 | MCLU-135to240-Mtl-CZ08-2003-17.5IEER | CZ08 | Mtl | 2003 | 135to240 | 12 | 17.5 | 45.1022 | 3288.7405 | 0.70401 | 3380.4966 | 0.73104 | 91.7562 | 0.027031
2587 | MCLU-135to240-Mtl-CZ08-2007-17.5IEER | CZ08 | Mtl | 2007 | 135to240 | 12 | 17.5 | 45.1022 | 3147.9461 | 0.65648 | 3239.7168 | 0.68349 | 91.7707 | 0.027009
2588 | MCLU-135to240-Mtl-CZ08-2011-17.5IEER | CZ08 | Mtl | 2011 | 135to240 | 12 | 17.5 | 43.0916 | 3279.2946 | 0.67459 | 3350.7002 | 0.69356 | 71.4056 | 0.018977
2589 | MCLU-135to240-Mtl-CZ08-2015-17.5IEER | CZ08 | Mtl | 2015 | 135to240 | 12 | 17.5 | 36.7987 | 3475.9121 | 0.68918 | 3552.1503 | 0.71012 | 76.2382 | 0.02094
2590 | MCLU-135to240-Mtl-CZ08-2020-17.5IEER | CZ08 | Mtl | 2020 | 135to240 | 12 | 17.5 | 36.6655 | 3365.4368 | 0.66977 | 3463.7161 | 0.69892 | 98.2793 | 0.029143
2591 | MCLU-135to240-Nrs-CZ08-2003-17.5IEER | CZ08 | Nrs | 2003 | 135to240 | 12 | 17.5 | 191.7875 | 4472.3595 | 0.80818 | 4701.817 | 0.88415 | 229.4576 | 0.075968
2592 | MCLU-135to240-Nrs-CZ08-2007-17.5IEER | CZ08 | Nrs | 2007 | 135to240 | 12 | 17.5 | 191.7875 | 4369.929 | 0.77985 | 4599.4839 | 0.85578 | 229.555 | 0.075933
2593 | MCLU-135to240-Nrs-CZ08-2011-17.5IEER | CZ08 | Nrs | 2011 | 135to240 | 12 | 17.5 | 191.7069 | 4418.8718 | 0.80077 | 4600.8737 | 0.85494 | 182.0019 | 0.054173
2594 | MCLU-135to240-Nrs-CZ08-2015-17.5IEER | CZ08 | Nrs | 2015 | 135to240 | 12 | 17.5 | 181.7574 | 4392.5909 | 0.76739 | 4567.6025 | 0.8202 | 175.0116 | 0.052805
2595 | MCLU-135to240-Nrs-CZ08-2020-17.5IEER | CZ08 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.607 | 3972.7211 | 0.68905 | 4186.0869 | 0.75984 | 213.3659 | 0.070787
2596 | MCLU-135to240-OfL-CZ08-2003-17.5IEER | CZ08 | OfL | 2003 | 135to240 | 12 | 17.5 | 476.745 | 3340.7416 | 0.49569 | 3628.6919 | 0.55608 | 287.9503 | 0.060392
2597 | MCLU-135to240-OfL-CZ08-2007-17.5IEER | CZ08 | OfL | 2007 | 135to240 | 12 | 17.5 | 476.745 | 3340.7416 | 0.49569 | 3628.6919 | 0.55608 | 287.9503 | 0.060392
2598 | MCLU-135to240-OfL-CZ08-2011-17.5IEER | CZ08 | OfL | 2011 | 135to240 | 12 | 17.5 | 459.0602 | 3524.6905 | 0.52132 | 3718.625 | 0.56357 | 193.9345 | 0.042249
2599 | MCLU-135to240-OfL-CZ08-2015-17.5IEER | CZ08 | OfL | 2015 | 135to240 | 12 | 17.5 | 432.9544 | 3653.6746 | 0.53909 | 3844.2056 | 0.58098 | 190.5309 | 0.041889
2600 | MCLU-135to240-OfL-CZ08-2020-17.5IEER | CZ08 | OfL | 2020 | 135to240 | 12 | 17.5 | 421.163 | 3384.9624 | 0.50167 | 3668.3387 | 0.56217 | 283.3763 | 0.0605
2601 | MCLU-135to240-OfS-CZ08-2003-17.5IEER | CZ08 | OfS | 2003 | 135to240 | 12 | 17.5 | 32.7528 | 2446.6294 | 0.36088 | 2723.9903 | 0.4212 | 277.3609 | 0.060327
2602 | MCLU-135to240-OfS-CZ08-2007-17.5IEER | CZ08 | OfS | 2007 | 135to240 | 12 | 17.5 | 32.7528 | 2446.6294 | 0.36088 | 2723.9903 | 0.4212 | 277.3609 | 0.060327
2603 | MCLU-135to240-OfS-CZ08-2011-17.5IEER | CZ08 | OfS | 2011 | 135to240 | 12 | 17.5 | 32.606 | 2511.6649 | 0.37663 | 2707.5327 | 0.41879 | 195.8678 | 0.042157
2604 | MCLU-135to240-OfS-CZ08-2015-17.5IEER | CZ08 | OfS | 2015 | 135to240 | 12 | 17.5 | 27.4482 | 2866.03 | 0.4176 | 3056.7977 | 0.45921 | 190.7677 | 0.041609
2605 | MCLU-135to240-OfS-CZ08-2020-17.5IEER | CZ08 | OfS | 2020 | 135to240 | 12 | 17.5 | 26.6586 | 2630.6075 | 0.37882 | 2902.5578 | 0.43889 | 271.9503 | 0.060068
2606 | MCLU-135to240-RFF-CZ08-2003-17.5IEER | CZ08 | RFF | 2003 | 135to240 | 12 | 17.5 | 7.4623 | 5526.5915 | 1.1307 | 6040.8213 | 1.3048 | 514.2298 | 0.17408
2607 | MCLU-135to240-RFF-CZ08-2007-17.5IEER | CZ08 | RFF | 2007 | 135to240 | 12 | 17.5 | 7.4623 | 5526.5915 | 1.1307 | 6040.8213 | 1.3048 | 514.2298 | 0.17408
2608 | MCLU-135to240-RFF-CZ08-2011-17.5IEER | CZ08 | RFF | 2011 | 135to240 | 12 | 17.5 | 7.3932 | 5719.1696 | 1.1913 | 6093.7583 | 1.3133 | 374.5887 | 0.12204
2609 | MCLU-135to240-RFF-CZ08-2015-17.5IEER | CZ08 | RFF | 2015 | 135to240 | 12 | 17.5 | 7.1095 | 5633.8108 | 1.1829 | 6011.9432 | 1.306 | 378.1324 | 0.12311
2610 | MCLU-135to240-RFF-CZ08-2020-17.5IEER | CZ08 | RFF | 2020 | 135to240 | 12 | 17.5 | 6.703 | 5091.4093 | 1.0739 | 5605.5717 | 1.25 | 514.1624 | 0.17616
2611 | MCLU-135to240-RSD-CZ08-2003-17.5IEER | CZ08 | RSD | 2003 | 135to240 | 12 | 17.5 | 14.3743 | 5197.2236 | 1.0678 | 5653.2859 | 1.2446 | 456.0623 | 0.1768
2612 | MCLU-135to240-RSD-CZ08-2007-17.5IEER | CZ08 | RSD | 2007 | 135to240 | 12 | 17.5 | 14.3743 | 5197.2236 | 1.0678 | 5653.2859 | 1.2446 | 456.0623 | 0.1768
2613 | MCLU-135to240-RSD-CZ08-2011-17.5IEER | CZ08 | RSD | 2011 | 135to240 | 12 | 17.5 | 14.2289 | 5384.1949 | 1.1313 | 5707.0682 | 1.2532 | 322.8733 | 0.12191
2614 | MCLU-135to240-RSD-CZ08-2015-17.5IEER | CZ08 | RSD | 2015 | 135to240 | 12 | 17.5 | 13.3666 | 5380.2635 | 1.1346 | 5707.1719 | 1.2573 | 326.9084 | 0.1227
2615 | MCLU-135to240-RSD-CZ08-2020-17.5IEER | CZ08 | RSD | 2020 | 135to240 | 12 | 17.5 | 12.3848 | 4771.0829 | 1.0012 | 5219.6834 | 1.1799 | 448.6004 | 0.17869
2616 | MCLU-135to240-Rt3-CZ08-2003-17.5IEER | CZ08 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 253.5929 | 5510.2177 | 1.0967 | 5911.3525 | 1.2736 | 401.1349 | 0.17692
2617 | MCLU-135to240-Rt3-CZ08-2007-17.5IEER | CZ08 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 253.5929 | 5510.2177 | 1.0967 | 5911.3525 | 1.2736 | 401.1349 | 0.17692
2618 | MCLU-135to240-Rt3-CZ08-2011-17.5IEER | CZ08 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 252.8055 | 5671.5005 | 1.1531 | 5927.8331 | 1.2754 | 256.3326 | 0.12231
2619 | MCLU-135to240-Rt3-CZ08-2015-17.5IEER | CZ08 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 243.1289 | 5322.489 | 1.1007 | 5578.4338 | 1.2237 | 255.9447 | 0.12294
2620 | MCLU-135to240-Rt3-CZ08-2020-17.5IEER | CZ08 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 232.2505 | 4810.0125 | 0.99031 | 5203.4382 | 1.1685 | 393.4257 | 0.17821
2621 | MCLU-135to240-RtL-CZ08-2003-17.5IEER | CZ08 | RtL | 2003 | 135to240 | 12 | 17.5 | 228.5227 | 5818.5489 | 1.1178 | 6239.1402 | 1.291 | 420.5913 | 0.17317
2622 | MCLU-135to240-RtL-CZ08-2007-17.5IEER | CZ08 | RtL | 2007 | 135to240 | 12 | 17.5 | 228.5227 | 5818.5489 | 1.1178 | 6239.1402 | 1.291 | 420.5913 | 0.17317
2623 | MCLU-135to240-RtL-CZ08-2011-17.5IEER | CZ08 | RtL | 2011 | 135to240 | 12 | 17.5 | 225.2852 | 6050.1531 | 1.1845 | 6321.6158 | 1.3046 | 271.4628 | 0.12007
2624 | MCLU-135to240-RtL-CZ08-2015-17.5IEER | CZ08 | RtL | 2015 | 135to240 | 12 | 17.5 | 217.4431 | 5840.0524 | 1.1664 | 6118.6874 | 1.2875 | 278.635 | 0.12118
2625 | MCLU-135to240-RtL-CZ08-2020-17.5IEER | CZ08 | RtL | 2020 | 135to240 | 12 | 17.5 | 202.5013 | 5529.4821 | 1.1134 | 5958.9437 | 1.2888 | 429.4616 | 0.1754
2626 | MCLU-135to240-RtS-CZ08-2003-17.5IEER | CZ08 | RtS | 2003 | 135to240 | 12 | 17.5 | 17.227 | 3521.5004 | 0.70107 | 4001.2029 | 0.85259 | 479.7026 | 0.15153
2627 | MCLU-135to240-RtS-CZ08-2007-17.5IEER | CZ08 | RtS | 2007 | 135to240 | 12 | 17.5 | 17.227 | 3521.5004 | 0.70107 | 4001.2029 | 0.85259 | 479.7026 | 0.15153
2628 | MCLU-135to240-RtS-CZ08-2011-17.5IEER | CZ08 | RtS | 2011 | 135to240 | 12 | 17.5 | 17.0104 | 3707.1258 | 0.75304 | 4044.0186 | 0.85865 | 336.8928 | 0.10561
2629 | MCLU-135to240-RtS-CZ08-2015-17.5IEER | CZ08 | RtS | 2015 | 135to240 | 12 | 17.5 | 16.1546 | 3481.701 | 0.73349 | 3746.5948 | 0.83972 | 264.8937 | 0.10622
2630 | MCLU-135to240-RtS-CZ08-2020-17.5IEER | CZ08 | RtS | 2020 | 135to240 | 12 | 17.5 | 15.3097 | 3222.7516 | 0.66776 | 3595.4364 | 0.82036 | 372.6847 | 0.1526
2631 | MCLU-135to240-SCn-CZ08-2003-17.5IEER | CZ08 | SCn | 2003 | 135to240 | 12 | 17.5 | 289.9873 | 2623.9676 | 0.32292 | 2915.884 | 0.41386 | 291.9164 | 0.090937
2632 | MCLU-135to240-SCn-CZ08-2007-17.5IEER | CZ08 | SCn | 2007 | 135to240 | 12 | 17.5 | 289.9873 | 2623.9676 | 0.32292 | 2915.884 | 0.41386 | 291.9164 | 0.090937
2633 | MCLU-135to240-SCn-CZ08-2011-17.5IEER | CZ08 | SCn | 2011 | 135to240 | 12 | 17.5 | 275.6771 | 2797.4092 | 0.36195 | 3037.7059 | 0.427 | 240.2967 | 0.065055
2634 | MCLU-135to240-SCn-CZ08-2015-17.5IEER | CZ08 | SCn | 2015 | 135to240 | 12 | 17.5 | 280.4415 | 2728.2167 | 0.35427 | 2958.0289 | 0.41829 | 229.8122 | 0.064025
2635 | MCLU-135to240-SCn-CZ08-2020-17.5IEER | CZ08 | SCn | 2020 | 135to240 | 12 | 17.5 | 242.8972 | 2658.1698 | 0.32768 | 2933.6059 | 0.41981 | 275.4361 | 0.092134
2636 | MCLU-135to240-WRf-CZ08-2003-17.5IEER | CZ08 | WRf | 2003 | 135to240 | 12 | 17.5 | 16.7253 | 239294.8978 | 31.1049 | 239701.6712 | 31.1698 | 406.7734 | 0.064908
2637 | MCLU-135to240-WRf-CZ08-2007-17.5IEER | CZ08 | WRf | 2007 | 135to240 | 12 | 17.5 | 16.7253 | 233516.9797 | 29.6034 | 233920.6761 | 29.6686 | 403.6964 | 0.065144
2638 | MCLU-135to240-WRf-CZ08-2011-17.5IEER | CZ08 | WRf | 2011 | 135to240 | 12 | 17.5 | 15.6598 | 235961.7567 | 29.2756 | 236374.1729 | 29.3371 | 412.4162 | 0.061463
2639 | MCLU-135to240-WRf-CZ08-2015-17.5IEER | CZ08 | WRf | 2015 | 135to240 | 12 | 17.5 | 14.8615 | 248334.642 | 30.8358 | 248619.3164 | 30.8978 | 284.6744 | 0.062002
2640 | MCLU-135to240-WRf-CZ08-2020-17.5IEER | CZ08 | WRf | 2020 | 135to240 | 12 | 17.5 | 13.8675 | 248074.0404 | 30.412 | 248343.8955 | 30.4685 | 269.8551 | 0.056563
2641 | MCLU-135to240-Asm-CZ09-2003-17.5IEER | CZ09 | Asm | 2003 | 135to240 | 12 | 17.5 | 456.7848 | 1788.3232 | 0.6724 | 2081.813 | 0.80746 | 293.4898 | 0.13506
2642 | MCLU-135to240-Asm-CZ09-2007-17.5IEER | CZ09 | Asm | 2007 | 135to240 | 12 | 17.5 | 456.7848 | 1788.3232 | 0.6724 | 2081.813 | 0.80746 | 293.4898 | 0.13506
2643 | MCLU-135to240-Asm-CZ09-2011-17.5IEER | CZ09 | Asm | 2011 | 135to240 | 12 | 17.5 | 445.283 | 1824.4309 | 0.68409 | 2119.8141 | 0.81775 | 295.3832 | 0.13366
2644 | MCLU-135to240-Asm-CZ09-2015-17.5IEER | CZ09 | Asm | 2015 | 135to240 | 12 | 17.5 | 409.3283 | 1884.1917 | 0.70702 | 2175.6791 | 0.84184 | 291.4875 | 0.13482
2645 | MCLU-135to240-Asm-CZ09-2020-17.5IEER | CZ09 | Asm | 2020 | 135to240 | 12 | 17.5 | 400.5513 | 1776.3493 | 0.68954 | 2067.0227 | 0.8246 | 290.6734 | 0.13507
2646 | MCLU-135to240-ECC-CZ09-2003-17.5IEER | CZ09 | ECC | 2003 | 135to240 | 12 | 17.5 | 1023.0287 | 2132.6149 | 0.73353 | 2334.9584 | 0.88774 | 202.3435 | 0.1542
2647 | MCLU-135to240-ECC-CZ09-2007-17.5IEER | CZ09 | ECC | 2007 | 135to240 | 12 | 17.5 | 1023.0287 | 2132.6149 | 0.73353 | 2334.9584 | 0.88774 | 202.3435 | 0.1542
2648 | MCLU-135to240-ECC-CZ09-2011-17.5IEER | CZ09 | ECC | 2011 | 135to240 | 12 | 17.5 | 1015.5732 | 2142.9332 | 0.7316 | 2343.9155 | 0.88498 | 200.9822 | 0.15338
2649 | MCLU-135to240-ECC-CZ09-2015-17.5IEER | CZ09 | ECC | 2015 | 135to240 | 12 | 17.5 | 954.2187 | 2231.8414 | 0.74667 | 2428.6852 | 0.90333 | 196.8439 | 0.15666
2650 | MCLU-135to240-ECC-CZ09-2020-17.5IEER | CZ09 | ECC | 2020 | 135to240 | 12 | 17.5 | 924.8732 | 1954.6809 | 0.70201 | 2152.0893 | 0.85968 | 197.4084 | 0.15768
2651 | MCLU-135to240-EPr-CZ09-2003-17.5IEER | CZ09 | EPr | 2003 | 135to240 | 12 | 17.5 | 180.7183 | 1311.0758 | 0.36166 | 1437.6604 | 0.45192 | 126.5846 | 0.090263
2652 | MCLU-135to240-EPr-CZ09-2007-17.5IEER | CZ09 | EPr | 2007 | 135to240 | 12 | 17.5 | 180.7183 | 1311.0758 | 0.36166 | 1437.6604 | 0.45192 | 126.5846 | 0.090263
2653 | MCLU-135to240-EPr-CZ09-2011-17.5IEER | CZ09 | EPr | 2011 | 135to240 | 12 | 17.5 | 172.041 | 1371.7689 | 0.36703 | 1496.6163 | 0.4564 | 124.8475 | 0.089373
2654 | MCLU-135to240-EPr-CZ09-2015-17.5IEER | CZ09 | EPr | 2015 | 135to240 | 12 | 17.5 | 159.109 | 1434.0935 | 0.37479 | 1556.5493 | 0.46553 | 122.4557 | 0.090738
2655 | MCLU-135to240-EPr-CZ09-2020-17.5IEER | CZ09 | EPr | 2020 | 135to240 | 12 | 17.5 | 153.4868 | 1282.3089 | 0.34846 | 1400.9618 | 0.4387 | 118.6529 | 0.09024
2656 | MCLU-135to240-ERC-CZ09-2003-17.5IEER | CZ09 | ERC | 2003 | 135to240 | 12 | 17.5 | 8.2534 | 1117.7019 | 0.23274 | 1234.8645 | 0.26146 | 117.1626 | 0.028718
2657 | MCLU-135to240-ERC-CZ09-2007-17.5IEER | CZ09 | ERC | 2007 | 135to240 | 12 | 17.5 | 8.2539 | 1117.5975 | 0.23271 | 1234.7535 | 0.26142 | 117.156 | 0.028712
2658 | MCLU-135to240-ERC-CZ09-2011-17.5IEER | CZ09 | ERC | 2011 | 135to240 | 12 | 17.5 | 7.8798 | 1159.9716 | 0.22756 | 1275.7442 | 0.25202 | 115.7726 | 0.024461
2659 | MCLU-135to240-ERC-CZ09-2015-17.5IEER | CZ09 | ERC | 2015 | 135to240 | 12 | 17.5 | 7.5994 | 1122.8043 | 0.22005 | 1215.1326 | 0.24161 | 92.3283 | 0.021556
2660 | MCLU-135to240-ERC-CZ09-2020-17.5IEER | CZ09 | ERC | 2020 | 135to240 | 12 | 17.5 | 7.4191 | 982.5939 | 0.19575 | 1074.3412 | 0.21572 | 91.7474 | 0.019967
2661 | MCLU-135to240-ESe-CZ09-2003-17.5IEER | CZ09 | ESe | 2003 | 135to240 | 12 | 17.5 | 543.9273 | 1492.6071 | 0.35146 | 1636.7983 | 0.43948 | 144.1912 | 0.088021
2662 | MCLU-135to240-ESe-CZ09-2007-17.5IEER | CZ09 | ESe | 2007 | 135to240 | 12 | 17.5 | 543.9273 | 1492.6071 | 0.35146 | 1636.7983 | 0.43948 | 144.1912 | 0.088021
2663 | MCLU-135to240-ESe-CZ09-2011-17.5IEER | CZ09 | ESe | 2011 | 135to240 | 12 | 17.5 | 537.0907 | 1507.9023 | 0.35148 | 1651.3739 | 0.4391 | 143.4716 | 0.087621
2664 | MCLU-135to240-ESe-CZ09-2015-17.5IEER | CZ09 | ESe | 2015 | 135to240 | 12 | 17.5 | 497.5362 | 1536.9961 | 0.33948 | 1671.9269 | 0.43038 | 134.9308 | 0.090891
2665 | MCLU-135to240-ESe-CZ09-2020-17.5IEER | CZ09 | ESe | 2020 | 135to240 | 12 | 17.5 | 482.4597 | 1337.8973 | 0.32559 | 1472.7057 | 0.41684 | 134.8084 | 0.091249
2666 | MCLU-135to240-EUn-CZ09-2003-17.5IEER | CZ09 | EUn | 2003 | 135to240 | 12 | 17.5 | 3069.2272 | 2269.5071 | 0.8609 | 2483.807 | 0.99342 | 214.2999 | 0.13252
2667 | MCLU-135to240-EUn-CZ09-2007-17.5IEER | CZ09 | EUn | 2007 | 135to240 | 12 | 17.5 | 3069.2272 | 2255.3859 | 0.85155 | 2469.6423 | 0.98405 | 214.2564 | 0.1325
2668 | MCLU-135to240-EUn-CZ09-2011-17.5IEER | CZ09 | EUn | 2011 | 135to240 | 12 | 17.5 | 2993.8999 | 2298.4299 | 0.86383 | 2512.8002 | 0.99657 | 214.3703 | 0.13274
2669 | MCLU-135to240-EUn-CZ09-2015-17.5IEER | CZ09 | EUn | 2015 | 135to240 | 12 | 17.5 | 2748.8325 | 2420.2622 | 0.89383 | 2631.7177 | 1.0299 | 211.4555 | 0.13606
2670 | MCLU-135to240-EUn-CZ09-2020-17.5IEER | CZ09 | EUn | 2020 | 135to240 | 12 | 17.5 | 2653.7451 | 2201.6229 | 0.84972 | 2412.706 | 0.98592 | 211.0831 | 0.1362
2671 | MCLU-135to240-Gro-CZ09-2003-17.5IEER | CZ09 | Gro | 2003 | 135to240 | 12 | 17.5 | 152.4134 | 11056.9963 | 1.7838 | 11460.982 | 1.9291 | 403.9857 | 0.1453
2672 | MCLU-135to240-Gro-CZ09-2007-17.5IEER | CZ09 | Gro | 2007 | 135to240 | 12 | 17.5 | 152.4134 | 10118.2163 | 1.6718 | 10503.1435 | 1.8273 | 384.9272 | 0.15556
2673 | MCLU-135to240-Gro-CZ09-2011-17.5IEER | CZ09 | Gro | 2011 | 135to240 | 12 | 17.5 | 148.0947 | 10389.4785 | 1.7031 | 10769.5712 | 1.8605 | 380.0927 | 0.15746
2674 | MCLU-135to240-Gro-CZ09-2015-17.5IEER | CZ09 | Gro | 2015 | 135to240 | 12 | 17.5 | 141.0037 | 10446.0908 | 1.7104 | 10820.9648 | 1.8648 | 374.874 | 0.15441
2675 | MCLU-135to240-Gro-CZ09-2020-17.5IEER | CZ09 | Gro | 2020 | 135to240 | 12 | 17.5 | 139.0578 | 10266.8294 | 1.6778 | 10637.0878 | 1.8319 | 370.2584 | 0.15411
2676 | MCLU-135to240-Hsp-CZ09-2003-17.5IEER | CZ09 | Hsp | 2003 | 135to240 | 12 | 17.5 | 699.7387 | 4255.7803 | 0.83187 | 4669.1049 | 0.97651 | 413.3246 | 0.14464
2677 | MCLU-135to240-Hsp-CZ09-2007-17.5IEER | CZ09 | Hsp | 2007 | 135to240 | 12 | 17.5 | 699.7387 | 4255.7803 | 0.83187 | 4669.1049 | 0.97651 | 413.3246 | 0.14464
2678 | MCLU-135to240-Hsp-CZ09-2011-17.5IEER | CZ09 | Hsp | 2011 | 135to240 | 12 | 17.5 | 698.9984 | 4256.9811 | 0.82948 | 4669.4025 | 0.97338 | 412.4215 | 0.1439
2679 | MCLU-135to240-Hsp-CZ09-2015-17.5IEER | CZ09 | Hsp | 2015 | 135to240 | 12 | 17.5 | 681.4518 | 4297.6597 | 0.8244 | 4713.5439 | 0.97071 | 415.8843 | 0.14631
2680 | MCLU-135to240-Hsp-CZ09-2020-17.5IEER | CZ09 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3773.595 | 0.74482 | 4192.5284 | 0.89073 | 418.9334 | 0.14591
2681 | MCLU-135to240-Htl-CZ09-2003-17.5IEER | CZ09 | Htl | 2003 | 135to240 | 12 | 17.5 | 311.0942 | 2884.0216 | 0.85132 | 2978.8663 | 0.88835 | 94.8447 | 0.037026
2682 | MCLU-135to240-Htl-CZ09-2007-17.5IEER | CZ09 | Htl | 2007 | 135to240 | 12 | 17.5 | 311.0942 | 2766.4726 | 0.79445 | 2861.2681 | 0.83138 | 94.7956 | 0.03693
2683 | MCLU-135to240-Htl-CZ09-2011-17.5IEER | CZ09 | Htl | 2011 | 135to240 | 12 | 17.5 | 299.8847 | 2825.3181 | 0.8011 | 2921.8856 | 0.83878 | 96.5675 | 0.037684
2684 | MCLU-135to240-Htl-CZ09-2015-17.5IEER | CZ09 | Htl | 2015 | 135to240 | 12 | 17.5 | 261.8418 | 2936.2121 | 0.7979 | 3037.3404 | 0.83867 | 101.1282 | 0.040765
2685 | MCLU-135to240-Htl-CZ09-2020-17.5IEER | CZ09 | Htl | 2020 | 135to240 | 12 | 17.5 | 259.9268 | 2845.7493 | 0.7872 | 2945.4317 | 0.8272 | 99.6824 | 0.040001
2686 | MCLU-135to240-MBT-CZ09-2003-17.5IEER | CZ09 | MBT | 2003 | 135to240 | 12 | 17.5 | 461.5437 | 3294.6823 | 0.54038 | 3498.1254 | 0.65299 | 203.4431 | 0.11262
2687 | MCLU-135to240-MBT-CZ09-2007-17.5IEER | CZ09 | MBT | 2007 | 135to240 | 12 | 17.5 | 461.5437 | 3294.6823 | 0.54038 | 3498.1254 | 0.65299 | 203.4431 | 0.11262
2688 | MCLU-135to240-MBT-CZ09-2011-17.5IEER | CZ09 | MBT | 2011 | 135to240 | 12 | 17.5 | 421.0045 | 3555.2883 | 0.56093 | 3753.2351 | 0.67247 | 197.9467 | 0.11154
2689 | MCLU-135to240-MBT-CZ09-2015-17.5IEER | CZ09 | MBT | 2015 | 135to240 | 12 | 17.5 | 395.1152 | 3718.0642 | 0.57557 | 3914.329 | 0.68883 | 196.2647 | 0.11327
2690 | MCLU-135to240-MBT-CZ09-2020-17.5IEER | CZ09 | MBT | 2020 | 135to240 | 12 | 17.5 | 371.6492 | 3540.1057 | 0.55608 | 3735.535 | 0.66997 | 195.4293 | 0.11388
2691 | MCLU-135to240-MLI-CZ09-2003-17.5IEER | CZ09 | MLI | 2003 | 135to240 | 12 | 17.5 | 280.5149 | 2464.9061 | 0.41214 | 2664.0689 | 0.49242 | 199.1628 | 0.080279
2692 | MCLU-135to240-MLI-CZ09-2007-17.5IEER | CZ09 | MLI | 2007 | 135to240 | 12 | 17.5 | 280.5149 | 2464.9061 | 0.41214 | 2664.0689 | 0.49242 | 199.1628 | 0.080279
2693 | MCLU-135to240-MLI-CZ09-2011-17.5IEER | CZ09 | MLI | 2011 | 135to240 | 12 | 17.5 | 263.5504 | 2603.5021 | 0.4245 | 2800.0493 | 0.50527 | 196.5472 | 0.080767
2694 | MCLU-135to240-MLI-CZ09-2015-17.5IEER | CZ09 | MLI | 2015 | 135to240 | 12 | 17.5 | 259.5471 | 2621.8884 | 0.42682 | 2818.4187 | 0.50785 | 196.5304 | 0.081026
2695 | MCLU-135to240-MLI-CZ09-2020-17.5IEER | CZ09 | MLI | 2020 | 135to240 | 12 | 17.5 | 246.1096 | 2324.8228 | 0.39567 | 2520.8823 | 0.47713 | 196.0595 | 0.081465
2696 | MCLU-135to240-Mtl-CZ09-2003-17.5IEER | CZ09 | Mtl | 2003 | 135to240 | 12 | 17.5 | 53.9002 | 2902.2564 | 0.80508 | 2976.9874 | 0.83043 | 74.731 | 0.025358
2697 | MCLU-135to240-Mtl-CZ09-2007-17.5IEER | CZ09 | Mtl | 2007 | 135to240 | 12 | 17.5 | 53.9002 | 2771.9543 | 0.74449 | 2846.8094 | 0.76977 | 74.8551 | 0.025281
2698 | MCLU-135to240-Mtl-CZ09-2011-17.5IEER | CZ09 | Mtl | 2011 | 135to240 | 12 | 17.5 | 51.4509 | 2859.7613 | 0.75302 | 2933.9438 | 0.77815 | 74.1825 | 0.025133
2699 | MCLU-135to240-Mtl-CZ09-2015-17.5IEER | CZ09 | Mtl | 2015 | 135to240 | 12 | 17.5 | 44.3656 | 2988.8415 | 0.75216 | 3069.4554 | 0.78027 | 80.6138 | 0.02811
2700 | MCLU-135to240-Mtl-CZ09-2020-17.5IEER | CZ09 | Mtl | 2020 | 135to240 | 12 | 17.5 | 44.2275 | 2916.8414 | 0.7432 | 2996.5104 | 0.77094 | 79.669 | 0.027739
2701 | MCLU-135to240-Nrs-CZ09-2003-17.5IEER | CZ09 | Nrs | 2003 | 135to240 | 12 | 17.5 | 201.0382 | 4384.2067 | 0.95335 | 4575.2128 | 1.0231 | 191.0061 | 0.069792
2702 | MCLU-135to240-Nrs-CZ09-2007-17.5IEER | CZ09 | Nrs | 2007 | 135to240 | 12 | 17.5 | 201.0382 | 4281.4038 | 0.91475 | 4472.5382 | 0.98451 | 191.1344 | 0.069759
2703 | MCLU-135to240-Nrs-CZ09-2011-17.5IEER | CZ09 | Nrs | 2011 | 135to240 | 12 | 17.5 | 197.3785 | 4374.4913 | 0.9145 | 4566.109 | 0.98393 | 191.6177 | 0.06943
2704 | MCLU-135to240-Nrs-CZ09-2015-17.5IEER | CZ09 | Nrs | 2015 | 135to240 | 12 | 17.5 | 183.0028 | 4423.2365 | 0.87535 | 4612.7544 | 0.94608 | 189.5179 | 0.070722
2705 | MCLU-135to240-Nrs-CZ09-2020-17.5IEER | CZ09 | Nrs | 2020 | 135to240 | 12 | 17.5 | 182.3568 | 4055.7164 | 0.81622 | 4244.9874 | 0.88624 | 189.271 | 0.070021
2706 | MCLU-135to240-OfL-CZ09-2003-17.5IEER | CZ09 | OfL | 2003 | 135to240 | 12 | 17.5 | 553.8734 | 2967.59 | 0.49528 | 3164.9951 | 0.55051 | 197.405 | 0.055221
2707 | MCLU-135to240-OfL-CZ09-2007-17.5IEER | CZ09 | OfL | 2007 | 135to240 | 12 | 17.5 | 553.8734 | 2967.59 | 0.49528 | 3164.9951 | 0.55051 | 197.405 | 0.055221
2708 | MCLU-135to240-OfL-CZ09-2011-17.5IEER | CZ09 | OfL | 2011 | 135to240 | 12 | 17.5 | 529.7923 | 3059.2564 | 0.50087 | 3253.8476 | 0.55615 | 194.5912 | 0.055281
2709 | MCLU-135to240-OfL-CZ09-2015-17.5IEER | CZ09 | OfL | 2015 | 135to240 | 12 | 17.5 | 504.1555 | 3141.5673 | 0.51031 | 3333.5999 | 0.56621 | 192.0326 | 0.055902
2710 | MCLU-135to240-OfL-CZ09-2020-17.5IEER | CZ09 | OfL | 2020 | 135to240 | 12 | 17.5 | 493.2312 | 2976.6368 | 0.49114 | 3168.9851 | 0.54695 | 192.3483 | 0.055812
2711 | MCLU-135to240-OfS-CZ09-2003-17.5IEER | CZ09 | OfS | 2003 | 135to240 | 12 | 17.5 | 38.5652 | 2174.2471 | 0.37803 | 2374.008 | 0.43305 | 199.7609 | 0.055011
2712 | MCLU-135to240-OfS-CZ09-2007-17.5IEER | CZ09 | OfS | 2007 | 135to240 | 12 | 17.5 | 38.5652 | 2174.2471 | 0.37803 | 2374.008 | 0.43305 | 199.7609 | 0.055011
2713 | MCLU-135to240-OfS-CZ09-2011-17.5IEER | CZ09 | OfS | 2011 | 135to240 | 12 | 17.5 | 37.4337 | 2212.6927 | 0.37841 | 2411.3478 | 0.43272 | 198.6551 | 0.054303
2714 | MCLU-135to240-OfS-CZ09-2015-17.5IEER | CZ09 | OfS | 2015 | 135to240 | 12 | 17.5 | 31.9746 | 2481.4947 | 0.40259 | 2674.947 | 0.45818 | 193.4523 | 0.055592
2715 | MCLU-135to240-OfS-CZ09-2020-17.5IEER | CZ09 | OfS | 2020 | 135to240 | 12 | 17.5 | 31.2166 | 2339.5245 | 0.38321 | 2533.2455 | 0.43863 | 193.7209 | 0.055418
2716 | MCLU-135to240-RFF-CZ09-2003-17.5IEER | CZ09 | RFF | 2003 | 135to240 | 12 | 17.5 | 9.8748 | 4368.0788 | 1.07 | 4705.1452 | 1.2186 | 337.0664 | 0.14868
2717 | MCLU-135to240-RFF-CZ09-2007-17.5IEER | CZ09 | RFF | 2007 | 135to240 | 12 | 17.5 | 9.8748 | 4368.0788 | 1.07 | 4705.1452 | 1.2186 | 337.0664 | 0.14868
2718 | MCLU-135to240-RFF-CZ09-2011-17.5IEER | CZ09 | RFF | 2011 | 135to240 | 12 | 17.5 | 9.5604 | 4498.9105 | 1.0909 | 4838.4548 | 1.239 | 339.5444 | 0.14813
2719 | MCLU-135to240-RFF-CZ09-2015-17.5IEER | CZ09 | RFF | 2015 | 135to240 | 12 | 17.5 | 9.265 | 4408.7682 | 1.0782 | 4749.4376 | 1.2279 | 340.6694 | 0.1497
2720 | MCLU-135to240-RFF-CZ09-2020-17.5IEER | CZ09 | RFF | 2020 | 135to240 | 12 | 17.5 | 8.9079 | 4030.4692 | 1.024 | 4373.1475 | 1.174 | 342.6782 | 0.15001
2721 | MCLU-135to240-RSD-CZ09-2003-17.5IEER | CZ09 | RSD | 2003 | 135to240 | 12 | 17.5 | 18.7065 | 4175.6131 | 1.0371 | 4453.7548 | 1.1886 | 278.1417 | 0.15149
2722 | MCLU-135to240-RSD-CZ09-2007-17.5IEER | CZ09 | RSD | 2007 | 135to240 | 12 | 17.5 | 18.7065 | 4175.6131 | 1.0371 | 4453.7548 | 1.1886 | 278.1417 | 0.15149
2723 | MCLU-135to240-RSD-CZ09-2011-17.5IEER | CZ09 | RSD | 2011 | 135to240 | 12 | 17.5 | 17.7838 | 4385.6818 | 1.0707 | 4672.7091 | 1.2201 | 287.0273 | 0.1494
2724 | MCLU-135to240-RSD-CZ09-2015-17.5IEER | CZ09 | RSD | 2015 | 135to240 | 12 | 17.5 | 16.8257 | 4357.1427 | 1.0712 | 4650.3375 | 1.2196 | 293.1948 | 0.14842
2725 | MCLU-135to240-RSD-CZ09-2020-17.5IEER | CZ09 | RSD | 2020 | 135to240 | 12 | 17.5 | 16.0122 | 3875.4905 | 0.99494 | 4174.964 | 1.1406 | 299.4735 | 0.14565
2726 | MCLU-135to240-Rt3-CZ09-2003-17.5IEER | CZ09 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 320.8201 | 4467.6675 | 1.0357 | 4755.0515 | 1.1971 | 287.3839 | 0.16142
2727 | MCLU-135to240-Rt3-CZ09-2007-17.5IEER | CZ09 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 320.8201 | 4467.6675 | 1.0357 | 4755.0515 | 1.1971 | 287.3839 | 0.16142
2728 | MCLU-135to240-Rt3-CZ09-2011-17.5IEER | CZ09 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 317.0184 | 4516.5334 | 1.0401 | 4801.9741 | 1.2009 | 285.4407 | 0.16085
2729 | MCLU-135to240-Rt3-CZ09-2015-17.5IEER | CZ09 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 306.5512 | 4220.8425 | 0.99395 | 4509.4932 | 1.157 | 288.6506 | 0.16304
2730 | MCLU-135to240-Rt3-CZ09-2020-17.5IEER | CZ09 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 295.9904 | 3888.9465 | 0.94293 | 4180.3217 | 1.1075 | 291.3752 | 0.16459
2731 | MCLU-135to240-RtL-CZ09-2003-17.5IEER | CZ09 | RtL | 2003 | 135to240 | 12 | 17.5 | 287.2347 | 4753.6482 | 1.073 | 5059.3736 | 1.236 | 305.7254 | 0.16297
2732 | MCLU-135to240-RtL-CZ09-2007-17.5IEER | CZ09 | RtL | 2007 | 135to240 | 12 | 17.5 | 287.2347 | 4753.6482 | 1.073 | 5059.3736 | 1.236 | 305.7254 | 0.16297
2733 | MCLU-135to240-RtL-CZ09-2011-17.5IEER | CZ09 | RtL | 2011 | 135to240 | 12 | 17.5 | 272.5852 | 4995.434 | 1.109 | 5294.9616 | 1.2724 | 299.5276 | 0.16346
2734 | MCLU-135to240-RtL-CZ09-2015-17.5IEER | CZ09 | RtL | 2015 | 135to240 | 12 | 17.5 | 264.7692 | 4800.1584 | 1.0896 | 5101.2169 | 1.2544 | 301.0585 | 0.16484
2735 | MCLU-135to240-RtL-CZ09-2020-17.5IEER | CZ09 | RtL | 2020 | 135to240 | 12 | 17.5 | 251.8133 | 4578.1637 | 1.0751 | 4878.7916 | 1.2417 | 300.628 | 0.16665
2736 | MCLU-135to240-RtS-CZ09-2003-17.5IEER | CZ09 | RtS | 2003 | 135to240 | 12 | 17.5 | 22.0327 | 2919.3822 | 0.70648 | 3261.682 | 0.84609 | 342.2998 | 0.13961
2737 | MCLU-135to240-RtS-CZ09-2007-17.5IEER | CZ09 | RtS | 2007 | 135to240 | 12 | 17.5 | 22.0327 | 2919.3822 | 0.70648 | 3261.682 | 0.84609 | 342.2998 | 0.13961
2738 | MCLU-135to240-RtS-CZ09-2011-17.5IEER | CZ09 | RtS | 2011 | 135to240 | 12 | 17.5 | 21.0047 | 3047.484 | 0.72086 | 3391.3824 | 0.86007 | 343.8984 | 0.13922
2739 | MCLU-135to240-RtS-CZ09-2015-17.5IEER | CZ09 | RtS | 2015 | 135to240 | 12 | 17.5 | 20.1303 | 2824.6886 | 0.69903 | 3118.1017 | 0.84037 | 293.4131 | 0.14134
2740 | MCLU-135to240-RtS-CZ09-2020-17.5IEER | CZ09 | RtS | 2020 | 135to240 | 12 | 17.5 | 19.4462 | 2660.7189 | 0.67519 | 2953.9852 | 0.81747 | 293.2664 | 0.14228
2741 | MCLU-135to240-SCn-CZ09-2003-17.5IEER | CZ09 | SCn | 2003 | 135to240 | 12 | 17.5 | 391.3412 | 2063.6185 | 0.34277 | 2308.5932 | 0.42873 | 244.9747 | 0.085964
2742 | MCLU-135to240-SCn-CZ09-2007-17.5IEER | CZ09 | SCn | 2007 | 135to240 | 12 | 17.5 | 391.3412 | 2063.6185 | 0.34277 | 2308.5932 | 0.42873 | 244.9747 | 0.085964
2743 | MCLU-135to240-SCn-CZ09-2011-17.5IEER | CZ09 | SCn | 2011 | 135to240 | 12 | 17.5 | 326.356 | 2412.0694 | 0.38506 | 2658.0363 | 0.4711 | 245.9669 | 0.08604
2744 | MCLU-135to240-SCn-CZ09-2015-17.5IEER | CZ09 | SCn | 2015 | 135to240 | 12 | 17.5 | 332.2533 | 2346.3425 | 0.37217 | 2585.0141 | 0.46008 | 238.6716 | 0.087915
2745 | MCLU-135to240-SCn-CZ09-2020-17.5IEER | CZ09 | SCn | 2020 | 135to240 | 12 | 17.5 | 305.7125 | 2205.9853 | 0.36638 | 2445.6776 | 0.45163 | 239.6923 | 0.085246
2746 | MCLU-135to240-WRf-CZ09-2003-17.5IEER | CZ09 | WRf | 2003 | 135to240 | 12 | 17.5 | 18.0615 | 221856.8626 | 31.5454 | 222260.218 | 31.6245 | 403.3554 | 0.079122
2747 | MCLU-135to240-WRf-CZ09-2007-17.5IEER | CZ09 | WRf | 2007 | 135to240 | 12 | 17.5 | 16.0098 | 244441.3793 | 34.4477 | 244896.3412 | 34.537 | 454.9619 | 0.089307
2748 | MCLU-135to240-WRf-CZ09-2011-17.5IEER | CZ09 | WRf | 2011 | 135to240 | 12 | 17.5 | 14.3883 | 249484.1161 | 32.8127 | 249940.6466 | 32.8906 | 456.5305 | 0.077856
2749 | MCLU-135to240-WRf-CZ09-2015-17.5IEER | CZ09 | WRf | 2015 | 135to240 | 12 | 17.5 | 18.0615 | 198468.4518 | 26.1235 | 198703.6399 | 26.184 | 235.1881 | 0.060549
2750 | MCLU-135to240-WRf-CZ09-2020-17.5IEER | CZ09 | WRf | 2020 | 135to240 | 12 | 17.5 | 15.1807 | 223018.7985 | 29.3778 | 223275.7683 | 29.4382 | 256.9697 | 0.06042
2751 | MCLU-135to240-Asm-CZ10-2003-17.5IEER | CZ10 | Asm | 2003 | 135to240 | 12 | 17.5 | 388.7587 | 2097.7659 | 0.76293 | 2412.0655 | 0.89673 | 314.2995 | 0.1338
2752 | MCLU-135to240-Asm-CZ10-2007-17.5IEER | CZ10 | Asm | 2007 | 135to240 | 12 | 17.5 | 385.9441 | 2109.5484 | 0.76668 | 2424.0716 | 0.9004 | 314.5231 | 0.13372
2753 | MCLU-135to240-Asm-CZ10-2011-17.5IEER | CZ10 | Asm | 2011 | 135to240 | 12 | 17.5 | 383.0505 | 2121.9681 | 0.77065 | 2436.7876 | 0.90449 | 314.8194 | 0.13384
2754 | MCLU-135to240-Asm-CZ10-2015-17.5IEER | CZ10 | Asm | 2015 | 135to240 | 12 | 17.5 | 373.8865 | 2130.7035 | 0.77232 | 2444.3003 | 0.90688 | 313.5969 | 0.13456
2755 | MCLU-135to240-Asm-CZ10-2020-17.5IEER | CZ10 | Asm | 2020 | 135to240 | 12 | 17.5 | 366.5988 | 2008.821 | 0.7504 | 2321.9334 | 0.88495 | 313.1124 | 0.13455
2756 | MCLU-135to240-ECC-CZ10-2003-17.5IEER | CZ10 | ECC | 2003 | 135to240 | 12 | 17.5 | 912.6597 | 2420.8448 | 0.8113 | 2634.4911 | 0.96087 | 213.6463 | 0.14957
2757 | MCLU-135to240-ECC-CZ10-2007-17.5IEER | CZ10 | ECC | 2007 | 135to240 | 12 | 17.5 | 910.6653 | 2425.0543 | 0.81124 | 2638.4038 | 0.96054 | 213.3495 | 0.14931
2758 | MCLU-135to240-ECC-CZ10-2011-17.5IEER | CZ10 | ECC | 2011 | 135to240 | 12 | 17.5 | 908.5397 | 2427.8612 | 0.81088 | 2640.919 | 0.95988 | 213.0577 | 0.149
2759 | MCLU-135to240-ECC-CZ10-2015-17.5IEER | CZ10 | ECC | 2015 | 135to240 | 12 | 17.5 | 875.6335 | 2471.7985 | 0.81419 | 2682.4759 | 0.96521 | 210.6774 | 0.15102
2760 | MCLU-135to240-ECC-CZ10-2020-17.5IEER | CZ10 | ECC | 2020 | 135to240 | 12 | 17.5 | 845.4984 | 2175.5978 | 0.76848 | 2388.3955 | 0.91991 | 212.7977 | 0.15143
2761 | MCLU-135to240-EPr-CZ10-2003-17.5IEER | CZ10 | EPr | 2003 | 135to240 | 12 | 17.5 | 156.5824 | 1533.6556 | 0.41284 | 1670.7644 | 0.4992 | 137.1089 | 0.086367
2762 | MCLU-135to240-EPr-CZ10-2007-17.5IEER | CZ10 | EPr | 2007 | 135to240 | 12 | 17.5 | 155.0193 | 1546.9261 | 0.41463 | 1683.9184 | 0.50064 | 136.9923 | 0.086005
2763 | MCLU-135to240-EPr-CZ10-2011-17.5IEER | CZ10 | EPr | 2011 | 135to240 | 12 | 17.5 | 151.5427 | 1596.9773 | 0.42016 | 1729.3619 | 0.50534 | 132.3846 | 0.08518
2764 | MCLU-135to240-EPr-CZ10-2015-17.5IEER | CZ10 | EPr | 2015 | 135to240 | 12 | 17.5 | 143.7652 | 1629.1684 | 0.42238 | 1761.32 | 0.50832 | 132.1516 | 0.085935
2765 | MCLU-135to240-EPr-CZ10-2020-17.5IEER | CZ10 | EPr | 2020 | 135to240 | 12 | 17.5 | 138.0283 | 1446.8906 | 0.39207 | 1580.4897 | 0.4773 | 133.5991 | 0.085225
2766 | MCLU-135to240-ERC-CZ10-2003-17.5IEER | CZ10 | ERC | 2003 | 135to240 | 12 | 17.5 | 7.0851 | 1307.0162 | 0.26407 | 1429.5743 | 0.29225 | 122.5581 | 0.028184
2767 | MCLU-135to240-ERC-CZ10-2007-17.5IEER | CZ10 | ERC | 2007 | 135to240 | 12 | 17.5 | 7.0616 | 1310.6956 | 0.2639 | 1433.0655 | 0.29151 | 122.3699 | 0.027615
2768 | MCLU-135to240-ERC-CZ10-2011-17.5IEER | CZ10 | ERC | 2011 | 135to240 | 12 | 17.5 | 6.8673 | 1338.051 | 0.26166 | 1459.1007 | 0.28697 | 121.0496 | 0.025311
2769 | MCLU-135to240-ERC-CZ10-2015-17.5IEER | CZ10 | ERC | 2015 | 135to240 | 12 | 17.5 | 6.7416 | 1302.2111 | 0.25814 | 1403.9494 | 0.28196 | 101.7383 | 0.023823
2770 | MCLU-135to240-ERC-CZ10-2020-17.5IEER | CZ10 | ERC | 2020 | 135to240 | 12 | 17.5 | 6.5655 | 1144.9284 | 0.2308 | 1246.4151 | 0.25335 | 101.4867 | 0.022556
2771 | MCLU-135to240-ESe-CZ10-2003-17.5IEER | CZ10 | ESe | 2003 | 135to240 | 12 | 17.5 | 465.7493 | 1712.3732 | 0.38755 | 1861.2322 | 0.4735 | 148.859 | 0.085954
2772 | MCLU-135to240-ESe-CZ10-2007-17.5IEER | CZ10 | ESe | 2007 | 135to240 | 12 | 17.5 | 464.0106 | 1717.7505 | 0.38769 | 1866.4619 | 0.47348 | 148.7114 | 0.085795
2773 | MCLU-135to240-ESe-CZ10-2011-17.5IEER | CZ10 | ESe | 2011 | 135to240 | 12 | 17.5 | 462.1829 | 1722.5784 | 0.3879 | 1871.1679 | 0.47353 | 148.5895 | 0.085629
2774 | MCLU-135to240-ESe-CZ10-2015-17.5IEER | CZ10 | ESe | 2015 | 135to240 | 12 | 17.5 | 451.7638 | 1726.8077 | 0.37978 | 1872.6372 | 0.46686 | 145.8296 | 0.087086
2775 | MCLU-135to240-ESe-CZ10-2020-17.5IEER | CZ10 | ESe | 2020 | 135to240 | 12 | 17.5 | 436.2432 | 1511.0213 | 0.3663 | 1657.8257 | 0.45321 | 146.8043 | 0.086912
2776 | MCLU-135to240-EUn-CZ10-2003-17.5IEER | CZ10 | EUn | 2003 | 135to240 | 12 | 17.5 | 2716.2035 | 2599.567 | 0.9569 | 2824.5601 | 1.0837 | 224.993 | 0.1268
2777 | MCLU-135to240-EUn-CZ10-2007-17.5IEER | CZ10 | EUn | 2007 | 135to240 | 12 | 17.5 | 2702.1292 | 2594.157 | 0.95017 | 2818.8719 | 1.0768 | 224.7149 | 0.12662
2778 | MCLU-135to240-EUn-CZ10-2011-17.5IEER | CZ10 | EUn | 2011 | 135to240 | 12 | 17.5 | 2674.5078 | 2612.1239 | 0.95512 | 2837.3474 | 1.082 | 225.2236 | 0.12691
2779 | MCLU-135to240-EUn-CZ10-2015-17.5IEER | CZ10 | EUn | 2015 | 135to240 | 12 | 17.5 | 2536.2488 | 2676.7579 | 0.97192 | 2901.9966 | 1.101 | 225.2387 | 0.12906
2780 | MCLU-135to240-EUn-CZ10-2020-17.5IEER | CZ10 | EUn | 2020 | 135to240 | 12 | 17.5 | 2444.2961 | 2443.085 | 0.92504 | 2668.4721 | 1.0539 | 225.3871 | 0.12884
2781 | MCLU-135to240-Gro-CZ10-2003-17.5IEER | CZ10 | Gro | 2003 | 135to240 | 12 | 17.5 | 138.0979 | 12225.4253 | 1.957 | 12634.7929 | 2.0983 | 409.3676 | 0.1413
2782 | MCLU-135to240-Gro-CZ10-2007-17.5IEER | CZ10 | Gro | 2007 | 135to240 | 12 | 17.5 | 135.8997 | 11361.8253 | 1.8728 | 11744.6102 | 2.0138 | 382.7849 | 0.14094
2783 | MCLU-135to240-Gro-CZ10-2011-17.5IEER | CZ10 | Gro | 2011 | 135to240 | 12 | 17.5 | 133.6844 | 11541.4701 | 1.8981 | 11922.7813 | 2.0394 | 381.3113 | 0.14134
2784 | MCLU-135to240-Gro-CZ10-2015-17.5IEER | CZ10 | Gro | 2015 | 135to240 | 12 | 17.5 | 129.0982 | 11446.7226 | 1.8807 | 11823.2308 | 2.0213 | 376.5082 | 0.14059
2785 | MCLU-135to240-Gro-CZ10-2020-17.5IEER | CZ10 | Gro | 2020 | 135to240 | 12 | 17.5 | 125.0696 | 11446.1249 | 1.8749 | 11818.7595 | 2.0156 | 372.6346 | 0.14073
2786 | MCLU-135to240-Hsp-CZ10-2003-17.5IEER | CZ10 | Hsp | 2003 | 135to240 | 12 | 17.5 | 681.5543 | 4367.1869 | 0.83453 | 4786.1663 | 0.9721 | 418.9795 | 0.13758
2787 | MCLU-135to240-Hsp-CZ10-2007-17.5IEER | CZ10 | Hsp | 2007 | 135to240 | 12 | 17.5 | 681.5532 | 4366.3626 | 0.83364 | 4785.0344 | 0.97101 | 418.6718 | 0.13737
2788 | MCLU-135to240-Hsp-CZ10-2011-17.5IEER | CZ10 | Hsp | 2011 | 135to240 | 12 | 17.5 | 681.5521 | 4365.5216 | 0.83274 | 4783.8808 | 0.96991 | 418.3592 | 0.13716
2789 | MCLU-135to240-Hsp-CZ10-2015-17.5IEER | CZ10 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.6818 | 4335.8241 | 0.82176 | 4754.084 | 0.9595 | 418.2599 | 0.13774
2790 | MCLU-135to240-Hsp-CZ10-2020-17.5IEER | CZ10 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3806.3667 | 0.74178 | 4228.0914 | 0.87925 | 421.7247 | 0.13746
2791 | MCLU-135to240-Htl-CZ10-2003-17.5IEER | CZ10 | Htl | 2003 | 135to240 | 12 | 17.5 | 274.5686 | 3258.1976 | 0.90207 | 3358.3746 | 0.93739 | 100.177 | 0.035315
2792 | MCLU-135to240-Htl-CZ10-2007-17.5IEER | CZ10 | Htl | 2007 | 135to240 | 12 | 17.5 | 274.2365 | 3129.6674 | 0.84359 | 3229.8307 | 0.87885 | 100.1633 | 0.035256
2793 | MCLU-135to240-Htl-CZ10-2011-17.5IEER | CZ10 | Htl | 2011 | 135to240 | 12 | 17.5 | 267.2675 | 3173.9573 | 0.84924 | 3275.6458 | 0.88508 | 101.6885 | 0.035845
2794 | MCLU-135to240-Htl-CZ10-2015-17.5IEER | CZ10 | Htl | 2015 | 135to240 | 12 | 17.5 | 240.8594 | 3265.9152 | 0.85384 | 3372.3865 | 0.89211 | 106.4713 | 0.038279
2795 | MCLU-135to240-Htl-CZ10-2020-17.5IEER | CZ10 | Htl | 2020 | 135to240 | 12 | 17.5 | 238.9549 | 3169.5367 | 0.84245 | 3274.5204 | 0.88012 | 104.9838 | 0.037663
2796 | MCLU-135to240-MBT-CZ10-2003-17.5IEER | CZ10 | MBT | 2003 | 135to240 | 12 | 17.5 | 403.7235 | 3775.7033 | 0.60086 | 3983.3931 | 0.70949 | 207.6898 | 0.10864
2797 | MCLU-135to240-MBT-CZ10-2007-17.5IEER | CZ10 | MBT | 2007 | 135to240 | 12 | 17.5 | 397.3649 | 3834.0726 | 0.60589 | 4040.7333 | 0.71417 | 206.6608 | 0.10828
2798 | MCLU-135to240-MBT-CZ10-2011-17.5IEER | CZ10 | MBT | 2011 | 135to240 | 12 | 17.5 | 375.8458 | 3993.0899 | 0.61833 | 4197.3203 | 0.7261 | 204.2304 | 0.10777
2799 | MCLU-135to240-MBT-CZ10-2015-17.5IEER | CZ10 | MBT | 2015 | 135to240 | 12 | 17.5 | 367.0415 | 4044.6188 | 0.62216 | 4248.2416 | 0.73014 | 203.6228 | 0.10798
2800 | MCLU-135to240-MBT-CZ10-2020-17.5IEER | CZ10 | MBT | 2020 | 135to240 | 12 | 17.5 | 343.6972 | 3869.7996 | 0.60325 | 4073.0377 | 0.71153 | 203.2382 | 0.10828
2801 | MCLU-135to240-MLI-CZ10-2003-17.5IEER | CZ10 | MLI | 2003 | 135to240 | 12 | 17.5 | 254.5192 | 2745.7535 | 0.46631 | 2948.7978 | 0.5422 | 203.0444 | 0.075894
2802 | MCLU-135to240-MLI-CZ10-2007-17.5IEER | CZ10 | MLI | 2007 | 135to240 | 12 | 17.5 | 249.4711 | 2794.9904 | 0.47147 | 2997.3396 | 0.54754 | 202.3492 | 0.076072
2803 | MCLU-135to240-MLI-CZ10-2011-17.5IEER | CZ10 | MLI | 2011 | 135to240 | 12 | 17.5 | 244.3303 | 2847.5076 | 0.47692 | 3049.1542 | 0.55316 | 201.6466 | 0.07624
2804 | MCLU-135to240-MLI-CZ10-2015-17.5IEER | CZ10 | MLI | 2015 | 135to240 | 12 | 17.5 | 242.1424 | 2852.0417 | 0.47763 | 3053.6327 | 0.55396 | 201.591 | 0.076326
2805 | MCLU-135to240-MLI-CZ10-2020-17.5IEER | CZ10 | MLI | 2020 | 135to240 | 12 | 17.5 | 228.3121 | 2545.9414 | 0.44613 | 2747.8598 | 0.52319 | 201.9183 | 0.07706
2806 | MCLU-135to240-Mtl-CZ10-2003-17.5IEER | CZ10 | Mtl | 2003 | 135to240 | 12 | 17.5 | 49.6158 | 3148.5034 | 0.8483 | 3227.051 | 0.87244 | 78.5476 | 0.024138
2807 | MCLU-135to240-Mtl-CZ10-2007-17.5IEER | CZ10 | Mtl | 2007 | 135to240 | 12 | 17.5 | 49.6158 | 3012.5731 | 0.78523 | 3091.0995 | 0.80932 | 78.5264 | 0.02409
2808 | MCLU-135to240-Mtl-CZ10-2011-17.5IEER | CZ10 | Mtl | 2011 | 135to240 | 12 | 17.5 | 48.1774 | 3056.7507 | 0.79023 | 3135.2555 | 0.81425 | 78.5048 | 0.024027
2809 | MCLU-135to240-Mtl-CZ10-2015-17.5IEER | CZ10 | Mtl | 2015 | 135to240 | 12 | 17.5 | 41.1672 | 3288.6413 | 0.80018 | 3371.7153 | 0.82636 | 83.074 | 0.026181
2810 | MCLU-135to240-Mtl-CZ10-2020-17.5IEER | CZ10 | Mtl | 2020 | 135to240 | 12 | 17.5 | 41.0319 | 3211.6732 | 0.79058 | 3293.7978 | 0.81638 | 82.1246 | 0.025801
2811 | MCLU-135to240-Nrs-CZ10-2003-17.5IEER | CZ10 | Nrs | 2003 | 135to240 | 12 | 17.5 | 183.7118 | 4663.4149 | 0.96408 | 4860.2882 | 1.033 | 196.8733 | 0.068946
2812 | MCLU-135to240-Nrs-CZ10-2007-17.5IEER | CZ10 | Nrs | 2007 | 135to240 | 12 | 17.5 | 183.6655 | 4565.1186 | 0.9271 | 4761.9457 | 0.9958 | 196.827 | 0.068697
2813 | MCLU-135to240-Nrs-CZ10-2011-17.5IEER | CZ10 | Nrs | 2011 | 135to240 | 12 | 17.5 | 183.2026 | 4586.498 | 0.91891 | 4782.4462 | 0.98713 | 195.9483 | 0.068217
2814 | MCLU-135to240-Nrs-CZ10-2015-17.5IEER | CZ10 | Nrs | 2015 | 135to240 | 12 | 17.5 | 182.1872 | 4474.9209 | 0.87067 | 4668.6556 | 0.93869 | 193.7348 | 0.068021
2815 | MCLU-135to240-Nrs-CZ10-2020-17.5IEER | CZ10 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.7891 | 4100.0429 | 0.81028 | 4293.5991 | 0.87765 | 193.5562 | 0.067372
2816 | MCLU-135to240-OfL-CZ10-2003-17.5IEER | CZ10 | OfL | 2003 | 135to240 | 12 | 17.5 | 490.1834 | 3385.6916 | 0.55488 | 3586.6096 | 0.60658 | 200.918 | 0.051696
2817 | MCLU-135to240-OfL-CZ10-2007-17.5IEER | CZ10 | OfL | 2007 | 135to240 | 12 | 17.5 | 489.4475 | 3390.3827 | 0.55543 | 3591.2919 | 0.60706 | 200.9091 | 0.051629
2818 | MCLU-135to240-OfL-CZ10-2011-17.5IEER | CZ10 | OfL | 2011 | 135to240 | 12 | 17.5 | 468.735 | 3492.2842 | 0.56286 | 3690.6979 | 0.61458 | 198.4137 | 0.051711
2819 | MCLU-135to240-OfL-CZ10-2015-17.5IEER | CZ10 | OfL | 2015 | 135to240 | 12 | 17.5 | 470.1578 | 3416.758 | 0.55732 | 3615.1832 | 0.60899 | 198.4251 | 0.051667
2820 | MCLU-135to240-OfL-CZ10-2020-17.5IEER | CZ10 | OfL | 2020 | 135to240 | 12 | 17.5 | 457.9924 | 3252.9239 | 0.53953 | 3452.2395 | 0.5914 | 199.3156 | 0.051867
2821 | MCLU-135to240-OfS-CZ10-2003-17.5IEER | CZ10 | OfS | 2003 | 135to240 | 12 | 17.5 | 33.5648 | 2514.5886 | 0.42414 | 2719.3154 | 0.47537 | 204.7268 | 0.051224
2822 | MCLU-135to240-OfS-CZ10-2007-17.5IEER | CZ10 | OfS | 2007 | 135to240 | 12 | 17.5 | 33.4756 | 2520.175 | 0.42436 | 2724.7142 | 0.47544 | 204.5392 | 0.05108
2823 | MCLU-135to240-OfS-CZ10-2011-17.5IEER | CZ10 | OfS | 2011 | 135to240 | 12 | 17.5 | 32.8327 | 2541.1663 | 0.42421 | 2745.0207 | 0.47505 | 203.8545 | 0.050839
2824 | MCLU-135to240-OfS-CZ10-2015-17.5IEER | CZ10 | OfS | 2015 | 135to240 | 12 | 17.5 | 29.8823 | 2701.1654 | 0.44105 | 2901.8012 | 0.49299 | 200.6358 | 0.051936
2825 | MCLU-135to240-OfS-CZ10-2020-17.5IEER | CZ10 | OfS | 2020 | 135to240 | 12 | 17.5 | 29.1294 | 2552.4971 | 0.42118 | 2753.5303 | 0.47282 | 201.0332 | 0.051643
2826 | MCLU-135to240-RFF-CZ10-2003-17.5IEER | CZ10 | RFF | 2003 | 135to240 | 12 | 17.5 | 8.4441 | 5146.3754 | 1.2404 | 5510.9525 | 1.3803 | 364.5771 | 0.13997
2827 | MCLU-135to240-RFF-CZ10-2007-17.5IEER | CZ10 | RFF | 2007 | 135to240 | 12 | 17.5 | 8.3619 | 5192.467 | 1.2484 | 5558.7269 | 1.3881 | 366.2598 | 0.1397
2828 | MCLU-135to240-RFF-CZ10-2011-17.5IEER | CZ10 | RFF | 2011 | 135to240 | 12 | 17.5 | 8.2766 | 5241.1063 | 1.2572 | 5609.7055 | 1.3964 | 368.5991 | 0.13919
2829 | MCLU-135to240-RFF-CZ10-2015-17.5IEER | CZ10 | RFF | 2015 | 135to240 | 12 | 17.5 | 8.2908 | 4989.8184 | 1.2125 | 5359.1948 | 1.3532 | 369.3763 | 0.14068
2830 | MCLU-135to240-RFF-CZ10-2020-17.5IEER | CZ10 | RFF | 2020 | 135to240 | 12 | 17.5 | 7.9475 | 4575.1967 | 1.155 | 4952.4461 | 1.2958 | 377.2494 | 0.14074
2831 | MCLU-135to240-RSD-CZ10-2003-17.5IEER | CZ10 | RSD | 2003 | 135to240 | 12 | 17.5 | 15.9093 | 4887.3179 | 1.178 | 5213.6977 | 1.3203 | 326.3798 | 0.14229
2832 | MCLU-135to240-RSD-CZ10-2007-17.5IEER | CZ10 | RSD | 2007 | 135to240 | 12 | 17.5 | 15.7381 | 4936.9325 | 1.1866 | 5265.8128 | 1.3283 | 328.8803 | 0.14169
2833 | MCLU-135to240-RSD-CZ10-2011-17.5IEER | CZ10 | RSD | 2011 | 135to240 | 12 | 17.5 | 15.4338 | 5033.2903 | 1.2008 | 5367.3025 | 1.3417 | 334.0121 | 0.14083
2834 | MCLU-135to240-RSD-CZ10-2015-17.5IEER | CZ10 | RSD | 2015 | 135to240 | 12 | 17.5 | 15.2915 | 4847.0038 | 1.1705 | 5176.4005 | 1.3119 | 329.3967 | 0.14142
2835 | MCLU-135to240-RSD-CZ10-2020-17.5IEER | CZ10 | RSD | 2020 | 135to240 | 12 | 17.5 | 14.5111 | 4329.0281 | 1.0884 | 4661.8318 | 1.2293 | 332.8037 | 0.14087
2836 | MCLU-135to240-Rt3-CZ10-2003-17.5IEER | CZ10 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 291.8068 | 4984.935 | 1.1405 | 5277.8354 | 1.2914 | 292.9004 | 0.1509
2837 | MCLU-135to240-Rt3-CZ10-2007-17.5IEER | CZ10 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 290.8431 | 5000.1006 | 1.142 | 5292.5011 | 1.2928 | 292.4005 | 0.15079
2838 | MCLU-135to240-Rt3-CZ10-2011-17.5IEER | CZ10 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 289.8732 | 5015.4621 | 1.1435 | 5307.3667 | 1.2941 | 291.9046 | 0.15066
2839 | MCLU-135to240-Rt3-CZ10-2015-17.5IEER | CZ10 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 281.1896 | 4679.8591 | 1.0919 | 4975.1026 | 1.2444 | 295.2435 | 0.15251
2840 | MCLU-135to240-Rt3-CZ10-2020-17.5IEER | CZ10 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 270.6424 | 4328.8156 | 1.0393 | 4627.2562 | 1.193 | 298.4406 | 0.15371
2841 | MCLU-135to240-RtL-CZ10-2003-17.5IEER | CZ10 | RtL | 2003 | 135to240 | 12 | 17.5 | 257.5351 | 5363.0303 | 1.1849 | 5675.4458 | 1.3371 | 312.4155 | 0.15213
2842 | MCLU-135to240-RtL-CZ10-2007-17.5IEER | CZ10 | RtL | 2007 | 135to240 | 12 | 17.5 | 253.6427 | 5440.9888 | 1.1972 | 5751.8687 | 1.3494 | 310.88 | 0.15229
2843 | MCLU-135to240-RtL-CZ10-2011-17.5IEER | CZ10 | RtL | 2011 | 135to240 | 12 | 17.5 | 249.6534 | 5523.8044 | 1.2103 | 5833.0761 | 1.3625 | 309.2718 | 0.15213
2844 | MCLU-135to240-RtL-CZ10-2015-17.5IEER | CZ10 | RtL | 2015 | 135to240 | 12 | 17.5 | 242.9278 | 5304.1946 | 1.1883 | 5615.4548 | 1.3415 | 311.2602 | 0.15318
2845 | MCLU-135to240-RtL-CZ10-2020-17.5IEER | CZ10 | RtL | 2020 | 135to240 | 12 | 17.5 | 229.9687 | 5084.9378 | 1.1772 | 5396.2894 | 1.3313 | 311.3517 | 0.15415
2846 | MCLU-135to240-RtS-CZ10-2003-17.5IEER | CZ10 | RtS | 2003 | 135to240 | 12 | 17.5 | 19.2854 | 3366.2999 | 0.79981 | 3723.3465 | 0.93408 | 357.0466 | 0.13427
2847 | MCLU-135to240-RtS-CZ10-2007-17.5IEER | CZ10 | RtS | 2007 | 135to240 | 12 | 17.5 | 19.0192 | 3408.5293 | 0.80512 | 3766.0743 | 0.93954 | 357.545 | 0.13442
2848 | MCLU-135to240-RtS-CZ10-2011-17.5IEER | CZ10 | RtS | 2011 | 135to240 | 12 | 17.5 | 18.7491 | 3452.8872 | 0.81065 | 3810.987 | 0.94494 | 358.0998 | 0.13429
2849 | MCLU-135to240-RtS-CZ10-2015-17.5IEER | CZ10 | RtS | 2015 | 135to240 | 12 | 17.5 | 18.4987 | 3143.1012 | 0.77252 | 3447.622 | 0.90742 | 304.5207 | 0.1349
2850 | MCLU-135to240-RtS-CZ10-2020-17.5IEER | CZ10 | RtS | 2020 | 135to240 | 12 | 17.5 | 17.7921 | 2976.0004 | 0.7499 | 3281.3359 | 0.88554 | 305.3355 | 0.13564
2851 | MCLU-135to240-SCn-CZ10-2003-17.5IEER | CZ10 | SCn | 2003 | 135to240 | 12 | 17.5 | 324.5743 | 2492.5714 | 0.41044 | 2758.9913 | 0.49548 | 266.4199 | 0.085046
2852 | MCLU-135to240-SCn-CZ10-2007-17.5IEER | CZ10 | SCn | 2007 | 135to240 | 12 | 17.5 | 307.0377 | 2615.2633 | 0.42738 | 2884.4441 | 0.51117 | 269.1808 | 0.08379
2853 | MCLU-135to240-SCn-CZ10-2011-17.5IEER | CZ10 | SCn | 2011 | 135to240 | 12 | 17.5 | 289.1649 | 2755.5363 | 0.44849 | 3023.7303 | 0.52921 | 268.194 | 0.08072
2854 | MCLU-135to240-SCn-CZ10-2015-17.5IEER | CZ10 | SCn | 2015 | 135to240 | 12 | 17.5 | 298.3611 | 2647.63 | 0.42749 | 2905.6143 | 0.51167 | 257.9843 | 0.084179
2855 | MCLU-135to240-SCn-CZ10-2020-17.5IEER | CZ10 | SCn | 2020 | 135to240 | 12 | 17.5 | 270.5635 | 2530.278 | 0.42923 | 2786.7264 | 0.50762 | 256.4484 | 0.078393
2856 | MCLU-135to240-WRf-CZ10-2003-17.5IEER | CZ10 | WRf | 2003 | 135to240 | 12 | 17.5 | 14.4381 | 267596.9971 | 36.7076 | 268008.5377 | 36.782 | 411.5406 | 0.074333
2857 | MCLU-135to240-WRf-CZ10-2007-17.5IEER | CZ10 | WRf | 2007 | 135to240 | 12 | 17.5 | 13.0557 | 284471.1011 | 37.676 | 284914.4697 | 37.7535 | 443.3686 | 0.077557
2858 | MCLU-135to240-WRf-CZ10-2011-17.5IEER | CZ10 | WRf | 2011 | 135to240 | 12 | 17.5 | 13.2245 | 271259.3555 | 34.8103 | 271704.6574 | 34.882 | 445.3019 | 0.071782
2859 | MCLU-135to240-WRf-CZ10-2015-17.5IEER | CZ10 | WRf | 2015 | 135to240 | 12 | 17.5 | 14.8449 | 241354.8744 | 31.0108 | 241602.9114 | 31.0628 | 248.037 | 0.052042
2860 | MCLU-135to240-WRf-CZ10-2020-17.5IEER | CZ10 | WRf | 2020 | 135to240 | 12 | 17.5 | 14.5444 | 232661.5244 | 29.7917 | 232913.532 | 29.8476 | 252.0076 | 0.055875
2861 | MCLU-135to240-Asm-CZ11-2003-17.5IEER | CZ11 | Asm | 2003 | 135to240 | 12 | 17.5 | 433.9864 | 1928.5788 | 0.74194 | 2245.2973 | 0.88922 | 316.7185 | 0.14728
2862 | MCLU-135to240-Asm-CZ11-2007-17.5IEER | CZ11 | Asm | 2007 | 135to240 | 12 | 17.5 | 430.7487 | 1939.0976 | 0.74454 | 2255.7671 | 0.89145 | 316.6695 | 0.14691
2863 | MCLU-135to240-Asm-CZ11-2011-17.5IEER | CZ11 | Asm | 2011 | 135to240 | 12 | 17.5 | 414.8281 | 1997.4862 | 0.7432 | 2313.7427 | 0.89039 | 316.2564 | 0.14719
2864 | MCLU-135to240-Asm-CZ11-2015-17.5IEER | CZ11 | Asm | 2015 | 135to240 | 12 | 17.5 | 403.5312 | 2009.2477 | 0.74039 | 2324.3081 | 0.88852 | 315.0605 | 0.14813
2865 | MCLU-135to240-Asm-CZ11-2020-17.5IEER | CZ11 | Asm | 2020 | 135to240 | 12 | 17.5 | 396.0328 | 1896.4708 | 0.71789 | 2211.117 | 0.86616 | 314.6461 | 0.14827
2866 | MCLU-135to240-ECC-CZ11-2003-17.5IEER | CZ11 | ECC | 2003 | 135to240 | 12 | 17.5 | 908.9867 | 2449.3581 | 0.49981 | 2684.5141 | 0.63667 | 235.156 | 0.13686
2867 | MCLU-135to240-ECC-CZ11-2007-17.5IEER | CZ11 | ECC | 2007 | 135to240 | 12 | 17.5 | 906.8026 | 2453.8191 | 0.49922 | 2688.5271 | 0.63599 | 234.708 | 0.13678
2868 | MCLU-135to240-ECC-CZ11-2011-17.5IEER | CZ11 | ECC | 2011 | 135to240 | 12 | 17.5 | 883.9192 | 2493.3458 | 0.48575 | 2724.0606 | 0.62198 | 230.7148 | 0.13622
2869 | MCLU-135to240-ECC-CZ11-2015-17.5IEER | CZ11 | ECC | 2015 | 135to240 | 12 | 17.5 | 844.1553 | 2552.0267 | 0.47677 | 2782.0035 | 0.61488 | 229.9768 | 0.13811
2870 | MCLU-135to240-ECC-CZ11-2020-17.5IEER | CZ11 | ECC | 2020 | 135to240 | 12 | 17.5 | 813.5123 | 2254.3346 | 0.45178 | 2487.3259 | 0.58876 | 232.9914 | 0.13698
2871 | MCLU-135to240-EPr-CZ11-2003-17.5IEER | CZ11 | EPr | 2003 | 135to240 | 12 | 17.5 | 155.0726 | 1563.7718 | 0.14405 | 1707.0803 | 0.19083 | 143.3085 | 0.046784
2872 | MCLU-135to240-EPr-CZ11-2007-17.5IEER | CZ11 | EPr | 2007 | 135to240 | 12 | 17.5 | 153.5926 | 1574.8503 | 0.14116 | 1717.8345 | 0.18713 | 142.9842 | 0.045973
2873 | MCLU-135to240-EPr-CZ11-2011-17.5IEER | CZ11 | EPr | 2011 | 135to240 | 12 | 17.5 | 150.0955 | 1604.5827 | 0.13674 | 1747.0496 | 0.18018 | 142.4669 | 0.043442
2874 | MCLU-135to240-EPr-CZ11-2015-17.5IEER | CZ11 | EPr | 2015 | 135to240 | 12 | 17.5 | 141.6743 | 1635.8582 | 0.11151 | 1775.6217 | 0.14547 | 139.7635 | 0.033959
2875 | MCLU-135to240-EPr-CZ11-2020-17.5IEER | CZ11 | EPr | 2020 | 135to240 | 12 | 17.5 | 134.8888 | 1464.3136 | 0.093476 | 1604.9913 | 0.12329 | 140.6777 | 0.029817
2876 | MCLU-135to240-ERC-CZ11-2003-17.5IEER | CZ11 | ERC | 2003 | 135to240 | 12 | 17.5 | 7.1463 | 1309.0301 | 0.19782 | 1437.9528 | 0.26827 | 128.9227 | 0.070451
2877 | MCLU-135to240-ERC-CZ11-2007-17.5IEER | CZ11 | ERC | 2007 | 135to240 | 12 | 17.5 | 7.1178 | 1313.4432 | 0.19645 | 1441.6424 | 0.26538 | 128.1992 | 0.068926
2878 | MCLU-135to240-ERC-CZ11-2011-17.5IEER | CZ11 | ERC | 2011 | 135to240 | 12 | 17.5 | 6.9 | 1342.2993 | 0.18611 | 1467.1238 | 0.24819 | 124.8245 | 0.062074
2879 | MCLU-135to240-ERC-CZ11-2015-17.5IEER | CZ11 | ERC | 2015 | 135to240 | 12 | 17.5 | 6.7943 | 1302.3067 | 0.17538 | 1413.1387 | 0.23367 | 110.832 | 0.058295
2880 | MCLU-135to240-ERC-CZ11-2020-17.5IEER | CZ11 | ERC | 2020 | 135to240 | 12 | 17.5 | 6.5005 | 1160.1381 | 0.16152 | 1270.6246 | 0.2154 | 110.4865 | 0.053882
2881 | MCLU-135to240-ESe-CZ11-2003-17.5IEER | CZ11 | ESe | 2003 | 135to240 | 12 | 17.5 | 458.4787 | 1748.2128 | 0.20505 | 1915.0927 | 0.2638 | 166.8799 | 0.058743
2882 | MCLU-135to240-ESe-CZ11-2007-17.5IEER | CZ11 | ESe | 2007 | 135to240 | 12 | 17.5 | 456.636 | 1753.8342 | 0.20437 | 1920.4526 | 0.26253 | 166.6184 | 0.05816
2883 | MCLU-135to240-ESe-CZ11-2011-17.5IEER | CZ11 | ESe | 2011 | 135to240 | 12 | 17.5 | 444.3995 | 1781.2114 | 0.18789 | 1941.9327 | 0.2384 | 160.7213 | 0.050518
2884 | MCLU-135to240-ESe-CZ11-2015-17.5IEER | CZ11 | ESe | 2015 | 135to240 | 12 | 17.5 | 431.2322 | 1791.7249 | 0.17178 | 1949.1225 | 0.21585 | 157.3976 | 0.044075
2885 | MCLU-135to240-ESe-CZ11-2020-17.5IEER | CZ11 | ESe | 2020 | 135to240 | 12 | 17.5 | 415.3177 | 1572.2111 | 0.15481 | 1731.5962 | 0.19775 | 159.385 | 0.042942
2886 | MCLU-135to240-EUn-CZ11-2003-17.5IEER | CZ11 | EUn | 2003 | 135to240 | 12 | 17.5 | 2751.9579 | 2649.1226 | 0.73573 | 2886.8283 | 0.87796 | 237.7057 | 0.14223
2887 | MCLU-135to240-EUn-CZ11-2007-17.5IEER | CZ11 | EUn | 2007 | 135to240 | 12 | 17.5 | 2735.2059 | 2640.9738 | 0.72634 | 2878.4035 | 0.86864 | 237.4297 | 0.1423
2888 | MCLU-135to240-EUn-CZ11-2011-17.5IEER | CZ11 | EUn | 2011 | 135to240 | 12 | 17.5 | 2633.7574 | 2717.6239 | 0.72492 | 2953.5239 | 0.86859 | 235.9001 | 0.14367
2889 | MCLU-135to240-EUn-CZ11-2015-17.5IEER | CZ11 | EUn | 2015 | 135to240 | 12 | 17.5 | 2477.7755 | 2795.6203 | 0.7214 | 3032.686 | 0.86931 | 237.0656 | 0.14791
2890 | MCLU-135to240-EUn-CZ11-2020-17.5IEER | CZ11 | EUn | 2020 | 135to240 | 12 | 17.5 | 2390.0536 | 2560.6042 | 0.69793 | 2798.7729 | 0.8448 | 238.1687 | 0.14687
2891 | MCLU-135to240-Gro-CZ11-2003-17.5IEER | CZ11 | Gro | 2003 | 135to240 | 12 | 17.5 | 149.6378 | 11318.4506 | 1.8652 | 11716.3684 | 2.0118 | 397.9178 | 0.14656
2892 | MCLU-135to240-Gro-CZ11-2007-17.5IEER | CZ11 | Gro | 2007 | 135to240 | 12 | 17.5 | 147.0559 | 10455.3478 | 1.76 | 10834.728 | 1.911 | 379.3801 | 0.15107
2893 | MCLU-135to240-Gro-CZ11-2011-17.5IEER | CZ11 | Gro | 2011 | 135to240 | 12 | 17.5 | 136.3442 | 11232.7324 | 1.8506 | 11607.8804 | 2.0032 | 375.1479 | 0.15263
2894 | MCLU-135to240-Gro-CZ11-2015-17.5IEER | CZ11 | Gro | 2015 | 135to240 | 12 | 17.5 | 131.6168 | 11135.6598 | 1.8286 | 11506.1506 | 1.9792 | 370.4908 | 0.15056
2895 | MCLU-135to240-Gro-CZ11-2020-17.5IEER | CZ11 | Gro | 2020 | 135to240 | 12 | 17.5 | 126.9746 | 11176.2024 | 1.8242 | 11542.2055 | 1.9734 | 366.0031 | 0.14921
2896 | MCLU-135to240-Hsp-CZ11-2003-17.5IEER | CZ11 | Hsp | 2003 | 135to240 | 12 | 17.5 | 686.3413 | 4388.2489 | 0.88051 | 4853.7656 | 1.0588 | 465.5167 | 0.17825
2897 | MCLU-135to240-Hsp-CZ11-2007-17.5IEER | CZ11 | Hsp | 2007 | 135to240 | 12 | 17.5 | 686.1782 | 4388.1135 | 0.87951 | 4853.3471 | 1.0576 | 465.2336 | 0.17805
2898 | MCLU-135to240-Hsp-CZ11-2011-17.5IEER | CZ11 | Hsp | 2011 | 135to240 | 12 | 17.5 | 680.4571 | 4392.1569 | 0.85327 | 4856.2201 | 1.0339 | 464.0632 | 0.18063
2899 | MCLU-135to240-Hsp-CZ11-2015-17.5IEER | CZ11 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 4354.9448 | 0.83674 | 4819.3796 | 1.0189 | 464.4348 | 0.18216
2900 | MCLU-135to240-Hsp-CZ11-2020-17.5IEER | CZ11 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3829.9598 | 0.7536 | 4295.3583 | 0.93567 | 465.3985 | 0.18207
2901 | MCLU-135to240-Htl-CZ11-2003-17.5IEER | CZ11 | Htl | 2003 | 135to240 | 12 | 17.5 | 301.7902 | 3286.5592 | 0.98525 | 3392.544 | 1.0301 | 105.9847 | 0.044808
2902 | MCLU-135to240-Htl-CZ11-2007-17.5IEER | CZ11 | Htl | 2007 | 135to240 | 12 | 17.5 | 301.3691 | 3147.3383 | 0.91656 | 3253.4004 | 0.96135 | 106.062 | 0.04479
2903 | MCLU-135to240-Htl-CZ11-2011-17.5IEER | CZ11 | Htl | 2011 | 135to240 | 12 | 17.5 | 291.1523 | 3185.8645 | 0.91986 | 3291.9553 | 0.9649 | 106.0907 | 0.04504
2904 | MCLU-135to240-Htl-CZ11-2015-17.5IEER | CZ11 | Htl | 2015 | 135to240 | 12 | 17.5 | 261.3204 | 3276.143 | 0.91486 | 3387.8562 | 0.96341 | 111.7132 | 0.048547
2905 | MCLU-135to240-Htl-CZ11-2020-17.5IEER | CZ11 | Htl | 2020 | 135to240 | 12 | 17.5 | 259.3332 | 3187.526 | 0.90434 | 3297.7416 | 0.95181 | 110.2156 | 0.047478
2906 | MCLU-135to240-MBT-CZ11-2003-17.5IEER | CZ11 | MBT | 2003 | 135to240 | 12 | 17.5 | 446.0467 | 3409.1377 | 0.58015 | 3628.238 | 0.71644 | 219.1003 | 0.13629
2907 | MCLU-135to240-MBT-CZ11-2007-17.5IEER | CZ11 | MBT | 2007 | 135to240 | 12 | 17.5 | 438.4871 | 3463.6394 | 0.58377 | 3680.7406 | 0.7198 | 217.1013 | 0.13603
2908 | MCLU-135to240-MBT-CZ11-2011-17.5IEER | CZ11 | MBT | 2011 | 135to240 | 12 | 17.5 | 414.0777 | 3603.9678 | 0.5914 | 3817.0434 | 0.72806 | 213.0756 | 0.13667
2909 | MCLU-135to240-MBT-CZ11-2015-17.5IEER | CZ11 | MBT | 2015 | 135to240 | 12 | 17.5 | 404.6533 | 3646.1697 | 0.59254 | 3858.8626 | 0.73007 | 212.693 | 0.13753
2910 | MCLU-135to240-MBT-CZ11-2020-17.5IEER | CZ11 | MBT | 2020 | 135to240 | 12 | 17.5 | 379.3007 | 3487.0216 | 0.57466 | 3699.2186 | 0.71361 | 212.197 | 0.13894
2911 | MCLU-135to240-MLI-CZ11-2003-17.5IEER | CZ11 | MLI | 2003 | 135to240 | 12 | 17.5 | 283.6372 | 2505.1024 | 0.45752 | 2720.631 | 0.55749 | 215.5287 | 0.099974
2912 | MCLU-135to240-MLI-CZ11-2007-17.5IEER | CZ11 | MLI | 2007 | 135to240 | 12 | 17.5 | 278.0136 | 2548.4684 | 0.45939 | 2763.4839 | 0.55963 | 215.0155 | 0.10024
2913 | MCLU-135to240-MLI-CZ11-2011-17.5IEER | CZ11 | MLI | 2011 | 135to240 | 12 | 17.5 | 244.6373 | 2847.857 | 0.46983 | 3058.9597 | 0.5688 | 211.1028 | 0.09897
2914 | MCLU-135to240-MLI-CZ11-2015-17.5IEER | CZ11 | MLI | 2015 | 135to240 | 12 | 17.5 | 242.5351 | 2851.165 | 0.46969 | 3062.295 | 0.56887 | 211.1299 | 0.099184
2915 | MCLU-135to240-MLI-CZ11-2020-17.5IEER | CZ11 | MLI | 2020 | 135to240 | 12 | 17.5 | 227.2176 | 2564.3556 | 0.43869 | 2775.7866 | 0.53913 | 211.431 | 0.10044
2916 | MCLU-135to240-Mtl-CZ11-2003-17.5IEER | CZ11 | Mtl | 2003 | 135to240 | 12 | 17.5 | 54.1491 | 3285.9837 | 0.94531 | 3371.6154 | 0.97472 | 85.6317 | 0.029416
2917 | MCLU-135to240-Mtl-CZ11-2007-17.5IEER | CZ11 | Mtl | 2007 | 135to240 | 12 | 17.5 | 54.1491 | 3133.3809 | 0.8705 | 3218.8085 | 0.89986 | 85.4276 | 0.029358
2918 | MCLU-135to240-Mtl-CZ11-2011-17.5IEER | CZ11 | Mtl | 2011 | 135to240 | 12 | 17.5 | 51.7623 | 3168.1591 | 0.87654 | 3253.6938 | 0.90587 | 85.5347 | 0.029324
2919 | MCLU-135to240-Mtl-CZ11-2015-17.5IEER | CZ11 | Mtl | 2015 | 135to240 | 12 | 17.5 | 43.8173 | 3317.5411 | 0.87424 | 3409.062 | 0.90614 | 91.5209 | 0.0319
2920 | MCLU-135to240-Mtl-CZ11-2020-17.5IEER | CZ11 | Mtl | 2020 | 135to240 | 12 | 17.5 | 43.6777 | 3247.0848 | 0.86529 | 3337.2038 | 0.89682 | 90.119 | 0.031532
2921 | MCLU-135to240-Nrs-CZ11-2003-17.5IEER | CZ11 | Nrs | 2003 | 135to240 | 12 | 17.5 | 186.1565 | 4565.4183 | 1.041 | 4790.0379 | 1.1275 | 224.6197 | 0.086493
2922 | MCLU-135to240-Nrs-CZ11-2007-17.5IEER | CZ11 | Nrs | 2007 | 135to240 | 12 | 17.5 | 185.9831 | 4472.4214 | 0.99743 | 4696.9762 | 1.0837 | 224.5548 | 0.086247
2923 | MCLU-135to240-Nrs-CZ11-2011-17.5IEER | CZ11 | Nrs | 2011 | 135to240 | 12 | 17.5 | 184.4728 | 4514.8378 | 0.9913 | 4738.8329 | 1.0774 | 223.9952 | 0.086097
2924 | MCLU-135to240-Nrs-CZ11-2015-17.5IEER | CZ11 | Nrs | 2015 | 135to240 | 12 | 17.5 | 182.8098 | 4417.1789 | 0.93182 | 4639.7117 | 1.0183 | 222.5327 | 0.086525
2925 | MCLU-135to240-Nrs-CZ11-2020-17.5IEER | CZ11 | Nrs | 2020 | 135to240 | 12 | 17.5 | 182.1215 | 4056.9384 | 0.86527 | 4279.0569 | 0.95091 | 222.1185 | 0.085633
2926 | MCLU-135to240-OfL-CZ11-2003-17.5IEER | CZ11 | OfL | 2003 | 135to240 | 12 | 17.5 | 523.0608 | 3155.5966 | 0.54596 | 3364.1097 | 0.61739 | 208.5131 | 0.071433
2927 | MCLU-135to240-OfL-CZ11-2007-17.5IEER | CZ11 | OfL | 2007 | 135to240 | 12 | 17.5 | 522.5201 | 3158.2692 | 0.54608 | 3366.6503 | 0.61742 | 208.3811 | 0.071347
2928 | MCLU-135to240-OfL-CZ11-2011-17.5IEER | CZ11 | OfL | 2011 | 135to240 | 12 | 17.5 | 498.2662 | 3255.916 | 0.54865 | 3460.3236 | 0.61837 | 204.4075 | 0.069718
2929 | MCLU-135to240-OfL-CZ11-2015-17.5IEER | CZ11 | OfL | 2015 | 135to240 | 12 | 17.5 | 501.1831 | 3184.0384 | 0.54112 | 3389.4632 | 0.61012 | 205.4248 | 0.069006
2930 | MCLU-135to240-OfL-CZ11-2020-17.5IEER | CZ11 | OfL | 2020 | 135to240 | 12 | 17.5 | 489.1 | 3029.4529 | 0.52263 | 3236.0209 | 0.59136 | 206.568 | 0.068737
2931 | MCLU-135to240-OfS-CZ11-2003-17.5IEER | CZ11 | OfS | 2003 | 135to240 | 12 | 17.5 | 36.1202 | 2346.4698 | 0.43374 | 2558.4805 | 0.50637 | 212.0106 | 0.072632
2932 | MCLU-135to240-OfS-CZ11-2007-17.5IEER | CZ11 | OfS | 2007 | 135to240 | 12 | 17.5 | 36.0169 | 2351.6854 | 0.43358 | 2563.3417 | 0.50585 | 211.6563 | 0.072278
2933 | MCLU-135to240-OfS-CZ11-2011-17.5IEER | CZ11 | OfS | 2011 | 135to240 | 12 | 17.5 | 35.2852 | 2370.3312 | 0.43038 | 2580.8143 | 0.50115 | 210.4832 | 0.070768
2934 | MCLU-135to240-OfS-CZ11-2015-17.5IEER | CZ11 | OfS | 2015 | 135to240 | 12 | 17.5 | 32.1987 | 2510.1595 | 0.43311 | 2717.2368 | 0.50162 | 207.0773 | 0.068517
2935 | MCLU-135to240-OfS-CZ11-2020-17.5IEER | CZ11 | OfS | 2020 | 135to240 | 12 | 17.5 | 31.0987 | 2395.2767 | 0.41437 | 2602.2432 | 0.48198 | 206.9665 | 0.067618
2936 | MCLU-135to240-RFF-CZ11-2003-17.5IEER | CZ11 | RFF | 2003 | 135to240 | 12 | 17.5 | 9.6396 | 4596.6351 | 1.1563 | 4972.0164 | 1.3209 | 375.3813 | 0.16462
2937 | MCLU-135to240-RFF-CZ11-2007-17.5IEER | CZ11 | RFF | 2007 | 135to240 | 12 | 17.5 | 9.5326 | 4642.3104 | 1.1638 | 5018.5966 | 1.3285 | 376.2862 | 0.1647
2938 | MCLU-135to240-RFF-CZ11-2011-17.5IEER | CZ11 | RFF | 2011 | 135to240 | 12 | 17.5 | 8.952 | 4899.4539 | 1.1948 | 5278.0333 | 1.3597 | 378.5794 | 0.16491
2939 | MCLU-135to240-RFF-CZ11-2015-17.5IEER | CZ11 | RFF | 2015 | 135to240 | 12 | 17.5 | 8.9272 | 4691.4957 | 1.1582 | 5072.9345 | 1.3241 | 381.4388 | 0.16589
2940 | MCLU-135to240-RFF-CZ11-2020-17.5IEER | CZ11 | RFF | 2020 | 135to240 | 12 | 17.5 | 8.5702 | 4311.3191 | 1.1014 | 4695.8312 | 1.2676 | 384.5121 | 0.16623
2941 | MCLU-135to240-RSD-CZ11-2003-17.5IEER | CZ11 | RSD | 2003 | 135to240 | 12 | 17.5 | 17.8071 | 4398.1333 | 1.1093 | 4720.1249 | 1.2831 | 321.9916 | 0.17381
2942 | MCLU-135to240-RSD-CZ11-2007-17.5IEER | CZ11 | RSD | 2007 | 135to240 | 12 | 17.5 | 17.5921 | 4445.9602 | 1.1169 | 4768.7962 | 1.29 | 322.836 | 0.1731
2943 | MCLU-135to240-RSD-CZ11-2011-17.5IEER | CZ11 | RSD | 2011 | 135to240 | 12 | 17.5 | 17.2012 | 4538.007 | 1.1304 | 4862.8772 | 1.3019 | 324.8701 | 0.17156
2944 | MCLU-135to240-RSD-CZ11-2015-17.5IEER | CZ11 | RSD | 2015 | 135to240 | 12 | 17.5 | 17.0344 | 4381.8171 | 1.1043 | 4707.1941 | 1.275 | 325.377 | 0.17066
2945 | MCLU-135to240-RSD-CZ11-2020-17.5IEER | CZ11 | RSD | 2020 | 135to240 | 12 | 17.5 | 16.0979 | 3944.9768 | 1.0331 | 4276.7078 | 1.2 | 331.7309 | 0.16691
2946 | MCLU-135to240-Rt3-CZ11-2003-17.5IEER | CZ11 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 325.9152 | 4454.8941 | 1.0539 | 4775.571 | 1.2437 | 320.6769 | 0.18978
2947 | MCLU-135to240-Rt3-CZ11-2007-17.5IEER | CZ11 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 324.7061 | 4469.4458 | 1.055 | 4789.5213 | 1.2446 | 320.0755 | 0.18961
2948 | MCLU-135to240-Rt3-CZ11-2011-17.5IEER | CZ11 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 303.8044 | 4747.9376 | 1.0772 | 5059.4213 | 1.2714 | 311.4837 | 0.1942
2949 | MCLU-135to240-Rt3-CZ11-2015-17.5IEER | CZ11 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 294.4644 | 4435.9708 | 1.0258 | 4752.8611 | 1.2229 | 316.8903 | 0.19712
2950 | MCLU-135to240-Rt3-CZ11-2020-17.5IEER | CZ11 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 282.5471 | 4118.7238 | 0.97571 | 4440.0387 | 1.1755 | 321.3149 | 0.19982
2951 | MCLU-135to240-RtL-CZ11-2003-17.5IEER | CZ11 | RtL | 2003 | 135to240 | 12 | 17.5 | 285.5465 | 4826.1213 | 1.1359 | 5176.9123 | 1.3341 | 350.791 | 0.19825
2952 | MCLU-135to240-RtL-CZ11-2007-17.5IEER | CZ11 | RtL | 2007 | 135to240 | 12 | 17.5 | 280.9241 | 4898.5586 | 1.1452 | 5247.405 | 1.3444 | 348.8464 | 0.19919
2953 | MCLU-135to240-RtL-CZ11-2011-17.5IEER | CZ11 | RtL | 2011 | 135to240 | 12 | 17.5 | 266.7403 | 5144.8943 | 1.1719 | 5486.4748 | 1.3748 | 341.5806 | 0.20288
2954 | MCLU-135to240-RtL-CZ11-2015-17.5IEER | CZ11 | RtL | 2015 | 135to240 | 12 | 17.5 | 259.3406 | 4946.9773 | 1.1526 | 5292.4684 | 1.3574 | 345.4911 | 0.20477
2955 | MCLU-135to240-RtL-CZ11-2020-17.5IEER | CZ11 | RtL | 2020 | 135to240 | 12 | 17.5 | 244.5213 | 4762.8375 | 1.1439 | 5110.0523 | 1.3525 | 347.2148 | 0.20856
2956 | MCLU-135to240-RtS-CZ11-2003-17.5IEER | CZ11 | RtS | 2003 | 135to240 | 12 | 17.5 | 21.5599 | 3043.1079 | 0.79974 | 3405.8537 | 0.96413 | 362.7458 | 0.16439
2957 | MCLU-135to240-RtS-CZ11-2007-17.5IEER | CZ11 | RtS | 2007 | 135to240 | 12 | 17.5 | 21.2267 | 3084.3625 | 0.80418 | 3447.1019 | 0.9689 | 362.7394 | 0.16472
2958 | MCLU-135to240-RtS-CZ11-2011-17.5IEER | CZ11 | RtS | 2011 | 135to240 | 12 | 17.5 | 19.8539 | 3265.5841 | 0.8157 | 3624.8663 | 0.98234 | 359.2822 | 0.16663
2959 | MCLU-135to240-RtS-CZ11-2015-17.5IEER | CZ11 | RtS | 2015 | 135to240 | 12 | 17.5 | 19.6273 | 2990.4655 | 0.77482 | 3315.4069 | 0.94364 | 324.9414 | 0.16882
2960 | MCLU-135to240-RtS-CZ11-2020-17.5IEER | CZ11 | RtS | 2020 | 135to240 | 12 | 17.5 | 18.8197 | 2843.9124 | 0.75375 | 3169.6599 | 0.92433 | 325.7475 | 0.17059
2961 | MCLU-135to240-SCn-CZ11-2003-17.5IEER | CZ11 | SCn | 2003 | 135to240 | 12 | 17.5 | 376.8908 | 2243.8425 | 0.3854 | 2532.976 | 0.49153 | 289.1334 | 0.10614
2962 | MCLU-135to240-SCn-CZ11-2007-17.5IEER | CZ11 | SCn | 2007 | 135to240 | 12 | 17.5 | 360.1393 | 2329.8507 | 0.39161 | 2619.117 | 0.49908 | 289.2663 | 0.10747
2963 | MCLU-135to240-SCn-CZ11-2011-17.5IEER | CZ11 | SCn | 2011 | 135to240 | 12 | 17.5 | 310 | 2650.9375 | 0.41378 | 2946.0717 | 0.52092 | 295.1342 | 0.10714
2964 | MCLU-135to240-SCn-CZ11-2015-17.5IEER | CZ11 | SCn | 2015 | 135to240 | 12 | 17.5 | 310.9321 | 2606.2905 | 0.40888 | 2892.4046 | 0.51644 | 286.114 | 0.10756
2965 | MCLU-135to240-SCn-CZ11-2020-17.5IEER | CZ11 | SCn | 2020 | 135to240 | 12 | 17.5 | 283.2272 | 2487.3919 | 0.40361 | 2775.0417 | 0.50629 | 287.6499 | 0.10268
2966 | MCLU-135to240-WRf-CZ11-2003-17.5IEER | CZ11 | WRf | 2003 | 135to240 | 12 | 17.5 | 14.7073 | 260076.805 | 36.1846 | 260504.3229 | 36.2859 | 427.518 | 0.10134
2967 | MCLU-135to240-WRf-CZ11-2007-17.5IEER | CZ11 | WRf | 2007 | 135to240 | 12 | 17.5 | 14.2444 | 259760.164 | 34.3032 | 260208.2197 | 34.4091 | 448.0557 | 0.10587
2968 | MCLU-135to240-WRf-CZ11-2011-17.5IEER | CZ11 | WRf | 2011 | 135to240 | 12 | 17.5 | 13.8146 | 258166.6288 | 32.9846 | 258589.7877 | 33.0738 | 423.1588 | 0.089201
2969 | MCLU-135to240-WRf-CZ11-2015-17.5IEER | CZ11 | WRf | 2015 | 135to240 | 12 | 17.5 | 16.1336 | 220737.145 | 28.2231 | 220996.0501 | 28.2915 | 258.9051 | 0.068408
2970 | MCLU-135to240-WRf-CZ11-2020-17.5IEER | CZ11 | WRf | 2020 | 135to240 | 12 | 17.5 | 16.2111 | 207393.393 | 26.4796 | 207636.4916 | 26.5482 | 243.0986 | 0.068605
2971 | MCLU-135to240-Asm-CZ12-2003-17.5IEER | CZ12 | Asm | 2003 | 135to240 | 12 | 17.5 | 382.1831 | 2031.1406 | 0.82362 | 2315.9998 | 0.96003 | 284.8592 | 0.13641
2972 | MCLU-135to240-Asm-CZ12-2007-17.5IEER | CZ12 | Asm | 2007 | 135to240 | 12 | 17.5 | 379.2192 | 2043.4305 | 0.82729 | 2328.3664 | 0.96349 | 284.9359 | 0.1362
2973 | MCLU-135to240-Asm-CZ12-2011-17.5IEER | CZ12 | Asm | 2011 | 135to240 | 12 | 17.5 | 372.0114 | 2078.0448 | 0.83144 | 2363.3878 | 0.96735 | 285.3429 | 0.13592
2974 | MCLU-135to240-Asm-CZ12-2015-17.5IEER | CZ12 | Asm | 2015 | 135to240 | 12 | 17.5 | 361.8626 | 2094.7501 | 0.83264 | 2378.9522 | 0.96914 | 284.2021 | 0.1365
2975 | MCLU-135to240-Asm-CZ12-2020-17.5IEER | CZ12 | Asm | 2020 | 135to240 | 12 | 17.5 | 354.7595 | 1970.3511 | 0.80944 | 2254.3234 | 0.94586 | 283.9723 | 0.13642
2976 | MCLU-135to240-ECC-CZ12-2003-17.5IEER | CZ12 | ECC | 2003 | 135to240 | 12 | 17.5 | 810.1927 | 2608.4562 | 0.53195 | 2811.2201 | 0.64211 | 202.7639 | 0.11016
2977 | MCLU-135to240-ECC-CZ12-2007-17.5IEER | CZ12 | ECC | 2007 | 135to240 | 12 | 17.5 | 808.2822 | 2613.5901 | 0.53184 | 2816.2347 | 0.64174 | 202.6446 | 0.10989
2978 | MCLU-135to240-ECC-CZ12-2011-17.5IEER | CZ12 | ECC | 2011 | 135to240 | 12 | 17.5 | 799.3418 | 2636.112 | 0.52755 | 2838.5329 | 0.63681 | 202.4209 | 0.10926
2979 | MCLU-135to240-ECC-CZ12-2015-17.5IEER | CZ12 | ECC | 2015 | 135to240 | 12 | 17.5 | 764.4466 | 2704.1527 | 0.52016 | 2906.6496 | 0.63111 | 202.4968 | 0.11095
2980 | MCLU-135to240-ECC-CZ12-2020-17.5IEER | CZ12 | ECC | 2020 | 135to240 | 12 | 17.5 | 734.8164 | 2380.5434 | 0.49368 | 2586.3338 | 0.60313 | 205.7904 | 0.10945
2981 | MCLU-135to240-EPr-CZ12-2003-17.5IEER | CZ12 | EPr | 2003 | 135to240 | 12 | 17.5 | 131.785 | 1735.6174 | 0.097255 | 1865.5526 | 0.12152 | 129.9352 | 0.024265
2982 | MCLU-135to240-EPr-CZ12-2007-17.5IEER | CZ12 | EPr | 2007 | 135to240 | 12 | 17.5 | 130.3376 | 1751.5242 | 0.096119 | 1881.8225 | 0.11987 | 130.2983 | 0.023751
2983 | MCLU-135to240-EPr-CZ12-2011-17.5IEER | CZ12 | EPr | 2011 | 135to240 | 12 | 17.5 | 127.1392 | 1791.529 | 0.091681 | 1922.7656 | 0.11399 | 131.2366 | 0.022306
2984 | MCLU-135to240-EPr-CZ12-2015-17.5IEER | CZ12 | EPr | 2015 | 135to240 | 12 | 17.5 | 119.5219 | 1847.6533 | 0.066492 | 1978.2858 | 0.079982 | 130.6326 | 0.013489
2985 | MCLU-135to240-EPr-CZ12-2020-17.5IEER | CZ12 | EPr | 2020 | 135to240 | 12 | 17.5 | 113.9737 | 1644.931 | 0.048143 | 1776.6997 | 0.057597 | 131.7688 | 0.0094537
2986 | MCLU-135to240-ERC-CZ12-2003-17.5IEER | CZ12 | ERC | 2003 | 135to240 | 12 | 17.5 | 6.1283 | 1407.6517 | 0.16373 | 1518.9029 | 0.20451 | 111.2512 | 0.040784
2987 | MCLU-135to240-ERC-CZ12-2007-17.5IEER | CZ12 | ERC | 2007 | 135to240 | 12 | 17.5 | 6.1068 | 1411.7413 | 0.16267 | 1523.1672 | 0.20256 | 111.4259 | 0.03989
2988 | MCLU-135to240-ERC-CZ12-2011-17.5IEER | CZ12 | ERC | 2011 | 135to240 | 12 | 17.5 | 5.9414 | 1438.9564 | 0.14703 | 1551.2311 | 0.18253 | 112.2747 | 0.035499
2989 | MCLU-135to240-ERC-CZ12-2015-17.5IEER | CZ12 | ERC | 2015 | 135to240 | 12 | 17.5 | 5.8182 | 1408.3772 | 0.13438 | 1507.6876 | 0.16679 | 99.3104 | 0.032415
2990 | MCLU-135to240-ERC-CZ12-2020-17.5IEER | CZ12 | ERC | 2020 | 135to240 | 12 | 17.5 | 5.636 | 1234.2599 | 0.12396 | 1335.8992 | 0.15665 | 101.6393 | 0.032695
2991 | MCLU-135to240-ESe-CZ12-2003-17.5IEER | CZ12 | ESe | 2003 | 135to240 | 12 | 17.5 | 402.7513 | 1875.3775 | 0.18698 | 2018.226 | 0.23125 | 142.8485 | 0.044275
2992 | MCLU-135to240-ESe-CZ12-2007-17.5IEER | CZ12 | ESe | 2007 | 135to240 | 12 | 17.5 | 401.1605 | 1881.4157 | 0.18633 | 2024.404 | 0.23009 | 142.9883 | 0.043764
2993 | MCLU-135to240-ESe-CZ12-2011-17.5IEER | CZ12 | ESe | 2011 | 135to240 | 12 | 17.5 | 396.5524 | 1898.3981 | 0.1797 | 2040.8471 | 0.2188 | 142.449 | 0.039099
2994 | MCLU-135to240-ESe-CZ12-2015-17.5IEER | CZ12 | ESe | 2015 | 135to240 | 12 | 17.5 | 384.8964 | 1918.0429 | 0.16233 | 2058.6246 | 0.19581 | 140.5817 | 0.033481
2995 | MCLU-135to240-ESe-CZ12-2020-17.5IEER | CZ12 | ESe | 2020 | 135to240 | 12 | 17.5 | 369.1336 | 1680.5221 | 0.14182 | 1822.9642 | 0.17433 | 142.4421 | 0.032505
2996 | MCLU-135to240-EUn-CZ12-2003-17.5IEER | CZ12 | EUn | 2003 | 135to240 | 12 | 17.5 | 2463.6728 | 2792.9398 | 0.78108 | 2998.7884 | 0.89693 | 205.8486 | 0.11586
2997 | MCLU-135to240-EUn-CZ12-2007-17.5IEER | CZ12 | EUn | 2007 | 135to240 | 12 | 17.5 | 2448.3167 | 2788.9716 | 0.77287 | 2994.6526 | 0.88846 | 205.6809 | 0.1156
2998 | MCLU-135to240-EUn-CZ12-2011-17.5IEER | CZ12 | EUn | 2011 | 135to240 | 12 | 17.5 | 2398.4705 | 2830.8867 | 0.77579 | 3038.031 | 0.8916 | 207.1443 | 0.11581
2999 | MCLU-135to240-EUn-CZ12-2015-17.5IEER | CZ12 | EUn | 2015 | 135to240 | 12 | 17.5 | 2253.014 | 2928.5841 | 0.7783 | 3137.0034 | 0.89629 | 208.4192 | 0.11799
3000 | MCLU-135to240-EUn-CZ12-2020-17.5IEER | CZ12 | EUn | 2020 | 135to240 | 12 | 17.5 | 2166.7052 | 2674.7548 | 0.75446 | 2884.4966 | 0.87078 | 209.7418 | 0.11632
3001 | MCLU-135to240-Gro-CZ12-2003-17.5IEER | CZ12 | Gro | 2003 | 135to240 | 12 | 17.5 | 149.6211 | 11150.2759 | 1.8425 | 11526.4509 | 1.9889 | 376.175 | 0.14636
3002 | MCLU-135to240-Gro-CZ12-2007-17.5IEER | CZ12 | Gro | 2007 | 135to240 | 12 | 17.5 | 147.0004 | 10303.5254 | 1.7566 | 10650.833 | 1.9044 | 347.3076 | 0.14779
3003 | MCLU-135to240-Gro-CZ12-2011-17.5IEER | CZ12 | Gro | 2011 | 135to240 | 12 | 17.5 | 141.5735 | 10683.2852 | 1.807 | 11028.875 | 1.9546 | 345.5899 | 0.14768
3004 | MCLU-135to240-Gro-CZ12-2015-17.5IEER | CZ12 | Gro | 2015 | 135to240 | 12 | 17.5 | 136.8956 | 10575.1658 | 1.7858 | 10917.3692 | 1.932 | 342.2033 | 0.14622
3005 | MCLU-135to240-Gro-CZ12-2020-17.5IEER | CZ12 | Gro | 2020 | 135to240 | 12 | 17.5 | 132.2148 | 10603.5726 | 1.7841 | 10942.6645 | 1.9308 | 339.0919 | 0.1467
3006 | MCLU-135to240-Hsp-CZ12-2003-17.5IEER | CZ12 | Hsp | 2003 | 135to240 | 12 | 17.5 | 680.6105 | 4276.4505 | 0.8463 | 4673.7042 | 0.99307 | 397.2536 | 0.14677
3007 | MCLU-135to240-Hsp-CZ12-2007-17.5IEER | CZ12 | Hsp | 2007 | 135to240 | 12 | 17.5 | 680.6105 | 4275.7205 | 0.8454 | 4672.7535 | 0.99193 | 397.033 | 0.14653
3008 | MCLU-135to240-Hsp-CZ12-2011-17.5IEER | CZ12 | Hsp | 2011 | 135to240 | 12 | 17.5 | 680.4571 | 4269.5966 | 0.83433 | 4665.9738 | 0.98088 | 396.3772 | 0.14654
3009 | MCLU-135to240-Hsp-CZ12-2015-17.5IEER | CZ12 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 4236.5648 | 0.82061 | 4633.0319 | 0.96763 | 396.4671 | 0.14703
3010 | MCLU-135to240-Hsp-CZ12-2020-17.5IEER | CZ12 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3717.5307 | 0.73997 | 4117.8796 | 0.88631 | 400.3489 | 0.14634
3011 | MCLU-135to240-Htl-CZ12-2003-17.5IEER | CZ12 | Htl | 2003 | 135to240 | 12 | 17.5 | 276.1602 | 3279.8433 | 0.97786 | 3369.2225 | 1.0146 | 89.3792 | 0.036746
3012 | MCLU-135to240-Htl-CZ12-2007-17.5IEER | CZ12 | Htl | 2007 | 135to240 | 12 | 17.5 | 275.81 | 3154.55 | 0.91192 | 3244.0425 | 0.9486 | 89.4925 | 0.03668
3013 | MCLU-135to240-Htl-CZ12-2011-17.5IEER | CZ12 | Htl | 2011 | 135to240 | 12 | 17.5 | 267.8372 | 3189.0374 | 0.91791 | 3279.6778 | 0.95496 | 90.6404 | 0.037051
3014 | MCLU-135to240-Htl-CZ12-2015-17.5IEER | CZ12 | Htl | 2015 | 135to240 | 12 | 17.5 | 239.6552 | 3308.2224 | 0.91997 | 3403.2374 | 0.95919 | 95.015 | 0.039224
3015 | MCLU-135to240-Htl-CZ12-2020-17.5IEER | CZ12 | Htl | 2020 | 135to240 | 12 | 17.5 | 237.7567 | 3212.8228 | 0.90877 | 3306.5177 | 0.9471 | 93.695 | 0.038327
3016 | MCLU-135to240-MBT-CZ12-2003-17.5IEER | CZ12 | MBT | 2003 | 135to240 | 12 | 17.5 | 399.8362 | 3706.7317 | 0.61564 | 3889.7096 | 0.72991 | 182.9778 | 0.11427
3017 | MCLU-135to240-MBT-CZ12-2007-17.5IEER | CZ12 | MBT | 2007 | 135to240 | 12 | 17.5 | 392.9451 | 3769.9848 | 0.62135 | 3951.1929 | 0.73503 | 181.2082 | 0.11368
3018 | MCLU-135to240-MBT-CZ12-2011-17.5IEER | CZ12 | MBT | 2011 | 135to240 | 12 | 17.5 | 370.5797 | 3937.0766 | 0.63526 | 4114.3026 | 0.74864 | 177.226 | 0.11338
3019 | MCLU-135to240-MBT-CZ12-2015-17.5IEER | CZ12 | MBT | 2015 | 135to240 | 12 | 17.5 | 361.3764 | 3994.2325 | 0.63895 | 4170.9611 | 0.75274 | 176.7286 | 0.1138
3020 | MCLU-135to240-MBT-CZ12-2020-17.5IEER | CZ12 | MBT | 2020 | 135to240 | 12 | 17.5 | 336.9447 | 3836.07 | 0.62359 | 4012.6321 | 0.73725 | 176.5621 | 0.11366
3021 | MCLU-135to240-MLI-CZ12-2003-17.5IEER | CZ12 | MLI | 2003 | 135to240 | 12 | 17.5 | 253.748 | 2687.5225 | 0.47071 | 2874.4821 | 0.54988 | 186.9596 | 0.079175
3022 | MCLU-135to240-MLI-CZ12-2007-17.5IEER | CZ12 | MLI | 2007 | 135to240 | 12 | 17.5 | 248.5607 | 2737.5967 | 0.47525 | 2923.9552 | 0.55451 | 186.3585 | 0.079263
3023 | MCLU-135to240-MLI-CZ12-2011-17.5IEER | CZ12 | MLI | 2011 | 135to240 | 12 | 17.5 | 234.4605 | 2886.5027 | 0.48612 | 3071.2934 | 0.56554 | 184.7907 | 0.079422
3024 | MCLU-135to240-MLI-CZ12-2015-17.5IEER | CZ12 | MLI | 2015 | 135to240 | 12 | 17.5 | 232.3899 | 2891.0452 | 0.48628 | 3075.961 | 0.56574 | 184.9158 | 0.07946
3025 | MCLU-135to240-MLI-CZ12-2020-17.5IEER | CZ12 | MLI | 2020 | 135to240 | 12 | 17.5 | 217.7749 | 2592.1226 | 0.45321 | 2777.5585 | 0.53311 | 185.4358 | 0.079901
3026 | MCLU-135to240-Mtl-CZ12-2003-17.5IEER | CZ12 | Mtl | 2003 | 135to240 | 12 | 17.5 | 50.2192 | 3218.0603 | 0.92022 | 3289.3419 | 0.94432 | 71.2816 | 0.024104
3027 | MCLU-135to240-Mtl-CZ12-2007-17.5IEER | CZ12 | Mtl | 2007 | 135to240 | 12 | 17.5 | 50.2192 | 3084.2575 | 0.84978 | 3155.4959 | 0.87385 | 71.2384 | 0.024075
3028 | MCLU-135to240-Mtl-CZ12-2011-17.5IEER | CZ12 | Mtl | 2011 | 135to240 | 12 | 17.5 | 48.7807 | 3111.2543 | 0.8537 | 3182.5286 | 0.87769 | 71.2743 | 0.023994
3029 | MCLU-135to240-Mtl-CZ12-2015-17.5IEER | CZ12 | Mtl | 2015 | 135to240 | 12 | 17.5 | 41.3975 | 3293.4364 | 0.86062 | 3369.3885 | 0.88632 | 75.9521 | 0.025693
3030 | MCLU-135to240-Mtl-CZ12-2020-17.5IEER | CZ12 | Mtl | 2020 | 135to240 | 12 | 17.5 | 41.2625 | 3219.1568 | 0.85105 | 3294.2203 | 0.87631 | 75.0635 | 0.025267
3031 | MCLU-135to240-Nrs-CZ12-2003-17.5IEER | CZ12 | Nrs | 2003 | 135to240 | 12 | 17.5 | 183.2867 | 4457.937 | 1.0008 | 4655.1847 | 1.0731 | 197.2477 | 0.072251
3032 | MCLU-135to240-Nrs-CZ12-2007-17.5IEER | CZ12 | Nrs | 2007 | 135to240 | 12 | 17.5 | 183.2409 | 4373.072 | 0.96105 | 4570.2964 | 1.033 | 197.2244 | 0.071973
3033 | MCLU-135to240-Nrs-CZ12-2011-17.5IEER | CZ12 | Nrs | 2011 | 135to240 | 12 | 17.5 | 182.872 | 4396.2899 | 0.95169 | 4592.3243 | 1.0233 | 196.0344 | 0.071581
3034 | MCLU-135to240-Nrs-CZ12-2015-17.5IEER | CZ12 | Nrs | 2015 | 135to240 | 12 | 17.5 | 181.9847 | 4298.6363 | 0.89547 | 4493.0467 | 0.96705 | 194.4103 | 0.071582
3035 | MCLU-135to240-Nrs-CZ12-2020-17.5IEER | CZ12 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.7306 | 3926.8284 | 0.83344 | 4121.8687 | 0.90434 | 195.0403 | 0.070904
3036 | MCLU-135to240-OfL-CZ12-2003-17.5IEER | CZ12 | OfL | 2003 | 135to240 | 12 | 17.5 | 486.0733 | 3297.8145 | 0.56675 | 3472.438 | 0.62399 | 174.6236 | 0.057241
3037 | MCLU-135to240-OfL-CZ12-2007-17.5IEER | CZ12 | OfL | 2007 | 135to240 | 12 | 17.5 | 485.614 | 3300.5395 | 0.56695 | 3475.078 | 0.62415 | 174.5384 | 0.057198
3038 | MCLU-135to240-OfL-CZ12-2011-17.5IEER | CZ12 | OfL | 2011 | 135to240 | 12 | 17.5 | 464.5576 | 3401.7074 | 0.57151 | 3571.8539 | 0.62855 | 170.1465 | 0.057045
3039 | MCLU-135to240-OfL-CZ12-2015-17.5IEER | CZ12 | OfL | 2015 | 135to240 | 12 | 17.5 | 465.1869 | 3337.4281 | 0.56574 | 3509.3398 | 0.62129 | 171.9117 | 0.055546
3040 | MCLU-135to240-OfL-CZ12-2020-17.5IEER | CZ12 | OfL | 2020 | 135to240 | 12 | 17.5 | 453.1559 | 3175.4799 | 0.54718 | 3349.0281 | 0.60301 | 173.5482 | 0.05583
3041 | MCLU-135to240-OfS-CZ12-2003-17.5IEER | CZ12 | OfS | 2003 | 135to240 | 12 | 17.5 | 33.3405 | 2433.9748 | 0.43897 | 2615.7759 | 0.49717 | 181.8012 | 0.058201
3042 | MCLU-135to240-OfS-CZ12-2007-17.5IEER | CZ12 | OfS | 2007 | 135to240 | 12 | 17.5 | 33.2508 | 2439.5713 | 0.43919 | 2621.2068 | 0.49702 | 181.6356 | 0.057832
3043 | MCLU-135to240-OfS-CZ12-2011-17.5IEER | CZ12 | OfS | 2011 | 135to240 | 12 | 17.5 | 32.6046 | 2459.8424 | 0.43834 | 2640.5605 | 0.49508 | 180.7181 | 0.05674
3044 | MCLU-135to240-OfS-CZ12-2015-17.5IEER | CZ12 | OfS | 2015 | 135to240 | 12 | 17.5 | 29.5371 | 2632.7489 | 0.44946 | 2810.0875 | 0.50414 | 177.3386 | 0.054687
3045 | MCLU-135to240-OfS-CZ12-2020-17.5IEER | CZ12 | OfS | 2020 | 135to240 | 12 | 17.5 | 28.7728 | 2487.3841 | 0.42939 | 2665.357 | 0.48391 | 177.9729 | 0.054519
3046 | MCLU-135to240-RFF-CZ12-2003-17.5IEER | CZ12 | RFF | 2003 | 135to240 | 12 | 17.5 | 8.4502 | 4990.2785 | 1.2781 | 5320.0274 | 1.4187 | 329.7489 | 0.14059
3047 | MCLU-135to240-RFF-CZ12-2007-17.5IEER | CZ12 | RFF | 2007 | 135to240 | 12 | 17.5 | 8.3563 | 5041.5801 | 1.2873 | 5372.8026 | 1.4276 | 331.2224 | 0.1403
3048 | MCLU-135to240-RFF-CZ12-2011-17.5IEER | CZ12 | RFF | 2011 | 135to240 | 12 | 17.5 | 8.1072 | 5182.5214 | 1.3075 | 5518.5088 | 1.4472 | 335.9875 | 0.13972
3049 | MCLU-135to240-RFF-CZ12-2015-17.5IEER | CZ12 | RFF | 2015 | 135to240 | 12 | 17.5 | 8.0631 | 4969.8396 | 1.2706 | 5307.4522 | 1.4104 | 337.6126 | 0.13979
3050 | MCLU-135to240-RFF-CZ12-2020-17.5IEER | CZ12 | RFF | 2020 | 135to240 | 12 | 17.5 | 7.7247 | 4553.4227 | 1.211 | 4897.5602 | 1.3501 | 344.1375 | 0.1391
3051 | MCLU-135to240-RSD-CZ12-2003-17.5IEER | CZ12 | RSD | 2003 | 135to240 | 12 | 17.5 | 15.6017 | 4844.3328 | 1.2532 | 5140.9604 | 1.3954 | 296.6276 | 0.14223
3052 | MCLU-135to240-RSD-CZ12-2007-17.5IEER | CZ12 | RSD | 2007 | 135to240 | 12 | 17.5 | 15.4186 | 4897.8032 | 1.2627 | 5195.5271 | 1.4046 | 297.7239 | 0.14188
3053 | MCLU-135to240-RSD-CZ12-2011-17.5IEER | CZ12 | RSD | 2011 | 135to240 | 12 | 17.5 | 15.0858 | 5002.5931 | 1.28 | 5302.5587 | 1.4216 | 299.9656 | 0.14159
3054 | MCLU-135to240-RSD-CZ12-2015-17.5IEER | CZ12 | RSD | 2015 | 135to240 | 12 | 17.5 | 14.9263 | 4827.0689 | 1.2496 | 5123.9838 | 1.3911 | 296.9149 | 0.14149
3055 | MCLU-135to240-RSD-CZ12-2020-17.5IEER | CZ12 | RSD | 2020 | 135to240 | 12 | 17.5 | 14.0962 | 4329.905 | 1.1734 | 4630.8269 | 1.3123 | 300.9219 | 0.139
3056 | MCLU-135to240-Rt3-CZ12-2003-17.5IEER | CZ12 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 291.743 | 4836.1094 | 1.1414 | 5105.3979 | 1.2985 | 269.2885 | 0.1571
3057 | MCLU-135to240-Rt3-CZ12-2007-17.5IEER | CZ12 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 290.7597 | 4851.1347 | 1.1429 | 5119.9348 | 1.2997 | 268.8001 | 0.15682
3058 | MCLU-135to240-Rt3-CZ12-2011-17.5IEER | CZ12 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 283.4182 | 4972.2807 | 1.1537 | 5237.4381 | 1.311 | 265.1574 | 0.15728
3059 | MCLU-135to240-Rt3-CZ12-2015-17.5IEER | CZ12 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 274.3752 | 4644.5643 | 1.101 | 4914.64 | 1.2601 | 270.0757 | 0.1591
3060 | MCLU-135to240-Rt3-CZ12-2020-17.5IEER | CZ12 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 263.528 | 4300.126 | 1.0475 | 4574.4492 | 1.208 | 274.3232 | 0.16049
3061 | MCLU-135to240-RtL-CZ12-2003-17.5IEER | CZ12 | RtL | 2003 | 135to240 | 12 | 17.5 | 254.7887 | 5269.7681 | 1.2233 | 5548.7943 | 1.3854 | 279.0263 | 0.16207
3062 | MCLU-135to240-RtL-CZ12-2007-17.5IEER | CZ12 | RtL | 2007 | 135to240 | 12 | 17.5 | 250.3348 | 5359.8885 | 1.2381 | 5636.4517 | 1.4003 | 276.5632 | 0.16223
3063 | MCLU-135to240-RtL-CZ12-2011-17.5IEER | CZ12 | RtL | 2011 | 135to240 | 12 | 17.5 | 242.9602 | 5521.5166 | 1.2612 | 5792.4363 | 1.4238 | 270.9197 | 0.16257
3064 | MCLU-135to240-RtL-CZ12-2015-17.5IEER | CZ12 | RtL | 2015 | 135to240 | 12 | 17.5 | 235.9592 | 5308.706 | 1.2412 | 5583.7256 | 1.4051 | 275.0197 | 0.1639
3065 | MCLU-135to240-RtL-CZ12-2020-17.5IEER | CZ12 | RtL | 2020 | 135to240 | 12 | 17.5 | 222.1715 | 5111.4078 | 1.236 | 5388.6714 | 1.4013 | 277.2636 | 0.16528
3066 | MCLU-135to240-RtS-CZ12-2003-17.5IEER | CZ12 | RtS | 2003 | 135to240 | 12 | 17.5 | 19.0007 | 3285.4843 | 0.83519 | 3611.847 | 0.97194 | 326.3628 | 0.13675
3067 | MCLU-135to240-RtS-CZ12-2007-17.5IEER | CZ12 | RtS | 2007 | 135to240 | 12 | 17.5 | 18.7153 | 3330.6809 | 0.84092 | 3657.0338 | 0.97756 | 326.3529 | 0.13664
3068 | MCLU-135to240-RtS-CZ12-2011-17.5IEER | CZ12 | RtS | 2011 | 135to240 | 12 | 17.5 | 18.0821 | 3438.0652 | 0.8516 | 3763.3016 | 0.98839 | 325.2364 | 0.13679
3069 | MCLU-135to240-RtS-CZ12-2015-17.5IEER | CZ12 | RtS | 2015 | 135to240 | 12 | 17.5 | 17.8008 | 3149.2813 | 0.81151 | 3429.3024 | 0.94959 | 280.0211 | 0.13808
3070 | MCLU-135to240-RtS-CZ12-2020-17.5IEER | CZ12 | RtS | 2020 | 135to240 | 12 | 17.5 | 17.0528 | 2989.1307 | 0.79016 | 3269.9634 | 0.92894 | 280.8327 | 0.13878
3071 | MCLU-135to240-SCn-CZ12-2003-17.5IEER | CZ12 | SCn | 2003 | 135to240 | 12 | 17.5 | 324.4537 | 2428.4948 | 0.39885 | 2672.4608 | 0.48628 | 243.966 | 0.087439
3072 | MCLU-135to240-SCn-CZ12-2007-17.5IEER | CZ12 | SCn | 2007 | 135to240 | 12 | 17.5 | 309.4289 | 2528.4942 | 0.40869 | 2772.485 | 0.49592 | 243.9908 | 0.087226
3073 | MCLU-135to240-SCn-CZ12-2011-17.5IEER | CZ12 | SCn | 2011 | 135to240 | 12 | 17.5 | 284.1581 | 2730.8131 | 0.42723 | 2978.336 | 0.51284 | 247.5229 | 0.085608
3074 | MCLU-135to240-SCn-CZ12-2015-17.5IEER | CZ12 | SCn | 2015 | 135to240 | 12 | 17.5 | 284.4132 | 2697.8293 | 0.42396 | 2938.8121 | 0.50997 | 240.9828 | 0.086003
3075 | MCLU-135to240-SCn-CZ12-2020-17.5IEER | CZ12 | SCn | 2020 | 135to240 | 12 | 17.5 | 259.3313 | 2560.3138 | 0.41793 | 2800.563 | 0.49816 | 240.2492 | 0.080229
3076 | MCLU-135to240-WRf-CZ12-2003-17.5IEER | CZ12 | WRf | 2003 | 135to240 | 12 | 17.5 | 15.2599 | 248679.9916 | 34.7552 | 249089.9305 | 34.8514 | 409.9389 | 0.096265
3077 | MCLU-135to240-WRf-CZ12-2007-17.5IEER | CZ12 | WRf | 2007 | 135to240 | 12 | 17.5 | 14.8234 | 247321.6172 | 32.7783 | 247759.2078 | 32.8793 | 437.5905 | 0.10108
3078 | MCLU-135to240-WRf-CZ12-2011-17.5IEER | CZ12 | WRf | 2011 | 135to240 | 12 | 17.5 | 14.6549 | 242215.8002 | 30.9623 | 242617.8002 | 31.0438 | 402 | 0.081558
3079 | MCLU-135to240-WRf-CZ12-2015-17.5IEER | CZ12 | WRf | 2015 | 135to240 | 12 | 17.5 | 16.6824 | 212438.4683 | 27.1805 | 212674.8901 | 27.2454 | 236.4217 | 0.064839
3080 | MCLU-135to240-WRf-CZ12-2020-17.5IEER | CZ12 | WRf | 2020 | 135to240 | 12 | 17.5 | 17.023 | 196558.7803 | 25.1127 | 196784.7302 | 25.1749 | 225.9499 | 0.062265
3081 | MCLU-135to240-Asm-CZ13-2003-17.5IEER | CZ13 | Asm | 2003 | 135to240 | 12 | 17.5 | 437.792 | 1950.6405 | 0.70996 | 2273.9322 | 0.85246 | 323.2918 | 0.14251
3082 | MCLU-135to240-Asm-CZ13-2007-17.5IEER | CZ13 | Asm | 2007 | 135to240 | 12 | 17.5 | 434.5534 | 1959.8645 | 0.71227 | 2283.055 | 0.85412 | 323.1905 | 0.14186
3083 | MCLU-135to240-Asm-CZ13-2011-17.5IEER | CZ13 | Asm | 2011 | 135to240 | 12 | 17.5 | 422.3799 | 1999.7818 | 0.71269 | 2322.5237 | 0.854 | 322.7419 | 0.14132
3084 | MCLU-135to240-Asm-CZ13-2015-17.5IEER | CZ13 | Asm | 2015 | 135to240 | 12 | 17.5 | 410.7948 | 2013.6463 | 0.71385 | 2335.3897 | 0.85577 | 321.7435 | 0.14191
3085 | MCLU-135to240-Asm-CZ13-2020-17.5IEER | CZ13 | Asm | 2020 | 135to240 | 12 | 17.5 | 403.2196 | 1901.168 | 0.69096 | 2222.2513 | 0.83304 | 321.0833 | 0.14208
3086 | MCLU-135to240-ECC-CZ13-2003-17.5IEER | CZ13 | ECC | 2003 | 135to240 | 12 | 17.5 | 919.4413 | 2465.1195 | 0.46804 | 2702.3493 | 0.5827 | 237.2298 | 0.11466
3087 | MCLU-135to240-ECC-CZ13-2007-17.5IEER | CZ13 | ECC | 2007 | 135to240 | 12 | 17.5 | 917.4022 | 2468.6663 | 0.46747 | 2705.2433 | 0.58184 | 236.577 | 0.11437
3088 | MCLU-135to240-ECC-CZ13-2011-17.5IEER | CZ13 | ECC | 2011 | 135to240 | 12 | 17.5 | 899.4358 | 2496.6096 | 0.46016 | 2729.6477 | 0.57358 | 233.0381 | 0.11342
3089 | MCLU-135to240-ECC-CZ13-2015-17.5IEER | CZ13 | ECC | 2015 | 135to240 | 12 | 17.5 | 863.7826 | 2544.1883 | 0.4525 | 2775.0708 | 0.56786 | 230.8825 | 0.11537
3090 | MCLU-135to240-ECC-CZ13-2020-17.5IEER | CZ13 | ECC | 2020 | 135to240 | 12 | 17.5 | 833.629 | 2249.0729 | 0.42562 | 2482.5882 | 0.5406 | 233.5152 | 0.11498
3091 | MCLU-135to240-EPr-CZ13-2003-17.5IEER | CZ13 | EPr | 2003 | 135to240 | 12 | 17.5 | 157.0822 | 1567.2848 | 0.11126 | 1721.1326 | 0.14338 | 153.8477 | 0.032115
3092 | MCLU-135to240-EPr-CZ13-2007-17.5IEER | CZ13 | EPr | 2007 | 135to240 | 12 | 17.5 | 155.7002 | 1594.0668 | 0.1118 | 1741.8977 | 0.14255 | 147.8309 | 0.030747
3093 | MCLU-135to240-EPr-CZ13-2011-17.5IEER | CZ13 | EPr | 2011 | 135to240 | 12 | 17.5 | 152.425 | 1619.9309 | 0.10797 | 1766.678 | 0.13651 | 146.7471 | 0.028534
3094 | MCLU-135to240-EPr-CZ13-2015-17.5IEER | CZ13 | EPr | 2015 | 135to240 | 12 | 17.5 | 144.8902 | 1642.7452 | 0.08521 | 1785.6042 | 0.10628 | 142.8589 | 0.021072
3095 | MCLU-135to240-EPr-CZ13-2020-17.5IEER | CZ13 | EPr | 2020 | 135to240 | 12 | 17.5 | 139.4703 | 1459.1856 | 0.072377 | 1602.5675 | 0.091141 | 143.3819 | 0.018764
3096 | MCLU-135to240-ERC-CZ13-2003-17.5IEER | CZ13 | ERC | 2003 | 135to240 | 12 | 17.5 | 7.2698 | 1327.7497 | 0.16106 | 1466.0565 | 0.20575 | 138.3068 | 0.044692
3097 | MCLU-135to240-ERC-CZ13-2007-17.5IEER | CZ13 | ERC | 2007 | 135to240 | 12 | 17.5 | 7.2454 | 1330.5511 | 0.15991 | 1467.7533 | 0.20319 | 137.2022 | 0.043279
3098 | MCLU-135to240-ERC-CZ13-2011-17.5IEER | CZ13 | ERC | 2011 | 135to240 | 12 | 17.5 | 7.062 | 1350.227 | 0.15129 | 1483.1761 | 0.18954 | 132.9491 | 0.038246
3099 | MCLU-135to240-ERC-CZ13-2015-17.5IEER | CZ13 | ERC | 2015 | 135to240 | 12 | 17.5 | 6.9288 | 1313.8742 | 0.14115 | 1429.0319 | 0.17644 | 115.1577 | 0.035293
3100 | MCLU-135to240-ERC-CZ13-2020-17.5IEER | CZ13 | ERC | 2020 | 135to240 | 12 | 17.5 | 6.7514 | 1162.3036 | 0.13282 | 1276.4002 | 0.16625 | 114.0966 | 0.033428
3101 | MCLU-135to240-ESe-CZ13-2003-17.5IEER | CZ13 | ESe | 2003 | 135to240 | 12 | 17.5 | 464.8197 | 1769.2884 | 0.18009 | 1940.02 | 0.22259 | 170.7316 | 0.042503
3102 | MCLU-135to240-ESe-CZ13-2007-17.5IEER | CZ13 | ESe | 2007 | 135to240 | 12 | 17.5 | 463.3 | 1773.1592 | 0.17923 | 1943.381 | 0.22121 | 170.2218 | 0.041974
3103 | MCLU-135to240-ESe-CZ13-2011-17.5IEER | CZ13 | ESe | 2011 | 135to240 | 12 | 17.5 | 455.463 | 1784.7344 | 0.16733 | 1950.1756 | 0.20421 | 165.4412 | 0.036882
3104 | MCLU-135to240-ESe-CZ13-2015-17.5IEER | CZ13 | ESe | 2015 | 135to240 | 12 | 17.5 | 443.4907 | 1790.9912 | 0.15382 | 1952.9793 | 0.18609 | 161.9882 | 0.032275
3105 | MCLU-135to240-ESe-CZ13-2020-17.5IEER | CZ13 | ESe | 2020 | 135to240 | 12 | 17.5 | 428.3074 | 1573.2652 | 0.13669 | 1736.2323 | 0.16793 | 162.9671 | 0.03124
3106 | MCLU-135to240-EUn-CZ13-2003-17.5IEER | CZ13 | EUn | 2003 | 135to240 | 12 | 17.5 | 2793.7097 | 2647.9266 | 0.6808 | 2886.4921 | 0.80153 | 238.5655 | 0.12073
3107 | MCLU-135to240-EUn-CZ13-2007-17.5IEER | CZ13 | EUn | 2007 | 135to240 | 12 | 17.5 | 2777.6551 | 2638.2133 | 0.67238 | 2876.3645 | 0.79309 | 238.1512 | 0.12072
3108 | MCLU-135to240-EUn-CZ13-2011-17.5IEER | CZ13 | EUn | 2011 | 135to240 | 12 | 17.5 | 2692.8144 | 2697.0376 | 0.67416 | 2934.1987 | 0.7954 | 237.1611 | 0.12124
3109 | MCLU-135to240-EUn-CZ13-2015-17.5IEER | CZ13 | EUn | 2015 | 135to240 | 12 | 17.5 | 2542.293 | 2766.4884 | 0.67336 | 3004.2801 | 0.79748 | 237.7917 | 0.12411
3110 | MCLU-135to240-EUn-CZ13-2020-17.5IEER | CZ13 | EUn | 2020 | 135to240 | 12 | 17.5 | 2459.6055 | 2528.8795 | 0.64599 | 2767.2743 | 0.76972 | 238.3948 | 0.12373
3111 | MCLU-135to240-Gro-CZ13-2003-17.5IEER | CZ13 | Gro | 2003 | 135to240 | 12 | 17.5 | 149.8747 | 11402.4115 | 1.8648 | 11821.0834 | 2.016 | 418.6719 | 0.15113
3112 | MCLU-135to240-Gro-CZ13-2007-17.5IEER | CZ13 | Gro | 2007 | 135to240 | 12 | 17.5 | 147.0799 | 10596.6308 | 1.7754 | 10987.0187 | 1.9293 | 390.3879 | 0.15393
3113 | MCLU-135to240-Gro-CZ13-2011-17.5IEER | CZ13 | Gro | 2011 | 135to240 | 12 | 17.5 | 138.9723 | 11175.8469 | 1.8487 | 11563.0696 | 2.0046 | 387.2227 | 0.15587
3114 | MCLU-135to240-Gro-CZ13-2015-17.5IEER | CZ13 | Gro | 2015 | 135to240 | 12 | 17.5 | 134.2705 | 11073.1973 | 1.8318 | 11457.4892 | 1.9858 | 384.2918 | 0.15401
3115 | MCLU-135to240-Gro-CZ13-2020-17.5IEER | CZ13 | Gro | 2020 | 135to240 | 12 | 17.5 | 129.236 | 11137.4005 | 1.8373 | 11519.2499 | 1.9918 | 381.8494 | 0.15449
3116 | MCLU-135to240-Hsp-CZ13-2003-17.5IEER | CZ13 | Hsp | 2003 | 135to240 | 12 | 17.5 | 686.8054 | 4438.2176 | 0.85136 | 4898.5477 | 1.0002 | 460.3301 | 0.14879
3117 | MCLU-135to240-Hsp-CZ13-2007-17.5IEER | CZ13 | Hsp | 2007 | 135to240 | 12 | 17.5 | 686.6393 | 4437.7602 | 0.85044 | 4897.7484 | 0.99905 | 459.9882 | 0.14862
3118 | MCLU-135to240-Hsp-CZ13-2011-17.5IEER | CZ13 | Hsp | 2011 | 135to240 | 12 | 17.5 | 680.6729 | 4448.322 | 0.83614 | 4907.6651 | 0.98557 | 459.3431 | 0.14943
3119 | MCLU-135to240-Hsp-CZ13-2015-17.5IEER | CZ13 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 4412.8194 | 0.82305 | 4872.4444 | 0.97316 | 459.625 | 0.1501
3120 | MCLU-135to240-Hsp-CZ13-2020-17.5IEER | CZ13 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3884.4048 | 0.7418 | 4345.3755 | 0.89119 | 460.9707 | 0.14939
3121 | MCLU-135to240-Htl-CZ13-2003-17.5IEER | CZ13 | Htl | 2003 | 135to240 | 12 | 17.5 | 307.42 | 3227.4247 | 0.8773 | 3332.5426 | 0.91627 | 105.1179 | 0.038972
3122 | MCLU-135to240-Htl-CZ13-2007-17.5IEER | CZ13 | Htl | 2007 | 135to240 | 12 | 17.5 | 307.0102 | 3088.6266 | 0.81795 | 3193.7936 | 0.85685 | 105.167 | 0.038905
3123 | MCLU-135to240-Htl-CZ13-2011-17.5IEER | CZ13 | Htl | 2011 | 135to240 | 12 | 17.5 | 297.2059 | 3125.5074 | 0.82246 | 3231.0527 | 0.86153 | 105.5453 | 0.039063
3124 | MCLU-135to240-Htl-CZ13-2015-17.5IEER | CZ13 | Htl | 2015 | 135to240 | 12 | 17.5 | 268.0086 | 3205.9425 | 0.82054 | 3317.0772 | 0.86256 | 111.1347 | 0.04201
3125 | MCLU-135to240-Htl-CZ13-2020-17.5IEER | CZ13 | Htl | 2020 | 135to240 | 12 | 17.5 | 266.115 | 3117.1709 | 0.80915 | 3226.9621 | 0.85054 | 109.7912 | 0.041393
3126 | MCLU-135to240-MBT-CZ13-2003-17.5IEER | CZ13 | MBT | 2003 | 135to240 | 12 | 17.5 | 449.3061 | 3422.5302 | 0.55428 | 3642.7025 | 0.66879 | 220.1723 | 0.11451
3127 | MCLU-135to240-MBT-CZ13-2007-17.5IEER | CZ13 | MBT | 2007 | 135to240 | 12 | 17.5 | 441.7352 | 3474.8274 | 0.55802 | 3692.6691 | 0.67203 | 217.8417 | 0.114
3128 | MCLU-135to240-MBT-CZ13-2011-17.5IEER | CZ13 | MBT | 2011 | 135to240 | 12 | 17.5 | 417.2517 | 3611.0576 | 0.56749 | 3824.3408 | 0.6812 | 213.2831 | 0.11371
3129 | MCLU-135to240-MBT-CZ13-2015-17.5IEER | CZ13 | MBT | 2015 | 135to240 | 12 | 17.5 | 407.5057 | 3655.9403 | 0.57028 | 3868.8262 | 0.6846 | 212.8859 | 0.11432
3130 | MCLU-135to240-MBT-CZ13-2020-17.5IEER | CZ13 | MBT | 2020 | 135to240 | 12 | 17.5 | 382.2927 | 3492.4807 | 0.55132 | 3704.3875 | 0.66613 | 211.9068 | 0.11481
3131 | MCLU-135to240-MLI-CZ13-2003-17.5IEER | CZ13 | MLI | 2003 | 135to240 | 12 | 17.5 | 285.1954 | 2532.1254 | 0.42347 | 2747.0574 | 0.50129 | 214.932 | 0.077821
3132 | MCLU-135to240-MLI-CZ13-2007-17.5IEER | CZ13 | MLI | 2007 | 135to240 | 12 | 17.5 | 279.3664 | 2575.832 | 0.42733 | 2790.0094 | 0.50527 | 214.1774 | 0.077941
3133 | MCLU-135to240-MLI-CZ13-2011-17.5IEER | CZ13 | MLI | 2011 | 135to240 | 12 | 17.5 | 253.9401 | 2793.1886 | 0.44382 | 3003.8754 | 0.52296 | 210.6868 | 0.079143
3134 | MCLU-135to240-MLI-CZ13-2015-17.5IEER | CZ13 | MLI | 2015 | 135to240 | 12 | 17.5 | 251.6817 | 2797.533 | 0.44426 | 3008.131 | 0.52348 | 210.598 | 0.079225
3135 | MCLU-135to240-MLI-CZ13-2020-17.5IEER | CZ13 | MLI | 2020 | 135to240 | 12 | 17.5 | 236.7879 | 2509.1227 | 0.41305 | 2719.7887 | 0.49307 | 210.666 | 0.080022
3136 | MCLU-135to240-Mtl-CZ13-2003-17.5IEER | CZ13 | Mtl | 2003 | 135to240 | 12 | 17.5 | 55.3366 | 3206.9855 | 0.8364 | 3290.7067 | 0.8625 | 83.7212 | 0.026099
3137 | MCLU-135to240-Mtl-CZ13-2007-17.5IEER | CZ13 | Mtl | 2007 | 135to240 | 12 | 17.5 | 55.3366 | 3055.3801 | 0.77207 | 3138.9468 | 0.79809 | 83.5667 | 0.026025
3138 | MCLU-135to240-Mtl-CZ13-2011-17.5IEER | CZ13 | Mtl | 2011 | 135to240 | 12 | 17.5 | 53.728 | 3081.6043 | 0.77536 | 3165.3271 | 0.8013 | 83.7228 | 0.025942
3139 | MCLU-135to240-Mtl-CZ13-2015-17.5IEER | CZ13 | Mtl | 2015 | 135to240 | 12 | 17.5 | 45.8587 | 3219.2001 | 0.7766 | 3308.961 | 0.80495 | 89.7609 | 0.028344
3140 | MCLU-135to240-Mtl-CZ13-2020-17.5IEER | CZ13 | Mtl | 2020 | 135to240 | 12 | 17.5 | 45.7189 | 3151.1543 | 0.76786 | 3239.5592 | 0.79587 | 88.4049 | 0.028012
3141 | MCLU-135to240-Nrs-CZ13-2003-17.5IEER | CZ13 | Nrs | 2003 | 135to240 | 12 | 17.5 | 186.7352 | 4657.6154 | 0.99876 | 4868.5919 | 1.0729 | 210.9765 | 0.074124
3142 | MCLU-135to240-Nrs-CZ13-2007-17.5IEER | CZ13 | Nrs | 2007 | 135to240 | 12 | 17.5 | 186.5604 | 4559.115 | 0.95867 | 4769.9722 | 1.0326 | 210.8572 | 0.073896
3143 | MCLU-135to240-Nrs-CZ13-2011-17.5IEER | CZ13 | Nrs | 2011 | 135to240 | 12 | 17.5 | 185.0579 | 4598.4597 | 0.9539 | 4808.7144 | 1.0276 | 210.2547 | 0.073747
3144 | MCLU-135to240-Nrs-CZ13-2015-17.5IEER | CZ13 | Nrs | 2015 | 135to240 | 12 | 17.5 | 182.9623 | 4510.5557 | 0.905 | 4719.8277 | 0.9788 | 209.2719 | 0.073806
3145 | MCLU-135to240-Nrs-CZ13-2020-17.5IEER | CZ13 | Nrs | 2020 | 135to240 | 12 | 17.5 | 182.3281 | 4142.9469 | 0.84495 | 4352.1554 | 0.91803 | 209.2086 | 0.073074
3146 | MCLU-135to240-OfL-CZ13-2003-17.5IEER | CZ13 | OfL | 2003 | 135to240 | 12 | 17.5 | 529.0731 | 3149.9483 | 0.51198 | 3359.0002 | 0.56732 | 209.0519 | 0.05533
3147 | MCLU-135to240-OfL-CZ13-2007-17.5IEER | CZ13 | OfL | 2007 | 135to240 | 12 | 17.5 | 528.5154 | 3152.4452 | 0.51212 | 3361.3453 | 0.56737 | 208.9001 | 0.055252
3148 | MCLU-135to240-OfL-CZ13-2011-17.5IEER | CZ13 | OfL | 2011 | 135to240 | 12 | 17.5 | 504.7961 | 3241.6099 | 0.51839 | 3446.1526 | 0.57248 | 204.5427 | 0.054084
3149 | MCLU-135to240-OfL-CZ13-2015-17.5IEER | CZ13 | OfL | 2015 | 135to240 | 12 | 17.5 | 507.056 | 3178.8971 | 0.5119 | 3384.9626 | 0.56605 | 206.0655 | 0.054154
3150 | MCLU-135to240-OfL-CZ13-2020-17.5IEER | CZ13 | OfL | 2020 | 135to240 | 12 | 17.5 | 494.9015 | 3025.2264 | 0.49409 | 3232.4645 | 0.54797 | 207.2381 | 0.053878
3151 | MCLU-135to240-OfS-CZ13-2003-17.5IEER | CZ13 | OfS | 2003 | 135to240 | 12 | 17.5 | 36.5785 | 2344.4491 | 0.39287 | 2557.4364 | 0.44852 | 212.9874 | 0.055653
3152 | MCLU-135to240-OfS-CZ13-2007-17.5IEER | CZ13 | OfS | 2007 | 135to240 | 12 | 17.5 | 36.4727 | 2349.3156 | 0.39287 | 2561.803 | 0.44821 | 212.4874 | 0.055344
3153 | MCLU-135to240-OfS-CZ13-2011-17.5IEER | CZ13 | OfS | 2011 | 135to240 | 12 | 17.5 | 35.7377 | 2366.3087 | 0.39193 | 2577.4165 | 0.44623 | 211.1078 | 0.054296
3154 | MCLU-135to240-OfS-CZ13-2015-17.5IEER | CZ13 | OfS | 2015 | 135to240 | 12 | 17.5 | 32.6598 | 2502.6823 | 0.4014 | 2710.5352 | 0.45484 | 207.8528 | 0.053444
3155 | MCLU-135to240-OfS-CZ13-2020-17.5IEER | CZ13 | OfS | 2020 | 135to240 | 12 | 17.5 | 31.8701 | 2367.1587 | 0.38252 | 2575.2927 | 0.43573 | 208.1341 | 0.053206
3156 | MCLU-135to240-RFF-CZ13-2003-17.5IEER | CZ13 | RFF | 2003 | 135to240 | 12 | 17.5 | 9.6608 | 4654.2271 | 1.1266 | 5036.8414 | 1.2797 | 382.6142 | 0.15302
3157 | MCLU-135to240-RFF-CZ13-2007-17.5IEER | CZ13 | RFF | 2007 | 135to240 | 12 | 17.5 | 9.5569 | 4697.3044 | 1.1337 | 5080.6621 | 1.2865 | 383.3577 | 0.15285
3158 | MCLU-135to240-RFF-CZ13-2011-17.5IEER | CZ13 | RFF | 2011 | 135to240 | 12 | 17.5 | 9.1222 | 4882.0708 | 1.1564 | 5267.1888 | 1.3087 | 385.118 | 0.15224
3159 | MCLU-135to240-RFF-CZ13-2015-17.5IEER | CZ13 | RFF | 2015 | 135to240 | 12 | 17.5 | 9.0892 | 4685.8391 | 1.1223 | 5072.8811 | 1.2747 | 387.042 | 0.15234
3160 | MCLU-135to240-RFF-CZ13-2020-17.5IEER | CZ13 | RFF | 2020 | 135to240 | 12 | 17.5 | 8.7309 | 4307.7013 | 1.0652 | 4697.6852 | 1.2178 | 389.9838 | 0.1526
3161 | MCLU-135to240-RSD-CZ13-2003-17.5IEER | CZ13 | RSD | 2003 | 135to240 | 12 | 17.5 | 17.9705 | 4410.8812 | 1.0944 | 4738.0469 | 1.2518 | 327.1657 | 0.15737
3162 | MCLU-135to240-RSD-CZ13-2007-17.5IEER | CZ13 | RSD | 2007 | 135to240 | 12 | 17.5 | 17.7592 | 4455.2482 | 1.1014 | 4783.2865 | 1.2582 | 328.0382 | 0.15679
3163 | MCLU-135to240-RSD-CZ13-2011-17.5IEER | CZ13 | RSD | 2011 | 135to240 | 12 | 17.5 | 17.3646 | 4544.0267 | 1.1152 | 4874.0771 | 1.2708 | 330.0504 | 0.15566
3164 | MCLU-135to240-RSD-CZ13-2015-17.5IEER | CZ13 | RSD | 2015 | 135to240 | 12 | 17.5 | 17.1986 | 4390.007 | 1.0884 | 4720.08 | 1.2434 | 330.0729 | 0.15505
3165 | MCLU-135to240-RSD-CZ13-2020-17.5IEER | CZ13 | RSD | 2020 | 135to240 | 12 | 17.5 | 16.3417 | 3935.1092 | 1.0133 | 4270.1339 | 1.1666 | 335.0247 | 0.15336
3166 | MCLU-135to240-Rt3-CZ13-2003-17.5IEER | CZ13 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 326.3677 | 4502.6497 | 1.0354 | 4821.6369 | 1.2001 | 318.9872 | 0.16468
3167 | MCLU-135to240-Rt3-CZ13-2007-17.5IEER | CZ13 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 325.1383 | 4516.9256 | 1.0365 | 4835.2425 | 1.201 | 318.3169 | 0.16446
3168 | MCLU-135to240-Rt3-CZ13-2011-17.5IEER | CZ13 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 309.8711 | 4711.3983 | 1.0543 | 5023.9526 | 1.2201 | 312.5542 | 0.1658
3169 | MCLU-135to240-Rt3-CZ13-2015-17.5IEER | CZ13 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 300.7165 | 4401.7839 | 1.0038 | 4718.7923 | 1.1715 | 317.0084 | 0.16762
3170 | MCLU-135to240-Rt3-CZ13-2020-17.5IEER | CZ13 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 289.2169 | 4081.999 | 0.95328 | 4402.7265 | 1.122 | 320.7275 | 0.16871
3171 | MCLU-135to240-RtL-CZ13-2003-17.5IEER | CZ13 | RtL | 2003 | 135to240 | 12 | 17.5 | 286.9775 | 4860.1563 | 1.1042 | 5207.5536 | 1.273 | 347.3973 | 0.1688
3172 | MCLU-135to240-RtL-CZ13-2007-17.5IEER | CZ13 | RtL | 2007 | 135to240 | 12 | 17.5 | 282.3732 | 4929.9291 | 1.1138 | 5274.8664 | 1.2826 | 344.9373 | 0.16885
3173 | MCLU-135to240-RtL-CZ13-2011-17.5IEER | CZ13 | RtL | 2011 | 135to240 | 12 | 17.5 | 270.613 | 5126.7484 | 1.1389 | 5465.2037 | 1.3084 | 338.4554 | 0.16948
3174 | MCLU-135to240-RtL-CZ13-2015-17.5IEER | CZ13 | RtL | 2015 | 135to240 | 12 | 17.5 | 263.3068 | 4928.4135 | 1.1192 | 5270.9204 | 1.2902 | 342.5069 | 0.171
3175 | MCLU-135to240-RtL-CZ13-2020-17.5IEER | CZ13 | RtL | 2020 | 135to240 | 12 | 17.5 | 248.8077 | 4734.2898 | 1.1079 | 5078.2827 | 1.2809 | 343.9928 | 0.17309
3176 | MCLU-135to240-RtS-CZ13-2003-17.5IEER | CZ13 | RtS | 2003 | 135to240 | 12 | 17.5 | 21.7617 | 3070.6938 | 0.7486 | 3440.4759 | 0.88901 | 369.782 | 0.14041
3177 | MCLU-135to240-RtS-CZ13-2007-17.5IEER | CZ13 | RtS | 2007 | 135to240 | 12 | 17.5 | 21.4433 | 3107.3946 | 0.75225 | 3476.6389 | 0.89262 | 369.2443 | 0.14037
3178 | MCLU-135to240-RtS-CZ13-2011-17.5IEER | CZ13 | RtS | 2011 | 135to240 | 12 | 17.5 | 20.3947 | 3236.8989 | 0.76242 | 3602.5656 | 0.90309 | 365.6667 | 0.14067
3179 | MCLU-135to240-RtS-CZ13-2015-17.5IEER | CZ13 | RtS | 2015 | 135to240 | 12 | 17.5 | 20.1365 | 2971.8919 | 0.7263 | 3296.3647 | 0.86828 | 324.4727 | 0.14198
3180 | MCLU-135to240-RtS-CZ13-2020-17.5IEER | CZ13 | RtS | 2020 | 135to240 | 12 | 17.5 | 19.3777 | 2817.8504 | 0.70265 | 3142.6488 | 0.84538 | 324.7984 | 0.14273
3181 | MCLU-135to240-SCn-CZ13-2003-17.5IEER | CZ13 | SCn | 2003 | 135to240 | 12 | 17.5 | 383.7162 | 2256.1406 | 0.34658 | 2551.273 | 0.43486 | 295.1324 | 0.088282
3182 | MCLU-135to240-SCn-CZ13-2007-17.5IEER | CZ13 | SCn | 2007 | 135to240 | 12 | 17.5 | 361.9802 | 2368.1917 | 0.3573 | 2657.8025 | 0.4476 | 289.6108 | 0.090296
3183 | MCLU-135to240-SCn-CZ13-2011-17.5IEER | CZ13 | SCn | 2011 | 135to240 | 12 | 17.5 | 319.307 | 2629.9936 | 0.37745 | 2931.4345 | 0.46943 | 301.4408 | 0.091988
3184 | MCLU-135to240-SCn-CZ13-2015-17.5IEER | CZ13 | SCn | 2015 | 135to240 | 12 | 17.5 | 325.6122 | 2543.8589 | 0.36664 | 2831.693 | 0.45838 | 287.8342 | 0.091739
3185 | MCLU-135to240-SCn-CZ13-2020-17.5IEER | CZ13 | SCn | 2020 | 135to240 | 12 | 17.5 | 292.7223 | 2456.3676 | 0.3651 | 2748.8432 | 0.4545 | 292.4756 | 0.089399
3186 | MCLU-135to240-WRf-CZ13-2003-17.5IEER | CZ13 | WRf | 2003 | 135to240 | 12 | 17.5 | 16.36 | 236101.0806 | 32.9278 | 236511.2568 | 33.0198 | 410.1762 | 0.092003
3187 | MCLU-135to240-WRf-CZ13-2007-17.5IEER | CZ13 | WRf | 2007 | 135to240 | 12 | 17.5 | 15.8967 | 234534.9015 | 31.4364 | 234951.7781 | 31.5274 | 416.8766 | 0.091011
3188 | MCLU-135to240-WRf-CZ13-2011-17.5IEER | CZ13 | WRf | 2011 | 135to240 | 12 | 17.5 | 15.0801 | 237423.9063 | 30.6594 | 237875.2515 | 30.7465 | 451.3452 | 0.087054
3189 | MCLU-135to240-WRf-CZ13-2015-17.5IEER | CZ13 | WRf | 2015 | 135to240 | 12 | 17.5 | 16.7147 | 213879.8242 | 27.6466 | 214170.618 | 27.7208 | 290.7939 | 0.074262
3190 | MCLU-135to240-WRf-CZ13-2020-17.5IEER | CZ13 | WRf | 2020 | 135to240 | 12 | 17.5 | 16.4028 | 205580.6926 | 26.5843 | 205853.5019 | 26.6532 | 272.8093 | 0.068901
3191 | MCLU-135to240-Asm-CZ14-2003-17.5IEER | CZ14 | Asm | 2003 | 135to240 | 12 | 17.5 | 440.8785 | 1905.8832 | 0.51949 | 2228.4649 | 0.63669 | 322.5816 | 0.11721
3192 | MCLU-135to240-Asm-CZ14-2007-17.5IEER | CZ14 | Asm | 2007 | 135to240 | 12 | 17.5 | 437.7576 | 1915.1754 | 0.52149 | 2237.6971 | 0.6383 | 322.5217 | 0.11681
3193 | MCLU-135to240-Asm-CZ14-2011-17.5IEER | CZ14 | Asm | 2011 | 135to240 | 12 | 17.5 | 422.3899 | 1968.4693 | 0.52296 | 2290.4101 | 0.63661 | 321.9408 | 0.11365
3194 | MCLU-135to240-Asm-CZ14-2015-17.5IEER | CZ14 | Asm | 2015 | 135to240 | 12 | 17.5 | 410.8774 | 1979.3049 | 0.52315 | 2299.8941 | 0.63658 | 320.5892 | 0.11343
3195 | MCLU-135to240-Asm-CZ14-2020-17.5IEER | CZ14 | Asm | 2020 | 135to240 | 12 | 17.5 | 402.931 | 1869.5652 | 0.50249 | 2189.3538 | 0.61555 | 319.7886 | 0.11306
3196 | MCLU-135to240-ECC-CZ14-2003-17.5IEER | CZ14 | ECC | 2003 | 135to240 | 12 | 17.5 | 966.4984 | 2315.112 | 0.6676 | 2551.9564 | 0.78778 | 236.8444 | 0.12018
3197 | MCLU-135to240-ECC-CZ14-2007-17.5IEER | CZ14 | ECC | 2007 | 135to240 | 12 | 17.5 | 964.6507 | 2317.9786 | 0.66764 | 2554.2997 | 0.78751 | 236.321 | 0.11987
3198 | MCLU-135to240-ECC-CZ14-2011-17.5IEER | CZ14 | ECC | 2011 | 135to240 | 12 | 17.5 | 940.6078 | 2357.257 | 0.66359 | 2588.9656 | 0.78199 | 231.7085 | 0.1184
3199 | MCLU-135to240-ECC-CZ14-2015-17.5IEER | CZ14 | ECC | 2015 | 135to240 | 12 | 17.5 | 905.3502 | 2394.6338 | 0.66547 | 2623.2955 | 0.78486 | 228.6617 | 0.11939
3200 | MCLU-135to240-ECC-CZ14-2020-17.5IEER | CZ14 | ECC | 2020 | 135to240 | 12 | 17.5 | 872.9918 | 2115.5748 | 0.61795 | 2346.2363 | 0.73828 | 230.6615 | 0.12034
3201 | MCLU-135to240-EPr-CZ14-2003-17.5IEER | CZ14 | EPr | 2003 | 135to240 | 12 | 17.5 | 167.673 | 1465.2769 | 0.38091 | 1616.8225 | 0.45877 | 151.5456 | 0.077866
3202 | MCLU-135to240-EPr-CZ14-2007-17.5IEER | CZ14 | EPr | 2007 | 135to240 | 12 | 17.5 | 166.1902 | 1475.2989 | 0.38229 | 1626.0766 | 0.45977 | 150.7777 | 0.077478
3203 | MCLU-135to240-EPr-CZ14-2011-17.5IEER | CZ14 | EPr | 2011 | 135to240 | 12 | 17.5 | 162.7585 | 1501.247 | 0.38568 | 1650.743 | 0.46261 | 149.496 | 0.076929
3204 | MCLU-135to240-EPr-CZ14-2015-17.5IEER | CZ14 | EPr | 2015 | 135to240 | 12 | 17.5 | 155.3718 | 1515.6897 | 0.38492 | 1661.8893 | 0.46355 | 146.1996 | 0.07863
3205 | MCLU-135to240-EPr-CZ14-2020-17.5IEER | CZ14 | EPr | 2020 | 135to240 | 12 | 17.5 | 149.8351 | 1361.7439 | 0.35555 | 1502.851 | 0.43398 | 141.1072 | 0.078437
3206 | MCLU-135to240-ERC-CZ14-2003-17.5IEER | CZ14 | ERC | 2003 | 135to240 | 12 | 17.5 | 7.7597 | 1236.8541 | 0.27412 | 1368.1138 | 0.30233 | 131.2597 | 0.028206
3207 | MCLU-135to240-ERC-CZ14-2007-17.5IEER | CZ14 | ERC | 2007 | 135to240 | 12 | 17.5 | 7.7345 | 1239.9468 | 0.27411 | 1370.4895 | 0.30203 | 130.5427 | 0.027914
3208 | MCLU-135to240-ERC-CZ14-2011-17.5IEER | CZ14 | ERC | 2011 | 135to240 | 12 | 17.5 | 7.5293 | 1261.0628 | 0.27151 | 1388.4938 | 0.2979 | 127.4311 | 0.026389
3209 | MCLU-135to240-ERC-CZ14-2015-17.5IEER | CZ14 | ERC | 2015 | 135to240 | 12 | 17.5 | 7.4193 | 1222.7189 | 0.26478 | 1338.7756 | 0.28721 | 116.0566 | 0.022426
3210 | MCLU-135to240-ERC-CZ14-2020-17.5IEER | CZ14 | ERC | 2020 | 135to240 | 12 | 17.5 | 7.2375 | 1080.5005 | 0.23575 | 1196.0324 | 0.25698 | 115.5319 | 0.02123
3211 | MCLU-135to240-ESe-CZ14-2003-17.5IEER | CZ14 | ESe | 2003 | 135to240 | 12 | 17.5 | 496.0523 | 1637.9521 | 0.36686 | 1805.3938 | 0.4438 | 167.4416 | 0.076938
3212 | MCLU-135to240-ESe-CZ14-2007-17.5IEER | CZ14 | ESe | 2007 | 135to240 | 12 | 17.5 | 494.4359 | 1641.9148 | 0.36716 | 1808.9049 | 0.44385 | 166.9901 | 0.076696
3213 | MCLU-135to240-ESe-CZ14-2011-17.5IEER | CZ14 | ESe | 2011 | 135to240 | 12 | 17.5 | 483.2472 | 1663.618 | 0.36183 | 1825.3822 | 0.43754 | 161.7642 | 0.07571
3214 | MCLU-135to240-ESe-CZ14-2015-17.5IEER | CZ14 | ESe | 2015 | 135to240 | 12 | 17.5 | 471.3107 | 1665.696 | 0.35656 | 1823.8184 | 0.43326 | 158.1224 | 0.076695
3215 | MCLU-135to240-ESe-CZ14-2020-17.5IEER | CZ14 | ESe | 2020 | 135to240 | 12 | 17.5 | 455.1292 | 1461.9655 | 0.33489 | 1620.3303 | 0.41217 | 158.3647 | 0.077277
3216 | MCLU-135to240-EUn-CZ14-2003-17.5IEER | CZ14 | EUn | 2003 | 135to240 | 12 | 17.5 | 2865.6659 | 2544.0366 | 0.77328 | 2786.8349 | 0.87866 | 242.7984 | 0.10538
3217 | MCLU-135to240-EUn-CZ14-2007-17.5IEER | CZ14 | EUn | 2007 | 135to240 | 12 | 17.5 | 2850.4503 | 2534.997 | 0.76851 | 2777.4611 | 0.87386 | 242.4641 | 0.10535
3218 | MCLU-135to240-EUn-CZ14-2011-17.5IEER | CZ14 | EUn | 2011 | 135to240 | 12 | 17.5 | 2750.5733 | 2602.2925 | 0.7774 | 2842.7406 | 0.88299 | 240.4481 | 0.10559
3219 | MCLU-135to240-EUn-CZ14-2015-17.5IEER | CZ14 | EUn | 2015 | 135to240 | 12 | 17.5 | 2623.7537 | 2656.357 | 0.78908 | 2896.8302 | 0.89589 | 240.4732 | 0.10681
3220 | MCLU-135to240-EUn-CZ14-2020-17.5IEER | CZ14 | EUn | 2020 | 135to240 | 12 | 17.5 | 2530.9415 | 2433.5006 | 0.74117 | 2674.507 | 0.8483 | 241.0063 | 0.10713
3221 | MCLU-135to240-Gro-CZ14-2003-17.5IEER | CZ14 | Gro | 2003 | 135to240 | 12 | 17.5 | 157.1387 | 10695.1367 | 1.6175 | 11076.4847 | 1.7345 | 381.348 | 0.11698
3222 | MCLU-135to240-Gro-CZ14-2007-17.5IEER | CZ14 | Gro | 2007 | 135to240 | 12 | 17.5 | 154.6277 | 9870.9725 | 1.5484 | 10242.8779 | 1.6666 | 371.9054 | 0.11819
3223 | MCLU-135to240-Gro-CZ14-2011-17.5IEER | CZ14 | Gro | 2011 | 135to240 | 12 | 17.5 | 145.1364 | 10475.3304 | 1.6181 | 10842.4785 | 1.7363 | 367.1481 | 0.11815
3224 | MCLU-135to240-Gro-CZ14-2015-17.5IEER | CZ14 | Gro | 2015 | 135to240 | 12 | 17.5 | 140.2655 | 10367.816 | 1.5986 | 10727.5929 | 1.7151 | 359.7769 | 0.11648
3225 | MCLU-135to240-Gro-CZ14-2020-17.5IEER | CZ14 | Gro | 2020 | 135to240 | 12 | 17.5 | 136.2616 | 10329.214 | 1.5851 | 10684.0245 | 1.7026 | 354.8105 | 0.11748
3226 | MCLU-135to240-Hsp-CZ14-2003-17.5IEER | CZ14 | Hsp | 2003 | 135to240 | 12 | 17.5 | 686.8236 | 4388.7891 | 0.75622 | 4856.8837 | 0.88071 | 468.0946 | 0.12449
3227 | MCLU-135to240-Hsp-CZ14-2007-17.5IEER | CZ14 | Hsp | 2007 | 135to240 | 12 | 17.5 | 686.6231 | 4388.8471 | 0.75576 | 4856.6421 | 0.88003 | 467.795 | 0.12427
3228 | MCLU-135to240-Hsp-CZ14-2011-17.5IEER | CZ14 | Hsp | 2011 | 135to240 | 12 | 17.5 | 680.4571 | 4399.0496 | 0.74204 | 4866.0874 | 0.86626 | 467.0378 | 0.12423
3229 | MCLU-135to240-Hsp-CZ14-2015-17.5IEER | CZ14 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 4361.853 | 0.73176 | 4829.0883 | 0.85614 | 467.2353 | 0.12438
3230 | MCLU-135to240-Hsp-CZ14-2020-17.5IEER | CZ14 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3837.4675 | 0.65595 | 4305.2127 | 0.77882 | 467.7452 | 0.12287
3231 | MCLU-135to240-Htl-CZ14-2003-17.5IEER | CZ14 | Htl | 2003 | 135to240 | 12 | 17.5 | 315.5883 | 3264.3584 | 0.6721 | 3370.04 | 0.70504 | 105.6816 | 0.032933
3232 | MCLU-135to240-Htl-CZ14-2007-17.5IEER | CZ14 | Htl | 2007 | 135to240 | 12 | 17.5 | 315.1763 | 3125.4295 | 0.62983 | 3231.1032 | 0.66269 | 105.6737 | 0.032863
3233 | MCLU-135to240-Htl-CZ14-2011-17.5IEER | CZ14 | Htl | 2011 | 135to240 | 12 | 17.5 | 305.0943 | 3152.958 | 0.63416 | 3258.3448 | 0.6669 | 105.3868 | 0.032745
3234 | MCLU-135to240-Htl-CZ14-2015-17.5IEER | CZ14 | Htl | 2015 | 135to240 | 12 | 17.5 | 271.1093 | 3209.7127 | 0.64033 | 3322.0014 | 0.67582 | 112.2888 | 0.035487
3235 | MCLU-135to240-Htl-CZ14-2020-17.5IEER | CZ14 | Htl | 2020 | 135to240 | 12 | 17.5 | 269.0611 | 3124.0088 | 0.62944 | 3234.557 | 0.66423 | 110.5482 | 0.034784
3236 | MCLU-135to240-MBT-CZ14-2003-17.5IEER | CZ14 | MBT | 2003 | 135to240 | 12 | 17.5 | 451.0231 | 3393.1511 | 0.57015 | 3624.5933 | 0.66806 | 231.4422 | 0.09791
3237 | MCLU-135to240-MBT-CZ14-2007-17.5IEER | CZ14 | MBT | 2007 | 135to240 | 12 | 17.5 | 443.3614 | 3446.6859 | 0.57642 | 3676.0394 | 0.67392 | 229.3536 | 0.097501
3238 | MCLU-135to240-MBT-CZ14-2011-17.5IEER | CZ14 | MBT | 2011 | 135to240 | 12 | 17.5 | 419.0126 | 3582.5659 | 0.59066 | 3808.0369 | 0.68783 | 225.471 | 0.097166
3239 | MCLU-135to240-MBT-CZ14-2015-17.5IEER | CZ14 | MBT | 2015 | 135to240 | 12 | 17.5 | 409.6827 | 3622.248 | 0.59401 | 3847.5208 | 0.6919 | 225.2728 | 0.097884
3240 | MCLU-135to240-MBT-CZ14-2020-17.5IEER | CZ14 | MBT | 2020 | 135to240 | 12 | 17.5 | 384.5398 | 3459.2279 | 0.57162 | 3683.9493 | 0.66981 | 224.7214 | 0.098192
3241 | MCLU-135to240-MLI-CZ14-2003-17.5IEER | CZ14 | MLI | 2003 | 135to240 | 12 | 17.5 | 284.3274 | 2517.0886 | 0.43451 | 2743.4058 | 0.51108 | 226.3173 | 0.076571
3242 | MCLU-135to240-MLI-CZ14-2007-17.5IEER | CZ14 | MLI | 2007 | 135to240 | 12 | 17.5 | 278.9365 | 2557.8263 | 0.43944 | 2783.5975 | 0.51622 | 225.7712 | 0.076783
3243 | MCLU-135to240-MLI-CZ14-2011-17.5IEER | CZ14 | MLI | 2011 | 135to240 | 12 | 17.5 | 246.4248 | 2845.8422 | 0.47051 | 3068.8222 | 0.54834 | 222.98 | 0.077837
3244 | MCLU-135to240-MLI-CZ14-2015-17.5IEER | CZ14 | MLI | 2015 | 135to240 | 12 | 17.5 | 243.7461 | 2855.4511 | 0.47171 | 3078.554 | 0.54973 | 223.103 | 0.078023
3245 | MCLU-135to240-MLI-CZ14-2020-17.5IEER | CZ14 | MLI | 2020 | 135to240 | 12 | 17.5 | 228.9084 | 2562.5116 | 0.43506 | 2785.283 | 0.5135 | 222.7714 | 0.078433
3246 | MCLU-135to240-Mtl-CZ14-2003-17.5IEER | CZ14 | Mtl | 2003 | 135to240 | 12 | 17.5 | 55.8975 | 3238.4078 | 0.64849 | 3321.4378 | 0.66982 | 83.03 | 0.02133
3247 | MCLU-135to240-Mtl-CZ14-2007-17.5IEER | CZ14 | Mtl | 2007 | 135to240 | 12 | 17.5 | 55.8975 | 3087.8705 | 0.60227 | 3170.7138 | 0.62356 | 82.8433 | 0.02129
3248 | MCLU-135to240-Mtl-CZ14-2011-17.5IEER | CZ14 | Mtl | 2011 | 135to240 | 12 | 17.5 | 53.3848 | 3121.5545 | 0.61024 | 3204.3826 | 0.63158 | 82.8281 | 0.021344
3249 | MCLU-135to240-Mtl-CZ14-2015-17.5IEER | CZ14 | Mtl | 2015 | 135to240 | 12 | 17.5 | 45.7445 | 3218.7394 | 0.61803 | 3307.8049 | 0.64149 | 89.0655 | 0.023462
3250 | MCLU-135to240-Mtl-CZ14-2020-17.5IEER | CZ14 | Mtl | 2020 | 135to240 | 12 | 17.5 | 45.6001 | 3151.5368 | 0.6095 | 3239.1106 | 0.63251 | 87.5738 | 0.023014
3251 | MCLU-135to240-Nrs-CZ14-2003-17.5IEER | CZ14 | Nrs | 2003 | 135to240 | 12 | 17.5 | 187.0738 | 4548.2174 | 0.85577 | 4772.8476 | 0.91401 | 224.6303 | 0.05824
3252 | MCLU-135to240-Nrs-CZ14-2007-17.5IEER | CZ14 | Nrs | 2007 | 135to240 | 12 | 17.5 | 186.8968 | 4455.8832 | 0.8258 | 4680.1931 | 0.88378 | 224.31 | 0.057978
3253 | MCLU-135to240-Nrs-CZ14-2011-17.5IEER | CZ14 | Nrs | 2011 | 135to240 | 12 | 17.5 | 185.4192 | 4494.197 | 0.82413 | 4717.3805 | 0.88186 | 223.1835 | 0.05773
3254 | MCLU-135to240-Nrs-CZ14-2015-17.5IEER | CZ14 | Nrs | 2015 | 135to240 | 12 | 17.5 | 183.1807 | 4403.9455 | 0.78801 | 4626.4844 | 0.84578 | 222.539 | 0.057775
3255 | MCLU-135to240-Nrs-CZ14-2020-17.5IEER | CZ14 | Nrs | 2020 | 135to240 | 12 | 17.5 | 182.4593 | 4041.0414 | 0.73207 | 4263.4579 | 0.78912 | 222.4165 | 0.057052
3256 | MCLU-135to240-OfL-CZ14-2003-17.5IEER | CZ14 | OfL | 2003 | 135to240 | 12 | 17.5 | 530.9693 | 3130.4385 | 0.53209 | 3351.4103 | 0.59194 | 220.9718 | 0.059856
3257 | MCLU-135to240-OfL-CZ14-2007-17.5IEER | CZ14 | OfL | 2007 | 135to240 | 12 | 17.5 | 530.2979 | 3133.6966 | 0.53246 | 3354.5318 | 0.59225 | 220.8351 | 0.059787
3258 | MCLU-135to240-OfL-CZ14-2011-17.5IEER | CZ14 | OfL | 2011 | 135to240 | 12 | 17.5 | 507.0063 | 3222.0038 | 0.54009 | 3439.0529 | 0.59978 | 217.0491 | 0.059691
3259 | MCLU-135to240-OfL-CZ14-2015-17.5IEER | CZ14 | OfL | 2015 | 135to240 | 12 | 17.5 | 512.2186 | 3141.5924 | 0.53067 | 3360.3695 | 0.59023 | 218.7771 | 0.059557
3260 | MCLU-135to240-OfL-CZ14-2020-17.5IEER | CZ14 | OfL | 2020 | 135to240 | 12 | 17.5 | 499.8227 | 2989.9419 | 0.51061 | 3209.8768 | 0.57035 | 219.9349 | 0.05974
3261 | MCLU-135to240-OfS-CZ14-2003-17.5IEER | CZ14 | OfS | 2003 | 135to240 | 12 | 17.5 | 36.3943 | 2346.6885 | 0.41742 | 2569.8394 | 0.47646 | 223.1509 | 0.059037
3262 | MCLU-135to240-OfS-CZ14-2007-17.5IEER | CZ14 | OfS | 2007 | 135to240 | 12 | 17.5 | 36.2891 | 2351.6829 | 0.41771 | 2574.4195 | 0.47655 | 222.7365 | 0.05884
3263 | MCLU-135to240-OfS-CZ14-2011-17.5IEER | CZ14 | OfS | 2011 | 135to240 | 12 | 17.5 | 35.5796 | 2368.122 | 0.41764 | 2589.7368 | 0.47655 | 221.6148 | 0.058908
3264 | MCLU-135to240-OfS-CZ14-2015-17.5IEER | CZ14 | OfS | 2015 | 135to240 | 12 | 17.5 | 32.8281 | 2487.1259 | 0.43136 | 2706.114 | 0.4898 | 218.9881 | 0.05844
3265 | MCLU-135to240-OfS-CZ14-2020-17.5IEER | CZ14 | OfS | 2020 | 135to240 | 12 | 17.5 | 32.0335 | 2352.0677 | 0.41053 | 2571.4052 | 0.46905 | 219.3375 | 0.058519
3266 | MCLU-135to240-RFF-CZ14-2003-17.5IEER | CZ14 | RFF | 2003 | 135to240 | 12 | 17.5 | 9.6557 | 4579.0687 | 0.92917 | 4951.7403 | 1.0463 | 372.6717 | 0.11709
3267 | MCLU-135to240-RFF-CZ14-2007-17.5IEER | CZ14 | RFF | 2007 | 135to240 | 12 | 17.5 | 9.5543 | 4621.1529 | 0.93541 | 4994.466 | 1.0526 | 373.3131 | 0.1172
3268 | MCLU-135to240-RFF-CZ14-2011-17.5IEER | CZ14 | RFF | 2011 | 135to240 | 12 | 17.5 | 8.994 | 4867.7807 | 0.96311 | 5243.0278 | 1.0798 | 375.2471 | 0.11669
3269 | MCLU-135to240-RFF-CZ14-2015-17.5IEER | CZ14 | RFF | 2015 | 135to240 | 12 | 17.5 | 8.9612 | 4663.2316 | 0.92858 | 5041.3075 | 1.046 | 378.0759 | 0.11738
3270 | MCLU-135to240-RFF-CZ14-2020-17.5IEER | CZ14 | RFF | 2020 | 135to240 | 12 | 17.5 | 8.6083 | 4279.3876 | 0.86953 | 4660.2207 | 0.98783 | 380.8331 | 0.11829
3271 | MCLU-135to240-RSD-CZ14-2003-17.5IEER | CZ14 | RSD | 2003 | 135to240 | 12 | 17.5 | 18.0913 | 4331.6425 | 0.86871 | 4651.5339 | 0.98916 | 319.8914 | 0.12045
3272 | MCLU-135to240-RSD-CZ14-2007-17.5IEER | CZ14 | RSD | 2007 | 135to240 | 12 | 17.5 | 17.8854 | 4374.9666 | 0.87465 | 4695.8148 | 0.99515 | 320.8482 | 0.1205
3273 | MCLU-135to240-RSD-CZ14-2011-17.5IEER | CZ14 | RSD | 2011 | 135to240 | 12 | 17.5 | 17.5089 | 4459.5197 | 0.88539 | 4782.3254 | 1.0062 | 322.8056 | 0.12078
3274 | MCLU-135to240-RSD-CZ14-2015-17.5IEER | CZ14 | RSD | 2015 | 135to240 | 12 | 17.5 | 17.3347 | 4305.5241 | 0.85978 | 4629.15 | 0.98139 | 323.6259 | 0.12161
3275 | MCLU-135to240-RSD-CZ14-2020-17.5IEER | CZ14 | RSD | 2020 | 135to240 | 12 | 17.5 | 16.4739 | 3854.2098 | 0.78701 | 4184.1992 | 0.90916 | 329.9894 | 0.12216
3276 | MCLU-135to240-Rt3-CZ14-2003-17.5IEER | CZ14 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 328.8981 | 4418.452 | 0.87227 | 4750.6051 | 0.99628 | 332.1532 | 0.12401
3277 | MCLU-135to240-Rt3-CZ14-2007-17.5IEER | CZ14 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 327.7277 | 4431.9416 | 0.87388 | 4763.4352 | 0.99756 | 331.4935 | 0.12368
3278 | MCLU-135to240-Rt3-CZ14-2011-17.5IEER | CZ14 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 306.4437 | 4712.2293 | 0.90209 | 5036.1657 | 1.0267 | 323.9363 | 0.12464
3279 | MCLU-135to240-Rt3-CZ14-2015-17.5IEER | CZ14 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 296.9699 | 4403.2427 | 0.8544 | 4731.8699 | 0.98023 | 328.6272 | 0.12583
3280 | MCLU-135to240-Rt3-CZ14-2020-17.5IEER | CZ14 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 285.2699 | 4083.2677 | 0.80601 | 4415.4727 | 0.93274 | 332.2051 | 0.12673
3281 | MCLU-135to240-RtL-CZ14-2003-17.5IEER | CZ14 | RtL | 2003 | 135to240 | 12 | 17.5 | 288.8702 | 4776.6149 | 0.93543 | 5137.9864 | 1.0689 | 361.3715 | 0.1335
3282 | MCLU-135to240-RtL-CZ14-2007-17.5IEER | CZ14 | RtL | 2007 | 135to240 | 12 | 17.5 | 284.3349 | 4844.959 | 0.94579 | 5204.235 | 1.0789 | 359.276 | 0.1331
3283 | MCLU-135to240-RtL-CZ14-2011-17.5IEER | CZ14 | RtL | 2011 | 135to240 | 12 | 17.5 | 270.5602 | 5076.7941 | 0.97538 | 5429.6941 | 1.1091 | 352.8999 | 0.13376
3284 | MCLU-135to240-RtL-CZ14-2015-17.5IEER | CZ14 | RtL | 2015 | 135to240 | 12 | 17.5 | 263.2521 | 4877.3898 | 0.94942 | 5233.9777 | 1.0847 | 356.588 | 0.13525
3285 | MCLU-135to240-RtL-CZ14-2020-17.5IEER | CZ14 | RtL | 2020 | 135to240 | 12 | 17.5 | 248.7868 | 4682.9631 | 0.92872 | 5041.0006 | 1.0657 | 358.0375 | 0.13703
3286 | MCLU-135to240-RtS-CZ14-2003-17.5IEER | CZ14 | RtS | 2003 | 135to240 | 12 | 17.5 | 21.7527 | 3022.0474 | 0.62471 | 3387.045 | 0.73883 | 364.9976 | 0.11413
3287 | MCLU-135to240-RtS-CZ14-2007-17.5IEER | CZ14 | RtS | 2007 | 135to240 | 12 | 17.5 | 21.4419 | 3058.9688 | 0.62958 | 3423.6825 | 0.74342 | 364.7137 | 0.11384
3288 | MCLU-135to240-RtS-CZ14-2011-17.5IEER | CZ14 | RtS | 2011 | 135to240 | 12 | 17.5 | 20.1147 | 3231.6981 | 0.64672 | 3593.2531 | 0.75906 | 361.555 | 0.11234
3289 | MCLU-135to240-RtS-CZ14-2015-17.5IEER | CZ14 | RtS | 2015 | 135to240 | 12 | 17.5 | 19.8354 | 2967.1657 | 0.60884 | 3301.5889 | 0.71867 | 334.4232 | 0.10982
3290 | MCLU-135to240-RtS-CZ14-2020-17.5IEER | CZ14 | RtS | 2020 | 135to240 | 12 | 17.5 | 19.0356 | 2818.3393 | 0.58662 | 3153.1126 | 0.69713 | 334.7734 | 0.11051
3291 | MCLU-135to240-SCn-CZ14-2003-17.5IEER | CZ14 | SCn | 2003 | 135to240 | 12 | 17.5 | 382.6483 | 2226.6579 | 0.35316 | 2531.7132 | 0.44156 | 305.0553 | 0.088395
3292 | MCLU-135to240-SCn-CZ14-2007-17.5IEER | CZ14 | SCn | 2007 | 135to240 | 12 | 17.5 | 362.0074 | 2332.5932 | 0.36662 | 2639.9669 | 0.45621 | 307.3737 | 0.089589
3293 | MCLU-135to240-SCn-CZ14-2011-17.5IEER | CZ14 | SCn | 2011 | 135to240 | 12 | 17.5 | 308.9728 | 2674.784 | 0.40113 | 2987.7719 | 0.49295 | 312.988 | 0.091816
3294 | MCLU-135to240-SCn-CZ14-2015-17.5IEER | CZ14 | SCn | 2015 | 135to240 | 12 | 17.5 | 317.2632 | 2578.3876 | 0.38379 | 2884.8264 | 0.47399 | 306.4388 | 0.090196
3295 | MCLU-135to240-SCn-CZ14-2020-17.5IEER | CZ14 | SCn | 2020 | 135to240 | 12 | 17.5 | 285.3895 | 2492.8578 | 0.37894 | 2799.6255 | 0.46699 | 306.7677 | 0.088053
3296 | MCLU-135to240-WRf-CZ14-2003-17.5IEER | CZ14 | WRf | 2003 | 135to240 | 12 | 17.5 | 13.1887 | 289674.9079 | 39.6441 | 290077.8715 | 39.7285 | 402.9636 | 0.084466
3297 | MCLU-135to240-WRf-CZ14-2007-17.5IEER | CZ14 | WRf | 2007 | 135to240 | 12 | 17.5 | 12.7592 | 289162.4827 | 38.5468 | 289571.5617 | 38.6297 | 409.079 | 0.082873
3298 | MCLU-135to240-WRf-CZ14-2011-17.5IEER | CZ14 | WRf | 2011 | 135to240 | 12 | 17.5 | 12.0274 | 295952.6662 | 38.3585 | 296366.5454 | 38.4297 | 413.8792 | 0.07124
3299 | MCLU-135to240-WRf-CZ14-2015-17.5IEER | CZ14 | WRf | 2015 | 135to240 | 12 | 17.5 | 14.4062 | 246755.5485 | 32.0052 | 247012.0015 | 32.0627 | 256.453 | 0.057541
3300 | MCLU-135to240-WRf-CZ14-2020-17.5IEER | CZ14 | WRf | 2020 | 135to240 | 12 | 17.5 | 14.1218 | 237665.817 | 30.8528 | 237901.8559 | 30.9034 | 236.0389 | 0.05067
3301 | MCLU-135to240-Asm-CZ15-2003-17.5IEER | CZ15 | Asm | 2003 | 135to240 | 12 | 17.5 | 568.5636 | 1928.591 | 0.54513 | 2383.9119 | 0.71519 | 455.3209 | 0.17006
3302 | MCLU-135to240-Asm-CZ15-2007-17.5IEER | CZ15 | Asm | 2007 | 135to240 | 12 | 17.5 | 562.9782 | 1941.8689 | 0.5481 | 2396.9057 | 0.7181 | 455.0368 | 0.17
3303 | MCLU-135to240-Asm-CZ15-2011-17.5IEER | CZ15 | Asm | 2011 | 135to240 | 12 | 17.5 | 534.8717 | 2005.5249 | 0.55271 | 2456.7441 | 0.72043 | 451.2192 | 0.16772
3304 | MCLU-135to240-Asm-CZ15-2015-17.5IEER | CZ15 | Asm | 2015 | 135to240 | 12 | 17.5 | 517.8653 | 2021.9566 | 0.55735 | 2471.6969 | 0.72463 | 449.7404 | 0.16728
3305 | MCLU-135to240-Asm-CZ15-2020-17.5IEER | CZ15 | Asm | 2020 | 135to240 | 12 | 17.5 | 504.8998 | 1947.129 | 0.54527 | 2395.4531 | 0.71083 | 448.3241 | 0.16556
3306 | MCLU-135to240-ECC-CZ15-2003-17.5IEER | CZ15 | ECC | 2003 | 135to240 | 12 | 17.5 | 1300.4476 | 2120.0614 | 0.63295 | 2475.3495 | 0.79918 | 355.2881 | 0.16623
3307 | MCLU-135to240-ECC-CZ15-2007-17.5IEER | CZ15 | ECC | 2007 | 135to240 | 12 | 17.5 | 1297.3734 | 2121.6935 | 0.6325 | 2475.9294 | 0.79825 | 354.2359 | 0.16574
3308 | MCLU-135to240-ECC-CZ15-2011-17.5IEER | CZ15 | ECC | 2011 | 135to240 | 12 | 17.5 | 1259.2123 | 2132.4099 | 0.62324 | 2476.8533 | 0.78659 | 344.4435 | 0.16335
3309 | MCLU-135to240-ECC-CZ15-2015-17.5IEER | CZ15 | ECC | 2015 | 135to240 | 12 | 17.5 | 1216.2218 | 2144.7691 | 0.62119 | 2485.4202 | 0.78678 | 340.651 | 0.16559
3310 | MCLU-135to240-ECC-CZ15-2020-17.5IEER | CZ15 | ECC | 2020 | 135to240 | 12 | 17.5 | 1181.4102 | 1921.4437 | 0.58437 | 2260.4069 | 0.75103 | 338.9632 | 0.16665
3311 | MCLU-135to240-EPr-CZ15-2003-17.5IEER | CZ15 | EPr | 2003 | 135to240 | 12 | 17.5 | 233.325 | 1336.4447 | 0.31323 | 1571.1332 | 0.40847 | 234.6884 | 0.09524
3312 | MCLU-135to240-EPr-CZ15-2007-17.5IEER | CZ15 | EPr | 2007 | 135to240 | 12 | 17.5 | 231.2117 | 1341.922 | 0.31368 | 1574.6469 | 0.40788 | 232.7249 | 0.094196
3313 | MCLU-135to240-EPr-CZ15-2011-17.5IEER | CZ15 | EPr | 2011 | 135to240 | 12 | 17.5 | 224.773 | 1357.5801 | 0.31193 | 1584.928 | 0.40472 | 227.3479 | 0.092789
3314 | MCLU-135to240-EPr-CZ15-2015-17.5IEER | CZ15 | EPr | 2015 | 135to240 | 12 | 17.5 | 216.7642 | 1347.2492 | 0.30596 | 1568.2012 | 0.40008 | 220.952 | 0.094124
3315 | MCLU-135to240-EPr-CZ15-2020-17.5IEER | CZ15 | EPr | 2020 | 135to240 | 12 | 17.5 | 209.9902 | 1215.2529 | 0.28408 | 1433.3239 | 0.37813 | 218.071 | 0.094044
3316 | MCLU-135to240-ERC-CZ15-2003-17.5IEER | CZ15 | ERC | 2003 | 135to240 | 12 | 17.5 | 10.7622 | 1212.1107 | 0.2402 | 1440.2866 | 0.27103 | 228.1759 | 0.030832
3317 | MCLU-135to240-ERC-CZ15-2007-17.5IEER | CZ15 | ERC | 2007 | 135to240 | 12 | 17.5 | 10.7178 | 1213.2135 | 0.24012 | 1439.7538 | 0.27002 | 226.5403 | 0.029902
3318 | MCLU-135to240-ERC-CZ15-2011-17.5IEER | CZ15 | ERC | 2011 | 135to240 | 12 | 17.5 | 10.2032 | 1221.9952 | 0.22934 | 1438.6613 | 0.25354 | 216.6662 | 0.024202
3319 | MCLU-135to240-ERC-CZ15-2015-17.5IEER | CZ15 | ERC | 2015 | 135to240 | 12 | 17.5 | 10.1324 | 1183.3857 | 0.22437 | 1377.9725 | 0.24737 | 194.5868 | 0.022997
3320 | MCLU-135to240-ERC-CZ15-2020-17.5IEER | CZ15 | ERC | 2020 | 135to240 | 12 | 17.5 | 9.9227 | 1071.4161 | 0.20516 | 1263.2591 | 0.22684 | 191.843 | 0.021671
3321 | MCLU-135to240-ESe-CZ15-2003-17.5IEER | CZ15 | ESe | 2003 | 135to240 | 12 | 17.5 | 675.9147 | 1529.8053 | 0.29876 | 1792.2107 | 0.393 | 262.4054 | 0.094242
3322 | MCLU-135to240-ESe-CZ15-2007-17.5IEER | CZ15 | ESe | 2007 | 135to240 | 12 | 17.5 | 673.4063 | 1532.3665 | 0.29863 | 1793.8846 | 0.3925 | 261.518 | 0.093869
3323 | MCLU-135to240-ESe-CZ15-2011-17.5IEER | CZ15 | ESe | 2011 | 135to240 | 12 | 17.5 | 653.3754 | 1528.2033 | 0.28801 | 1777.3536 | 0.37927 | 249.1504 | 0.091262
3324 | MCLU-135to240-ESe-CZ15-2015-17.5IEER | CZ15 | ESe | 2015 | 135to240 | 12 | 17.5 | 639.3777 | 1515.8253 | 0.28186 | 1759.3313 | 0.37392 | 243.5061 | 0.09206
3325 | MCLU-135to240-ESe-CZ15-2020-17.5IEER | CZ15 | ESe | 2020 | 135to240 | 12 | 17.5 | 620.8234 | 1356.7197 | 0.27023 | 1598.4353 | 0.36272 | 241.7155 | 0.092488
3326 | MCLU-135to240-EUn-CZ15-2003-17.5IEER | CZ15 | EUn | 2003 | 135to240 | 12 | 17.5 | 3802.125 | 2332.3581 | 0.74045 | 2686.4367 | 0.88642 | 354.0786 | 0.14598
3327 | MCLU-135to240-EUn-CZ15-2007-17.5IEER | CZ15 | EUn | 2007 | 135to240 | 12 | 17.5 | 3780.2432 | 2317.8726 | 0.73384 | 2671.4944 | 0.87975 | 353.6218 | 0.1459
3328 | MCLU-135to240-EUn-CZ15-2011-17.5IEER | CZ15 | EUn | 2011 | 135to240 | 12 | 17.5 | 3624.2497 | 2371.4593 | 0.73859 | 2722.6089 | 0.88478 | 351.1496 | 0.14619
3329 | MCLU-135to240-EUn-CZ15-2015-17.5IEER | CZ15 | EUn | 2015 | 135to240 | 12 | 17.5 | 3473.9696 | 2393.742 | 0.74318 | 2745.4744 | 0.89209 | 351.7325 | 0.14891
3330 | MCLU-135to240-EUn-CZ15-2020-17.5IEER | CZ15 | EUn | 2020 | 135to240 | 12 | 17.5 | 3356.3042 | 2222.3389 | 0.7068 | 2572.9801 | 0.8566 | 350.6413 | 0.1498
3331 | MCLU-135to240-Gro-CZ15-2003-17.5IEER | CZ15 | Gro | 2003 | 135to240 | 12 | 17.5 | 194.7031 | 8679.212 | 1.2334 | 9192.907 | 1.3884 | 513.695 | 0.15499
3332 | MCLU-135to240-Gro-CZ15-2007-17.5IEER | CZ15 | Gro | 2007 | 135to240 | 12 | 17.5 | 191.6158 | 8124.2767 | 1.2267 | 8654.6116 | 1.3867 | 530.3348 | 0.16001
3333 | MCLU-135to240-Gro-CZ15-2011-17.5IEER | CZ15 | Gro | 2011 | 135to240 | 12 | 17.5 | 178.5636 | 8635.6925 | 1.2734 | 9162.299 | 1.4342 | 526.6064 | 0.1608
3334 | MCLU-135to240-Gro-CZ15-2015-17.5IEER | CZ15 | Gro | 2015 | 135to240 | 12 | 17.5 | 173.1801 | 8504.3358 | 1.2478 | 9025.2707 | 1.4073 | 520.9349 | 0.15953
3335 | MCLU-135to240-Gro-CZ15-2020-17.5IEER | CZ15 | Gro | 2020 | 135to240 | 12 | 17.5 | 167.2154 | 8506.2357 | 1.2387 | 9023.2061 | 1.3982 | 516.9705 | 0.1595
3336 | MCLU-135to240-Hsp-CZ15-2003-17.5IEER | CZ15 | Hsp | 2003 | 135to240 | 12 | 17.5 | 756.9592 | 4516.8844 | 0.81487 | 5147.1747 | 0.98542 | 630.2903 | 0.17055
3337 | MCLU-135to240-Hsp-CZ15-2007-17.5IEER | CZ15 | Hsp | 2007 | 135to240 | 12 | 17.5 | 756.5433 | 4516.7703 | 0.81427 | 5146.5369 | 0.98464 | 629.7666 | 0.17038
3338 | MCLU-135to240-Hsp-CZ15-2011-17.5IEER | CZ15 | Hsp | 2011 | 135to240 | 12 | 17.5 | 724.9077 | 4633.367 | 0.817 | 5269.5794 | 0.99145 | 636.2124 | 0.17445
3339 | MCLU-135to240-Hsp-CZ15-2015-17.5IEER | CZ15 | Hsp | 2015 | 135to240 | 12 | 17.5 | 718.1895 | 4628.4762 | 0.81181 | 5266.9372 | 0.98795 | 638.461 | 0.17614
3340 | MCLU-135to240-Hsp-CZ15-2020-17.5IEER | CZ15 | Hsp | 2020 | 135to240 | 12 | 17.5 | 707.971 | 4155.0893 | 0.74499 | 4796.0861 | 0.9225 | 640.9968 | 0.17751
3341 | MCLU-135to240-Htl-CZ15-2003-17.5IEER | CZ15 | Htl | 2003 | 135to240 | 12 | 17.5 | 391.4027 | 3090.9276 | 0.76387 | 3250.8807 | 0.81155 | 159.9531 | 0.047672
3342 | MCLU-135to240-Htl-CZ15-2007-17.5IEER | CZ15 | Htl | 2007 | 135to240 | 12 | 17.5 | 390.8607 | 2926.0456 | 0.70989 | 3085.7479 | 0.75753 | 159.7023 | 0.047639
3343 | MCLU-135to240-Htl-CZ15-2011-17.5IEER | CZ15 | Htl | 2011 | 135to240 | 12 | 17.5 | 378.1084 | 2961.9764 | 0.70971 | 3120.6988 | 0.75747 | 158.7224 | 0.047761
3344 | MCLU-135to240-Htl-CZ15-2015-17.5IEER | CZ15 | Htl | 2015 | 135to240 | 12 | 17.5 | 337.4722 | 3027.2082 | 0.7004 | 3195.9298 | 0.75189 | 168.7216 | 0.051486
3345 | MCLU-135to240-Htl-CZ15-2020-17.5IEER | CZ15 | Htl | 2020 | 135to240 | 12 | 17.5 | 335.3123 | 2952.9629 | 0.69077 | 3119.5934 | 0.74198 | 166.6305 | 0.05121
3346 | MCLU-135to240-MBT-CZ15-2003-17.5IEER | CZ15 | MBT | 2003 | 135to240 | 12 | 17.5 | 569.3717 | 3018.2713 | 0.47416 | 3352.7141 | 0.60293 | 334.4428 | 0.12877
3347 | MCLU-135to240-MBT-CZ15-2007-17.5IEER | CZ15 | MBT | 2007 | 135to240 | 12 | 17.5 | 560.78 | 3051.6161 | 0.47572 | 3383.5805 | 0.60411 | 331.9644 | 0.12839
3348 | MCLU-135to240-MBT-CZ15-2011-17.5IEER | CZ15 | MBT | 2011 | 135to240 | 12 | 17.5 | 532.7467 | 3133.0129 | 0.47744 | 3459.7379 | 0.60521 | 326.7249 | 0.12777
3349 | MCLU-135to240-MBT-CZ15-2015-17.5IEER | CZ15 | MBT | 2015 | 135to240 | 12 | 17.5 | 523.5151 | 3147.0418 | 0.47706 | 3473.1978 | 0.60575 | 326.156 | 0.12869
3350 | MCLU-135to240-MBT-CZ15-2020-17.5IEER | CZ15 | MBT | 2020 | 135to240 | 12 | 17.5 | 496.2159 | 2984.1214 | 0.45775 | 3308.0049 | 0.58707 | 323.8835 | 0.12931
3351 | MCLU-135to240-MLI-CZ15-2003-17.5IEER | CZ15 | MLI | 2003 | 135to240 | 12 | 17.5 | 358.5191 | 2341.8764 | 0.38294 | 2657.806 | 0.47528 | 315.9296 | 0.092341
3352 | MCLU-135to240-MLI-CZ15-2007-17.5IEER | CZ15 | MLI | 2007 | 135to240 | 12 | 17.5 | 353.0865 | 2364.9935 | 0.38435 | 2679.7786 | 0.4768 | 314.7851 | 0.092452
3353 | MCLU-135to240-MLI-CZ15-2011-17.5IEER | CZ15 | MLI | 2011 | 135to240 | 12 | 17.5 | 314.5767 | 2560.1033 | 0.38569 | 2868.7016 | 0.47533 | 308.5982 | 0.089639
3354 | MCLU-135to240-MLI-CZ15-2015-17.5IEER | CZ15 | MLI | 2015 | 135to240 | 12 | 17.5 | 311.987 | 2561.406 | 0.38591 | 2869.7892 | 0.47549 | 308.3832 | 0.08958
3355 | MCLU-135to240-MLI-CZ15-2020-17.5IEER | CZ15 | MLI | 2020 | 135to240 | 12 | 17.5 | 296.3414 | 2300.5908 | 0.35797 | 2606.7998 | 0.44765 | 306.209 | 0.089687
3356 | MCLU-135to240-Mtl-CZ15-2003-17.5IEER | CZ15 | Mtl | 2003 | 135to240 | 12 | 17.5 | 70.1059 | 3085.2396 | 0.733 | 3202.8624 | 0.76402 | 117.6229 | 0.03102
3357 | MCLU-135to240-Mtl-CZ15-2007-17.5IEER | CZ15 | Mtl | 2007 | 135to240 | 12 | 17.5 | 70.1059 | 2900.8587 | 0.67461 | 3018.247 | 0.70555 | 117.3884 | 0.030938
3358 | MCLU-135to240-Mtl-CZ15-2011-17.5IEER | CZ15 | Mtl | 2011 | 135to240 | 12 | 17.5 | 67.0998 | 2958.7582 | 0.67695 | 3076.9496 | 0.70849 | 118.1914 | 0.031548
3359 | MCLU-135to240-Mtl-CZ15-2015-17.5IEER | CZ15 | Mtl | 2015 | 135to240 | 12 | 17.5 | 57.8311 | 3077.4853 | 0.66182 | 3205.0437 | 0.69671 | 127.5584 | 0.034892
3360 | MCLU-135to240-Mtl-CZ15-2020-17.5IEER | CZ15 | Mtl | 2020 | 135to240 | 12 | 17.5 | 57.6814 | 3020.3667 | 0.65475 | 3146.3178 | 0.68932 | 125.9511 | 0.034575
3361 | MCLU-135to240-Nrs-CZ15-2003-17.5IEER | CZ15 | Nrs | 2003 | 135to240 | 12 | 17.5 | 208.028 | 4912.9209 | 0.95886 | 5204.3629 | 1.0396 | 291.4419 | 0.080709
3362 | MCLU-135to240-Nrs-CZ15-2007-17.5IEER | CZ15 | Nrs | 2007 | 135to240 | 12 | 17.5 | 207.5777 | 4774.8815 | 0.91892 | 5066.0589 | 0.99945 | 291.1774 | 0.080524
3363 | MCLU-135to240-Nrs-CZ15-2011-17.5IEER | CZ15 | Nrs | 2011 | 135to240 | 12 | 17.5 | 200.5828 | 4894.3074 | 0.92455 | 5189.6347 | 1.0061 | 295.3273 | 0.081557
3364 | MCLU-135to240-Nrs-CZ15-2015-17.5IEER | CZ15 | Nrs | 2015 | 135to240 | 12 | 17.5 | 194.4846 | 4832.2496 | 0.89256 | 5129.8796 | 0.97551 | 297.63 | 0.082942
3365 | MCLU-135to240-Nrs-CZ15-2020-17.5IEER | CZ15 | Nrs | 2020 | 135to240 | 12 | 17.5 | 191.9867 | 4508.0337 | 0.8433 | 4804.0393 | 0.92568 | 296.0056 | 0.082383
3366 | MCLU-135to240-OfL-CZ15-2003-17.5IEER | CZ15 | OfL | 2003 | 135to240 | 12 | 17.5 | 643.0033 | 2921.1301 | 0.44091 | 3235.9553 | 0.50182 | 314.8252 | 0.060905
3367 | MCLU-135to240-OfL-CZ15-2007-17.5IEER | CZ15 | OfL | 2007 | 135to240 | 12 | 17.5 | 642.8288 | 2920.5674 | 0.44069 | 3235.0369 | 0.50144 | 314.4695 | 0.060754
3368 | MCLU-135to240-OfL-CZ15-2011-17.5IEER | CZ15 | OfL | 2011 | 135to240 | 12 | 17.5 | 613.4512 | 2984.324 | 0.44273 | 3294.9157 | 0.50195 | 310.5917 | 0.059219
3369 | MCLU-135to240-OfL-CZ15-2015-17.5IEER | CZ15 | OfL | 2015 | 135to240 | 12 | 17.5 | 621.3032 | 2918.0573 | 0.43804 | 3228.1435 | 0.49751 | 310.0862 | 0.059478
3370 | MCLU-135to240-OfL-CZ15-2020-17.5IEER | CZ15 | OfL | 2020 | 135to240 | 12 | 17.5 | 608.1217 | 2782.9225 | 0.42234 | 3092.5233 | 0.48172 | 309.6008 | 0.059376
3371 | MCLU-135to240-OfS-CZ15-2003-17.5IEER | CZ15 | OfS | 2003 | 135to240 | 12 | 17.5 | 44.1867 | 2282.6103 | 0.35311 | 2598.6728 | 0.41548 | 316.0626 | 0.062366
3372 | MCLU-135to240-OfS-CZ15-2007-17.5IEER | CZ15 | OfS | 2007 | 135to240 | 12 | 17.5 | 44.0569 | 2285.8214 | 0.35313 | 2600.8131 | 0.41506 | 314.9917 | 0.061926
3373 | MCLU-135to240-OfS-CZ15-2011-17.5IEER | CZ15 | OfS | 2011 | 135to240 | 12 | 17.5 | 42.491 | 2318.1215 | 0.34951 | 2628.7925 | 0.40909 | 310.6711 | 0.059576
3374 | MCLU-135to240-OfS-CZ15-2015-17.5IEER | CZ15 | OfS | 2015 | 135to240 | 12 | 17.5 | 39.4408 | 2400.0498 | 0.35428 | 2707.3806 | 0.41295 | 307.3309 | 0.058671
3375 | MCLU-135to240-OfS-CZ15-2020-17.5IEER | CZ15 | OfS | 2020 | 135to240 | 12 | 17.5 | 38.5418 | 2281.6353 | 0.33767 | 2587.9167 | 0.39616 | 306.2814 | 0.05849
3376 | MCLU-135to240-RFF-CZ15-2003-17.5IEER | CZ15 | RFF | 2003 | 135to240 | 12 | 17.5 | 13.0616 | 4079.7302 | 0.88054 | 4600.6535 | 1.0334 | 520.9233 | 0.15289
3377 | MCLU-135to240-RFF-CZ15-2007-17.5IEER | CZ15 | RFF | 2007 | 135to240 | 12 | 17.5 | 12.9472 | 4106.8027 | 0.88393 | 4627.0668 | 1.0367 | 520.2641 | 0.15273
3378 | MCLU-135to240-RFF-CZ15-2011-17.5IEER | CZ15 | RFF | 2011 | 135to240 | 12 | 17.5 | 12.2962 | 4242.1753 | 0.88934 | 4754.384 | 1.0409 | 512.2086 | 0.15152
3379 | MCLU-135to240-RFF-CZ15-2015-17.5IEER | CZ15 | RFF | 2015 | 135to240 | 12 | 17.5 | 12.3051 | 4072.956 | 0.86432 | 4584.1829 | 1.0162 | 511.2269 | 0.15188
3380 | MCLU-135to240-RFF-CZ15-2020-17.5IEER | CZ15 | RFF | 2020 | 135to240 | 12 | 17.5 | 11.8961 | 3768.3497 | 0.8166 | 4280.9019 | 0.97016 | 512.5522 | 0.15356
3381 | MCLU-135to240-RSD-CZ15-2003-17.5IEER | CZ15 | RSD | 2003 | 135to240 | 12 | 17.5 | 24.4278 | 3736.3239 | 0.82607 | 4164.7903 | 0.98349 | 428.4664 | 0.15742
3382 | MCLU-135to240-RSD-CZ15-2007-17.5IEER | CZ15 | RSD | 2007 | 135to240 | 12 | 17.5 | 24.1711 | 3764.4436 | 0.82902 | 4193.4473 | 0.98673 | 429.0037 | 0.15772
3383 | MCLU-135to240-RSD-CZ15-2011-17.5IEER | CZ15 | RSD | 2011 | 135to240 | 12 | 17.5 | 23.3742 | 3860.5326 | 0.83806 | 4291.6445 | 0.99698 | 431.1119 | 0.15892
3384 | MCLU-135to240-RSD-CZ15-2015-17.5IEER | CZ15 | RSD | 2015 | 135to240 | 12 | 17.5 | 23.1295 | 3743.538 | 0.82051 | 4176.4161 | 0.98119 | 432.878 | 0.16068
3385 | MCLU-135to240-RSD-CZ15-2020-17.5IEER | CZ15 | RSD | 2020 | 135to240 | 12 | 17.5 | 21.7761 | 3429.3858 | 0.76952 | 3868.6271 | 0.9332 | 439.2413 | 0.16369
3386 | MCLU-135to240-Rt3-CZ15-2003-17.5IEER | CZ15 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 420.7984 | 3959.7524 | 0.84459 | 4426.7467 | 1.0211 | 466.9944 | 0.17655
3387 | MCLU-135to240-Rt3-CZ15-2007-17.5IEER | CZ15 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 419.3588 | 3968.7002 | 0.84513 | 4434.9342 | 1.0213 | 466.234 | 0.1762
3388 | MCLU-135to240-Rt3-CZ15-2011-17.5IEER | CZ15 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 393.1942 | 4149.9537 | 0.85476 | 4612.5971 | 1.0333 | 462.6434 | 0.17853
3389 | MCLU-135to240-Rt3-CZ15-2015-17.5IEER | CZ15 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 383.5419 | 3880.5883 | 0.81223 | 4344.5684 | 0.99254 | 463.98 | 0.18032
3390 | MCLU-135to240-Rt3-CZ15-2020-17.5IEER | CZ15 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 371.2312 | 3602.5507 | 0.7681 | 4067.3538 | 0.94986 | 464.8031 | 0.18176
3391 | MCLU-135to240-RtL-CZ15-2003-17.5IEER | CZ15 | RtL | 2003 | 135to240 | 12 | 17.5 | 375.6304 | 4175.6379 | 0.86871 | 4693.9307 | 1.0581 | 518.2927 | 0.1894
3392 | MCLU-135to240-RtL-CZ15-2007-17.5IEER | CZ15 | RtL | 2007 | 135to240 | 12 | 17.5 | 370.5663 | 4216.0186 | 0.87264 | 4732.6368 | 1.0621 | 516.6182 | 0.18945
3393 | MCLU-135to240-RtL-CZ15-2011-17.5IEER | CZ15 | RtL | 2011 | 135to240 | 12 | 17.5 | 354.4987 | 4356.9382 | 0.88167 | 4871.2981 | 1.073 | 514.3599 | 0.19132
3394 | MCLU-135to240-RtL-CZ15-2015-17.5IEER | CZ15 | RtL | 2015 | 135to240 | 12 | 17.5 | 346.2544 | 4189.2499 | 0.86387 | 4705.666 | 1.0571 | 516.4161 | 0.19323
3395 | MCLU-135to240-RtL-CZ15-2020-17.5IEER | CZ15 | RtL | 2020 | 135to240 | 12 | 17.5 | 328.4626 | 4024.8837 | 0.85062 | 4542.7594 | 1.0471 | 517.8757 | 0.19649
3396 | MCLU-135to240-RtS-CZ15-2003-17.5IEER | CZ15 | RtS | 2003 | 135to240 | 12 | 17.5 | 28.3009 | 2843.2044 | 0.62564 | 3353.1297 | 0.78514 | 509.9253 | 0.1595
3397 | MCLU-135to240-RtS-CZ15-2007-17.5IEER | CZ15 | RtS | 2007 | 135to240 | 12 | 17.5 | 27.9236 | 2868.6823 | 0.62761 | 3378.7862 | 0.78723 | 510.1039 | 0.15962
3398 | MCLU-135to240-RtS-CZ15-2011-17.5IEER | CZ15 | RtS | 2011 | 135to240 | 12 | 17.5 | 26.3689 | 2959.9827 | 0.6268 | 3465.2241 | 0.78588 | 505.2414 | 0.15908
3399 | MCLU-135to240-RtS-CZ15-2015-17.5IEER | CZ15 | RtS | 2015 | 135to240 | 12 | 17.5 | 26.2124 | 2732.668 | 0.60024 | 3190.9378 | 0.75949 | 458.2698 | 0.15925
3400 | MCLU-135to240-RtS-CZ15-2020-17.5IEER | CZ15 | RtS | 2020 | 135to240 | 12 | 17.5 | 25.3898 | 2596.7928 | 0.57879 | 3054.4872 | 0.73888 | 457.6944 | 0.16009
3401 | MCLU-135to240-SCn-CZ15-2003-17.5IEER | CZ15 | SCn | 2003 | 135to240 | 12 | 17.5 | 529.9396 | 1986.2565 | 0.28838 | 2401.782 | 0.38902 | 415.5255 | 0.10064
3402 | MCLU-135to240-SCn-CZ15-2007-17.5IEER | CZ15 | SCn | 2007 | 135to240 | 12 | 17.5 | 507.5827 | 2045.1846 | 0.2934 | 2462.4443 | 0.39513 | 417.2597 | 0.10173
3403 | MCLU-135to240-SCn-CZ15-2011-17.5IEER | CZ15 | SCn | 2011 | 135to240 | 12 | 17.5 | 449.0653 | 2214.0498 | 0.29411 | 2638.278 | 0.39763 | 424.2282 | 0.10352
3404 | MCLU-135to240-SCn-CZ15-2015-17.5IEER | CZ15 | SCn | 2015 | 135to240 | 12 | 17.5 | 453.3259 | 2170.2059 | 0.29017 | 2582.9878 | 0.39318 | 412.7819 | 0.10302
3405 | MCLU-135to240-SCn-CZ15-2020-17.5IEER | CZ15 | SCn | 2020 | 135to240 | 12 | 17.5 | 420.4229 | 2057.8931 | 0.27889 | 2472.1394 | 0.38376 | 414.2463 | 0.10487
3406 | MCLU-135to240-WRf-CZ15-2003-17.5IEER | CZ15 | WRf | 2003 | 135to240 | 12 | 17.5 | 20.0021 | 204702.9188 | 26.9307 | 205146.2319 | 27.0177 | 443.3131 | 0.08701
3407 | MCLU-135to240-WRf-CZ15-2007-17.5IEER | CZ15 | WRf | 2007 | 135to240 | 12 | 17.5 | 19.4739 | 201394.272 | 25.5505 | 201859.7539 | 25.6437 | 465.4819 | 0.093287
3408 | MCLU-135to240-WRf-CZ15-2011-17.5IEER | CZ15 | WRf | 2011 | 135to240 | 12 | 17.5 | 18.6007 | 199719.8544 | 24.6231 | 200300.6169 | 24.7334 | 580.7625 | 0.11037
3409 | MCLU-135to240-WRf-CZ15-2015-17.5IEER | CZ15 | WRf | 2015 | 135to240 | 12 | 17.5 | 16.8833 | 219808.8414 | 27.1047 | 220323.7425 | 27.2123 | 514.9011 | 0.1076
3410 | MCLU-135to240-WRf-CZ15-2020-17.5IEER | CZ15 | WRf | 2020 | 135to240 | 12 | 17.5 | 17.1501 | 204175.771 | 25.0921 | 204646.8321 | 25.1927 | 471.0611 | 0.10065
3411 | MCLU-135to240-Asm-CZ16-2003-17.5IEER | CZ16 | Asm | 2003 | 135to240 | 12 | 17.5 | 350.4692 | 1902.1578 | 0.56428 | 2106.3608 | 0.67647 | 204.2031 | 0.11219
3412 | MCLU-135to240-Asm-CZ16-2007-17.5IEER | CZ16 | Asm | 2007 | 135to240 | 12 | 17.5 | 346.4223 | 1914.2171 | 0.56884 | 2121.9873 | 0.68097 | 207.7703 | 0.11212
3413 | MCLU-135to240-Asm-CZ16-2011-17.5IEER | CZ16 | Asm | 2011 | 135to240 | 12 | 17.5 | 329.8082 | 1991.6503 | 0.57837 | 2204.6656 | 0.6899 | 213.0153 | 0.11152
3414 | MCLU-135to240-Asm-CZ16-2015-17.5IEER | CZ16 | Asm | 2015 | 135to240 | 12 | 17.5 | 314.5654 | 2050.1007 | 0.5892 | 2261.8951 | 0.70069 | 211.7944 | 0.11149
3415 | MCLU-135to240-Asm-CZ16-2020-17.5IEER | CZ16 | Asm | 2020 | 135to240 | 12 | 17.5 | 303.149 | 1936.412 | 0.56848 | 2148.5604 | 0.67991 | 212.1484 | 0.11143
3416 | MCLU-135to240-ECC-CZ16-2003-17.5IEER | CZ16 | ECC | 2003 | 135to240 | 12 | 17.5 | 858.1646 | 2252.5309 | 0.36478 | 2395.0161 | 0.44046 | 142.4852 | 0.075681
3417 | MCLU-135to240-ECC-CZ16-2007-17.5IEER | CZ16 | ECC | 2007 | 135to240 | 12 | 17.5 | 857.7277 | 2253.3366 | 0.36422 | 2395.67 | 0.43974 | 142.3334 | 0.075515
3418 | MCLU-135to240-ECC-CZ16-2011-17.5IEER | CZ16 | ECC | 2011 | 135to240 | 12 | 17.5 | 843.8958 | 2281.4992 | 0.35643 | 2420.6597 | 0.43026 | 139.1605 | 0.073829
3419 | MCLU-135to240-ECC-CZ16-2015-17.5IEER | CZ16 | ECC | 2015 | 135to240 | 12 | 17.5 | 790.8101 | 2397.6876 | 0.36247 | 2537.727 | 0.43635 | 140.0394 | 0.073881
3420 | MCLU-135to240-ECC-CZ16-2020-17.5IEER | CZ16 | ECC | 2020 | 135to240 | 12 | 17.5 | 748.5374 | 2124.8149 | 0.33673 | 2269.0588 | 0.4105 | 144.2439 | 0.073772
3421 | MCLU-135to240-EPr-CZ16-2003-17.5IEER | CZ16 | EPr | 2003 | 135to240 | 12 | 17.5 | 131.4668 | 1566.089 | 0.041276 | 1660.9466 | 0.046979 | 94.8576 | 0.0057023
3422 | MCLU-135to240-EPr-CZ16-2007-17.5IEER | CZ16 | EPr | 2007 | 135to240 | 12 | 17.5 | 131.0519 | 1570.4499 | 0.040841 | 1665.0188 | 0.046309 | 94.5689 | 0.0054683
3423 | MCLU-135to240-EPr-CZ16-2011-17.5IEER | CZ16 | EPr | 2011 | 135to240 | 12 | 17.5 | 129.3239 | 1590.4362 | 0.040748 | 1684.669 | 0.046179 | 94.2328 | 0.0054312
3424 | MCLU-135to240-EPr-CZ16-2015-17.5IEER | CZ16 | EPr | 2015 | 135to240 | 12 | 17.5 | 119.5484 | 1681.072 | 0.03064 | 1775.7457 | 0.032243 | 94.6738 | 0.0016026
3425 | MCLU-135to240-EPr-CZ16-2020-17.5IEER | CZ16 | EPr | 2020 | 135to240 | 12 | 17.5 | 114.0673 | 1484.5031 | 0.020757 | 1580.2499 | 0.022005 | 95.7469 | 0.0012482
3426 | MCLU-135to240-ERC-CZ16-2003-17.5IEER | CZ16 | ERC | 2003 | 135to240 | 12 | 17.5 | 5.7931 | 1308.2362 | 0.059237 | 1393.1701 | 0.068271 | 84.9339 | 0.0090345
3427 | MCLU-135to240-ERC-CZ16-2007-17.5IEER | CZ16 | ERC | 2007 | 135to240 | 12 | 17.5 | 5.7895 | 1309.1906 | 0.058811 | 1393.9693 | 0.067744 | 84.7787 | 0.0089331
3428 | MCLU-135to240-ERC-CZ16-2011-17.5IEER | CZ16 | ERC | 2011 | 135to240 | 12 | 17.5 | 5.6685 | 1331.8196 | 0.055503 | 1416.6079 | 0.063511 | 84.7883 | 0.0080078
3429 | MCLU-135to240-ERC-CZ16-2015-17.5IEER | CZ16 | ERC | 2015 | 135to240 | 12 | 17.5 | 5.4807 | 1342.5724 | 0.042368 | 1423.0451 | 0.04695 | 80.4727 | 0.0045823
3430 | MCLU-135to240-ERC-CZ16-2020-17.5IEER | CZ16 | ERC | 2020 | 135to240 | 12 | 17.5 | 5.2203 | 1184.3978 | 0.032811 | 1267.9542 | 0.037459 | 83.5564 | 0.0046474
3431 | MCLU-135to240-ESe-CZ16-2003-17.5IEER | CZ16 | ESe | 2003 | 135to240 | 12 | 17.5 | 421.9249 | 1637.4241 | 0.11647 | 1741.3781 | 0.13587 | 103.9539 | 0.019399
3432 | MCLU-135to240-ESe-CZ16-2007-17.5IEER | CZ16 | ESe | 2007 | 135to240 | 12 | 17.5 | 420.9762 | 1640.7771 | 0.11597 | 1744.6171 | 0.13528 | 103.8399 | 0.019309
3433 | MCLU-135to240-ESe-CZ16-2011-17.5IEER | CZ16 | ESe | 2011 | 135to240 | 12 | 17.5 | 408.4978 | 1683.8578 | 0.10584 | 1784.8368 | 0.12052 | 100.979 | 0.014674
3434 | MCLU-135to240-ESe-CZ16-2015-17.5IEER | CZ16 | ESe | 2015 | 135to240 | 12 | 17.5 | 389.061 | 1742.5934 | 0.096923 | 1843.4589 | 0.10766 | 100.8655 | 0.010738
3435 | MCLU-135to240-ESe-CZ16-2020-17.5IEER | CZ16 | ESe | 2020 | 135to240 | 12 | 17.5 | 369.3876 | 1528.8623 | 0.077427 | 1632.1443 | 0.086939 | 103.282 | 0.0095125
3436 | MCLU-135to240-EUn-CZ16-2003-17.5IEER | CZ16 | EUn | 2003 | 135to240 | 12 | 17.5 | 2597.7736 | 2541.3149 | 0.54458 | 2686.3733 | 0.62736 | 145.0583 | 0.082773
3437 | MCLU-135to240-EUn-CZ16-2007-17.5IEER | CZ16 | EUn | 2007 | 135to240 | 12 | 17.5 | 2591.5158 | 2523.9239 | 0.53784 | 2668.7378 | 0.62049 | 144.8139 | 0.082642
3438 | MCLU-135to240-EUn-CZ16-2011-17.5IEER | CZ16 | EUn | 2011 | 135to240 | 12 | 17.5 | 2528.2219 | 2564.7285 | 0.53854 | 2706.8977 | 0.62055 | 142.1692 | 0.08201
3439 | MCLU-135to240-EUn-CZ16-2015-17.5IEER | CZ16 | EUn | 2015 | 135to240 | 12 | 17.5 | 2264.7005 | 2786.2433 | 0.55689 | 2931.3101 | 0.6411 | 145.0668 | 0.084215
3440 | MCLU-135to240-EUn-CZ16-2020-17.5IEER | CZ16 | EUn | 2020 | 135to240 | 12 | 17.5 | 2164.7717 | 2566.8285 | 0.53094 | 2711.5155 | 0.61398 | 144.687 | 0.083036
3441 | MCLU-135to240-Gro-CZ16-2003-17.5IEER | CZ16 | Gro | 2003 | 135to240 | 12 | 17.5 | 97.1936 | 16159.1858 | 2.3745 | 16478.0162 | 2.4744 | 318.8304 | 0.099889
3442 | MCLU-135to240-Gro-CZ16-2007-17.5IEER | CZ16 | Gro | 2007 | 135to240 | 12 | 17.5 | 95.3686 | 14827.0786 | 2.3108 | 15104.2434 | 2.4131 | 277.1647 | 0.10225
3443 | MCLU-135to240-Gro-CZ16-2011-17.5IEER | CZ16 | Gro | 2011 | 135to240 | 12 | 17.5 | 89.3994 | 15802.6678 | 2.4279 | 16060.9778 | 2.5282 | 258.3099 | 0.10026
3444 | MCLU-135to240-Gro-CZ16-2015-17.5IEER | CZ16 | Gro | 2015 | 135to240 | 12 | 17.5 | 85.2707 | 15843.0758 | 2.4201 | 16080.8732 | 2.5129 | 237.7974 | 0.092806
3445 | MCLU-135to240-Gro-CZ16-2020-17.5IEER | CZ16 | Gro | 2020 | 135to240 | 12 | 17.5 | 82.3494 | 15880.8592 | 2.4148 | 16097.3465 | 2.5022 | 216.4873 | 0.087387
3446 | MCLU-135to240-Hsp-CZ16-2003-17.5IEER | CZ16 | Hsp | 2003 | 135to240 | 12 | 17.5 | 680.4571 | 4088.182 | 0.71764 | 4424.775 | 0.81904 | 336.5929 | 0.1014
3447 | MCLU-135to240-Hsp-CZ16-2007-17.5IEER | CZ16 | Hsp | 2007 | 135to240 | 12 | 17.5 | 680.4571 | 4087.8073 | 0.71701 | 4424.3423 | 0.81821 | 336.535 | 0.1012
3448 | MCLU-135to240-Hsp-CZ16-2011-17.5IEER | CZ16 | Hsp | 2011 | 135to240 | 12 | 17.5 | 680.4571 | 4075.9872 | 0.69959 | 4411.134 | 0.79998 | 335.1468 | 0.10039
3449 | MCLU-135to240-Hsp-CZ16-2015-17.5IEER | CZ16 | Hsp | 2015 | 135to240 | 12 | 17.5 | 680.4571 | 4049.0538 | 0.6915 | 4384.0435 | 0.7916 | 334.9897 | 0.10011
3450 | MCLU-135to240-Hsp-CZ16-2020-17.5IEER | CZ16 | Hsp | 2020 | 135to240 | 12 | 17.5 | 680.4571 | 3548.7984 | 0.61894 | 3885.6881 | 0.71642 | 336.8897 | 0.097483
3451 | MCLU-135to240-Htl-CZ16-2003-17.5IEER | CZ16 | Htl | 2003 | 135to240 | 12 | 17.5 | 277.9858 | 3845.1992 | 0.68378 | 3914.948 | 0.71111 | 69.7488 | 0.027326
3452 | MCLU-135to240-Htl-CZ16-2007-17.5IEER | CZ16 | Htl | 2007 | 135to240 | 12 | 17.5 | 277.9559 | 3698.6036 | 0.64271 | 3768.7243 | 0.66994 | 70.1206 | 0.027227
3453 | MCLU-135to240-Htl-CZ16-2011-17.5IEER | CZ16 | Htl | 2011 | 135to240 | 12 | 17.5 | 271.4046 | 3658.0424 | 0.64448 | 3729.872 | 0.67157 | 71.8296 | 0.027089
3454 | MCLU-135to240-Htl-CZ16-2015-17.5IEER | CZ16 | Htl | 2015 | 135to240 | 12 | 17.5 | 236.1642 | 3835.4554 | 0.64763 | 3911.2396 | 0.67618 | 75.7842 | 0.028551
3455 | MCLU-135to240-Htl-CZ16-2020-17.5IEER | CZ16 | Htl | 2020 | 135to240 | 12 | 17.5 | 234.7191 | 3732.0581 | 0.63447 | 3806.4114 | 0.66229 | 74.3533 | 0.02782
3456 | MCLU-135to240-MBT-CZ16-2003-17.5IEER | CZ16 | MBT | 2003 | 135to240 | 12 | 17.5 | 347.0573 | 4047.7721 | 0.5638 | 4191.3408 | 0.64157 | 143.5687 | 0.077769
3457 | MCLU-135to240-MBT-CZ16-2007-17.5IEER | CZ16 | MBT | 2007 | 135to240 | 12 | 17.5 | 343.3037 | 4091.2105 | 0.56699 | 4233.874 | 0.64414 | 142.6634 | 0.077146
3458 | MCLU-135to240-MBT-CZ16-2011-17.5IEER | CZ16 | MBT | 2011 | 135to240 | 12 | 17.5 | 328.7522 | 4209.3312 | 0.57544 | 4349.7767 | 0.65193 | 140.4454 | 0.076489
3459 | MCLU-135to240-MBT-CZ16-2015-17.5IEER | CZ16 | MBT | 2015 | 135to240 | 12 | 17.5 | 320.1948 | 4279.9019 | 0.58052 | 4420.1504 | 0.65681 | 140.2485 | 0.076294
3460 | MCLU-135to240-MBT-CZ16-2020-17.5IEER | CZ16 | MBT | 2020 | 135to240 | 12 | 17.5 | 299.0438 | 4097.9647 | 0.55889 | 4236.9452 | 0.63412 | 138.9805 | 0.075227
3461 | MCLU-135to240-MLI-CZ16-2003-17.5IEER | CZ16 | MLI | 2003 | 135to240 | 12 | 17.5 | 229.1842 | 2829.6871 | 0.39239 | 2987.8452 | 0.4473 | 158.1581 | 0.054905
3462 | MCLU-135to240-MLI-CZ16-2007-17.5IEER | CZ16 | MLI | 2007 | 135to240 | 12 | 17.5 | 224.9642 | 2878.8579 | 0.39685 | 3036.5637 | 0.45143 | 157.7057 | 0.054582
3463 | MCLU-135to240-MLI-CZ16-2011-17.5IEER | CZ16 | MLI | 2011 | 135to240 | 12 | 17.5 | 185.0938 | 3465.2394 | 0.45864 | 3618.3926 | 0.51289 | 153.1531 | 0.054246
3464 | MCLU-135to240-MLI-CZ16-2015-17.5IEER | CZ16 | MLI | 2015 | 135to240 | 12 | 17.5 | 183.377 | 3472.8297 | 0.45868 | 3626.5178 | 0.51299 | 153.6881 | 0.054316
3465 | MCLU-135to240-MLI-CZ16-2020-17.5IEER | CZ16 | MLI | 2020 | 135to240 | 12 | 17.5 | 168.9977 | 3150.0244 | 0.42272 | 3304.5351 | 0.47611 | 154.5107 | 0.05339
3466 | MCLU-135to240-Mtl-CZ16-2003-17.5IEER | CZ16 | Mtl | 2003 | 135to240 | 12 | 17.5 | 51.7653 | 3849.2324 | 0.58472 | 3916.1401 | 0.60429 | 66.9076 | 0.019569
3467 | MCLU-135to240-Mtl-CZ16-2007-17.5IEER | CZ16 | Mtl | 2007 | 135to240 | 12 | 17.5 | 51.7653 | 3705.2107 | 0.54679 | 3771.8963 | 0.56632 | 66.6856 | 0.019536
3468 | MCLU-135to240-Mtl-CZ16-2011-17.5IEER | CZ16 | Mtl | 2011 | 135to240 | 12 | 17.5 | 50.7449 | 3653.9756 | 0.54545 | 3721.6075 | 0.56507 | 67.632 | 0.01962
3469 | MCLU-135to240-Mtl-CZ16-2015-17.5IEER | CZ16 | Mtl | 2015 | 135to240 | 12 | 17.5 | 42.6208 | 3754.4888 | 0.56167 | 3829.6048 | 0.5833 | 75.1159 | 0.021632
3470 | MCLU-135to240-Mtl-CZ16-2020-17.5IEER | CZ16 | Mtl | 2020 | 135to240 | 12 | 17.5 | 42.4853 | 3687.5921 | 0.55232 | 3761.4232 | 0.57346 | 73.8311 | 0.021146
3471 | MCLU-135to240-Nrs-CZ16-2003-17.5IEER | CZ16 | Nrs | 2003 | 135to240 | 12 | 17.5 | 182.1406 | 4162.5849 | 0.78658 | 4330.3728 | 0.83527 | 167.7879 | 0.048687
3472 | MCLU-135to240-Nrs-CZ16-2007-17.5IEER | CZ16 | Nrs | 2007 | 135to240 | 12 | 17.5 | 182.1371 | 4103.4528 | 0.76224 | 4270.6218 | 0.81072 | 167.169 | 0.048478
3473 | MCLU-135to240-Nrs-CZ16-2011-17.5IEER | CZ16 | Nrs | 2011 | 135to240 | 12 | 17.5 | 181.9538 | 4083.9339 | 0.75744 | 4249.1086 | 0.80557 | 165.1747 | 0.048136
3474 | MCLU-135to240-Nrs-CZ16-2015-17.5IEER | CZ16 | Nrs | 2015 | 135to240 | 12 | 17.5 | 181.647 | 3985.1993 | 0.72014 | 4147.7792 | 0.76764 | 162.5799 | 0.047491
3475 | MCLU-135to240-Nrs-CZ16-2020-17.5IEER | CZ16 | Nrs | 2020 | 135to240 | 12 | 17.5 | 181.607 | 3627.6231 | 0.6627 | 3790.9893 | 0.70894 | 163.3662 | 0.046234
3476 | MCLU-135to240-OfL-CZ16-2003-17.5IEER | CZ16 | OfL | 2003 | 135to240 | 12 | 17.5 | 522.0671 | 2904.0901 | 0.45679 | 3044.1232 | 0.50094 | 140.033 | 0.044151
3477 | MCLU-135to240-OfL-CZ16-2007-17.5IEER | CZ16 | OfL | 2007 | 135to240 | 12 | 17.5 | 521.6201 | 2906.3688 | 0.45697 | 3046.3308 | 0.50112 | 139.962 | 0.044148
3478 | MCLU-135to240-OfL-CZ16-2011-17.5IEER | CZ16 | OfL | 2011 | 135to240 | 12 | 17.5 | 506.8313 | 2949.6472 | 0.45864 | 3087.2123 | 0.50191 | 137.565 | 0.043265
3479 | MCLU-135to240-OfL-CZ16-2015-17.5IEER | CZ16 | OfL | 2015 | 135to240 | 12 | 17.5 | 503.1822 | 2923.1277 | 0.45208 | 3062.0201 | 0.49427 | 138.8925 | 0.042191
3480 | MCLU-135to240-OfL-CZ16-2020-17.5IEER | CZ16 | OfL | 2020 | 135to240 | 12 | 17.5 | 491.1268 | 2773.0868 | 0.43453 | 2912.9899 | 0.47664 | 139.9031 | 0.042117
3481 | MCLU-135to240-OfS-CZ16-2003-17.5IEER | CZ16 | OfS | 2003 | 135to240 | 12 | 17.5 | 33.2131 | 2277.6448 | 0.36128 | 2422.2857 | 0.40647 | 144.6409 | 0.045189
3482 | MCLU-135to240-OfS-CZ16-2007-17.5IEER | CZ16 | OfS | 2007 | 135to240 | 12 | 17.5 | 33.2051 | 2277.9261 | 0.36075 | 2422.4137 | 0.40584 | 144.4876 | 0.045091
3483 | MCLU-135to240-OfS-CZ16-2011-17.5IEER | CZ16 | OfS | 2011 | 135to240 | 12 | 17.5 | 32.791 | 2281.1708 | 0.35917 | 2424.8395 | 0.4038 | 143.6687 | 0.044627
3484 | MCLU-135to240-OfS-CZ16-2015-17.5IEER | CZ16 | OfS | 2015 | 135to240 | 12 | 17.5 | 28.9962 | 2508.5927 | 0.37865 | 2651.2922 | 0.42095 | 142.6996 | 0.042293
3485 | MCLU-135to240-OfS-CZ16-2020-17.5IEER | CZ16 | OfS | 2020 | 135to240 | 12 | 17.5 | 28.2704 | 2362.6119 | 0.35839 | 2505.8111 | 0.40021 | 143.1991 | 0.041823
3486 | MCLU-135to240-RFF-CZ16-2003-17.5IEER | CZ16 | RFF | 2003 | 135to240 | 12 | 17.5 | 8.189 | 4782.1343 | 1.0161 | 5023.1943 | 1.1225 | 241.06 | 0.10639
3487 | MCLU-135to240-RFF-CZ16-2007-17.5IEER | CZ16 | RFF | 2007 | 135to240 | 12 | 17.5 | 8.1027 | 4830.2892 | 1.0232 | 5073.1926 | 1.1304 | 242.9034 | 0.1071
3488 | MCLU-135to240-RFF-CZ16-2011-17.5IEER | CZ16 | RFF | 2011 | 135to240 | 12 | 17.5 | 7.5371 | 5166.4015 | 1.0654 | 5421.4242 | 1.1773 | 255.0227 | 0.11186
3489 | MCLU-135to240-RFF-CZ16-2015-17.5IEER | CZ16 | RFF | 2015 | 135to240 | 12 | 17.5 | 7.3494 | 5050.5281 | 1.0438 | 5308.5028 | 1.1573 | 257.9746 | 0.11351
3490 | MCLU-135to240-RFF-CZ16-2020-17.5IEER | CZ16 | RFF | 2020 | 135to240 | 12 | 17.5 | 6.8824 | 4705.0016 | 0.99075 | 4972.8013 | 1.1078 | 267.7997 | 0.11704
3491 | MCLU-135to240-RSD-CZ16-2003-17.5IEER | CZ16 | RSD | 2003 | 135to240 | 12 | 17.5 | 13.5662 | 5137.5382 | 1.0859 | 5367.1702 | 1.2089 | 229.6319 | 0.12307
3492 | MCLU-135to240-RSD-CZ16-2007-17.5IEER | CZ16 | RSD | 2007 | 135to240 | 12 | 17.5 | 13.3777 | 5206.934 | 1.0976 | 5437.8651 | 1.2207 | 230.9312 | 0.1231
3493 | MCLU-135to240-RSD-CZ16-2011-17.5IEER | CZ16 | RSD | 2011 | 135to240 | 12 | 17.5 | 13.0533 | 5333.8479 | 1.1183 | 5567.2185 | 1.2416 | 233.3705 | 0.12325
3494 | MCLU-135to240-RSD-CZ16-2015-17.5IEER | CZ16 | RSD | 2015 | 135to240 | 12 | 17.5 | 12.596 | 5275.8459 | 1.1099 | 5505.9854 | 1.2328 | 230.1395 | 0.12293
3495 | MCLU-135to240-RSD-CZ16-2020-17.5IEER | CZ16 | RSD | 2020 | 135to240 | 12 | 17.5 | 11.5247 | 4853.2176 | 1.04 | 5075.2152 | 1.1593 | 221.9977 | 0.11927
3496 | MCLU-135to240-Rt3-CZ16-2003-17.5IEER | CZ16 | Rt3 | 2003 | 135to240 | 12 | 17.5 | 236.4914 | 5578.5113 | 1.1611 | 5784.2057 | 1.2671 | 205.6944 | 0.10602
3497 | MCLU-135to240-Rt3-CZ16-2007-17.5IEER | CZ16 | Rt3 | 2007 | 135to240 | 12 | 17.5 | 236.4183 | 5579.6781 | 1.16 | 5785.1717 | 1.2659 | 205.4935 | 0.10595
3498 | MCLU-135to240-Rt3-CZ16-2011-17.5IEER | CZ16 | Rt3 | 2011 | 135to240 | 12 | 17.5 | 219.7192 | 5996.8068 | 1.209 | 6192.9411 | 1.3142 | 196.1342 | 0.10518
3499 | MCLU-135to240-Rt3-CZ16-2015-17.5IEER | CZ16 | Rt3 | 2015 | 135to240 | 12 | 17.5 | 207.9842 | 5710.34 | 1.1655 | 5911.0267 | 1.2704 | 200.6867 | 0.10495
3500 | MCLU-135to240-Rt3-CZ16-2020-17.5IEER | CZ16 | Rt3 | 2020 | 135to240 | 12 | 17.5 | 198.0109 | 5311.9482 | 1.103 | 5516.4948 | 1.2076 | 204.5466 | 0.10463
3501 | MCLU-135to240-RtL-CZ16-2003-17.5IEER | CZ16 | RtL | 2003 | 135to240 | 12 | 17.5 | 193.2842 | 6429.8633 | 1.3021 | 6671.5259 | 1.4156 | 241.6626 | 0.1135
3502 | MCLU-135to240-RtL-CZ16-2007-17.5IEER | CZ16 | RtL | 2007 | 135to240 | 12 | 17.5 | 191.9157 | 6474.3423 | 1.3075 | 6715.2723 | 1.4203 | 240.93 | 0.11281
3503 | MCLU-135to240-RtL-CZ16-2011-17.5IEER | CZ16 | RtL | 2011 | 135to240 | 12 | 17.5 | 184.0041 | 6761.9971 | 1.346 | 6999.6781 | 1.4578 | 237.681 | 0.11182
3504 | MCLU-135to240-RtL-CZ16-2015-17.5IEER | CZ16 | RtL | 2015 | 135to240 | 12 | 17.5 | 175.5009 | 6596.8013 | 1.3372 | 6846.6677 | 1.4512 | 249.8664 | 0.1141
3505 | MCLU-135to240-RtL-CZ16-2020-17.5IEER | CZ16 | RtL | 2020 | 135to240 | 12 | 17.5 | 164.0615 | 6372.9065 | 1.3319 | 6630.8017 | 1.4453 | 257.8952 | 0.11339
3506 | MCLU-135to240-RtS-CZ16-2003-17.5IEER | CZ16 | RtS | 2003 | 135to240 | 12 | 17.5 | 14.4422 | 3912.017 | 0.83975 | 4160.8097 | 0.93348 | 248.7927 | 0.093729
3507 | MCLU-135to240-RtS-CZ16-2007-17.5IEER | CZ16 | RtS | 2007 | 135to240 | 12 | 17.5 | 14.3466 | 3936.0402 | 0.84058 | 4184.5957 | 0.93393 | 248.5555 | 0.093356
3508 | MCLU-135to240-RtS-CZ16-2011-17.5IEER | CZ16 | RtS | 2011 | 135to240 | 12 | 17.5 | 13.9081 | 4048.3093 | 0.83693 | 4290.7645 | 0.92904 | 242.4552 | 0.092109
3509 | MCLU-135to240-RtS-CZ16-2015-17.5IEER | CZ16 | RtS | 2015 | 135to240 | 12 | 17.5 | 13.5488 | 3758.9742 | 0.79293 | 3966.3068 | 0.88475 | 207.3326 | 0.091814
3510 | MCLU-135to240-RtS-CZ16-2020-17.5IEER | CZ16 | RtS | 2020 | 135to240 | 12 | 17.5 | 13.1721 | 3500.0093 | 0.7507 | 3707.2054 | 0.84255 | 207.1961 | 0.091845
3511 | MCLU-135to240-SCn-CZ16-2003-17.5IEER | CZ16 | SCn | 2003 | 135to240 | 12 | 17.5 | 360.337 | 2084.6926 | 0.25346 | 2283.436 | 0.30476 | 198.7434 | 0.051296
3512 | MCLU-135to240-SCn-CZ16-2007-17.5IEER | CZ16 | SCn | 2007 | 135to240 | 12 | 17.5 | 358.6668 | 2090.6263 | 0.25029 | 2289.083 | 0.30045 | 198.4567 | 0.050168
3513 | MCLU-135to240-SCn-CZ16-2011-17.5IEER | CZ16 | SCn | 2011 | 135to240 | 12 | 17.5 | 323.5777 | 2300.1966 | 0.26092 | 2493.1296 | 0.30985 | 192.933 | 0.048927
3514 | MCLU-135to240-SCn-CZ16-2015-17.5IEER | CZ16 | SCn | 2015 | 135to240 | 12 | 17.5 | 323.2202 | 2282.2236 | 0.25979 | 2472.9915 | 0.30853 | 190.7679 | 0.048738
3515 | MCLU-135to240-SCn-CZ16-2020-17.5IEER | CZ16 | SCn | 2020 | 135to240 | 12 | 17.5 | 320.3503 | 2002.329 | 0.226 | 2192.2881 | 0.27186 | 189.9591 | 0.045856
3516 | MCLU-135to240-WRf-CZ16-2003-17.5IEER | CZ16 | WRf | 2003 | 135to240 | 12 | 17.5 | 10.1257 | 350420.3304 | 47.3487 | 350705.116 | 47.4097 | 284.7855 | 0.061049
3517 | MCLU-135to240-WRf-CZ16-2007-17.5IEER | CZ16 | WRf | 2007 | 135to240 | 12 | 17.5 | 9.7767 | 353316.0164 | 45.7843 | 353612.0827 | 45.8445 | 296.0664 | 0.060262
3518 | MCLU-135to240-WRf-CZ16-2011-17.5IEER | CZ16 | WRf | 2011 | 135to240 | 12 | 17.5 | 9.1375 | 368777.1425 | 46.3727 | 369110.725 | 46.4282 | 333.5825 | 0.055498
3519 | MCLU-135to240-WRf-CZ16-2015-17.5IEER | CZ16 | WRf | 2015 | 135to240 | 12 | 17.5 | 11.0414 | 304730.2703 | 38.3612 | 304947.9384 | 38.4018 | 217.6681 | 0.04068
3520 | MCLU-135to240-WRf-CZ16-2020-17.5IEER | CZ16 | WRf | 2020 | 135to240 | 12 | 17.5 | 10.8152 | 293304.3942 | 36.8772 | 293510.2468 | 36.9121 | 205.8527 | 0.03492