## Summary
HVAC Equipment | Tier | Average Unit Material Only Cost | Sample Size | SW Measure ID | Baseline Description | Baseline Cost ID | Baseline Material Cost | Total Baseline Material Cost | Baseline Labor Cost | Total Baseline Cost | Measure Case Description | Measure Cost ID | Measure Case Material Cost | Measure Labor Cost | Total Measure Cost | Incremental Cost
Natural Gas Wall Furnace | N/A | 676.9 | 14 | SWHC044A | Natural Gas Wall Furnace | SWHC044_02_B001 | 676.9 | 1082.83 | 280.6 | 1363.43 | Ductless Mini-Split Heat Pump (SEER 15) | SWHC044_02_M001 | 1185.23 | 533.17 | 1718.4 | 354.97
Electric Window AC | N/A | 405.9314 | 11 |  | Electric Window AC |  | 405.9314
Ductless Mini-Split Heat Pump (SEER 15) | 1 | 1016.2306 | 15 | SWHC044B | Natural Gas Wall Furnace | SWHC044_02_B001 | 676.9 | 1082.83 | 280.6 | 1363.43 | Ductless Mini-Split Heat Pump (SEER 16) | SWHC044_02_M002 | 1190.79 | 533.17 | 1723.96 | 360.53
Ductless Mini-Split Heat Pump (SEER 16) | 2 | 1021.7898 | 29 |  | Electric Window AC |  | 405.9314
Ductless Mini-Split Heat Pump (SEER 17) | 3 | 1100.8757 | 23 | SWHC044C | Natural Gas Wall Furnace | SWHC044_02_B001 | 676.9 | 1082.83 | 280.6 | 1363.43 | Ductless Mini-Split Heat Pump (SEER 17) | SWHC044_02_M003 | 1269.88 | 533.17 | 1803.05 | 439.62
Ductless Mini-Split Heat Pump (SEER 18) | 4 | 1155.6477 | 41 |  | Electric Window AC |  | 405.9314
|  |  |  | SWHC044D | Natural Gas Wall Furnace | SWHC044_02_B001 | 676.9 | 1082.83 | 280.6 | 1363.43 | Ductless Mini-Split Heat Pump (SEER 18) | SWHC044_02_M004 | 1324.65 | 533.17 | 1857.82 | 494.39
[5 empty] | Electric Window AC |  | 405.9314
Measure | Tier | IMC |  | SWHC044I | Natural Gas Wall Furnace | SWHC044_02_C001 | 676.9 | 676.9 | 145.5 | 822.4 | Ductless Mini-Split Heat Pump (SEER 15) | SWHC044_02_M001 | 1185.23 | 533.17 | 1718.4 | 896
Ductless Mini-Split Heat Pump (SEER 15) | 1 | 354.97
Ductless Mini-Split Heat Pump (SEER 16) | 2 | 360.53 |  | SWHC044J | Natural Gas Wall Furnace | SWHC044_02_C001 | 676.9 | 676.9 | 145.5 | 822.4 | Ductless Mini-Split Heat Pump (SEER 16) | SWHC044_02_M002 | 1190.79 | 533.17 | 1723.96 | 901.56
Ductless Mini-Split Heat Pump (SEER 17) | 3 | 439.62
Ductless Mini-Split Heat Pump (SEER 18) | 4 | 494.39 |  | SWHC044K | Natural Gas Wall Furnace | SWHC044_02_C001 | 676.9 | 676.9 | 145.5 | 822.4 | Ductless Mini-Split Heat Pump (SEER 17) | SWHC044_02_M003 | 1269.88 | 533.17 | 1803.05 | 980.65
Ductless Mini-Split Heat Pump (SEER 15) | 1 (NO AC) | 896
Ductless Mini-Split Heat Pump (SEER 16) | 2 (NO AC) | 901.56 |  | SWHC044L | Natural Gas Wall Furnace | SWHC044_02_C001 | 676.9 | 676.9 | 145.5 | 822.4 | Ductless Mini-Split Heat Pump (SEER 18) | SWHC044_02_M004 | 1324.65 | 533.17 | 1857.82 | 1035.42
Ductless Mini-Split Heat Pump (SEER 17) | 3 (NO AC) | 980.65
Ductless Mini-Split Heat Pump (SEER 18) | 4 (NO AC) | 1035.42

## RSMeans Facilities Construction (hidden)
Line Number | Description | Unit | Crew | Daily Output | Labor Hours | Bare Material | Bare Labor
92910.5 | High Abuse Gypsum Board
510 | 5/8" thick, on walls, on finish included | sqft | 2 Carp | 1800 | 0.009 | 0.77 | 0.41
99123.72 | Walls and Ceilings, Interior
0.44 | Paint 1 coat, smooth finish, roller | sqft | 1 Pord | 1300 | 0.006 | 0.06 | 0.24

## Raw Data Cost
Natural Gas Wall Furnace Horizontal Flow (14.9-37.5kBtuh)
AFUE: 67%
Make | Model | Heating Capacity (BTUH) | AFUE | Height (in) | Width (in) | Unit | Material Cost | Retailer | Source
Williams | 2559622A | 25000 | 70% | 65.75 | 16 | Ea | 556.63 | Home Depot | https://www.homedepot.com/p/Williams-25-000-BTU-Hr-Monterey-Top-Vent-Natural-Gas-Wall-Furnace-High-Altitude-6-000-ft-8-000-ft-2559622A/303170511
Williams | 2509622A | 25000 | 70% | 65.75 | 16 | Ea | 564.3 | Home Depot | https://www.homedepot.com/p/Williams-25-000-BTU-Hr-Monterey-Top-Vent-Wall-Furnace-Natural-Gas-2509622A/303169802
Williams | 2509822 | 25000 | 71% | 65.75 | 16 | Ea | 725 | eComfort | https://www.ecomfort.com/Williams-2509822/p67974.html
Williams | 2519822 | 25000 | 71% | 65.75 | 16 | Ea | 801.6 | Alpine Home Air | https://www.alpinehomeair.com/viewproduct.cfm?productID=453069660
Williams | 3509822 | 35000 | 69% | 65.75 | 16 | Ea | 763.2 | Alpine Home Air | https://www.alpinehomeair.com/viewproduct.cfm?productID=453069474
Williams | 3508232 | 35000 | 75% | 65.75 | 16 | Ea | 1329 | eComfort | https://www.ecomfort.com/Williams-3508232/p71197.html
Williams | 3508632 | 35000 | 75% | 65.75 | 16 | Ea | 1109 | eComfort | https://www.ecomfort.com/Williams-3508632/p71199.html
Williams | 2203822 | 22000 | 67% | 65.75 | 16 | Ea | 955 | eComfort | https://www.ecomfort.com/Williams-2203822/p62307.html
Williams | 2233822 | 22000 | 67% | 28 | 32.125 | Ea | 1038 | Alpine Home Air | https://www.alpinehomeair.com/viewproduct.cfm?productID=453069652
Rinnai | EX22CTN | 21500 | 81% | 22.9 | 29.9 | Ea | 1726.5 | AC Wholesaler | https://www.acwholesalers.com/Rinnai-EX22CTN/p80681.html
Ashley Hearth | DVAG17N | 17000 | 70% | 20 | 27.36 | Ea | 549.99 | Home Depot | https://www.homedepot.com/p/Ashley-Hearth-Products-17-000-BTU-Direct-Vent-Natural-Gas-Heater-DVAG17N/309809918
Williams | 1773512 | 17700 | 76% | 28.125 | 21.75 | Ea | 1564 | eComfort | https://www.ecomfort.com/Williams-1773512/p72691.html
Rinnai | EX17CTN | 16700 | 81% | 22.9 | 29.9 | Ea | 1561.5 | Alpine Home Air | https://www.alpinehomeair.com/viewproduct.cfm?productID=453075464
Empire | DV215SGNAT | 15000 | 69% | 24.88 | 20.25 | Ea | 971.1 | Total Home Supply | https://www.totalhomesupply.com/empire-comfort-systems-dv-215-sgx-15-000-btu-direct-vent-wall-furnace/p/empire-dv215sgx
Window AC (1-2 tons)
Make | Model | Ton | Cooling Capacity (BTUH) | Efficiency |  | Unit | Material Cost | Cost per Ton | Energy Star | Retailer | Source
|  |  |  | EER | SEER
LG | LW1217ERSM | 1 | 12000 | 12 | 14.44 | Ea | 459 | 459 | Yes | Home Depot | https://www.homedepot.com/p/LG-Electronics-12-000-BTU-Window-Smart-Wi-Fi-Air-Conditioner-with-Remote-ENERGY-STAR-in-White-LW1217ERSM/300422888
Toshiba | RAC-WK1211ESCWU | 1 | 12000 | 12 | 14.44 | Ea | 449 | 449 | Yes | Home Depot | https://www.homedepot.com/p/Toshiba-12-000-BTU-115-Volt-Smart-Wi-Fi-Window-Air-Conditioner-with-Remote-and-ENERGY-STAR-RAC-WK1211ESCWU/303408312
Frigidaire | FFRE1233U1 | 1 | 12100 | 12.1 | 14.62 | Ea | 379.99 | 379.99 | Yes | Best Buy | https://www.bestbuy.com/site/frigidaire-550-sq-ft-window-air-conditioner-white/6175508.p?skuId=6175508
GE | AEM14AX | 1.2 | 14300 | 11.9 | 14.25 | Ea | 449 | 374.1667 | Yes | AJ Madison | https://www.ajmadison.com/cgi-bin/ajmadison/AEM14AX.html
Whirlpool | WHAW151BW | 1.25 | 15000 | 11.9 | 14.25 | Ea | 473.99 | 379.192 | Yes | Best Buy | https://www.bestbuy.com/site/whirlpool-700-sq-ft-window-air-conditioner-white/6132636.p?skuId=6132636
LG | LW1516ER | 1.25 | 15000 | 11.9 | 14.25 | Ea | 429.99 | 343.992 | Yes | Lowes | https://www.lowes.com/pd/LG-800-sq-ft-Window-Air-Conditioner-115-Volt-15000-BTU-ENERGY-STAR/1000776706
Friedrich | CP15G10B | 1.25 | 15500 | 11.9 | 14.25 | Ea | 749 | 599.2 | Yes | Amazon | https://www.amazon.com/Friedrich-CP15G10B-Window-Conditioner-ENERGY/dp/B00GM32L1U
Amana | AMAP182BW | 1.5 | 18000 | 11.9 | 14.25 | Ea | 545.99 | 363.9933 | No | Best Buy | https://www.bestbuy.com/site/amana-1000-sq-ft-window-air-conditioner-white/6132608.p?skuId=6132608
LG | LW1816ER | 1.5 | 18000 | 11.8 | 14.07 | Ea | 589 | 392.6667 | Yes | Home Depot | https://www.homedepot.com/p/LG-Electronics-18-000-BTU-230-208-Volt-Window-Air-Conditioner-with-Remote-and-ENERGY-STAR-in-White-LW1816ER/206520618
TCL | TWC-18CR2/UH | 1.5 | 18000 | 11.9 | 14.25 | Ea | 532.7 | 355.1333 | Yes | Lowes | https://www.lowes.com/pd/TCL-1000-sq-ft-Window-Air-Conditioner-115-Volt-18000-BTU-ENERGY-STAR/1000929606
Soleus Air | WS2-18E-201 | 1.525 | 18300 | 11.8 | 14.07 | Ea | 562.59 | 368.9115 | Yes | Lowes | https://www.lowes.com/pd/Soleus-Air-1025-sq-ft-Window-Air-Conditioner-115-Volt-18300-BTU-ENERGY-STAR/1000925858?cm_mmc=shp-_-c-_-prd-_-app-_-google-_-pla-_-235-_-soscooling-_-1000925858-_-0&cm_mmc=src-_-c-_-prd-_-app-_-google-_-appliances-_-PLA_APP_Appliances_Low%20Priority-_--_-0-_-0&gclid=EAIaIQobChMIpLHP3o365QIVmK_sCh1fcAkIEAkYASABEgJF8_D_BwE&gclsrc=aw.ds
Mini-Split Heat Pump
Tier 1: SEER 15, EER: 12.8, HSPF 8.7
Make | Model | Ton | Capacity (BTUH) |  | Efficiency |  |  | Unit | Material Cost | Cost per Ton | Energy Star |  |  | Retailer | Source
|  |  | Cooling | Heating | EER | SEER | HSPF |  |  |  |  | # of Zones | Mount Type
Daikin | X18RMVJUW (RX18RMVJU9 / FTXR18TVJUW) | 1.5 | 18000 | 20000 |  | 14.5 | 9.8 | Ea | 2336 | 1557.3333 | Yes | 1 | Wall | eComfort | https://www.ecomfort.com/Daikin-X18RMVJUW/p99746.html
Daikin | X18RMVJUW (RX18RMVJU9 / FTXR18TVJUW) | 1.5 | 18000 | 20000 |  | 14.5 | 9.8 | Ea | 2465 | 1643.3333 | Yes | 1 | Wall | Total Home Supply | https://www.totalhomesupply.com/p/daikin-ftxr18tvjuw-rx18rmvju9-emura-series-18000-btu-heat-pump-14-5-seer-single-zone-mini-split-system
Daikin | X18RMVJUW (RX18RMVJU9 / FTXR18TVJUW) | 1.5 | 18000 | 20000 |  | 14.5 | 9.8 | Ea | 2336 | 1557.3333 | Yes | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Daikin-X18RMVJUW/p99746.html
ClimateRight | CR12000SACH | 1 | 12000 | 14000 |  | 15 |  | Ea | 1022.79 | 1022.79 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/ClimateRight-ClimateRight-CR12000SACH-12-000-BTU-Ductless-Mini-Split-BTU-Air-Conditioner-Heater-CR12000SACH/304624913
Celiera | 37GWX | 1 | 12500 | 12500 |  | 15.2 | 9.2 | Ea | 994 | 994 | No | 1 | Wall | Lowes | https://www.lowes.com/pd/Celiera-GWX-12500-BTU-540-sq-ft-Single-Ductless-Mini-Split-Air-Conditioner-with-Heater/50236343
Hallman | HMS15A12 | 1 | 12000 | 12000 |  | 15 |  | Ea | 890.98 | 890.98 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Hallman-12-000-BTU-1-Ton-Ductless-Mini-Split-Air-Conditioner-with-Heat-Pump-115V-60HZ-HMS15A12/300169953
Della | 048-MS-18K2V-17S-I+O | 1.5 | 18000 | 18000 |  | 15 |  | Ea | 799.96 | 533.3067 | No | 1 | Wall | Walmart | https://www.walmart.com/ip/DELLA-18-000-BTU-230V-15-SEER-16-5-Installation-Kit-Mini-Split-Heat-Pump-Air-Conditioner-AHRI-Certificate/721196069
Daikin | RXN18NMVJU - FTXN18NMVJU | 1.5 | 18000 | 18000 |  | 15 |  | Ea | 1419 | 946 | No | 1 | Wall | Air Conditioners R Us | http://airconditionersrus.com/en/15-series-wall-mount-15-seer/52-daikin-18000-btu-15-seer-heat-pump-air-conditioner-ductless-mini-split-ftxn18nmvju-rxn18nmvju.html
Hallman | HMS15B18 | 1.5 | 18000 | 18000 |  | 15 |  | Ea | 1096.91 | 731.2733 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Hallman-18-000-BTU-1-5-Ton-Ductless-Mini-Split-Air-Conditioner-with-Heat-Pump-230V-60HZ-HMS15B18/300170707
Hallman | HMS15B24 | 1.8 | 22000 | 22000 |  | 15 |  | Ea | 1199 | 666.1111 | No | 1 | Wall | Hallman | https://hallmanindustries.com/air-conditioners/hms15b24/
Hallman | HMS15B24 | 1.8 | 22000 | 22000 |  | 15 |  | Ea | 1292.63 | 718.1278 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Hallman-22-000-BTU-2-Ton-Ductless-Mini-Split-Air-Conditioner-with-Heat-Pump-230-Volt-60HZ-HMS15B24/300171015
Soleus Air | KFTHP522 | 1.8 | 22000 | 22000 |  | 15 |  | Ea | 1113 | 618.3333 | No | 1 | Wall | AJMadison | https://www.ajmadison.com/cgi-bin/ajmadison/KFTHP522.html
Mitsubishi | MZ-D30NA-1 (MUZ-D30NA-1 / MSZ-D30NA-8) | 2.5 | 30700 | 32600 |  | 14.5 |  | Ea | 2928.75 | 1171.5 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Mitsubishi-MZ-D30NA-1/p56100.html
Fujitsu | 36RLXB (AOU36RLX, ASU36RLXB) | 3 | 36000 | 36000 |  | 15.5 | 9 | Ea | 3373.9 | 1124.6333 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Fujitsu-36RLXB/p65519.html
Fujitsu | 36RLXB (AOU36RLX, ASU36RLXB) | 3 | 36000 | 36000 |  | 15.5 | 9 | Ea | 3205.21 | 1068.4033 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Fujitsu-36RLXB/p65519.html
Mini-Split Heat Pump
Tier 2: SEER 16, EER: 12.5, HSPF 9.0
Make | Model | Ton | Capacity (BTUH) |  | Efficiency |  |  | Unit | Material Cost |  | Energy Star |  |  | Retailer | Source
|  |  | Cooling | Heating | EER | SEER | HSPF |  |  | Cost per Ton |  | # of Zones | Mount Type
Fujitsu | 12RL2 | 1 | 12000 | 14000 |  | 16 | 9 | Ea | 1361 | 1361 | No | 1 | Wall | HVAC Direct | https://hvacdirect.com/fujitsu-12-000-btu-16-seer-ductless-mini-split-heat-pump-system-12rl2.html
Fujitsu | 12RL2 | 1 | 12000 | 14000 |  | 16 | 9 | Ea | 1176.01 | 1176.01 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Fujitsu-12RL2/p65506.html
Panasonic | RE12SKUA | 1 | 12000 | 12000 |  | 16 |  | Ea | 1102 | 1102 | No | 1 | Wall | Walmart | https://www.walmart.com/ip/Panasonic-RE12SKUA-12-000-BTU-16-SEER-Pro-Series-Wall-Mount-Ductless-Mini-Split-Air-Conditioner-Heat-Pump-208-230V/299168365
Panasonic | RE12SKUA | 1 | 12000 | 12000 |  | 16 |  | Ea | 925 | 925 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Panasonic-Heating-and-Cooling-RE12SKUA/p63123.html
Celiera | 35GWX | 1 | 12000 | 12000 |  | 16 |  | Ea | 1484.44 | 1484.44 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Celiera-12-000-BTU-1-Ton-Ductless-Mini-Split-Air-Conditioner-with-Heat-Pump-110V-60Hz-35GWX/204307235
Fujitsu | 18RULX (AOU18RLX / ABU18RULX) | 1.5 | 17800 | 21500 |  | 16 |  | Ea | 2362.56 | 1575.04 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Fujitsu-18RULX/p65770.html
Fujitsu | 18RULX (AOU18RLX / AUU18RCLX) | 1.5 | 17800 | 21000 |  | 16 |  | Ea | 3165.31 | 2110.2067 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Fujitsu-18RCLX/p65604.html
MrCool | DIY-18-HP-230AE | 1.5 | 18000 | 18000 |  | 16 | 9.5 | Ea | 1568 | 1045.3333 | No | 1 | Wall | HVAC Direct | https://hvacdirect.com/mrcool-diy-18-000-btu-ductless-mini-split-ac-and-heat-pump-with-wireless-enabled-smart-controller.html
Carrier | 38MHRBQ18-3 / 40MHHQ18-3 | 1.5 | 18000 | 18000 |  | 16 |  | Ea | 1787 | 1191.3333 | No | 1 | Wall | HVAC Direct | https://hvacdirect.com/carrier-18-000-btu-16-seer-single-zone-heat-pump-system-id9791.html
Ramsond | 55GW2 | 1.5 | 18000 | 18000 |  | 16 |  | Ea | 1423.07 | 948.7133 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Ramsond-18-000-BTU-1-5-Ton-Ductless-Mini-Split-Air-Conditioner-and-Heat-Pump-220V-60Hz-55GW2/203013148
Friedrich | MM18YJ | 1.5 | 18000 | 18000 |  | 16 |  | Ea | 1179 | 786 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Friedrich-MM18YJ/p85754.html
Gree | LIVS24HP230V1BW | 1.8 | 22000 | 26000 |  | 16 |  | Ea | 1499 | 832.7778 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/GREE-LIVO-22-000-BTU-2-Ton-Wi-Fi-Programmable-Ductless-Mini-Split-Air-Conditioner-with-Inverter-Heat-Remote-208-230V-60Hz-LIVS24HP230V1BW/301983314
Gree | LIVS24HP230V1B | 1.8 | 23200 | 26000 |  | 16 |  | Ea | 1532.59 | 851.4389 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/GREE-LIVO-22000-BTU-Ductless-Mini-Split-Air-Conditioner-with-Inverter-Heat-and-Remote-230-Volt-LIVS24HP230V1B/301377904
Friedrich | MM24YJ | 2 | 24000 | 24000 |  | 16 |  | Ea | 1430 | 715 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Friedrich-MM24YJ/p85755.html
MrCool | DIY-24-HP-C-230AE, DIY-24-HP-WMAH-230AE | 2 | 24000 | 25000 |  | 16 | 9 | Ea | 1593.81 | 796.905 | No | 1 | Wall | Amazon | https://www.amazon.com/dp/B07Q5KDKT6/ref=emc_b_5_t
Perfect Aire | 2PAMSH24B-16 | 2 | 24000 | 25000 |  | 16 |  | Ea | 1460.53 | 730.265 | No | 1 | Wall | HVAC Direct | https://hvacdirect.com/perfect-aire-24-000-btu-16-seer-ductless-mini-split-heat-pump-2pamsh24b-16.html
Ramsond | 74GW2 | 2 | 24000 | 24000 |  | 16.4 |  | Ea | 1532.08 | 766.04 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Ramsond-24-000-BTU-2-Ton-Ductless-Mini-Split-Air-Conditioner-and-Heat-Pump-220V-60Hz-74GW2/203013150
Mitsubishi | MZ-WR24NA | 2 | 24000 | 24000 |  | 16 |  | Ea | 1749.95 | 874.975 | No | 1 | Wall | Sylvane | https://www.sylvane.com/mitsubishi-16-seer-24000-btu-wr-series-mini-split-heat-pump.html
Daizuki | DX24X426-16 | 2 | 24000 | 24000 |  | 16 |  | Ea | 1391.51 | 695.755 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Daizuki-24-000-BTU-2-Ton-Ductless-Mini-Split-Air-Conditioner-and-Heat-Pump-208-230V-60Hz-DX24X426-16/302931576
Fujitsu | 30RLXB | 2.5 | 30000 | 30000 |  | 16.5 | 9 | Ea | 2601.9 | 1040.76 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Fujitsu-30RLXB/p65518.html
Fujitsu | 30RLXB | 2.5 | 30000 | 30000 |  | 16.5 | 9 | Ea | 2471.81 | 988.724 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Fujitsu-30RLXB/p65518.html
Gree | LIVS30HP230V1B | 2.5 | 30000 | 33000 |  | 16 |  | Ea | 2019.38 | 807.752 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/GREE-LIVO-28000-BTU-Ductless-Mini-Split-Air-Conditioner-with-Inverter-Heat-and-Remote-230Volt-LIVS30HP230V1B/301377901
Panasonic | KE30NKU | 2.5 | 30600 | 33000 |  | 16 |  | Ea | 2845.74 | 1138.296 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Panasonic-30-000-BTU-2-5-Ton-Ductless-Mini-Split-Air-Conditioner-with-Heat-Pump-208-or-230V-60Hz-KE30NKU/206130549
Daikin | X36NMVJU (RX36NMVJU / FTX36NVJU) | 2.9 | 34400 | 36000 |  | 15.9 | 9.2 | Ea | 2867 | 988.6207 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Daikin-X36NMVJU/p96967.html
EMI | SZ1H36D WALH36D | 3 | 36000 | 36000 |  | 16 | 10 | Ea | 1844 | 614.6667 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/EMI-SZ1H36D-WALH36D/p87755.html
Daikin | RX36NMVJU FTX36NVJU | 3 | 36000 | 36000 |  | 15.9 | 9.2 | Ea | 2649 | 883 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Daikin-RX36NMVJU-FTX36NVJU/p88959.html
Daikin | RX36NMVJU FTX36NVJU | 3 | 36000 | 36000 |  | 15.9 | 9.2 | Ea | 3560.19 | 1186.73 | No | 1 | Wall | The AC Outlet | https://www.theacoutlet.com/rx36nmvju-ftx36nvju-36-000-btu-15-9-seer-daikin-single-zone-ductless-heat-pump-system.html
Pioneer | WYS036GMFI17RL-16 | 3 | 36000 | 36000 |  | 16 |  | Ea | 1998 | 666 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Pioneer-36-000-BTU-3-Ton-16-SEER-Ductless-Mini-Split-Air-Inverter-Wall-Mounted-Air-Conditioner-with-Heat-Pump-208-230V-WYS036GMFI17RL-16/311454573
Mitsubishi | MXZ-8C48NA 2-MSZ-GL24NA-U1 | 4 | 48000 | 48000 |  | 16.8 | 9.5 | Ea | 5396.49 | 1349.1225 | No | 2 | Wall | AC Wholesalers | https://www.acwholesalers.com/Mitsubishi-MXZ-8C48NA-2-MSZ-GL24NA-U1/p57182.html
Mini-Split Heat Pump
Tier 3: SEER 17, EER: 13.3, HSPF 9.4
Make | Model | Ton | Capacity (BTUH) |  | Efficiency |  |  | Unit | Material Cost | Cost per Ton | Energy Star |  |  | Retailer | Source
|  |  | Cooling | Heating | EER | SEER | HSPF |  |  |  |  | # of Zones | Mount Type
Daikin | X12RMVJUS | 1 | 12000 | 13500 |  | 17 | 10 | Ea | 1691 | 1691 | Yes | 1 | Wall | eComfort | https://www.ecomfort.com/Daikin-X12RMVJUS/p99742.html
Daikin | X12RMVJUS | 1 | 12000 | 13500 |  | 17 | 10 | Ea | 1691 | 1691 | Yes | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Daikin-X12RMVJUS/p99742.html
Daikin | X12RMVJUS | 1 | 12000 | 13500 |  | 17 | 10 | Ea | 1691 | 1691 | Yes | 1 | Wall | Power Equipment Direct | https://www.powerequipmentdirect.com/Daikin-X12RMVJUS/p99742.html
Daikin | X12RMVJUW | 1 | 12000 | 13500 |  | 17 | 10 | Ea | 1780 | 1780 | Yes | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Daikin-X12RMVJUW/p99745.html
Daikin | X12RMVJUW | 1 | 12000 | 13500 |  | 17 | 10 | Ea | 1691 | 1691 | Yes | 1 | Wall | eComfort | https://www.ecomfort.com/Daikin-X12RMVJUW/p99745.html
Daikin | X12RMVJUW | 1 | 12000 | 13500 |  | 17 | 10 | Ea | 1691 | 1691 | Yes | 1 | Wall | Power Equipment Direct | https://www.powerequipmentdirect.com/Daikin-X12RMVJUW/p99745.html
Royal Sovereign | RSAC-1817 | 1.5 | 18000 | 18500 |  | 17 |  | Ea | 999.99 | 666.66 | Yes | 1 | Wall | Home Depot | https://www.homedepot.com/p/Royal-Sovereign-18-000-BTU-1-5-Ton-Ductless-Mini-Split-Air-Conditioner-and-Heat-Pump-RSAC-1817/310500431
Royal Sovereign | RSAC-2417 | 2 | 24000 | 24000 |  | 17 |  | Ea | 1399.99 | 699.995 | Yes | 1 | Wall | Home Depot | https://www.homedepot.com/p/Royal-Sovereign-24-000-BTU-2-Ton-Ductless-Mini-Split-Air-Conditioner-and-Heat-Pump-RSAC-2417/310500453
Carrier | 38MHRBQ12-1 / 40MHHQ12-1 | 1 | 12000 | 12000 |  | 17 |  | Ea | 1220 | 1220 | No | 1 | Wall | HVAC Direct | https://hvacdirect.com/carrier-12-000-btu-17-seer-single-zone-heat-pump-system-id9788.html
Perfect Aire | 2PAMSH12A-17.2 | 1 | 12000 | 12000 |  | 17 |  | Ea | 1063.2 | 1063.2 | No | 1 | Wall | HVAC Direct | https://hvacdirect.com/perfect-aire-12-000-btu-17-seer-ductless-mini-split-heat-pump-2pamsh12a-17-2.html
Hessaire | H12HP2A | 1 | 12000 | 12000 |  | 17 |  | Ea | 719 | 719 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Hessaire-12-000-BTU-1-0-Ton-208-230V-Ductless-Mini-Split-Air-Conditioner-Inverter-Heat-Pump-Remote-and-16-ft-Copper-Line-Set-H12HP2A/302894718
Daikin | RXB18AXVJU / FTXB18AXVJU | 1.5 | 18000 | 17900 |  | 17 |  | Ea | 1312 | 874.6667 | No | 1 | Wall | HVAC Direct | https://hvacdirect.com/daikin-17-series-18-000-btu-17-seer-single-zone-ductless-mini-split-heat-pump-system-wall-mounted-xb18axvju-rxb18axvju-ftxb18axvju.html
Daikin | RXB18AXVJU / FTXB18AXVJU | 1.5 | 18000 | 17900 |  | 17 |  | Ea | 1187 | 791.3333 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Daikin-XB18AXVJU/p92459.html
Carrier | 38MHRBQ24-3 / 40MHHQ24-3 | 1.8 | 22000 | 25000 |  | 17 |  | Ea | 2265 | 1258.3333 | No | 1 | Wall | HVAC Direct | https://hvacdirect.com/carrier-22-000-btu-17-seer-single-zone-heat-pump-system-id9792.html
Pioneer | WYS024GMFI19RL-16 | 2 | 24000 | 24000 |  | 17 |  | Ea | 1185.6 | 592.8 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Pioneer-24-000-BTU-2-Ton-17-SEER-Ductless-Mini-Split-Inverter-Wall-Mounted-Air-Conditioner-with-Heat-Pump-208-230-Volt-WYS024GMFI19RL-16/311628196
Daikin | XB24AXVJU (RXB24AXVJU+ FTXB24AXVJU) | 2 | 24000 | 24000 |  | 17 |  | Ea | 1448.9 | 724.45 | No | 1 | Wall | Amazon | https://www.amazon.com/Daikin-Wall-Mounted-Mini-Split-Conditioner-Installation/dp/B07DYD5HJ3
Daikin | XB24AXVJU (RXB24AXVJU+ FTXB24AXVJU) | 2 | 24000 | 24000 |  | 17 |  | Ea | 1405 | 702.5 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Daikin-XB24AXVJU/p92460.html
MrCool | A-24-HP-230B / A-24-HP-WMAH-230B | 2 | 24000 | 24000 |  | 17 |  | Ea | 1296 | 648 | No | 1 | Wall | HVAC Direct | https://hvacdirect.com/advantage-3rd-gen-24-000-btu-2-ton-ductless-mini-split-air-conditioner-and-heat-pump-230-volt-60hz.html
Panasonic | E24RKUA (CU-E24RKUA / CS-E24RKUAW) | 2 | 24000 | 28800 |  | 17.5 |  | Ea | 1770 | 885 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Panasonic-Heating-and-Cooling-E24RKUA/p63121.html
Daikin | RX30NMVJU FTX30NVJU | 2.5 | 30000 | 30000 |  | 17 | 9.8 | Ea | 2330 | 932 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Daikin-RX30NMVJU-FTX30NVJU/p88996.html
LG | LS363HLV | 2.75 | 33000 | 36000 |  | 17.5 | 10.1 | Ea | 2729 | 992.3636 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/LG-LS363HLV/p72547.html
LG | LS363HLV | 2.75 | 33000 | 36000 |  | 17.5 | 10.1 | Ea | 2729 | 992.3636 | No | 1 | Wall | eComfort | https://www.ecomfort.com/LG-LS363HLV/p72547.html
Mitsubishi | MXZ-5C42NA2 2-MSZ-GL24NA-U1 MAC-A456JP-E | 4 | 48000 | 48000 |  | 17.5 | 9.7 | Ea | 5289.9 | 1322.475 | No | 2 | Wall | AC Wholesalers | https://www.acwholesalers.com/Mitsubishi-MXZ-5C42NA2-2-MSZ-GL24NA-U1-MAC-A456JP-E/p57083.html
Mini-Split Heat Pump
Tier 4: SEER 18, EER: 14, HSPF 9.7
Make | Model | Ton | Capacity (BTUH) |  | Efficiency |  |  | Unit | Material Cost | Cost per Ton | Energy Star |  |  | Retailer | Source
|  |  | Cooling | Heating | EER | SEER | HSPF |  |  |  |  | # of Zones | Mount Type
Pioneer | WYS018GMFI19RL-16 | 1.5 | 18000 | 18000 |  | 19 | 10 | Ea | 958 | 638.6667 | Yes | 1 | Wall | Home Depot | https://www.homedepot.com/p/Pioneer-18-000-BTU-1-5-Ton-19-SEER-Ductless-Mini-Split-Inverter-Wall-Mounted-Air-Conditioner-with-Heat-Pump-208-230V-WYS018GMFI19RL-16/311627362
Pioneer | WYS018GMFI19RL-16 | 1.5 | 18000 | 18000 |  | 19 | 10 | Ea | 958 | 638.6667 | Yes | 1 | Wall | Pioneer Mini Split Store | https://www.pioneerminisplit.com/products/18-000-btu-ductless-dc-inverter-mini-split-air-conditioner-heat-pump-230-vac
Pioneer | WYS018GMFI19RL-16 | 1.5 | 18000 | 18000 |  | 19 | 10 | Ea | 828 | 552 | Yes | 1 | Wall | High Seer | https://www.highseer.com/products/18-000-btu-ductless-dc-inverter-mini-split-air-conditioner-heat-pump-230-vac?variant=27003569963072
Daikin | RX18NMVJU / FTX18NMVJU | 1.5 | 18000 | 21600 |  | 18 |  | Ea | 1799 | 1199.3333 | Yes | 1 | Wall | HVAC Direct | https://hvacdirect.com/daikin-19-series-18-000-btu-18-seer-ductless-mini-split-heat-pump-system-rx18nmvju-ftx18nmvju.html
Daikin | RX18NMVJU / FTX18NMVJU | 1.5 | 18000 | 21600 |  | 18 |  | Ea | 1576.05 | 1050.7 | Yes | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Daikin-RX18NMVJU-FTX18NMVJU/p65543.html
Daikin | RX18NMVJU / FTX18NMVJU | 1.5 | 18000 | 21600 |  | 18 |  | Ea | 1497 | 998 | Yes | 1 | Wall | eComfort | https://www.ecomfort.com/Daikin-X18NMVJU/p65543.html
Daikin | RX18NMVJU / FTX18NMVJU | 1.5 | 18000 | 21600 |  | 18 |  | Ea | 1799 | 1199.3333 | Yes | 1 | Wall | Total Home Supply | https://www.totalhomesupply.com/19-series-18000-btu-heat-pump-18-seer-single-zone-system/p/daikin-156818
Daikin | RX18NMVJU / FTX18NMVJU | 1.5 | 18000 | 21600 |  | 18 |  | Ea | 1584.45 | 1056.3 | Yes | 1 | Wall | The AC Outlet | https://www.theacoutlet.com/rx18nmvju-ftx18nmvju-18-000-btu-18-seer-daikin-single-zone-ductless-mini-split-heat-pump-system.html
Panasonic | E18RKUA, CU-E18RKUA-OUTDOOR, CS-E18RKUAW-INDOOR | 1.5 | 18000 | 21600 |  | 19.5 | 10 | Ea | 1739 | 1159.3333 | Yes | 1 | Wall | appliances connection | https://www.appliancesconnection.com/panasonic-e18rkua.html
Panasonic | E18RKUA, CU-E18RKUA-OUTDOOR, CS-E18RKUAW-INDOOR | 1.5 | 18000 | 21600 |  | 19.5 | 10 | Ea | 1590 | 1060 | Yes | 1 | Wall | eComfort | https://www.ecomfort.com/Panasonic-Heating-and-Cooling-E18RKUA/p63120.html
Panasonic | E18RKUA, CU-E18RKUA-OUTDOOR, CS-E18RKUAW-INDOOR | 1.5 | 18000 | 21600 |  | 19.5 | 10 | Ea | 1799 | 1199.3333 | Yes | 1 | Wall | Total Home Supply | https://www.totalhomesupply.com/17200-btu-outdoor-unit-heat-pump/p/PANASONIC-E18RKUA
Fujitsu | AOU18RLXFW-OUTDOOR, ASU18RLF-INDOOR | 1.5 | 18000 | 21600 |  | 19.2 | 10 | Ea | 2398.65 | 1599.1 | Yes | 1 | Wall | Amazon | https://www.amazon.com/Fujitsu-Seer-Single-Split-System/dp/B007TY29HM
Fujitsu | AOU18RLXFW-OUTDOOR, ASU18RLF-INDOOR | 1.5 | 18000 | 21600 |  | 19.2 | 10 | Ea | 2101 | 1400.6667 | Yes | 1 | Wall | The AC Outlet | https://www.theacoutlet.com/18rlxfw-asu18rlf-aou18rlxfw-18-000-btu-19-seer-fujitsu-single-zone-ductless-mini-split-heat-pump-system.html
Fujitsu | AOU18RLXFW-OUTDOOR, ASU18RLF-INDOOR | 1.5 | 18000 | 21600 |  | 19.2 | 10 | Ea | 2779.65 | 1853.1 | Yes | 1 | Wall | eComfort | https://www.ecomfort.com/Fujitsu-18RLXFW/p67275.html
Daikin | RX24NMVJU FTX24NMVJU | 1.8 | 21200 | 24000 |  | 18 |  | Ea | 1758.45 | 976.9167 | Yes | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Daikin-RX24NMVJU-FTX24NMVJU/p65544.html
Daikin | RX24NMVJU FTX24NMVJU | 1.8 | 21200 | 24000 |  | 18 |  | Ea | 1671 | 928.3333 | Yes | 1 | Wall | eComfort | https://www.ecomfort.com/Daikin-X24NMVJU/p65544.html
Fujitsu | AOU24RLXFW-OUTDOOR, ASU24RLF-INDOOR | 1.8 | 22000 | 27600 |  | 18 | 10 | Ea | 2153.05 | 1196.1389 | Yes | 1 | Wall | Amazon | https://www.amazon.com/Fujitsu-Seer-Single-Split-System/dp/B007TY27HE
Fujitsu | AOU24RLXFW-OUTDOOR, ASU24RLF-INDOOR | 1.8 | 22000 | 27600 |  | 18 | 10 | Ea | 2806 | 1558.8889 | Yes | 1 | Wall | The AC Outlet | https://www.theacoutlet.com/24rlxfw-asu24rlf-aou24rlxfw-24-000-btu-19-5-seer-fujitsu-single-zone-ductless-mini-split-heat-pump-system.html
YMGI | WMMS-24K-V2B(58)2, WMMS-24C-V2B(58)2-OUTDOOR,WMMS-24E-V2B(58)2-INDOOR | 2 | 24000 | 26000 |  | 18 | 10.2 | Ea | 1599.99 | 799.995 | Yes | 1 | Wall | rhnewtons | https://rhnewtons.com/product/wmms-24k-v2b582-single-18seer/
Mitsubishi | MZ-HM12NA | 1 | 12000 | 12000 |  | 18 | 10 | Ea | 1220.25 | 1220.25 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Mitsubishi-MZ-HM12NA/p81584.html
Mitsubishi | MZ-HM12NA | 1 | 12000 | 12000 |  | 18 | 10 | Ea | 1220.25 | 1220.25 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Mitsubishi-MZ-HM12NA/p81584.html
Mitsubishi | MZ-HM15NA | 1.2 | 14000 | 18000 |  | 18 | 10 | Ea | 1482 | 1235 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Mitsubishi-MZ-HM15NA/p81585.html
Mitsubishi | MZ-HM15NA | 1.2 | 14000 | 18000 |  | 18 | 10 | Ea | 1482 | 1235 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Mitsubishi-MZ-HM15NA/p81585.html
Mitsubishi | MZ-HM18NA | 1.4 | 17200 | 18000 |  | 18 | 10 | Ea | 1746 | 1247.1429 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Mitsubishi-MZ-HM18NA/p81586.html
Mitsubishi | MZ-HM18NA | 1.4 | 17200 | 18000 |  | 18 | 10 | Ea | 1746 | 1247.1429 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Mitsubishi-MZ-HM18NA/p81586.html
Mitsubishi | PUZ-A18NKA7 PKA-A18HA7 | 1.5 | 18000 | 19000 |  | 18.5 | 10.2 | Ea | 2942.25 | 1961.5 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Mitsubishi-PUZ-A18NKA7-PKA-A18HA7/p88241.html
Mitsubishi | PUZ-A18NKA7 PKA-A18HA7 | 1.5 | 18000 | 19000 |  | 18.5 | 10.2 | Ea | 2942.25 | 1961.5 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Mitsubishi-PUZ-A18NKA7-PKA-A18HA7/p88241.html
Friedrich | M18YJ | 1.5 | 18000 | 18000 |  | 18 | 9.7 | Ea | 1806 | 1204 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Friedrich-M18YJ/p85749.html
Frigidaire | FFHP182SQ2 | 1.5 | 18000 | 19800 |  | 18 | 10 | Ea | 1998 | 1332 | No | 1 | Wall | Frigidaire | https://www.frigidaire.com/Home-Comfort/Air-Conditioning/Ductless-Split-Systems/FFHP182SQ2/?gclid=EAIaIQobChMIuOjmtYjK5QIVFBx9Ch1buwG-EAAYAiAAEgKVbfD_BwE&gclsrc=aw.ds
Mitsubishi | MZ-HM24NA | 1.875 | 22500 | 26000 |  | 18 |  | Ea | 1869 | 996.8 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Mitsubishi-MZ-HM24NA/p81587.html
Mitsubishi | MZ-HM24NA | 1.875 | 22500 | 26000 |  | 18 |  | Ea | 1869 | 996.8 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Mitsubishi-MZ-HM24NA/p81587.html
Fujitsu | 24RLB | 2 | 24000 | 24000 |  | 18 | 10.6 | Ea | 1895 | 947.5 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Fujitsu-24RLB/p65517.html
Fujitsu | 24RLB | 2 | 24000 | 24000 |  | 18 | 10.6 | Ea | 1800.25 | 900.125 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Fujitsu-24RLB/p65517.html
Fujitsu | 30RLXEH | 2.5 | 30000 | 30000 |  | 18.7 | 11.8 | Ea | 3212.9 | 1285.16 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Fujitsu-30RLXEH/p93261.html
Pioneer | WYS030GMFI17RL-16 | 2.5 | 30000 | 30000 |  | 18 |  | Ea | 1828 | 731.2 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/Pioneer-30-000-2-5-Ton-18-SEER-Ductless-Mini-Split-Inverter-Wall-Mounted-Air-Conditioner-with-Heat-Pump-208-230-Volt-WYS030GMFI17RL-16/311628263
Gree | VIR36HP230V1A | 3 | 36000 | 36000 |  | 18 |  | Ea | 2153 | 717.6667 | No | 1 | Wall | Home Depot | https://www.homedepot.com/p/GREE-Vireo-33600-BTU-Ductless-Mini-Split-Air-Conditioner-and-Heat-Pump-230-Volt-VIR36HP230V1A/301072111
Mitsubishi | PUZ-A36NKA7 PKA-A36KA7 | 3 | 36000 | 38000 |  | 18.8 |  | Ea | 4513.63 | 1504.5433 | No | 1 | Wall | AC Wholesalers | https://www.acwholesalers.com/Mitsubishi-PUZ-A36NKA7-PKA-A36KA7/p88245.html
Mitsubishi | PUZ-A36NKA7 PKA-A36KA7 | 3 | 36000 | 38000 |  | 18.8 |  | Ea | 4513.63 | 1504.5433 | No | 1 | Wall | eComfort | https://www.ecomfort.com/Mitsubishi-PUZ-A36NKA7-PKA-A36KA7/p88245.html
Daikin | D2H48W24240000 | 4 | 48000 | 48000 |  | 18.8 | 11.3 | Ea | 3818 | 954.5 | No | 2 | Wall | eComfort | https://www.ecomfort.com/Daikin-D2H48W24240000/p66093.html
Daikin | D2H48W24240000 | 4 | 48000 | 48000 |  | 18.8 | 11.3 | Ea | 4018.5 | 1004.625 | No | 2 | Wall | AC Wholesalers | https://www.acwholesalers.com/Daikin-RMXS48LVJU-2-FTXS24LVJU/p66093.html
Pioneer | UYB048GMFILCAD-16 | 4 | 48000 | 50000 |  | 17.8 | 11 | Ea | 3638 | 909.5 | No | 1 | Wall/Floor | Pioneer Mini Split Store | https://www.pioneerminisplit.com/products/48000-btu-17-seer-floor-ceiling-mini-split-air-conditioner-heat-pump-system-full-set

## Labor & Infrastructure Costs
Baseline Installation - Labor and Material components | [9 empty] | Baseline Labor Install Cost
Description | Labor Hrs Min | Labor Hrs Max | Avg Labor Hrs | Electrician Hourly Rate with O&P | Labor Cost | Material Cost | Total Cost | Labor Type | Notes
Gas Fired Wall Furnace, Horizontal Flow (14-49 MBH) | 2.462 | 4 | 3.231 | 67.55 | 218.254 | 0 | 218.254 | Install | RSMeans: 235416133212, 235416133216, 235416133220
Window Unit Air Conditioner, portable, grounded (12-25 KBTUH) | 2 | 4 | 3 | 67.55 | 202.65 | 0 | 202.65 | Install | RSMeans: 238119104520, 238119104780, 238119104940
Total |  |  | 6.231 |  | 420.9 | 0 | 420.9
Total Cost per Ton (Average tonnage = 1.5) |  |  |  |  | 280.6 | 0 | 280.6
Measure Case Installation - Labor and Material components
Description | Labor Hrs Min | Labor Hrs Max | Avg Labor Hrs | Electrician Hourly Rate with O&P | Labor Cost | Material Cost | Total Cost | Labor Type | Notes
Install: Mini-Split Heat Pump, ductless, cooling/heating (1-1.5 tons) | 9.412 | 10.667 | 10.0395 | 67.55 | 678.1682 | 0 | 678.1682 | Install | RSMeans: 238126105110, 238126105120
Install: Mini-Split Heat Pump, tube / wiring kit, 50' | 0.8 | 0.8 | 0.8 | 67.55 | 54.04 | 206 | 260.04 | Install | RSMeans: 238126107050
Install: Condensing Unit Pad prefabricated, fiberglass reinforced concrete with polystyrene foam core, 2” thick, 24”x42” | 1 | 1 | 1 | 67.55 | 67.55 | 47.5 | 115.05 | Install | RSMeans: 239110106110
Total |  |  | 11.8395 |  | 799.76 | 253.5 | 1053.26
Total Cost per Ton (Average tonnage = 1.5) |  |  |  |  | 533.17 | 169 | 702.17
Labor Rate (Res Electrician w/ O&P) RSMeansOnline | 67.55
Labor Rate (Res Building Laborer w/ O&P) RSMeansOnline | 45.45
Measure Case Labor Install Cost
Infrastructure
Work | Labor Hrs Min | Labor Hrs Max | Avg Labor Hrs | Labor Rate | Labor Cost | Material Cost | Total Cost | Labor Type | Notes
Demo: Demolish Wall Furnace | 4 | 4 | 4 | 67.55 | 270.2 | 0 | 270.2 | Demo | RSMeans: 230505102300
Demo: Demolish Window AC | 0.5 | 0.5 | 0.5 | 67.55 | 33.775 | 0 | 33.775 | Demo | RSMeans: 230505108400
Demo: 5/8in thick Dry Wall* | 0.054 | 0.108 | 0.081 | 45.45 | 3.6814 | 13.47 | 17.1515 | Demo | RSMeans for labor, Home Depot Material
Demo: Paint Interior Wall 1 Coat, Smooth Finish with Roller** | 0.036 | 0.072 | 0.054 | 45.45 | 2.4543 | 0 | 2.4543 | Demo | Assumes paint cost is negligible
Cap Existing Gas Line. Brass Plug for Natural Gas lines |  |  | 0.25 | 67.55 | 16.8875 | 4 | 20.8875 | Infrastructure | Engineering Estimates for labor, Grainger Material
Mini-Split Heat Pump hook-up, 1-40 & 1-100 amp 2 pole circuit breaker, 40' of #8/2 & 30' of #3/2 |  |  | 7.404 | 67.55 | 500.1402 | 550 | 1050.1402 | Infrastructure | RSMeans: 260590109240, Type MC cable
Total |  |  | 12.289 |  | 827.14 | 567.47 | 1394.61
Total Cost per Ton (Average tonnage = 1.5) |  |  |  |  | 551.43 | 378.31 | 929.74
Baseline Labor- NO AC | [9 empty] | Baseline Labor Install Cost
Description | Labor Hrs Min | Labor Hrs Max | Avg Labor Hrs | Electrician Hourly Rate with O&P | Labor Cost | Material Cost | Total Cost | Labor Type | Notes
Gas Fired Wall Furnace, Horizontal Flow (14-49 MBH) | 2.462 | 4 | 3.231 | 67.55 | 218.254 | 0 | 218.254 | Install | RSMeans: 235416133212, 235416133216, 235416133220
Total |  |  | 3.231 |  | 218.25 | 0 | 218.25
Total Cost per Ton (Average tonnage = 1.5) |  |  |  |  | 145.5 | 0 | 145.5
Measure Case Labor -NO AC
Description | Labor Hrs Min | Labor Hrs Max | Avg Labor Hrs | Electrician Hourly Rate with O&P | Labor Cost | Material Cost | Total Cost | Labor Type | Notes
Install: Mini-Split Heat Pump, ductless, cooling/heating (1-1.5 tons) | 9.412 | 10.667 | 10.0395 | 67.55 | 678.1682 | 0 | 678.1682 | Install | RSMeans: 238126105110, 238126105120
Install: Mini-Split Heat Pump, tube / wiring kit, 50' | 0.8 | 0.8 | 0.8 | 67.55 | 54.04 | 206 | 260.04 | Install | RSMeans: 238126107050
Install: Condensing Unit Pad prefabricated, fiberglass reinforced concrete with polystyrene foam core, 2” thick, 24”x42” | 1 | 1 | 1 | 67.55 | 67.55 | 47.5 | 115.05 | Install | RSMeans: 239110106110
Total |  |  | 11.8395 |  | 799.76 | 253.5 | 1053.26
Total Cost per Ton (Average tonnage = 1.5) |  |  |  |  | 533.17 | 169 | 702.17
Labor Rate (Res Electrician w/ O&P) RSMeansOnline | 67.55
Labor Rate (Res Building Laborer w/ O&P) RSMeansOnline | 45.45
Measure Case Labor Install Cost
Infrastructure- NO AC
Work | Labor Hrs Min | Labor Hrs Max | Avg Labor Hrs | Labor Rate | Labor Cost | Material Cost | Total Cost | Labor Type | Notes
Demo: Demolish Wall Furnace | 4 | 4 | 4 | 67.55 | 270.2 | 0 | 270.2 | Demo | RSMeans: 230505102300
Demo: 5/8in thick Dry Wall* | 0.054 | 0.108 | 0.081 | 45.45 | 3.6814 | 13.47 | 17.1515 | Demo | RSMeans for labor, Home Depot Material
Demo: Paint Interior Wall 1 Coat, Smooth Finish with Roller** | 0.036 | 0.072 | 0.054 | 45.45 | 2.4543 | 0 | 2.4543 | Demo | Assumes paint cost is negligible
Cap Existing Gas Line. Brass Plug for Natural Gas lines |  |  | 0.25 | 67.55 | 16.8875 | 4 | 20.8875 | Infrastructure | Engineering Estimates for labor, Grainger Material
Mini-Split Heat Pump hook-up, 1-40 & 1-100 amp 2 pole circuit breaker, 40' of #8/2 & 30' of #3/2 |  |  | 7.404 | 67.55 | 500.1402 | 550 | 1050.1402 | Infrastructure | RSMeans: 260590109240, Type MC cable
Total |  |  | 11.789 |  | 793.36 | 567.47 | 1360.83
Total Cost per Ton (Average tonnage = 1.5) |  |  |  |  | 528.91 | 378.31 | 907.22
Measure Case Labor Demo Cost
*Square footage of wall area estimated based on furnace dimension; min 6sqft (2ftx3ft) and max 12sqft (6ftx2ft)
**Paint material cost for min 6sqft and max 12sqft interior wall is negligible
Infrastructure Cost