## Summary
Path B Screw ACC IMCs
2020-11-25
Assembled by Energy Solutions
The following table shows the average of measure cost data collected for Path-B based air-cooled chillers in California. Data was collected from four major chiller manufacturers through their CA distributors. Manufacturer names have been anonymized for security.
Screw Air-Cooled Chiller Size | Path B Tier | EER Requirement | IPLV Requirement | FMC ($/ton) | IMC ($/ton)
<150 tons | Code | 9.7 | 15.8 | 719.1767
<150 tons | Tier 1 | 10.38 | 17.696 | 815.9253 | 96.7486
<150 tons | Tier 2 | 10.38 | 18.96 | 892.5973 | 173.4206
≥150 tons and ≤300 tons | Code | 9.7 | 16.1 | 586.0837
≥150 tons and ≤300 tons | Tier 1 | 10.38 | 18.032 | 644.7157 | 58.632
≥150 tons and ≤300 tons | Tier 2 | 10.38 | 19.32 | 710.6871 | 124.6033

## ACC Path B cost data by OEM
Manufacturer A | [10 empty] | Data in uniform table format:
Label | Tier | Requested/Target Values |  |  | Actual ACC Data
|  | Size Range | EER | IPLV | Model Number | Unit Size (tons) | EER | IPLV | Cost ($) | $/ton | Screw Air-Cooled Chiller Size | Path B Tier | EER Requirement | IPLV Requirement | FMC ($/ton) | IMC ($/ton)
ACC 1 | Code | <150 tons | 9.7 | 15.8 |  | 140 | 9.71 | 17 | 115730 | 826.6429 | <150 tons | Code | 9.7 | 15.8 | 826.6429
ACC 2 | Tier 1 | <150 tons | 10.67 | 17.38 |  | 140 | 10.84 | 17.1 | 121320 | 866.5714 | <150 tons | Tier 1 | 10.38 | 17.696 | 866.5714 | 39.9286
ACC 3 | Tier 2 | <150 tons | 10.67 | 18.96 |  | 140 | 10.83 | 19.8 | 127200 | 908.5714 | <150 tons | Tier 2 | 10.38 | 18.96 | 908.5714 | 81.9286
ACC 4 | Code | ≥150 tons and ≤300 tons | 9.7 | 16.1 |  | 250 | 9.73 | 17.56 | 142378 | 569.512 | ≥150 tons and ≤300 tons | Code | 9.7 | 16.1 | 569.512
ACC 5 | Tier 1 | ≥150 tons and ≤300 tons | 10.67 | 17.71 |  | 250 | 10.79 | 17.87 | 157240 | 628.96 | ≥150 tons and ≤300 tons | Tier 1 | 10.38 | 18.032 | 628.96 | 59.448
ACC 6 | Tier 2 | ≥150 tons and ≤300 tons | 10.67 | 19.32 |  | 250 | 10.75 | 20.31 | 167924 | 671.696 | ≥150 tons and ≤300 tons | Tier 2 | 10.38 | 19.32 | 671.696 | 102.184
Manufacturer B
Label | Tier | Requested/Target Values |  |  | Actual ACC Data
|  | Size Range | EER | IPLV | Model Number | Unit Size (tons) | EER | IPLV | Cost ($) | $/ton | Screw Air-Cooled Chiller Size | Path B Tier | EER Requirement | IPLV Requirement | FMC ($/ton) | IMC ($/ton)
| Path A | <150 tons | 10.1 per T24 | 13.7 per T24 |  | 155 | 10.95 | 14.81 | 94000 | 606.4516 | <150 tons | Code | 9.7 | 15.8 | 670
ACC 1 | Code | <150 tons | 9.7 | 15.8 |  | 150 | 10.9 | 17.1 | 100500 | 670 | <150 tons | Tier 1 | 10.38 | 17.696 | 853.3333 | 183.3333
ACC 2 | Tier 1 | <150 tons | 10.67 | 17.38 |  | 150 | 11.68 | 19.75 | 128000 | 853.3333 | <150 tons | Tier 2 | 10.38 | 18.96 | 933.3333 | 263.3333
ACC 3 | Tier 2 | <150 tons | 10.67 | 18.96 |  | 150 | 11.69 | 19.69 | 140000 | 933.3333 | ≥150 tons and ≤300 tons | Code | 9.7 | 16.1 | 600
| Path A | ≥150 tons and ≤300 tons | 10.1 per T24 | 14.0 per T24 |  | 200 | 10.66 | 14.17 | 113000 | 565 | ≥150 tons and ≤300 tons | Tier 1 | 10.38 | 18.032 | 735 | 135
ACC 4 | Code | ≥150 tons and ≤300 tons | 9.7 | 16.1 |  | 200 | 10.65 | 17.78 | 120000 | 600 | ≥150 tons and ≤300 tons | Tier 2 | 10.38 | 19.32 | 815 | 215
ACC 5 | Tier 1 | ≥150 tons and ≤300 tons | 10.67 | 17.71 |  | 200 | 11.19 | 20.27 | 147000 | 735
ACC 6 | Tier 2 | ≥150 tons and ≤300 tons | 10.67 | 19.32 |  | 200 | 11.86 | 21.2 | 163000 | 815
Manufacturer C
Label | Tier | Requested/Target Values |  |  | Actual ACC Data
|  | Size Range | EER | IPLV | Model Number | Unit Size (tons) | EER | IPLV | Cost ($) | $ / Ton | Screw Air-Cooled Chiller Size | Path B Tier | EER Requirement | IPLV Requirement | FMC ($/ton) | IMC ($/ton)
ACC 1 | Code | <150 tons | 9.7 | 15.8 |  | 96.35 | 9.701 | 16.09 | 51168 | 531.0638 | <150 tons | Code | 9.7 | 15.8 | 531.0638
ACC 2 | Tier 1 | <150 tons | 10.67 | 17.38 |  | 85.59 | 10.96 | 17.48 | 49368 | 576.7964 | <150 tons | Tier 1 | 10.38 | 17.696 | 576.7964 | 45.7325
ACC 3 | Tier 2 | <150 tons | 10.67 | 18.96 |  | N/A | N/A | N/A | N/A | N/A | <150 tons | Tier 2 | 10.38 | 18.96 |  |  | 173.4206 | Tier 2 <150 ton IMC for Mfr A, B, & D… used to calculate Tier 2 FMC since Manufacturer C doesn't have a unit at Tier 2 which would throw off the baseline/Tier 2 FMC/IMC differential
ACC 4 | Code | ≥150 tons and ≤300 tons | 9.7 | 16.1 |  | 265.4 | 9.918 | 17.9 | 126018 | 474.8229 | ≥150 tons and ≤300 tons | Code | 9.7 | 16.1 | 474.8229
ACC 5 | Tier 1 | ≥150 tons and ≤300 tons | 10.67 | 17.71 |  | 272.5 | 10.72 | 19.24 | 133226 | 488.9028 | ≥150 tons and ≤300 tons | Tier 1 | 10.38 | 18.032 | 488.9028 | 14.0798
ACC 6 | Tier 2 | ≥150 tons and ≤300 tons | 10.67 | 19.32 |  | 277.3 | 10.99 | 19.83 | 148370 | 535.0523 | ≥150 tons and ≤300 tons | Tier 2 | 10.38 | 19.32 | 535.0523 | 60.2294
Manufacturer D
Label | Tier | Requested/Target Values |  |  | Actual ACC Data
|  | Size Range | EER | IPLV | Model Number | Unit Size (tons) | EER | IPLV | Cost ($) | $ / Ton | Screw Air-Cooled Chiller Size | Path B Tier | EER Requirement | IPLV Requirement | FMC ($/ton) | IMC ($/ton)
ACC 1 | Code | <150 tons | 9.7 | 15.8 |  |  | 9.7 | 15.8 |  | 849 | <150 tons | Code | 9.7 | 15.8 | 849
ACC 2 | Tier 1 | <150 tons | 10.67 | 17.38 |  |  | 10.38 | 17.7 |  | 967 | <150 tons | Tier 1 | 10.38 | 17.696 | 967 | 118
ACC 3 | Tier 2 | <150 tons | 10.67 | 18.96 |  |  | 10.38 | 18.96 |  | 1024 | <150 tons | Tier 2 | 10.38 | 18.96 | 1024 | 175
ACC 4 | Code | ≥150 tons and ≤300 tons | 9.7 | 16.1 |  |  | 9.7 | 16.1 |  | 700 | ≥150 tons and ≤300 tons | Code | 9.7 | 16.1 | 700
ACC 5 | Tier 1 | ≥150 tons and ≤300 tons | 10.67 | 17.71 |  |  | 10.38 | 18.03 |  | 726 | ≥150 tons and ≤300 tons | Tier 1 | 10.38 | 18.032 | 726 | 26
ACC 6 | Tier 2 | ≥150 tons and ≤300 tons | 10.67 | 19.32 |  |  | 10.38 | 19.32 |  | 821 | ≥150 tons and ≤300 tons | Tier 2 | 10.38 | 19.32 | 821 | 121
(Manufacturer D only reported the $/ton costs)