## MeasureExAnte
PA | MeasureID | MeasQualifierGroup | SourceDesc | Sector | EnergyImpactID | MeasCostID | StdCostID | EUL_ID | RUL_ID | Version | VersionSource | LastMod | Description | MeasDesc | MeasTechID | MeasImpactType | EnImpCalcType | UseCategory | UseSubCategory | TechGroup | TechType | Status | Comment | PreDesc | PreMultiTech | PreTechID | PreTechGroup | PreTechType | StdDesc | StdMultiTech | StdTechID | StdTechGroup | StdTechType | ImpScaleBasis | TechBased | ApplyIE | IETableName | ImpWeighting | WeightGroupID | LegacyID | StdScaleVal | PreScaleVal | ProposedEULValue | StartDate | ExpiryDate
Any | SWHC052A | None | SWHC052-01 | Com | SWHC052A | SWHC052_01_M001 | SWHC052_01_B001 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2021-02-01 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | Air-Cooled Chiller, Path B Standard Efficiency, < 150 tons, 9.7 EER, 15.8 IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [6 empty] | 2022-01-01
Any | SWHC052B | None | SWHC052-01 | Com | SWHC052B | SWHC052_01_M002 | SWHC052_01_B001 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2021-02-01 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | Air-Cooled Chiller, Path B Standard Efficiency, < 150 tons, 9.7 EER, 15.8 IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [6 empty] | 2022-01-01
Any | SWHC052C | None | SWHC052-01 | Com | SWHC052C | SWHC052_01_M003 | SWHC052_01_B002 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2021-02-01 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | Air-Cooled Chiller, Path B Standard Efficiency, >= 150 tons, 9.7 EER, 16.1 IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [6 empty] | 2022-01-01
Any | SWHC052D | None | SWHC052-01 | Com | SWHC052D | SWHC052_01_M004 | SWHC052_01_B002 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2021-02-01 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | Air-Cooled Chiller, Path B Standard Efficiency, >= 150 tons, 9.7 EER, 16.1 IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [6 empty] | 2022-01-01
Any | SWHC052A | None | SWHC052-01 | Ind | SWHC052A | SWHC052_01_M001 | SWHC052_01_B001 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2021-02-01 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | Air-Cooled Chiller, Path B Standard Efficiency, < 150 tons, 9.7 EER, 15.8 IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [6 empty] | 2022-01-01
Any | SWHC052B | None | SWHC052-01 | Ind | SWHC052B | SWHC052_01_M002 | SWHC052_01_B001 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2021-02-01 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | Air-Cooled Chiller, Path B Standard Efficiency, < 150 tons, 9.7 EER, 15.8 IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [6 empty] | 2022-01-01
Any | SWHC052C | None | SWHC052-01 | Ind | SWHC052C | SWHC052_01_M003 | SWHC052_01_B002 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2021-02-01 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | Air-Cooled Chiller, Path B Standard Efficiency, >= 150 tons, 9.7 EER, 16.1 IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [6 empty] | 2022-01-01
Any | SWHC052D | None | SWHC052-01 | Ind | SWHC052D | SWHC052_01_M004 | SWHC052_01_B002 | HVAC-Chlr |  | ExAnte2022 | IOU Workpaper | 2021-02-01 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Standard | HVAC | SpaceCool | Chiller | Screw | Proposed | [6 empty] | Air-Cooled Chiller, Path B Standard Efficiency, >= 150 tons, 9.7 EER, 16.1 IPLV |  |  | Chiller | Screw | None |  | FALSE | None | [6 empty] | 2022-01-01

## ImplementationExAnte
PA | ImplementationID | StartDate | ExpiryDate | SourceDesc | MeasAppType | DelivType | MeasureID | MeasQualifierGroup | Sector | GSIA_ID | NTG_ID | CostQualifier | MeasCostID | StdCostID | Version | VersionSource | LastMod | Description | ImplementerID | MeasImpactType | Status | Comment
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
PGE | HV490 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
PGE | HV491 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
PGE | HV492 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
PGE | HV493 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961ComAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962ComAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963ComAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964ComAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961ComAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962ComAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963ComAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964ComAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961ComAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962ComAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963ComAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964ComAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961ComAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962ComAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963ComAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964ComAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961ComAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962ComAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963ComAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964ComAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961ComAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962ComAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963ComAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964ComAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961IndAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962IndAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963IndAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964IndAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961IndAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962IndAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963IndAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964IndAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961IndAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962IndAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963IndAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964IndAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961IndAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962IndAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963IndAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964IndAnyUpSUSI | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961IndAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962IndAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963IndAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964IndAnyFiSDwSD | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SCE | AC-21961IndAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SCE | AC-21962IndAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21963IndAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SCE | AC-21964IndAnyFiSDrI | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469391 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469392 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469393 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469394 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469395 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469396 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469397 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469398 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469399 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469400 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469401 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469402 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469403 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469404 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469405 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469406 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469407 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469408 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469409 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469410 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469411 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052A | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469412 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052B | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469413 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052C | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469414 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052D | None | Com | Def-GSIA | Com-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469391 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469392 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469393 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469394 | 1/1/2022 |  | SWHC052-01 | NR | UpDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469395 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469396 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469397 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469398 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469399 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469400 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469401 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469402 | 1/1/2022 |  | SWHC052-01 | NR | DnDeemDI | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469403 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469404 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469405 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469406 | 1/1/2022 |  | SWHC052-01 | NC | UpDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469407 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469408 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469409 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469410 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemed | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed
SDG | 469411 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052A | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M001 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 17.7 IPLV) |  | Deem-WP | Proposed
SDG | 469412 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052B | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M002 | SWHC052_01_B001 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (< 150 tons, 10.4 EER, 19.0 IPLV) |  | Deem-WP | Proposed
SDG | 469413 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052C | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M003 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 18.0 IPLV) |  | Deem-WP | Proposed
SDG | 469414 | 1/1/2022 |  | SWHC052-01 | NC | DnDeemDI | SWHC052D | None | Ind | Def-GSIA | Ind-Default>2yrs | None | SWHC052_01_M004 | SWHC052_01_B002 | ExAnte2022 | IOU Workpaper | 2/1/2021 | Air Cooled Screw Chiller, Path B (>= 150 tons, 10.4 EER, 19.3 IPLV) |  | Deem-WP | Proposed

## EnergyImpactExAnte
PA | EnergyImpactID | BldgType | BldgVint | BldgLoc | BldgHVAC | SourceDesc | Version | VersionSource | LastMod | NormUnit | NumUnit | MeasArea | ScaleBasis | APreWBkWh | APreWBkW | APreWBtherm | AStdWBkWh | AStdWBkW | AStdWBtherm | APreEUkWh | APreEUkW | APreEUtherm | AStdEUkWh | AStdEUkW | AStdEUtherm | ElecImpactProfileID | GasImpactProfileID | Flag
Any | SWHC052A | Com | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 63.26 | 0.036185 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 173.03 | 0.14416 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166.81 | 0.078127 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 218.64 | 0.19588 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166.4 | 0.04153 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.06 | 0.066302 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 223.09 | 0.04837 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 217.93 | 0.08581 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 236.16 | 0.12856 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 308.91 | 0.15913 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 348.66 | 0.35707 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 257.49 | 0.2345 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 374.19 | 0.30111 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 331.51 | 0.28741 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 643.3 | 0.52513 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.79 | 0.082063 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.41 | 0.006747 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 163.53 | 0.13627 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149.25 | 0.090972 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 209.8 | 0.21379 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155.26 | 0.048631 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 225.87 | 0.055657 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 216.35 | 0.038181 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 254.97 | 0.097612 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 249.96 | 0.13914 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 284.44 | 0.15946 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 356.05 | 0.23536 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.84 | 0.25466 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 361.16 | 0.32305 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 317.36 | 0.30232 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 588.03 | 0.51655 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 132.22 | 0.076919 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 20.98 | 0.015141 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.79 | 0.10661 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.73 | 0.03249 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.41 | 0.14474 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.29 | 0.012308 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.47 | 0.022682 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.96 | 0.004354 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.76 | 0.058767 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.99 | 0.12004 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 117.19 | 0.06106 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 311.01 | 0.22621 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109.93 | 0.10917 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 304.19 | 0.15887 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 265.33 | 0.14197 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 498.46 | 0.2432 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.61 | 0.033834 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 58.56 | 0.046622 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.3 | 0.12046 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.33 | 0.025835 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 148.18 | 0.18955 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.91 | 0.01184 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136.24 | 0.034792 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.97 | 0.022658 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 181.26 | 0.082896 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 186.4 | 0.12751 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 221.34 | 0.12644 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 271.93 | 0.20628 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 194.3 | 0.22596 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 283.77 | 0.29043 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 264.37 | 0.27291 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 501.9 | 0.50828 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.1 | 0.048797 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 28.85 | 0.040278 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.77 | 0.10318 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 123.32 | 0.045961 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 191.33 | 0.15163 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.81 | 0.036616 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 228.57 | 0.039472 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 231.47 | 0.042445 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 242.55 | 0.060948 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 227.71 | 0.095585 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 258.25 | 0.081641 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 280.01 | 0.29234 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 209.19 | 0.14667 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 296.83 | 0.21171 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 257.28 | 0.17884 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 489.62 | 0.34074 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 121.47 | 0.061248 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 209.14 | 0.10446 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 313.96 | 0.22082 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 300.25 | 0.11747 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 361.06 | 0.29428 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 321.52 | 0.08815 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 358.85 | 0.083999 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 363.87 | 0.095403 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 416.02 | 0.17162 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 360.42 | 0.21174 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 445.86 | 0.21922 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 514.47 | 0.57019 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 410.84 | 0.34203 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 540.26 | 0.41628 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 459.37 | 0.37497 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 815.3 | 0.67678 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 299.81 | 0.15922 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 34.88 | 0.034011 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.58 | 0.11736 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 159.66 | 0.081417 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 96.39 | 0.15573 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.9 | 0.023462 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 238.21 | 0.069587 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.01 | 0.030378 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134.49 | 0.066515 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120.33 | 0.089952 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 285.01 | 0.16193 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 321.61 | 0.37256 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232.99 | 0.24634 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 336.47 | 0.32404 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 303.06 | 0.29559 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 583.65 | 0.52334 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.58 | 0.087553 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 23.6 | 0.019381 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.86 | 0.14605 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.07 | 0.055494 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166.85 | 0.2022 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 103.05 | 0.030337 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 114.17 | 0.021722 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.88 | 0.025403 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 169.08 | 0.094502 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 187.61 | 0.17002 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 310.55 | 0.16995 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 335.64 | 0.48589 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 236.24 | 0.2605 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 350.47 | 0.33183 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 358.1 | 0.35804 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 754.24 | 0.66668 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124.97 | 0.079591 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 23.38 | 0.006193 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 190.82 | 0.14444 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 159.37 | 0.076224 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 229.87 | 0.19784 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 181.1 | 0.04004 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232.85 | 0.06843 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 209.79 | 0.044307 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 259.71 | 0.087854 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 226.39 | 0.11636 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 298.95 | 0.14471 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 342.88 | 0.35803 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 254.85 | 0.22793 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 356.98 | 0.28317 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 324.37 | 0.25694 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 579.32 | 0.40916 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.96 | 0.095686 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.23 | 0.021272 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 258.84 | 0.13709 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 254.49 | 0.08087 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 296.76 | 0.17022 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155.43 | 0.018507 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 316.78 | 0.05919 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 315.88 | 0.046596 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 351.49 | 0.091289 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 369.31 | 0.13698 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 422.31 | 0.14841 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 410.89 | 0.35579 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 329.36 | 0.20652 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 467.87 | 0.2835 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 433.77 | 0.25664 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 694.03 | 0.44666 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 192.63 | 0.085378 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.88 | 0.074847 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 215.46 | 0.19565 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 182.44 | 0.12185 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.91 | 0.25354 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 202.48 | 0.063641 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 262.21 | 0.10253 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 240.29 | 0.069348 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136.94 | 0.088472 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 269.57 | 0.15587 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 349.17 | 0.21379 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 397.97 | 0.53305 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 298.56 | 0.32377 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 419.13 | 0.41695 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 360.48 | 0.36959 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 713.14 | 0.66096 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 142.04 | 0.15043 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.98 | 0.044175 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170.96 | 0.13963 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143.9 | 0.06574 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 207.72 | 0.18267 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 168.59 | 0.044526 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 221.79 | 0.061531 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 222.82 | 0.049068 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.4 | 0.092837 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 230.72 | 0.12699 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 267.99 | 0.13911 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 330.89 | 0.34291 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 242.16 | 0.22918 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 359.38 | 0.2901 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 304.47 | 0.27023 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 593.9 | 0.49678 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Com | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 123.37 | 0.077757 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.06 | -0.000143 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 157.39 | 0.13211 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.71 | 0.035344 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 194.39 | 0.17778 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.25 | 0.020968 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 227.04 | 0.071149 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 216.34 | 0.041167 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 251.7 | 0.09309 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 246.14 | 0.13245 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 276.51 | 0.167 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 343.36 | 0.22069 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232.95 | 0.27155 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 340.41 | 0.32193 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 301.84 | 0.29786 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 566.41 | 0.50614 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ECC | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126.35 | 0.061231 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 38.52 | 0.030642 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.9 | 0.12871 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.35 | 0.034063 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.16 | 0.15574 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 92.65 | 0.026206 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 161.78 | 0.031967 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 147.23 | 0.033462 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 189.07 | 0.073457 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 177.63 | 0.096166 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 210.11 | 0.077733 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 258.32 | 0.20293 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 174.57 | 0.13378 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 255.63 | 0.14423 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 217.36 | 0.11398 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 414.42 | 0.20933 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | ESe | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.41 | 0.057866 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 48.77 | 0.046732 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 128.72 | 0.12183 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.98 | 0.01821 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 144.18 | 0.18569 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.97 | 0.01485 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134.01 | 0.050904 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139.74 | 0.022858 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 179.63 | 0.079946 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 180.49 | 0.11282 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 216.6 | 0.1278 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 265.58 | 0.19516 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 190.23 | 0.21842 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 276.41 | 0.27871 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 258.42 | 0.28049 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 480.87 | 0.49334 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | EUn | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 88.51 | 0.045913 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 29.13 | 0.039671 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.86 | 0.090284 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124.52 | 0.052255 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 184.82 | 0.13046 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126.69 | 0.040176 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 224.13 | 0.047215 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 219.73 | 0.046031 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 235.16 | 0.07186 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 211.92 | 0.09714 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 245.84 | 0.089843 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 261.71 | 0.26205 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 198.66 | 0.14197 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 279.79 | 0.18378 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 239.57 | 0.15904 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 450.17 | 0.28186 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Hsp | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118.64 | 0.059931 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 192.59 | 0.097217 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 301.97 | 0.21924 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 291.26 | 0.10943 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 354.27 | 0.29263 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 329.15 | 0.094179 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 358.73 | 0.06927 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 368.38 | 0.087928 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 405.68 | 0.1656 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 365.08 | 0.20608 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 434.27 | 0.21511 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 499.85 | 0.56487 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 396.59 | 0.33158 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 526.38 | 0.41106 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 461.86 | 0.36581 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 791.85 | 0.65944 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Htl | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 286.67 | 0.16029 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 57.04 | 0.054857 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.03 | 0.13949 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 92.2 | 0.055764 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 138.02 | 0.18283 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.97 | 0.045612 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 180.14 | 0.073636 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170.77 | 0.050717 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 182.55 | 0.07794 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.4 | 0.10797 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 206.65 | 0.15301 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 256.12 | 0.34958 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.43 | 0.23496 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 265.52 | 0.30586 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 246.98 | 0.27779 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 497.68 | 0.48984 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | MBT | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.98 | 0.074375 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 37.93 | 0.074537 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 214.17 | 0.20077 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 164.68 | 0.09571 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 296.46 | 0.27564 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 184.11 | 0.064072 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 320.25 | 0.080197 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 312.54 | 0.078379 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 373.19 | 0.16687 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 345.62 | 0.22665 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 426.8 | 0.20899 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 499.48 | 0.54911 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 349.47 | 0.31461 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 539.11 | 0.39964 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 473.32 | 0.39815 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 903.52 | 0.70086 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Nrs | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 187.62 | 0.13071 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.49 | 0.020002 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.18 | 0.12994 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 128.43 | 0.063501 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183.91 | 0.16868 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 153.77 | 0.040753 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 198.51 | 0.058512 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.45 | 0.038727 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 222.6 | 0.083357 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 191.28 | 0.10872 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 262.29 | 0.13473 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 310.95 | 0.33357 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 222.62 | 0.2147 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 326.07 | 0.25522 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 295.96 | 0.2361 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 539.13 | 0.39434 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfL | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120.21 | 0.078342 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.71 | 0.033209 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 224.06 | 0.11148 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.32 | 0.069789 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 318.66 | 0.18089 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 222.47 | 0.033109 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 271.45 | 0.04142 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 272.67 | 0.037108 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 307.88 | 0.080829 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 347.27 | 0.1214 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 336.99 | 0.099503 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 359.58 | 0.30937 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 285.5 | 0.18079 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 440.78 | 0.26443 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 409.51 | 0.23908 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 628.04 | 0.38906 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | OfS | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.81 | 0.059398 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 66.6 | 0.053572 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183.33 | 0.14553 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155.96 | 0.10103 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 190.06 | 0.1912 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 174.07 | 0.062099 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 225.22 | 0.068797 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 197.52 | 0.053265 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232.94 | 0.11393 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 240.53 | 0.14778 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 280.62 | 0.15099 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 370.16 | 0.5049 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 270.2 | 0.31211 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 389.68 | 0.39384 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 315.62 | 0.31628 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 649.94 | 0.59844 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052A | Rt3 | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 123.37 | 0.14311 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 146.12 | 0.10019 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 331.76 | 0.1672 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 348.03 | 0.1486 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 425.98 | 0.20976 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 381.53 | 0.10608 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 537.17 | 0.14661 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 506.77 | 0.11428 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 470.94 | 0.1123 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 438.95 | 0.14697 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 515.73 | 0.19246 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 497.28 | 0.32968 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 429.36 | 0.25235 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 546.03 | 0.30133 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 488.98 | 0.28656 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 790.02 | 0.466 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 298.4 | 0.14001 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 121.41 | 0.082902 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 294.14 | 0.12186 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 314.06 | 0.16571 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 388.26 | 0.18924 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 350.02 | 0.11865 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 496.44 | 0.11754 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 473.99 | 0.10602 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 485.21 | 0.11519 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 432.16 | 0.134 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 450.74 | 0.16443 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 493.34 | 0.21355 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 382.15 | 0.21773 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 509.5 | 0.28831 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 456.37 | 0.27709 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 693.13 | 0.40723 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 295.22 | 0.11963 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.89 | 0.055505 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170.36 | 0.081302 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 196.17 | 0.085444 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 236.26 | 0.092998 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 238.52 | 0.06153 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 299.33 | 0.056398 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 273 | 0.049863 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 297.28 | 0.06654 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 420.88 | 0.16131 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 240.93 | 0.055505 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 451.21 | 0.20416 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 217.25 | 0.079176 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 452.19 | 0.15367 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 402.59 | 0.13952 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 659.32 | 0.20844 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 169.91 | 0.058234 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124.44 | 0.1294 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 254.62 | 0.14002 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232.23 | 0.1002 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 304.49 | 0.18991 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 273.94 | 0.086139 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 360.64 | 0.10334 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 342.58 | 0.098412 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 380.68 | 0.10859 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 340.05 | 0.12478 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 372.25 | 0.13618 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 386.21 | 0.19153 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 335.63 | 0.20437 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 414.28 | 0.24373 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 388.54 | 0.23577 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 592.66 | 0.41026 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 256 | 0.08985 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.66 | 0.076516 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 226.42 | 0.12563 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 225.62 | 0.092062 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 327.27 | 0.15447 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 238.32 | 0.076169 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 427.06 | 0.090619 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 423.34 | 0.09042 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 424.69 | 0.090956 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 378.32 | 0.11165 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 405.2 | 0.10195 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 391.51 | 0.2478 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 323.85 | 0.14768 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 420.07 | 0.18735 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 374.26 | 0.16681 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 610.7 | 0.27055 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 223.59 | 0.11321 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 379.06 | 0.21104 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 548.43 | 0.27242 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 576.95 | 0.21905 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 642.63 | 0.33624 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 644.25 | 0.17539 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 755.09 | 0.20491 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 754.48 | 0.19509 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 779.97 | 0.22679 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 617.76 | 0.22875 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 715.58 | 0.25251 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 718.61 | 0.55023 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 652.46 | 0.36319 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 769.07 | 0.42123 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 661.41 | 0.36154 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 963.12 | 0.59355 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 615.29 | 0.27472 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115.14 | 0.077325 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 221.44 | 0.11113 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 343.68 | 0.14681 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 277.62 | 0.1333 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 283.09 | 0.069822 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 534.97 | 0.15004 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 374.02 | 0.081092 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 371.18 | 0.083368 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 299.18 | 0.086841 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 490.26 | 0.20516 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 474.23 | 0.36482 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 394.31 | 0.27897 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 508.4 | 0.34693 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 456.16 | 0.30885 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 741.98 | 0.4833 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 264.66 | 0.15319 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.12 | 0.10603 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 307 | 0.17068 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 337 | 0.14993 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 417.21 | 0.18264 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 367.91 | 0.12423 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 522.27 | 0.11869 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 548.83 | 0.12932 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 539.78 | 0.13591 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 467.68 | 0.15299 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 550.13 | 0.17818 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 472.53 | 0.33638 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 421.87 | 0.22392 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 509.37 | 0.24448 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 532.51 | 0.28809 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 844.13 | 0.48163 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 345.35 | 0.17853 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.53 | 0.05057 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 364.14 | 0.17892 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 337.98 | 0.13786 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 443.68 | 0.22906 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 387.98 | 0.087471 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 533.62 | 0.14106 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 476.33 | 0.09422 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 522.31 | 0.13077 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 424.61 | 0.14415 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 519.43 | 0.18473 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 509.47 | 0.35368 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 436.68 | 0.25772 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 538.98 | 0.30307 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 490.94 | 0.26515 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 735.19 | 0.38399 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 304.34 | 0.15602 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 152.67 | 0.075177 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 442.23 | 0.15347 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 455.21 | 0.14433 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 512.34 | 0.17472 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 382.71 | 0.057961 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 592.57 | 0.11412 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 590.5 | 0.08772 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 608.96 | 0.11176 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 625.85 | 0.1682 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 659.85 | 0.17933 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 570.24 | 0.30905 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 514.53 | 0.21327 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 675.17 | 0.30779 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 634.93 | 0.27031 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 848.22 | 0.36813 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 359.11 | 0.13534 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 156.67 | 0.15634 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 391.19 | 0.24927 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 373.89 | 0.24387 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 448.62 | 0.26715 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 423.68 | 0.15245 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 586.96 | 0.21899 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 537.41 | 0.18063 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 388.86 | 0.091628 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 466.03 | 0.18243 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 568.97 | 0.25864 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 562.34 | 0.54011 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 483.91 | 0.38598 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 595.88 | 0.447 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 516.48 | 0.3766 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 853.5 | 0.60847 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 310.19 | 0.25328 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143.49 | 0.099619 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 308.13 | 0.15678 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 304.5 | 0.12272 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 389.27 | 0.19177 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 365.59 | 0.10137 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 486.82 | 0.1281 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 477.34 | 0.10458 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 459.8 | 0.11619 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 409.52 | 0.13958 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 427.46 | 0.14535 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 454.48 | 0.3087 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 386.99 | 0.2325 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 507.8 | 0.28498 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 427.9 | 0.24452 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 688.79 | 0.41382 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Com | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 277.49 | 0.12624 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118.51 | 0.077842 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 285.78 | 0.11295 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 302.75 | 0.094646 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 368.55 | 0.1274 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 326.58 | 0.086198 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 498.83 | 0.1276 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 470.35 | 0.10108 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 478.67 | 0.11037 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 425.43 | 0.12694 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 441.06 | 0.18064 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 479.45 | 0.20128 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 377.09 | 0.25637 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 476.94 | 0.29986 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 435.26 | 0.28431 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 682.27 | 0.43483 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ECC | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 287.24 | 0.093595 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.49 | 0.069386 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 213.86 | 0.11911 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 201.63 | 0.062534 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 262.22 | 0.12599 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 229.61 | 0.061955 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 341.06 | 0.055912 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 307.99 | 0.06585 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 352.78 | 0.087306 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 314.04 | 0.10956 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 335.54 | 0.10047 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 362.39 | 0.18568 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 279.7 | 0.1387 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 371.13 | 0.14267 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 320.22 | 0.12206 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 512.89 | 0.18523 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | ESe | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 188.77 | 0.088568 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 105.14 | 0.12849 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 248.81 | 0.14175 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 229.5 | 0.099412 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 299 | 0.18665 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 273.25 | 0.084634 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 354.61 | 0.12298 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 338.84 | 0.099948 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 369.15 | 0.11226 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 328.96 | 0.12493 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 363.45 | 0.1507 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 376.82 | 0.17411 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 326.7 | 0.2088 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 403.97 | 0.24363 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 381.55 | 0.25214 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 571.89 | 0.39092 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | EUn | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 239.02 | 0.076269 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.23 | 0.07282 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 214.29 | 0.11653 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 223.68 | 0.10199 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 310.39 | 0.155 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 223.15 | 0.073533 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 399.96 | 0.0881 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 393.88 | 0.081971 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 398.85 | 0.09638 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 352.61 | 0.11054 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 386.56 | 0.11586 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 369.72 | 0.2426 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 307.89 | 0.14888 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 402.1 | 0.18515 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 347.74 | 0.1667 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 572.9 | 0.254 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Hsp | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 210.4 | 0.10467 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 345.74 | 0.19351 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 519.89 | 0.26856 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 545.7 | 0.21045 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 618.32 | 0.33288 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 630.44 | 0.1798 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 732.78 | 0.18626 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 735.42 | 0.18793 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 753.45 | 0.21698 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 613.7 | 0.22162 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 690.31 | 0.24654 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 692.71 | 0.54194 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 626.49 | 0.35712 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 743.6 | 0.411 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 666.07 | 0.35018 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 934.75 | 0.57431 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Htl | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 586.8 | 0.26818 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 135.51 | 0.10335 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 247.83 | 0.15808 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 260.03 | 0.096564 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 301.7 | 0.19312 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 290.29 | 0.083815 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 443.28 | 0.13556 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 411.34 | 0.09404 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 391.76 | 0.10547 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 339.71 | 0.12486 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 353.14 | 0.16806 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 350.36 | 0.31275 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 296.51 | 0.21891 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 374.94 | 0.2871 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 349.7 | 0.25073 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 568.48 | 0.40061 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | MBT | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 203.08 | 0.12156 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.68 | 0.12826 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 357.55 | 0.23962 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 302.49 | 0.17549 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 506 | 0.30383 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 337.05 | 0.12971 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 603.24 | 0.16167 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 583.73 | 0.16059 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 660.16 | 0.21961 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 580 | 0.25495 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 662.68 | 0.24699 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 678.44 | 0.49966 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 532.68 | 0.328 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 745.16 | 0.3846 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 670.51 | 0.39649 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 1090.93 | 0.61042 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Nrs | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 359.96 | 0.22018 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115.59 | 0.050643 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 297.73 | 0.15406 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 286.77 | 0.11077 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 361.17 | 0.18354 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 338.94 | 0.078913 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 459.98 | 0.11672 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 407.96 | 0.082461 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 445.46 | 0.10906 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 358.23 | 0.12348 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 436.82 | 0.15572 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 434.95 | 0.3085 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 366.08 | 0.22284 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 468.72 | 0.25713 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 424.46 | 0.22829 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 630.19 | 0.35259 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfL | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 260.54 | 0.1258 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 157.92 | 0.070274 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 386.28 | 0.11968 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 424.77 | 0.11627 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 541.7 | 0.21015 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 425.27 | 0.070709 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 526.62 | 0.089276 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 525.37 | 0.065823 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 540.19 | 0.08776 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 590.62 | 0.13996 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 520.21 | 0.10199 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 487.14 | 0.23042 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 445.11 | 0.16738 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 637.44 | 0.27399 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 599.64 | 0.23872 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 744.35 | 0.30207 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | OfS | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 306.96 | 0.10312 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 129.42 | 0.11928 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 322.21 | 0.13587 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 321.31 | 0.20319 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 349.31 | 0.13145 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 365.27 | 0.13232 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 508.26 | 0.15826 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 454.89 | 0.12382 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 454.5 | 0.12624 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 403.11 | 0.14493 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 419.7 | 0.12115 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 484.22 | 0.47036 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 413.19 | 0.32877 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 516.2 | 0.38928 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 401.2 | 0.2389 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 689.29 | 0.46146 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052B | Rt3 | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 277.35 | 0.22154 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 63.26 | 0.036185 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 173.03 | 0.14416 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166.81 | 0.078127 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 218.64 | 0.19588 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166.4 | 0.04153 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.06 | 0.066302 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 223.09 | 0.04837 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 217.93 | 0.08581 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 236.16 | 0.12856 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 308.91 | 0.15913 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 348.66 | 0.35707 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 257.49 | 0.2345 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 374.19 | 0.30111 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 331.51 | 0.28741 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 643.3 | 0.52513 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.79 | 0.082063 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.41 | 0.006747 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 163.53 | 0.13627 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 149.25 | 0.090972 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 209.8 | 0.21379 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155.26 | 0.048631 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 225.87 | 0.055657 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 216.35 | 0.038181 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 254.97 | 0.097612 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 249.96 | 0.13914 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 284.44 | 0.15946 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 356.05 | 0.23536 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.84 | 0.25466 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 361.16 | 0.32305 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 317.36 | 0.30232 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 588.03 | 0.51655 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 132.22 | 0.076919 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 20.98 | 0.015141 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 65.79 | 0.10661 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.73 | 0.03249 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.41 | 0.14474 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 54.29 | 0.012308 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.47 | 0.022682 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.96 | 0.004354 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.76 | 0.058767 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.99 | 0.12004 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 117.19 | 0.06106 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 311.01 | 0.22621 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 109.93 | 0.10917 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 304.19 | 0.15887 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 265.33 | 0.14197 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 498.46 | 0.2432 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 40.61 | 0.033834 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 58.56 | 0.046622 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.3 | 0.12046 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.33 | 0.025835 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 148.18 | 0.18955 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.91 | 0.01184 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136.24 | 0.034792 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.97 | 0.022658 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 181.26 | 0.082896 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 186.4 | 0.12751 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 221.34 | 0.12644 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 271.93 | 0.20628 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 194.3 | 0.22596 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 283.77 | 0.29043 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 264.37 | 0.27291 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 501.9 | 0.50828 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.1 | 0.048797 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 28.85 | 0.040278 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.77 | 0.10318 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 123.32 | 0.045961 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 191.33 | 0.15163 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.81 | 0.036616 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 228.57 | 0.039472 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 231.47 | 0.042445 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 242.55 | 0.060948 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 227.71 | 0.095585 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 258.25 | 0.081641 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 280.01 | 0.29234 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 209.19 | 0.14667 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 296.83 | 0.21171 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 257.28 | 0.17884 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 489.62 | 0.34074 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 121.47 | 0.061248 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 209.14 | 0.10446 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 313.96 | 0.22082 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 300.25 | 0.11747 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 361.06 | 0.29428 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 321.52 | 0.08815 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 358.85 | 0.083999 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 363.87 | 0.095403 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 416.02 | 0.17162 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 360.42 | 0.21174 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 445.86 | 0.21922 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 514.47 | 0.57019 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 410.84 | 0.34203 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 540.26 | 0.41628 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 459.37 | 0.37497 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 815.3 | 0.67678 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 299.81 | 0.15922 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 34.88 | 0.034011 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 79.58 | 0.11736 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 159.66 | 0.081417 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 96.39 | 0.15573 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.9 | 0.023462 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 238.21 | 0.069587 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.01 | 0.030378 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134.49 | 0.066515 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120.33 | 0.089952 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 285.01 | 0.16193 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 321.61 | 0.37256 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232.99 | 0.24634 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 336.47 | 0.32404 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 303.06 | 0.29559 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 583.65 | 0.52334 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.58 | 0.087553 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 23.6 | 0.019381 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.86 | 0.14605 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.07 | 0.055494 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 166.85 | 0.2022 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 103.05 | 0.030337 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 114.17 | 0.021722 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.88 | 0.025403 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 169.08 | 0.094502 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 187.61 | 0.17002 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 310.55 | 0.16995 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 335.64 | 0.48589 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 236.24 | 0.2605 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 350.47 | 0.33183 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 358.1 | 0.35804 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 754.24 | 0.66668 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124.97 | 0.079591 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 23.38 | 0.006193 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 190.82 | 0.14444 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 159.37 | 0.076224 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 229.87 | 0.19784 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 181.1 | 0.04004 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232.85 | 0.06843 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 209.79 | 0.044307 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 259.71 | 0.087854 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 226.39 | 0.11636 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 298.95 | 0.14471 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 342.88 | 0.35803 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 254.85 | 0.22793 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 356.98 | 0.28317 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 324.37 | 0.25694 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 579.32 | 0.40916 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.96 | 0.095686 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 60.23 | 0.021272 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 258.84 | 0.13709 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 254.49 | 0.08087 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 296.76 | 0.17022 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155.43 | 0.018507 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 316.78 | 0.05919 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 315.88 | 0.046596 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 351.49 | 0.091289 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 369.31 | 0.13698 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 422.31 | 0.14841 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 410.89 | 0.35579 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 329.36 | 0.20652 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 467.87 | 0.2835 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 433.77 | 0.25664 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 694.03 | 0.44666 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 192.63 | 0.085378 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 81.88 | 0.074847 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 215.46 | 0.19565 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 182.44 | 0.12185 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.91 | 0.25354 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 202.48 | 0.063641 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 262.21 | 0.10253 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 240.29 | 0.069348 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 136.94 | 0.088472 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 269.57 | 0.15587 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 349.17 | 0.21379 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 397.97 | 0.53305 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 298.56 | 0.32377 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 419.13 | 0.41695 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 360.48 | 0.36959 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 713.14 | 0.66096 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 142.04 | 0.15043 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 72.98 | 0.044175 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170.96 | 0.13963 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143.9 | 0.06574 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 207.72 | 0.18267 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 168.59 | 0.044526 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 221.79 | 0.061531 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 222.82 | 0.049068 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.4 | 0.092837 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 230.72 | 0.12699 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 267.99 | 0.13911 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 330.89 | 0.34291 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 242.16 | 0.22918 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 359.38 | 0.2901 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 304.47 | 0.27023 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 593.9 | 0.49678 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Com | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 123.37 | 0.077757 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.06 | -0.000143 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 157.39 | 0.13211 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 137.71 | 0.035344 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 194.39 | 0.17778 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 131.25 | 0.020968 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 227.04 | 0.071149 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 216.34 | 0.041167 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 251.7 | 0.09309 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 246.14 | 0.13245 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 276.51 | 0.167 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 343.36 | 0.22069 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232.95 | 0.27155 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 340.41 | 0.32193 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 301.84 | 0.29786 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 566.41 | 0.50614 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ECC | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126.35 | 0.061231 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 38.52 | 0.030642 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.9 | 0.12871 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 95.35 | 0.034063 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 140.16 | 0.15574 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 92.65 | 0.026206 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 161.78 | 0.031967 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 147.23 | 0.033462 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 189.07 | 0.073457 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 177.63 | 0.096166 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 210.11 | 0.077733 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 258.32 | 0.20293 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 174.57 | 0.13378 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 255.63 | 0.14423 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 217.36 | 0.11398 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 414.42 | 0.20933 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | ESe | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 84.41 | 0.057866 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 48.77 | 0.046732 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 128.72 | 0.12183 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 93.98 | 0.01821 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 144.18 | 0.18569 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.97 | 0.01485 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 134.01 | 0.050904 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 139.74 | 0.022858 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 179.63 | 0.079946 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 180.49 | 0.11282 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 216.6 | 0.1278 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 265.58 | 0.19516 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 190.23 | 0.21842 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 276.41 | 0.27871 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 258.42 | 0.28049 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 480.87 | 0.49334 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | EUn | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 88.51 | 0.045913 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 29.13 | 0.039671 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 130.86 | 0.090284 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124.52 | 0.052255 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 184.82 | 0.13046 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 126.69 | 0.040176 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 224.13 | 0.047215 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 219.73 | 0.046031 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 235.16 | 0.07186 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 211.92 | 0.09714 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 245.84 | 0.089843 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 261.71 | 0.26205 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 198.66 | 0.14197 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 279.79 | 0.18378 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 239.57 | 0.15904 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 450.17 | 0.28186 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Hsp | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118.64 | 0.059931 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 192.59 | 0.097217 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 301.97 | 0.21924 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 291.26 | 0.10943 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 354.27 | 0.29263 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 329.15 | 0.094179 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 358.73 | 0.06927 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 368.38 | 0.087928 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 405.68 | 0.1656 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 365.08 | 0.20608 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 434.27 | 0.21511 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 499.85 | 0.56487 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 396.59 | 0.33158 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 526.38 | 0.41106 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 461.86 | 0.36581 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 791.85 | 0.65944 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Htl | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 286.67 | 0.16029 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 57.04 | 0.054857 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 119.03 | 0.13949 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 92.2 | 0.055764 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 138.02 | 0.18283 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.97 | 0.045612 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 180.14 | 0.073636 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170.77 | 0.050717 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 182.55 | 0.07794 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.4 | 0.10797 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 206.65 | 0.15301 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 256.12 | 0.34958 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.43 | 0.23496 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 265.52 | 0.30586 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 246.98 | 0.27779 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 497.68 | 0.48984 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | MBT | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 77.98 | 0.074375 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 37.93 | 0.074537 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 214.17 | 0.20077 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 164.68 | 0.09571 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 296.46 | 0.27564 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 184.11 | 0.064072 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 320.25 | 0.080197 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 312.54 | 0.078379 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 373.19 | 0.16687 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 345.62 | 0.22665 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 426.8 | 0.20899 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 499.48 | 0.54911 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 349.47 | 0.31461 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 539.11 | 0.39964 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 473.32 | 0.39815 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 903.52 | 0.70086 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Nrs | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 187.62 | 0.13071 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 55.49 | 0.020002 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.18 | 0.12994 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 128.43 | 0.063501 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183.91 | 0.16868 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 153.77 | 0.040753 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 198.51 | 0.058512 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 175.45 | 0.038727 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 222.6 | 0.083357 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 191.28 | 0.10872 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 262.29 | 0.13473 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 310.95 | 0.33357 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 222.62 | 0.2147 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 326.07 | 0.25522 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 295.96 | 0.2361 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 539.13 | 0.39434 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfL | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 120.21 | 0.078342 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 83.71 | 0.033209 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 224.06 | 0.11148 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 237.32 | 0.069789 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 318.66 | 0.18089 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 222.47 | 0.033109 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 271.45 | 0.04142 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 272.67 | 0.037108 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 307.88 | 0.080829 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 347.27 | 0.1214 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 336.99 | 0.099503 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 359.58 | 0.30937 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 285.5 | 0.18079 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 440.78 | 0.26443 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 409.51 | 0.23908 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 628.04 | 0.38906 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | OfS | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 158.81 | 0.059398 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 66.6 | 0.053572 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 183.33 | 0.14553 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 155.96 | 0.10103 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 190.06 | 0.1912 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 174.07 | 0.062099 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 225.22 | 0.068797 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 197.52 | 0.053265 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232.94 | 0.11393 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 240.53 | 0.14778 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 280.62 | 0.15099 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 370.16 | 0.5049 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 270.2 | 0.31211 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 389.68 | 0.39384 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 315.62 | 0.31628 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 649.94 | 0.59844 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052C | Rt3 | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 123.37 | 0.14311 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 146.12 | 0.10019 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 331.76 | 0.1672 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 348.03 | 0.1486 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 425.98 | 0.20976 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 381.53 | 0.10608 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 537.17 | 0.14661 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 506.77 | 0.11428 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 470.94 | 0.1123 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 438.95 | 0.14697 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 515.73 | 0.19246 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 497.28 | 0.32968 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 429.36 | 0.25235 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 546.03 | 0.30133 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 488.98 | 0.28656 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 790.02 | 0.466 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 298.4 | 0.14001 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 121.41 | 0.082902 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 294.14 | 0.12186 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 314.06 | 0.16571 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 388.26 | 0.18924 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 350.02 | 0.11865 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 496.44 | 0.11754 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 473.99 | 0.10602 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 485.21 | 0.11519 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 432.16 | 0.134 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 450.74 | 0.16443 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 493.34 | 0.21355 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 382.15 | 0.21773 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 509.5 | 0.28831 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 456.37 | 0.27709 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 693.13 | 0.40723 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 295.22 | 0.11963 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 74.89 | 0.055505 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 170.36 | 0.081302 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 196.17 | 0.085444 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 236.26 | 0.092998 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 238.52 | 0.06153 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 299.33 | 0.056398 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 273 | 0.049863 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 297.28 | 0.06654 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 420.88 | 0.16131 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 240.93 | 0.055505 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 451.21 | 0.20416 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 217.25 | 0.079176 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 452.19 | 0.15367 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 402.59 | 0.13952 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 659.32 | 0.20844 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 169.91 | 0.058234 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 124.44 | 0.1294 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 254.62 | 0.14002 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 232.23 | 0.1002 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 304.49 | 0.18991 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 273.94 | 0.086139 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 360.64 | 0.10334 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 342.58 | 0.098412 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 380.68 | 0.10859 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 340.05 | 0.12478 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 372.25 | 0.13618 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 386.21 | 0.19153 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 335.63 | 0.20437 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 414.28 | 0.24373 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 388.54 | 0.23577 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 592.66 | 0.41026 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 256 | 0.08985 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 51.66 | 0.076516 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 226.42 | 0.12563 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 225.62 | 0.092062 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 327.27 | 0.15447 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 238.32 | 0.076169 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 427.06 | 0.090619 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 423.34 | 0.09042 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 424.69 | 0.090956 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 378.32 | 0.11165 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 405.2 | 0.10195 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 391.51 | 0.2478 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 323.85 | 0.14768 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 420.07 | 0.18735 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 374.26 | 0.16681 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 610.7 | 0.27055 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 223.59 | 0.11321 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 379.06 | 0.21104 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 548.43 | 0.27242 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 576.95 | 0.21905 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 642.63 | 0.33624 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 644.25 | 0.17539 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 755.09 | 0.20491 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 754.48 | 0.19509 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 779.97 | 0.22679 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 617.76 | 0.22875 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 715.58 | 0.25251 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 718.61 | 0.55023 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 652.46 | 0.36319 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 769.07 | 0.42123 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 661.41 | 0.36154 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 963.12 | 0.59355 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 615.29 | 0.27472 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115.14 | 0.077325 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 221.44 | 0.11113 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 343.68 | 0.14681 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 277.62 | 0.1333 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 283.09 | 0.069822 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 534.97 | 0.15004 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 374.02 | 0.081092 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 371.18 | 0.083368 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 299.18 | 0.086841 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 490.26 | 0.20516 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 474.23 | 0.36482 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 394.31 | 0.27897 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 508.4 | 0.34693 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 456.16 | 0.30885 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 741.98 | 0.4833 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 264.66 | 0.15319 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 82.12 | 0.10603 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 307 | 0.17068 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 337 | 0.14993 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 417.21 | 0.18264 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 367.91 | 0.12423 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 522.27 | 0.11869 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 548.83 | 0.12932 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 539.78 | 0.13591 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 467.68 | 0.15299 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 550.13 | 0.17818 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 472.53 | 0.33638 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 421.87 | 0.22392 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 509.37 | 0.24448 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 532.51 | 0.28809 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 844.13 | 0.48163 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 345.35 | 0.17853 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 101.53 | 0.05057 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 364.14 | 0.17892 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 337.98 | 0.13786 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 443.68 | 0.22906 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 387.98 | 0.087471 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 533.62 | 0.14106 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 476.33 | 0.09422 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 522.31 | 0.13077 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 424.61 | 0.14415 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 519.43 | 0.18473 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 509.47 | 0.35368 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 436.68 | 0.25772 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 538.98 | 0.30307 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 490.94 | 0.26515 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 735.19 | 0.38399 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 304.34 | 0.15602 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 152.67 | 0.075177 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 442.23 | 0.15347 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 455.21 | 0.14433 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 512.34 | 0.17472 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 382.71 | 0.057961 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 592.57 | 0.11412 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 590.5 | 0.08772 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 608.96 | 0.11176 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 625.85 | 0.1682 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 659.85 | 0.17933 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 570.24 | 0.30905 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 514.53 | 0.21327 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 675.17 | 0.30779 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 634.93 | 0.27031 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 848.22 | 0.36813 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 359.11 | 0.13534 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 156.67 | 0.15634 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 391.19 | 0.24927 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 373.89 | 0.24387 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 448.62 | 0.26715 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 423.68 | 0.15245 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 586.96 | 0.21899 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 537.41 | 0.18063 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 388.86 | 0.091628 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 466.03 | 0.18243 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 568.97 | 0.25864 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 562.34 | 0.54011 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 483.91 | 0.38598 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 595.88 | 0.447 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 516.48 | 0.3766 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 853.5 | 0.60847 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | Ex | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 310.19 | 0.25328 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 143.49 | 0.099619 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 308.13 | 0.15678 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 304.5 | 0.12272 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 389.27 | 0.19177 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 365.59 | 0.10137 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 486.82 | 0.1281 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 477.34 | 0.10458 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 459.8 | 0.11619 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 409.52 | 0.13958 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 427.46 | 0.14535 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 454.48 | 0.3087 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 386.99 | 0.2325 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 507.8 | 0.28498 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 427.9 | 0.24452 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 688.79 | 0.41382 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Com | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 277.49 | 0.12624 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 118.51 | 0.077842 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 285.78 | 0.11295 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 302.75 | 0.094646 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 368.55 | 0.1274 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 326.58 | 0.086198 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 498.83 | 0.1276 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 470.35 | 0.10108 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 478.67 | 0.11037 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 425.43 | 0.12694 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 441.06 | 0.18064 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 479.45 | 0.20128 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 377.09 | 0.25637 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 476.94 | 0.29986 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 435.26 | 0.28431 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 682.27 | 0.43483 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ECC | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 287.24 | 0.093595 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 85.49 | 0.069386 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 213.86 | 0.11911 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 201.63 | 0.062534 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 262.22 | 0.12599 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 229.61 | 0.061955 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 341.06 | 0.055912 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 307.99 | 0.06585 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 352.78 | 0.087306 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 314.04 | 0.10956 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 335.54 | 0.10047 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 362.39 | 0.18568 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 279.7 | 0.1387 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 371.13 | 0.14267 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 320.22 | 0.12206 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 512.89 | 0.18523 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | ESe | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 188.77 | 0.088568 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 105.14 | 0.12849 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 248.81 | 0.14175 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 229.5 | 0.099412 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 299 | 0.18665 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 273.25 | 0.084634 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 354.61 | 0.12298 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 338.84 | 0.099948 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 369.15 | 0.11226 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 328.96 | 0.12493 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 363.45 | 0.1507 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 376.82 | 0.17411 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 326.7 | 0.2088 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 403.97 | 0.24363 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 381.55 | 0.25214 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 571.89 | 0.39092 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | EUn | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 239.02 | 0.076269 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 52.23 | 0.07282 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 214.29 | 0.11653 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 223.68 | 0.10199 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 310.39 | 0.155 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 223.15 | 0.073533 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 399.96 | 0.0881 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 393.88 | 0.081971 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 398.85 | 0.09638 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 352.61 | 0.11054 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 386.56 | 0.11586 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 369.72 | 0.2426 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 307.89 | 0.14888 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 402.1 | 0.18515 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 347.74 | 0.1667 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 572.9 | 0.254 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Hsp | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 210.4 | 0.10467 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 345.74 | 0.19351 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 519.89 | 0.26856 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 545.7 | 0.21045 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 618.32 | 0.33288 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 630.44 | 0.1798 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 732.78 | 0.18626 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 735.42 | 0.18793 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 753.45 | 0.21698 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 613.7 | 0.22162 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 690.31 | 0.24654 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 692.71 | 0.54194 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 626.49 | 0.35712 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 743.6 | 0.411 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 666.07 | 0.35018 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 934.75 | 0.57431 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Htl | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 586.8 | 0.26818 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 135.51 | 0.10335 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 247.83 | 0.15808 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 260.03 | 0.096564 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 301.7 | 0.19312 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 290.29 | 0.083815 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 443.28 | 0.13556 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 411.34 | 0.09404 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 391.76 | 0.10547 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 339.71 | 0.12486 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 353.14 | 0.16806 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 350.36 | 0.31275 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 296.51 | 0.21891 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 374.94 | 0.2871 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 349.7 | 0.25073 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 568.48 | 0.40061 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | MBT | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 203.08 | 0.12156 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 68.68 | 0.12826 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 357.55 | 0.23962 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 302.49 | 0.17549 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 506 | 0.30383 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 337.05 | 0.12971 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 603.24 | 0.16167 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 583.73 | 0.16059 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 660.16 | 0.21961 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 580 | 0.25495 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 662.68 | 0.24699 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 678.44 | 0.49966 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 532.68 | 0.328 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 745.16 | 0.3846 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 670.51 | 0.39649 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 1090.93 | 0.61042 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Nrs | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 359.96 | 0.22018 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 115.59 | 0.050643 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 297.73 | 0.15406 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 286.77 | 0.11077 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 361.17 | 0.18354 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 338.94 | 0.078913 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 459.98 | 0.11672 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 407.96 | 0.082461 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 445.46 | 0.10906 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 358.23 | 0.12348 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 436.82 | 0.15572 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 434.95 | 0.3085 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 366.08 | 0.22284 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 468.72 | 0.25713 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 424.46 | 0.22829 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 630.19 | 0.35259 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfL | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 260.54 | 0.1258 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 157.92 | 0.070274 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 386.28 | 0.11968 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 424.77 | 0.11627 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 541.7 | 0.21015 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 425.27 | 0.070709 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 526.62 | 0.089276 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 525.37 | 0.065823 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 540.19 | 0.08776 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 590.62 | 0.13996 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 520.21 | 0.10199 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 487.14 | 0.23042 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 445.11 | 0.16738 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 637.44 | 0.27399 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 599.64 | 0.23872 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 744.35 | 0.30207 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | OfS | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 306.96 | 0.10312 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ01 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 129.42 | 0.11928 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ02 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 322.21 | 0.13587 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ03 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 321.31 | 0.20319 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ04 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 349.31 | 0.13145 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ05 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 365.27 | 0.13232 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ06 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 508.26 | 0.15826 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ07 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 454.89 | 0.12382 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ08 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 454.5 | 0.12624 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ09 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 403.11 | 0.14493 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ10 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 419.7 | 0.12115 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ11 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 484.22 | 0.47036 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ12 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 413.19 | 0.32877 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ13 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 516.2 | 0.38928 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ14 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 401.2 | 0.2389 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ15 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 689.29 | 0.46146 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual
Any | SWHC052D | Rt3 | New | CZ16 | cWtd | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | 1 |  | None | 0 | 0 | 0 | 277.35 | 0.22154 | 0 | [6 empty] | DEER:HVAC_Chillers | Annual

## CostExAnte
PA | MeasCostID | CostQualifier | BldgType | BldgVint | BldgLoc | DelivType | SourceDesc | Version | VersionSource | LastMod | NormUnit | CostType | GenCost | LaborCost | MatlCost | Description | Sector | UseCategory | UseSubCategory | TechGroup | TechType | TechID | MeasAppType | InstallHrs | LaborRate | LocCostAdj | Status | Comment | MeasLaborID | StdLaborRateID
Any | SWHC052_01_M001 | None | Any | Any | Any | Any | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | Full |  |  | 815.9253 | Air-Cooled Chiller, Path B, < 150 tons, 10.4 EER, 17.7 IPLV | Any | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed
Any | SWHC052_01_M002 | None | Any | Any | Any | Any | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | Full |  |  | 892.5973 | Air-Cooled Chiller, Path B, < 150 tons, 10.4 EER, 19.0 IPLV | Any | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed
Any | SWHC052_01_M003 | None | Any | Any | Any | Any | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | Full |  |  | 644.7157 | Air-Cooled Chiller, Path B, >= 150 tons, 10.4 EER, 18.0 IPLV | Any | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed
Any | SWHC052_01_M004 | None | Any | Any | Any | Any | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | Full |  |  | 710.6871 | Air-Cooled Chiller, Path B, >= 150 tons, 10.4 EER, 19.3 IPLV | Any | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed
Any | SWHC052_01_B001 | None | Any | Any | Any | Any | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | Full |  |  | 719.1767 | Air-Cooled Chiller, Path B Standard Efficiency, < 150 tons, 9.7 EER, 15.8 IPLV | Any | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed
Any | SWHC052_01_B002 | None | Any | Any | Any | Any | SWHC052-01 | ExAnte2022 | IOU workpaper | 2021-02-01 | Cap-Tons | Full |  |  | 586.0837 | Air-Cooled Chiller, Path B Standard Efficiency, >= 150 tons, 9.7 EER, 16.1 IPLV | Any | HVAC | SpaceCool | Chiller | Screw |  | NR |  |  | None | Proposed