## Overview
ACC Path B Workpaper Modeling Plan
Prepared on November 13, 2020
Building Types |  |  | Climate Zones |  | Vintages |  | Chiller Models
No. | BT Code | BT Name | No. | Name | No. | Year | No. | Chiller | Tier
1 | ECC | Education – Community College | 1 | CZ01 | 1 | 2003 | 1 | Model 7 | Tier 2
2 | ESe | Education – Secondary School | 2 | CZ02 | 2 | 2007 | 2 | Model 11 | Title 24
3 | EUn | Education – University | 3 | CZ03 | 3 | 2011 | 3 | Model 17 | Tier 1
4 | Hsp | Health/Medical – Hospital | 4 | CZ04 | 4 | 2015
5 | Htl | Lodging – Hotel | 5 | CZ05 | 5 | 2020
6 | MBT | Manufacturing Biotech | 6 | CZ06
7 | Nrs | Health/Medical – Nursing Home | 7 | CZ07
8 | OfL | Office – Large | 8 | CZ08
9 | OfS | Office – Small | 9 | CZ09
10 | Rt3 | Retail – Multistory Large | 10 | CZ10
|  |  | 11 | CZ11
|  |  | 12 | CZ12
|  |  | 13 | CZ13
|  |  | 14 | CZ14
|  |  | 15 | CZ15
|  |  | 16 | CZ16
Other Notes
Use the CZ2022 Weather data files
Override full-load EIR for all chiller models (instructions in "Chiller Performance Data" tab)
Total number of runs
= (10 BT) x (16 CZ) x (5 Vint) x (3 chillers)
2400

## Chiller Performance Data
Chiller | Cap f(OADBT, LCHWT) | [5 empty] | EIR f(OADBT, LCHWT) | [5 empty] | EIR f(PLR, dT) | [5 empty] | Overridden Full Load EIR (W/W) | kW/Ton
Model 7 | -5.2148 | 0.18612 | -0.0013437 | 0.038994 | -0.00010448 | -0.00050442 | -10.3413 | 0.33751 | -0.0027786 | 0.061482 | -3.8974e-05 | -0.00085138 | -0.020619 | 0.64526 | -0.24621 | -0.0050037 | 6.1617e-05 | 0.013338 | 0.32871 | 1.1561
Model 11 | 0.0601 | 0.026 | -0.000104 | 4.93e-18 | -6.81e-21 | -9.08e-20 | 5.7569 | -0.15411 | 0.0019889 | -0.052356 | 0.00042505 | -0.00017262 | 0.103 | 0.398 | 0.0178 | -0.00498 | 6.08e-05 | 0.0104 | 0.35175 | 1.2371
Model 17 | 0.38503 | 0.02213 | 7.1936e-05 | 0.00086944 | -1.9113e-05 | -9.7598e-05 | 0.77207 | -0.0076535 | 9.3454e-05 | 8.75e-05 | 8.9125e-05 | -0.00010261 | 0.02606 | 0.58088 | 0.39306 | 0 | 0 | 0 | 0.32871 | 1.1561
Coefficient labels | a | b | c | d | e | f | a | b | c | d | e | f | a | b | c | d | e | f
(also occasionally labeled as) | c0 | c1 | c2 | c3 | c4 | c5 | c0 | c1 | c2 | c3 | c4 | c5 | c0 | c1 | c2 | c3 | c4 | c5
| const | x | x^2 or x*x | y | y^2 or y*y | x*y | const | x | x^2 or x*x | y | y^2 or y*y | x*y | const | x | x^2 or x*x | y | y^2 or y*y | x*y
EIR Override:
EER | a c0: Resulting EIR
9.7 | a c0: 0.35175
10.38 | a c0: 0.32871

## Modeling Results
Chiller Number | BldgType | BldgVint | BldgLoc | BldgHVAC | Modeling ID | normunit | System Tons | Annual Cooling Energy (kWh) | Annual Fan Energy (kWh) (not anticipated to be chiller dependent) | Total Building Energy Consumption (kWh) | Peak kW Power Demand over "heat wave" period (varies by CZ) | Energy Consumption per Ton (kWh/ton) | Peak Demand per Ton (kW/ton)
Model 11 | ECC | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ01 | ChlrCap | 363.0903 | 69393.66 | 13191.63 | 3517342.7644 | 449.5531 | 191.1195 | 1.2381
Model 11 | ECC | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ01 | ChlrCap | 362.3947 | 68793.3 | 13128.86 | 3471338.7433 | 447.6453 | 189.8298 | 1.2352
Model 11 | ECC | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ01 | ChlrCap | 358.621 | 69085.78 | 14694.4 | 3397864.136 | 446.3035 | 192.6429 | 1.2445
Model 11 | ECC | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ01 | ChlrCap | 337.2 | 65797.45 | 13961.43 | 3285379.5698 | 429.4947 | 195.1289 | 1.2737
Model 11 | ECC | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ01 | ChlrCap | 308.2373 | 59883.9 | 4634.174 | 3200081.1665 | 383.8349 | 194.2785 | 1.2453
Model 11 | ESe | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ01 | ChlrCap | 177.9213 | 20704.06 | 950.8166 | 1628250.4524 | 119.7207 | 116.3664 | 0.67289
Model 11 | ESe | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ01 | ChlrCap | 172.2432 | 23843.83 | 979.5164 | 1558181.9688 | 116.9993 | 138.4312 | 0.67927
Model 11 | ESe | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ01 | ChlrCap | 171.2935 | 24206.64 | 1103.1 | 1514518.1862 | 116.8675 | 141.3167 | 0.68226
Model 11 | ESe | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ01 | ChlrCap | 162.6435 | 22715.96 | 604.3058 | 1468952.7318 | 110.9747 | 139.6672 | 0.68232
Model 11 | ESe | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ01 | ChlrCap | 147.6032 | 20774.4 | 411.2522 | 1435567.62 | 102.3906 | 140.7449 | 0.69369
Model 11 | EUn | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ01 | ChlrCap | 1393.3897 | 259417.8 | 67188.92 | 11836124.1501 | 1599.0574 | 186.1775 | 1.1476
Model 11 | EUn | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ01 | ChlrCap | 1386.448 | 253802 | 62268.68 | 11646979.612 | 1595.2921 | 183.0592 | 1.1506
Model 11 | EUn | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ01 | ChlrCap | 1376.0627 | 259886.2 | 68036.7 | 11304871.3869 | 1593.4015 | 188.8622 | 1.1579
Model 11 | EUn | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ01 | ChlrCap | 1253.919 | 202476.7 | 58726.98 | 10610223.7878 | 1508.0948 | 161.4751 | 1.2027
Model 11 | EUn | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ01 | ChlrCap | 1169.1157 | 184393.1 | 37437.4 | 10233439.8265 | 1358.1727 | 157.7202 | 1.1617
Model 11 | Hsp | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ01 | ChlrCap | 534.269 | 35763.49 | 1086.875 | 4303403.5768 | 472.3346 | 66.9391 | 0.88408
Model 11 | Hsp | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ01 | ChlrCap | 533.8913 | 35736.91 | 1084.233 | 4287096.0938 | 471.4063 | 66.9367 | 0.88296
Model 11 | Hsp | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ01 | ChlrCap | 533.2168 | 35562.68 | 1107.53 | 4235718.5487 | 470.38 | 66.6946 | 0.88216
Model 11 | Hsp | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ01 | ChlrCap | 532.3435 | 35382.4 | 829.3423 | 4155389.2532 | 463.3321 | 66.4654 | 0.87036
Model 11 | Hsp | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ01 | ChlrCap | 528.477 | 34866.42 | 660.4199 | 4056847.993 | 417.1723 | 65.9753 | 0.78939
Model 11 | Htl | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ01 | ChlrCap | 121.6717 | 68979.52 | 8765.047 | 1563707.3342 | 144.7897 | 566.9317 | 1.19
Model 11 | Htl | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ01 | ChlrCap | 115.4313 | 57885.48 | 7115.589 | 1347798.2892 | 131.0711 | 501.4712 | 1.1355
Model 11 | Htl | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ01 | ChlrCap | 112.9238 | 58879.96 | 7417.794 | 1280073.6089 | 130.5657 | 521.4131 | 1.1562
Model 11 | Htl | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ01 | ChlrCap | 95.2545 | 44312.98 | 5723.375 | 1161005.5565 | 118.4423 | 465.2063 | 1.2434
Model 11 | Htl | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ01 | ChlrCap | 93.868 | 43760.9 | 5644.045 | 1156820.2372 | 115.0773 | 466.1961 | 1.2259
Model 11 | MBT | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ01 | ChlrCap | 197.4575 | 33075.8 | 3894.1 | 2083137.4138 | 180.6097 | 167.5085 | 0.91468
Model 11 | MBT | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ01 | ChlrCap | 192.24 | 39787.18 | 4266.294 | 1914278.4842 | 181.1409 | 206.9662 | 0.94226
Model 11 | MBT | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ01 | ChlrCap | 189.7313 | 39385.7 | 4257.489 | 1868389.0457 | 178.3675 | 207.5867 | 0.94011
Model 11 | MBT | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ01 | ChlrCap | 189.4815 | 40037.13 | 1646.272 | 1810788.6659 | 170.4515 | 211.2984 | 0.89957
Model 11 | MBT | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ01 | ChlrCap | 173.0733 | 38535.93 | 1739.917 | 1679710.932 | 155.7068 | 222.6567 | 0.89966
Model 11 | Nrs | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ01 | ChlrCap | 65.0155 | 8249.475 | 2526.695 | 1513157.2505 | 126.7279 | 126.8847 | 1.9492
Model 11 | Nrs | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ01 | ChlrCap | 64.0681 | 8069.643 | 1811.591 | 1400205.0434 | 120.4248 | 125.9541 | 1.8796
Model 11 | Nrs | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ01 | ChlrCap | 64.0681 | 8069.643 | 1811.591 | 1400205.0434 | 120.4248 | 125.9541 | 1.8796
Model 11 | Nrs | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ01 | ChlrCap | 63.8031 | 6179.417 | 1217.931 | 1366385.5641 | 116.6978 | 96.8514 | 1.829
Model 11 | Nrs | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ01 | ChlrCap | 62.0487 | 5374.693 | 995.0484 | 1340714.8732 | 106.2086 | 86.6206 | 1.7117
Model 11 | OfL | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ01 | ChlrCap | 267.187 | 43765.63 | 3926.175 | 1731328.9355 | 242.7528 | 163.8015 | 0.90855
Model 11 | OfL | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ01 | ChlrCap | 262.4838 | 51576.89 | 3233.353 | 1639889.7245 | 237.6579 | 196.4955 | 0.90542
Model 11 | OfL | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ01 | ChlrCap | 258.7623 | 51591.89 | 4154.23 | 1592951.1079 | 234.8333 | 199.3794 | 0.90752
Model 11 | OfL | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ01 | ChlrCap | 251.6 | 46699.01 | 3814.419 | 1631123.3376 | 224.2075 | 185.6081 | 0.89113
Model 11 | OfL | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ01 | ChlrCap | 239.618 | 43192.61 | 165.0933 | 1513935.3107 | 206.2242 | 180.2561 | 0.86064
Model 11 | OfS | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ01 | ChlrCap | 16.798 | 2693.135 | 256.0124 | 121116.0677 | 12.6298 | 160.3251 | 0.75186
Model 11 | OfS | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ01 | ChlrCap | 16.4158 | 3685.245 | 218.1972 | 117202.0008 | 12.4757 | 224.4937 | 0.75998
Model 11 | OfS | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ01 | ChlrCap | 16.3121 | 3651.051 | 216.8951 | 116574.1671 | 12.3726 | 223.8252 | 0.75849
Model 11 | OfS | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ01 | ChlrCap | 14.6981 | 3175.768 | 117.0017 | 105748.4199 | 10.9894 | 216.0664 | 0.74767
Model 11 | OfS | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ01 | ChlrCap | 13.954 | 2773.829 | 90.2619 | 101325.9308 | 10.2563 | 198.7836 | 0.73501
Model 11 | Rt3 | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ01 | ChlrCap | 153.7271 | 37736.88 | 21212.68 | 1538457.4162 | 280.7585 | 245.4797 | 1.8263
Model 11 | Rt3 | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ01 | ChlrCap | 152.8906 | 31913.04 | 20308.61 | 1452891.4666 | 268.0734 | 208.7312 | 1.7534
Model 11 | Rt3 | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ01 | ChlrCap | 150.8586 | 33431.21 | 22719.39 | 1424335.1524 | 268.2563 | 221.6063 | 1.7782
Model 11 | Rt3 | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ01 | ChlrCap | 139.6182 | 28280.81 | 18718.63 | 1332554.8933 | 242.2199 | 202.5581 | 1.7349
Model 11 | Rt3 | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ01 | ChlrCap | 128.2081 | 23930.88 | 13578.82 | 1258905.0645 | 219.8427 | 186.6566 | 1.7147
Model 11 | ECC | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ02 | ChlrCap | 622.7143 | 435635.8 | 59003.07 | 3446966.5205 | 745.8502 | 699.5757 | 1.1977
Model 11 | ECC | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ02 | ChlrCap | 620.6888 | 432211.7 | 58594.28 | 3387378.6389 | 741.8477 | 696.342 | 1.1952
Model 11 | ECC | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ02 | ChlrCap | 618.5397 | 431294.8 | 58534.98 | 3382081.8816 | 740.1357 | 697.2791 | 1.1966
Model 11 | ECC | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ02 | ChlrCap | 589.2032 | 398693.2 | 51019.9 | 3232161.694 | 704.1675 | 676.6651 | 1.1951
Model 11 | ECC | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ02 | ChlrCap | 557.0718 | 377698.3 | 35147.46 | 3066775.1348 | 643.6549 | 678.0065 | 1.1554
Model 11 | ESe | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ02 | ChlrCap | 318.2727 | 144867.3 | 14852.03 | 1523973.4839 | 247.3907 | 455.1673 | 0.77729
Model 11 | ESe | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ02 | ChlrCap | 309.8685 | 160738.5 | 15006.12 | 1434383.3594 | 237.5963 | 518.7313 | 0.76676
Model 11 | ESe | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ02 | ChlrCap | 308.0745 | 160199.1 | 14964.26 | 1429421.5374 | 236.8735 | 520.0012 | 0.76888
Model 11 | ESe | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ02 | ChlrCap | 300.8848 | 145124 | 10234.08 | 1358671.8061 | 213.8828 | 482.3241 | 0.71085
Model 11 | ESe | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ02 | ChlrCap | 285.2343 | 136799.7 | 10187.84 | 1304181.1503 | 203.8912 | 479.6046 | 0.71482
Model 11 | EUn | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ02 | ChlrCap | 2222.8973 | 1393255 | 326349.4 | 11101799.3517 | 2509.4422 | 626.7743 | 1.1289
Model 11 | EUn | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ02 | ChlrCap | 2209.6417 | 1374098 | 316416.5 | 10869363.9461 | 2500.8539 | 621.8646 | 1.1318
Model 11 | EUn | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ02 | ChlrCap | 2186.6183 | 1368945 | 315133.8 | 10720757.8242 | 2488.3594 | 626.0558 | 1.138
Model 11 | EUn | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ02 | ChlrCap | 2065.393 | 1236180 | 262352.1 | 9972723.4936 | 2324.5847 | 598.5205 | 1.1255
Model 11 | EUn | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ02 | ChlrCap | 1962.3893 | 1176432 | 220592.8 | 9532762.4478 | 2180.2697 | 599.4896 | 1.111
Model 11 | Hsp | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ02 | ChlrCap | 819.109 | 350777 | 16193.16 | 4336202.9672 | 682.9088 | 428.2422 | 0.83372
Model 11 | Hsp | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ02 | ChlrCap | 818.5588 | 349599 | 16180.47 | 4315454.9859 | 681.8049 | 427.0909 | 0.83293
Model 11 | Hsp | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ02 | ChlrCap | 818.008 | 349369.4 | 16180.47 | 4312125.129 | 681.5015 | 427.0978 | 0.83312
Model 11 | Hsp | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ02 | ChlrCap | 827.012 | 339856.2 | 10796.78 | 4225304.1325 | 667.4632 | 410.9447 | 0.80708
Model 11 | Hsp | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ02 | ChlrCap | 844.9847 | 323683 | 10247.04 | 4061290.8781 | 610.5665 | 383.0637 | 0.72258
Model 11 | Htl | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ02 | ChlrCap | 192.1052 | 212335.4 | 23433.63 | 1550223.372 | 236.8569 | 1105.3081 | 1.233
Model 11 | Htl | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ02 | ChlrCap | 183.6192 | 188332.4 | 20285.07 | 1264019.5428 | 219.4813 | 1025.6685 | 1.1953
Model 11 | Htl | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ02 | ChlrCap | 179.1558 | 186951.1 | 20419.85 | 1219520.4163 | 215.9655 | 1043.5111 | 1.2055
Model 11 | Htl | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ02 | ChlrCap | 162.5328 | 162056.7 | 18110.79 | 1135977.3815 | 201.2149 | 997.0705 | 1.238
Model 11 | Htl | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ02 | ChlrCap | 161.267 | 160283 | 17823.04 | 1125463.7773 | 197.0984 | 993.8984 | 1.2222
Model 11 | MBT | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ02 | ChlrCap | 321.5922 | 187272.7 | 23032.04 | 2195514.8441 | 290.6113 | 582.3298 | 0.90366
Model 11 | MBT | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ02 | ChlrCap | 311.943 | 208996.5 | 22850.62 | 2019840.2896 | 287.9907 | 669.983 | 0.92322
Model 11 | MBT | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ02 | ChlrCap | 307.7235 | 204241.3 | 21971.36 | 1942969.9343 | 280.6091 | 663.7169 | 0.91189
Model 11 | MBT | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ02 | ChlrCap | 305.3705 | 191986.6 | 8169.578 | 1872192.3447 | 261.2033 | 628.7005 | 0.85537
Model 11 | MBT | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ02 | ChlrCap | 285.5302 | 179687 | 7364.581 | 1750121.5862 | 237.5201 | 629.31 | 0.83186
Model 11 | Nrs | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ02 | ChlrCap | 105.7102 | 81776.16 | 17907.3 | 1445443.6545 | 185.7001 | 773.588 | 1.7567
Model 11 | Nrs | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ02 | ChlrCap | 101.8806 | 84717.03 | 16428.9 | 1290349.62 | 177.1973 | 831.5322 | 1.7393
Model 11 | Nrs | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ02 | ChlrCap | 100.7931 | 84143.82 | 16594.82 | 1264556.4631 | 175.8854 | 834.8175 | 1.745
Model 11 | Nrs | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ02 | ChlrCap | 98.5594 | 76249.88 | 15159.05 | 1227387.9921 | 170.0055 | 773.6438 | 1.7249
Model 11 | Nrs | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ02 | ChlrCap | 100.1231 | 71121.06 | 14471.78 | 1190763.8023 | 158.6957 | 710.3363 | 1.585
Model 11 | OfL | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ02 | ChlrCap | 380.9968 | 304292.5 | 55721.41 | 2017738.1958 | 366.1541 | 798.6746 | 0.96104
Model 11 | OfL | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ02 | ChlrCap | 380.0078 | 272486 | 51992.04 | 1854386.2802 | 345.1981 | 717.0536 | 0.9084
Model 11 | OfL | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ02 | ChlrCap | 367.1977 | 269257.6 | 60529.44 | 1784732.4701 | 330.368 | 733.277 | 0.8997
Model 11 | OfL | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ02 | ChlrCap | 366.8677 | 251370.9 | 47316.09 | 1799779.9812 | 326.5313 | 685.1814 | 0.89005
Model 11 | OfL | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ02 | ChlrCap | 355.431 | 239559.1 | 4563.785 | 1701862.4021 | 312.3325 | 673.9961 | 0.87874
Model 11 | OfS | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ02 | ChlrCap | 23.8356 | 20696.14 | 1691.151 | 132054.5284 | 21.5823 | 868.2863 | 0.90547
Model 11 | OfS | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ02 | ChlrCap | 23.5463 | 18709.87 | 1577.193 | 123404.3815 | 19.8814 | 794.6003 | 0.84435
Model 11 | OfS | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ02 | ChlrCap | 23.1363 | 18511.2 | 1639.146 | 120157.2381 | 19.0309 | 800.0928 | 0.82255
Model 11 | OfS | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ02 | ChlrCap | 21.2725 | 16064.56 | 1338.68 | 110671.487 | 17.0284 | 755.1812 | 0.80049
Model 11 | OfS | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ02 | ChlrCap | 20.6019 | 15311.41 | 1132.597 | 105420.5553 | 16.2271 | 743.2029 | 0.78765
Model 11 | Rt3 | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ02 | ChlrCap | 247.1868 | 223426.3 | 65294.24 | 1653602.6413 | 409.8888 | 903.8762 | 1.6582
Model 11 | Rt3 | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ02 | ChlrCap | 245.7843 | 203631.6 | 65227.64 | 1569245.4478 | 394.4719 | 828.4971 | 1.605
Model 11 | Rt3 | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ02 | ChlrCap | 244.856 | 203517.9 | 65522.18 | 1568185.7925 | 393.9007 | 831.1738 | 1.6087
Model 11 | Rt3 | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ02 | ChlrCap | 235.4288 | 185991.5 | 57213.32 | 1443943.9672 | 356.8761 | 790.0116 | 1.5159
Model 11 | Rt3 | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ02 | ChlrCap | 224.1828 | 174248.3 | 43872.4 | 1358737.5018 | 331.3405 | 777.2598 | 1.478
Model 11 | ECC | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ03 | ChlrCap | 509.1507 | 291944.7 | 47100.38 | 3196016.6096 | 589.5189 | 573.3955 | 1.1578
Model 11 | ECC | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ03 | ChlrCap | 507.977 | 289227.6 | 46734.79 | 3134372.9062 | 586.9381 | 569.3714 | 1.1554
Model 11 | ECC | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ03 | ChlrCap | 506.7695 | 289057.3 | 46772.95 | 3131464.1172 | 586.0901 | 570.3921 | 1.1565
Model 11 | ECC | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ03 | ChlrCap | 456.682 | 264459.1 | 46357.56 | 2942532.7726 | 552.5013 | 579.0881 | 1.2098
Model 11 | ECC | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ03 | ChlrCap | 427.4718 | 245809 | 27423.67 | 2782019.7831 | 483.4838 | 575.0297 | 1.131
Model 11 | ESe | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ03 | ChlrCap | 268.731 | 101720.9 | 13741.71 | 1380493.8666 | 178.4197 | 378.5231 | 0.66393
Model 11 | ESe | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ03 | ChlrCap | 265.0458 | 120537.3 | 13839.75 | 1296707.1165 | 180.2585 | 454.7791 | 0.6801
Model 11 | ESe | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ03 | ChlrCap | 264.0397 | 120386.5 | 13838.29 | 1292670.8843 | 179.8805 | 455.941 | 0.68126
Model 11 | ESe | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ03 | ChlrCap | 235.9863 | 90324.27 | 4932.658 | 1210728.6691 | 139.0852 | 382.7521 | 0.58938
Model 11 | ESe | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ03 | ChlrCap | 220.4452 | 83474.06 | 4248.158 | 1155934.6604 | 128.3852 | 378.6613 | 0.58239
Model 11 | EUn | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ03 | ChlrCap | 1824.8797 | 859419.5 | 217717.5 | 10245888.6061 | 1923.4425 | 470.9458 | 1.054
Model 11 | EUn | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ03 | ChlrCap | 1815.8227 | 844330.6 | 207241 | 9995012.5744 | 1917.3143 | 464.9852 | 1.0559
Model 11 | EUn | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ03 | ChlrCap | 1794.5313 | 847475.4 | 207300 | 9834221.898 | 1910.5092 | 472.2544 | 1.0646
Model 11 | EUn | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ03 | ChlrCap | 1622.691 | 750068.4 | 223028.2 | 8925678.0469 | 1797.3386 | 462.2374 | 1.1076
Model 11 | EUn | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ03 | ChlrCap | 1524.3833 | 703302.5 | 176849.2 | 8449405.3318 | 1632.0901 | 461.3685 | 1.0707
Model 11 | Hsp | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ03 | ChlrCap | 647.9992 | 229803.2 | 13571.25 | 3997103.9941 | 561.7817 | 354.635 | 0.86695
Model 11 | Hsp | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ03 | ChlrCap | 647.6155 | 229044.3 | 13567.33 | 3977437.1946 | 561.1743 | 353.6733 | 0.86652
Model 11 | Hsp | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ03 | ChlrCap | 647.2195 | 228985 | 13567.32 | 3973702.8957 | 561.0118 | 353.7981 | 0.8668
Model 11 | Hsp | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ03 | ChlrCap | 581.0735 | 204947.5 | 9872.729 | 3873509.1536 | 537.7247 | 352.705 | 0.9254
Model 11 | Hsp | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ03 | ChlrCap | 577.2075 | 195382.5 | 9032.592 | 3703866.5475 | 486.4651 | 338.4961 | 0.84279
Model 11 | Htl | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ03 | ChlrCap | 159.5386 | 157224.1 | 20439 | 1386996.5149 | 176.4675 | 985.4923 | 1.1061
Model 11 | Htl | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ03 | ChlrCap | 152.7626 | 136819.1 | 17023.23 | 1102662.9124 | 161.1351 | 895.6322 | 1.0548
Model 11 | Htl | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ03 | ChlrCap | 147.5439 | 138059.4 | 17760.62 | 1055715.1164 | 158.2732 | 935.7176 | 1.0727
Model 11 | Htl | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ03 | ChlrCap | 127.486 | 112249.7 | 15207.85 | 979626.9482 | 146.3521 | 880.4868 | 1.148
Model 11 | Htl | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ03 | ChlrCap | 126.2083 | 110474.6 | 14932.18 | 968310.6397 | 143.0852 | 875.3351 | 1.1337
Model 11 | MBT | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ03 | ChlrCap | 259.136 | 167567.2 | 20682.01 | 2130869.6061 | 239.8525 | 646.6381 | 0.92559
Model 11 | MBT | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ03 | ChlrCap | 252.9723 | 146267.4 | 21129.2 | 1919948.7304 | 222.5833 | 578.1952 | 0.87987
Model 11 | MBT | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ03 | ChlrCap | 244.9833 | 144551.4 | 21740.42 | 1862638.6284 | 218.3785 | 590.0459 | 0.8914
Model 11 | MBT | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ03 | ChlrCap | 237.1992 | 130858.8 | 6608.244 | 1780042.354 | 191.1267 | 551.6832 | 0.80576
Model 11 | MBT | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ03 | ChlrCap | 222.3173 | 122524.3 | 6173.85 | 1661930.0445 | 173.1388 | 551.1235 | 0.77879
Model 11 | Nrs | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ03 | ChlrCap | 95.3464 | 54961.96 | 15922 | 1317575.5749 | 152.3083 | 576.4452 | 1.5974
Model 11 | Nrs | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ03 | ChlrCap | 90.3487 | 58880.65 | 13893.3 | 1159844.4549 | 146.3798 | 651.7043 | 1.6202
Model 11 | Nrs | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ03 | ChlrCap | 89.974 | 58884.76 | 13951.68 | 1155789.9785 | 146.2265 | 654.4643 | 1.6252
Model 11 | Nrs | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ03 | ChlrCap | 79.6068 | 40664.86 | 10161.75 | 1118207.1287 | 136.7609 | 510.8213 | 1.718
Model 11 | Nrs | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ03 | ChlrCap | 79.9441 | 37252.55 | 9187.981 | 1084776.2525 | 125.7671 | 465.9827 | 1.5732
Model 11 | OfL | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ03 | ChlrCap | 328.7545 | 212741.7 | 33205.82 | 1930100.9203 | 298.303 | 647.1142 | 0.90737
Model 11 | OfL | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ03 | ChlrCap | 336.8908 | 187999.5 | 30449.86 | 1783699.7057 | 280.6346 | 558.0428 | 0.83301
Model 11 | OfL | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ03 | ChlrCap | 329.1995 | 187506.2 | 33892.62 | 1726686.7855 | 275.8689 | 569.5823 | 0.838
Model 11 | OfL | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ03 | ChlrCap | 303.0842 | 167474.2 | 39938.05 | 1669473.354 | 256.6216 | 552.5666 | 0.8467
Model 11 | OfL | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ03 | ChlrCap | 290.8142 | 157756.3 | 3185.456 | 1568799.6295 | 243.4114 | 542.4643 | 0.837
Model 11 | OfS | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ03 | ChlrCap | 22.1567 | 15037.25 | 963.34 | 129514.9817 | 16.5029 | 678.6768 | 0.74482
Model 11 | OfS | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ03 | ChlrCap | 22.0175 | 14252.4 | 886.4683 | 122122.2859 | 15.6239 | 647.3227 | 0.70961
Model 11 | OfS | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ03 | ChlrCap | 21.8341 | 14150.22 | 882.0974 | 121267.9878 | 15.492 | 648.0782 | 0.70953
Model 11 | OfS | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ03 | ChlrCap | 18.6829 | 11774.97 | 762.4254 | 102475.8427 | 13.3327 | 630.2541 | 0.71363
Model 11 | OfS | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ03 | ChlrCap | 17.9189 | 10956.33 | 670.6345 | 96964.5882 | 12.3745 | 611.441 | 0.69058
Model 11 | Rt3 | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ03 | ChlrCap | 200.361 | 144501.9 | 59987.23 | 1529930.8605 | 343.3884 | 721.2077 | 1.7138
Model 11 | Rt3 | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ03 | ChlrCap | 199.5548 | 129630.1 | 59786.1 | 1452726.8476 | 332.3423 | 649.5964 | 1.6654
Model 11 | Rt3 | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ03 | ChlrCap | 199.4083 | 129460.9 | 60050.95 | 1451884.4924 | 332.1861 | 649.2251 | 1.6659
Model 11 | Rt3 | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ03 | ChlrCap | 188.1127 | 116950.3 | 52153.26 | 1328769.0457 | 302.0451 | 621.7035 | 1.6057
Model 11 | Rt3 | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ03 | ChlrCap | 178.2805 | 105574.3 | 39765.98 | 1235884.8851 | 276.4199 | 592.1809 | 1.5505
Model 11 | ECC | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ04 | ChlrCap | 650.4283 | 569262.5 | 83732.71 | 3376432.6249 | 871.8365 | 875.2117 | 1.3404
Model 11 | ECC | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ04 | ChlrCap | 648.8233 | 564373.8 | 83135.57 | 3309948.3623 | 868.2081 | 869.842 | 1.3381
Model 11 | ECC | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ04 | ChlrCap | 647.1595 | 563327.2 | 82936.44 | 3305811.3798 | 866.3453 | 870.4611 | 1.3387
Model 11 | ECC | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ04 | ChlrCap | 587.8033 | 509108.9 | 73765.59 | 3082754.6178 | 806.9181 | 866.1212 | 1.3728
Model 11 | ECC | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ04 | ChlrCap | 554.5638 | 479552.3 | 56954.32 | 2880651.2368 | 740.5705 | 864.7378 | 1.3354
Model 11 | ESe | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ04 | ChlrCap | 337.8123 | 210940.6 | 26776.76 | 1476073.9437 | 309.2341 | 624.4313 | 0.9154
Model 11 | ESe | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ04 | ChlrCap | 333.9507 | 240196.6 | 26797.51 | 1380709.6658 | 295.2835 | 719.2577 | 0.88421
Model 11 | ESe | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ04 | ChlrCap | 332.8495 | 239170.8 | 26741.47 | 1376086.3068 | 294.1494 | 718.5554 | 0.88373
Model 11 | ESe | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ04 | ChlrCap | 300.5353 | 182771.3 | 14079.45 | 1249522.3601 | 250.0961 | 608.1525 | 0.83217
Model 11 | ESe | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ04 | ChlrCap | 285.7465 | 171894.7 | 13950.85 | 1177586.0027 | 231.6885 | 601.5636 | 0.81082
Model 11 | EUn | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ04 | ChlrCap | 2256.9483 | 1748889 | 384519.9 | 10694018.9519 | 2972.5335 | 774.891 | 1.3171
Model 11 | EUn | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ04 | ChlrCap | 2245.425 | 1726172 | 374137.5 | 10432571.3834 | 2962.1768 | 768.7507 | 1.3192
Model 11 | EUn | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ04 | ChlrCap | 2217.3363 | 1719961 | 372468.6 | 10285542.3822 | 2936.8409 | 775.6879 | 1.3245
Model 11 | EUn | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ04 | ChlrCap | 2015.395 | 1501196 | 341677.3 | 9224826.2497 | 2689.0238 | 744.8644 | 1.3342
Model 11 | EUn | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ04 | ChlrCap | 1919.6637 | 1430864 | 299198.5 | 8707069.4572 | 2513.8324 | 745.3722 | 1.3095
Model 11 | Hsp | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ04 | ChlrCap | 779.1722 | 495645.3 | 29434.04 | 4250470.8312 | 777.9299 | 636.1178 | 0.99841
Model 11 | Hsp | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ04 | ChlrCap | 778.4675 | 493863.2 | 29406.78 | 4226526.8828 | 776.6579 | 634.4044 | 0.99768
Model 11 | Hsp | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ04 | ChlrCap | 780.4422 | 494013.7 | 29406.62 | 4224616.8195 | 776.3144 | 632.992 | 0.99471
Model 11 | Hsp | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ04 | ChlrCap | 797.7558 | 458402.4 | 22087.41 | 4096515.0223 | 744.5657 | 574.615 | 0.93333
Model 11 | Hsp | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ04 | ChlrCap | 809.9295 | 436833.7 | 21211.66 | 3893014.3623 | 686.3783 | 539.3478 | 0.84745
Model 11 | Htl | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ04 | ChlrCap | 205.5478 | 268340.8 | 29345.73 | 1498586.3399 | 285.9087 | 1305.4908 | 1.391
Model 11 | Htl | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ04 | ChlrCap | 197.8562 | 241059.8 | 25408.77 | 1187634.7916 | 267.0806 | 1218.3588 | 1.3499
Model 11 | Htl | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ04 | ChlrCap | 190.3282 | 238017.4 | 25685.36 | 1138035.7028 | 260.1374 | 1250.5632 | 1.3668
Model 11 | Htl | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ04 | ChlrCap | 169.797 | 201490.8 | 22881.12 | 1052142.8267 | 238.7747 | 1186.657 | 1.4062
Model 11 | Htl | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ04 | ChlrCap | 168.1872 | 199442.1 | 22432.3 | 1039605.456 | 234.5708 | 1185.8342 | 1.3947
Model 11 | MBT | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ04 | ChlrCap | 322.3633 | 242303.8 | 32766.01 | 2223738.9379 | 329.8727 | 751.6481 | 1.0233
Model 11 | MBT | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ04 | ChlrCap | 314.02 | 266252.9 | 32421.01 | 2039786.2438 | 320.9038 | 847.8852 | 1.0219
Model 11 | MBT | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ04 | ChlrCap | 299.6248 | 262278 | 32138.77 | 1973946.6284 | 311.9231 | 875.3547 | 1.041
Model 11 | MBT | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ04 | ChlrCap | 297.989 | 233235.8 | 11034.52 | 1865756.925 | 287.3985 | 782.6994 | 0.96446
Model 11 | MBT | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ04 | ChlrCap | 278.5123 | 218296.7 | 9664.832 | 1736290.2802 | 267.2113 | 783.7955 | 0.95942
Model 11 | Nrs | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ04 | ChlrCap | 123.1325 | 122153 | 26261.91 | 1372049.5318 | 222.3461 | 992.0452 | 1.8057
Model 11 | Nrs | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ04 | ChlrCap | 117.7474 | 129539.6 | 23761.27 | 1190700.6308 | 211.3673 | 1100.148 | 1.7951
Model 11 | Nrs | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ04 | ChlrCap | 114.654 | 128837.3 | 24029.19 | 1164117.3913 | 208.9372 | 1123.7047 | 1.8223
Model 11 | Nrs | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ04 | ChlrCap | 97.6834 | 101599.4 | 20781.66 | 1113755.7635 | 192.7008 | 1040.0883 | 1.9727
Model 11 | Nrs | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ04 | ChlrCap | 96.34 | 94904.75 | 19800.91 | 1069642.1411 | 181.4461 | 985.1024 | 1.8834
Model 11 | OfL | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ04 | ChlrCap | 390.6946 | 376239.8 | 66209.88 | 2121857.755 | 426.0498 | 963.0023 | 1.0905
Model 11 | OfL | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ04 | ChlrCap | 389.5658 | 339699.8 | 62659.91 | 1961489.8605 | 403.7239 | 871.9959 | 1.0363
Model 11 | OfL | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ04 | ChlrCap | 376.0428 | 333622.7 | 68829.77 | 1887569 | 377.076 | 887.1933 | 1.0027
Model 11 | OfL | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ04 | ChlrCap | 356.0055 | 300941.3 | 67928.24 | 1812141.4361 | 354.1011 | 845.3277 | 0.99465
Model 11 | OfL | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ04 | ChlrCap | 355.2392 | 287769.2 | 11445.51 | 1712745.6131 | 339.7415 | 810.0717 | 0.95637
Model 11 | OfS | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ04 | ChlrCap | 26.9893 | 26590.78 | 2255.009 | 140731.014 | 25.6299 | 985.2326 | 0.94963
Model 11 | OfS | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ04 | ChlrCap | 26.8214 | 24295.48 | 2132.048 | 131239.1659 | 23.5553 | 905.8228 | 0.87822
Model 11 | OfS | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ04 | ChlrCap | 26.1455 | 23968.8 | 2182.958 | 127728.2858 | 23.114 | 916.747 | 0.88405
Model 11 | OfS | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ04 | ChlrCap | 22.0493 | 19453.31 | 2184.425 | 108002.695 | 19.0799 | 882.2636 | 0.86533
Model 11 | OfS | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ04 | ChlrCap | 21.4147 | 19655.87 | 1655.161 | 103567.4679 | 18.8709 | 917.867 | 0.88121
Model 11 | Rt3 | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ04 | ChlrCap | 250.458 | 281939.9 | 80787.95 | 1670887.9543 | 472.3417 | 1125.6973 | 1.8859
Model 11 | Rt3 | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ04 | ChlrCap | 249.161 | 247721.9 | 80850.19 | 1575212.2626 | 438.6977 | 994.2242 | 1.7607
Model 11 | Rt3 | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ04 | ChlrCap | 248.2993 | 247397.3 | 81050.84 | 1574266.286 | 437.9446 | 996.3672 | 1.7638
Model 11 | Rt3 | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ04 | ChlrCap | 237.1232 | 229294.8 | 71092.48 | 1437964.8851 | 407.0574 | 966.9861 | 1.7166
Model 11 | Rt3 | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ04 | ChlrCap | 226.1252 | 214235.1 | 56908.45 | 1337269.8839 | 379.0474 | 947.4182 | 1.6763
Model 11 | ECC | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ05 | ChlrCap | 447.8013 | 331606.4 | 53765.07 | 3160194.5944 | 474.1725 | 740.5212 | 1.0589
Model 11 | ECC | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ05 | ChlrCap | 446.702 | 329409.1 | 53385.78 | 3103565.6166 | 471.1827 | 737.4247 | 1.0548
Model 11 | ECC | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ05 | ChlrCap | 446.6988 | 329409.8 | 53291.11 | 3103891.3669 | 470.9272 | 737.4315 | 1.0542
Model 11 | ECC | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ05 | ChlrCap | 399.244 | 292094.2 | 52640.82 | 2913360.0891 | 442.1954 | 731.6183 | 1.1076
Model 11 | ECC | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ05 | ChlrCap | 371.7423 | 274976.3 | 31681.46 | 2750916.4127 | 395.6361 | 739.696 | 1.0643
Model 11 | ESe | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ05 | ChlrCap | 236.3515 | 128046.1 | 16354.35 | 1363129.7725 | 132.7649 | 541.7613 | 0.56173
Model 11 | ESe | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ05 | ChlrCap | 231.9907 | 147840.5 | 16301.85 | 1280708.0757 | 134.4743 | 637.2692 | 0.57965
Model 11 | ESe | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ05 | ChlrCap | 231.9883 | 147833.2 | 16291.87 | 1280910.134 | 134.4534 | 637.2441 | 0.57957
Model 11 | ESe | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ05 | ChlrCap | 204.1847 | 108153.9 | 6274.536 | 1197403.2971 | 114.2491 | 529.6867 | 0.55954
Model 11 | ESe | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ05 | ChlrCap | 186.52 | 100221.1 | 5620.719 | 1129404.3615 | 104.5856 | 537.3209 | 0.56072
Model 11 | EUn | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ05 | ChlrCap | 1621.1973 | 1004184 | 252944.3 | 10169277.17 | 1595.7215 | 619.4089 | 0.98429
Model 11 | EUn | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ05 | ChlrCap | 1613.4453 | 987359.6 | 242447.6 | 9918954.8441 | 1592.0369 | 611.9573 | 0.98673
Model 11 | EUn | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ05 | ChlrCap | 1604.207 | 989909.9 | 242205.6 | 9803922.8429 | 1589.5654 | 617.0712 | 0.99087
Model 11 | EUn | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ05 | ChlrCap | 1441.5957 | 871761.4 | 249327.2 | 8948113.7421 | 1515.5677 | 604.7198 | 1.0513
Model 11 | EUn | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ05 | ChlrCap | 1337.6327 | 816228.9 | 192177.6 | 8380123.2098 | 1364.861 | 610.2041 | 1.0204
Model 11 | Hsp | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ05 | ChlrCap | 631.9267 | 257205.4 | 14304.9 | 4052795.7608 | 496.6316 | 407.0177 | 0.7859
Model 11 | Hsp | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ05 | ChlrCap | 631.3238 | 256461.6 | 14290.42 | 4034922.5979 | 496.2181 | 406.2283 | 0.786
Model 11 | Hsp | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ05 | ChlrCap | 631.3238 | 256461.6 | 14290.42 | 4034922.5979 | 496.2181 | 406.2283 | 0.786
Model 11 | Hsp | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ05 | ChlrCap | 647.081 | 236238.2 | 9726.682 | 3936317.0891 | 486.5889 | 365.0829 | 0.75198
Model 11 | Hsp | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ05 | ChlrCap | 642.7437 | 224554.3 | 8870.128 | 3760033.1946 | 438.087 | 349.3683 | 0.68159
Model 11 | Htl | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ05 | ChlrCap | 139.7557 | 166920.1 | 22575 | 1396651.2817 | 141.8305 | 1194.3703 | 1.0148
Model 11 | Htl | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ05 | ChlrCap | 133.036 | 145182 | 19179.53 | 1108044.8729 | 129.5791 | 1091.2986 | 0.97402
Model 11 | Htl | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ05 | ChlrCap | 129.0901 | 146028.7 | 19757.58 | 1061621.3939 | 128.5691 | 1131.2152 | 0.99596
Model 11 | Htl | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ05 | ChlrCap | 108.9339 | 118583.1 | 16828.71 | 983049.2285 | 120.3402 | 1088.5782 | 1.1047
Model 11 | Htl | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ05 | ChlrCap | 107.2058 | 116550.3 | 16576.58 | 971318.1471 | 116.7889 | 1087.1636 | 1.0894
Model 11 | MBT | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ05 | ChlrCap | 250.9265 | 151063 | 24725.91 | 2125511.177 | 191.2547 | 602.0209 | 0.76219
Model 11 | MBT | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ05 | ChlrCap | 243.1638 | 173957.6 | 24911.02 | 1955342.0563 | 189.8574 | 715.3926 | 0.78078
Model 11 | MBT | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ05 | ChlrCap | 240.6907 | 174968.4 | 24998.31 | 1901449.2755 | 187.0615 | 726.943 | 0.77719
Model 11 | MBT | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ05 | ChlrCap | 238.0023 | 156049.7 | 7610.978 | 1807663.3857 | 169.6151 | 655.6646 | 0.71266
Model 11 | MBT | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ05 | ChlrCap | 214.5538 | 144991.3 | 7116.194 | 1680372.9004 | 154.8245 | 675.7805 | 0.72161
Model 11 | Nrs | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ05 | ChlrCap | 83.5064 | 63505.75 | 18438.81 | 1343071.4137 | 134.7489 | 760.4898 | 1.6136
Model 11 | Nrs | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ05 | ChlrCap | 81.0218 | 67041.14 | 16350.3 | 1183487.6637 | 128.002 | 827.446 | 1.5798
Model 11 | Nrs | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ05 | ChlrCap | 81.0218 | 67041.14 | 16350.3 | 1183487.6637 | 128.002 | 827.446 | 1.5798
Model 11 | Nrs | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ05 | ChlrCap | 77.6435 | 47619.3 | 12490.44 | 1146758.3016 | 120.6996 | 613.3072 | 1.5545
Model 11 | Nrs | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ05 | ChlrCap | 77.4103 | 43372.77 | 11478.85 | 1107262.9927 | 109.6495 | 560.2974 | 1.4165
Model 11 | OfL | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ05 | ChlrCap | 334.4605 | 258121.1 | 36096.56 | 1968086.7081 | 249.3778 | 771.7536 | 0.74561
Model 11 | OfL | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ05 | ChlrCap | 333.5467 | 230137.8 | 32452.93 | 1814142.993 | 239.8061 | 689.9718 | 0.71896
Model 11 | OfL | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ05 | ChlrCap | 325.9472 | 229993.1 | 40301.44 | 1749536.4936 | 235.9291 | 705.6147 | 0.72383
Model 11 | OfL | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ05 | ChlrCap | 299.6537 | 206708.5 | 42862.02 | 1687881.1208 | 226.4267 | 689.8247 | 0.75563
Model 11 | OfL | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ05 | ChlrCap | 286.4257 | 195256 | 2898.611 | 1583661.857 | 214.033 | 681.6987 | 0.74725
Model 11 | OfS | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ05 | ChlrCap | 20.0139 | 12536.82 | 1051.739 | 125995.2794 | 12.0026 | 626.4043 | 0.59971
Model 11 | OfS | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ05 | ChlrCap | 19.4836 | 15505.39 | 997.5092 | 122162.3764 | 12.0217 | 795.8172 | 0.61701
Model 11 | OfS | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ05 | ChlrCap | 19.3847 | 15416.12 | 991.8772 | 121364.8361 | 11.9235 | 795.2726 | 0.6151
Model 11 | OfS | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ05 | ChlrCap | 16.6051 | 12589.62 | 787.8894 | 101808.7313 | 10.9749 | 758.1783 | 0.66094
Model 11 | OfS | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ05 | ChlrCap | 15.8386 | 11856.29 | 689.3859 | 96459.9332 | 10.2472 | 748.5677 | 0.64698
Model 11 | Rt3 | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ05 | ChlrCap | 191.4887 | 164690.3 | 67221.55 | 1542028.0715 | 293.4605 | 860.0525 | 1.5325
Model 11 | Rt3 | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ05 | ChlrCap | 190.3688 | 148364.3 | 67254.98 | 1459805.2016 | 284.7947 | 779.3518 | 1.496
Model 11 | Rt3 | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ05 | ChlrCap | 190.3688 | 148364.3 | 67254.98 | 1459805.2016 | 284.7947 | 779.3518 | 1.496
Model 11 | Rt3 | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ05 | ChlrCap | 179.1423 | 132814.3 | 58298.41 | 1327646.8042 | 255.6551 | 741.3898 | 1.4271
Model 11 | Rt3 | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ05 | ChlrCap | 167.5133 | 121177.8 | 43843.06 | 1224578.2896 | 234.0296 | 723.392 | 1.3971
Model 11 | ECC | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ06 | ChlrCap | 690.1455 | 711849.6 | 97022.41 | 3226647.1172 | 464.1249 | 1031.4486 | 0.6725
Model 11 | ECC | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ06 | ChlrCap | 690.1455 | 707883.1 | 96501.84 | 3176202.3787 | 463.218 | 1025.7012 | 0.67119
Model 11 | ECC | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ06 | ChlrCap | 690.1378 | 707867.7 | 96455.5 | 3176027.5158 | 463.0449 | 1025.6903 | 0.67095
Model 11 | ECC | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ06 | ChlrCap | 634.5987 | 649771.9 | 88576.36 | 2976248.4302 | 423.9984 | 1023.91 | 0.66814
Model 11 | ECC | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ06 | ChlrCap | 598.1787 | 615515.5 | 69682.8 | 2738112.5955 | 389.2828 | 1028.9827 | 0.65078
Model 11 | ESe | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ06 | ChlrCap | 377.0638 | 252748.7 | 29755.34 | 1371619.3822 | 112.0477 | 670.3075 | 0.29716
Model 11 | ESe | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ06 | ChlrCap | 372.102 | 298829.3 | 29978.27 | 1276560.871 | 105.7069 | 803.0844 | 0.28408
Model 11 | ESe | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ06 | ChlrCap | 372.0698 | 298803.3 | 29920.63 | 1276363.0996 | 105.6763 | 803.0839 | 0.28402
Model 11 | ESe | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ06 | ChlrCap | 342.9848 | 229921.2 | 12681.8 | 1145311.8128 | 75.1681 | 670.3538 | 0.21916
Model 11 | ESe | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ06 | ChlrCap | 322.4653 | 214953.5 | 12078.88 | 1053883.9069 | 64.5958 | 666.5941 | 0.20032
Model 11 | EUn | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ06 | ChlrCap | 2324.592 | 1983746 | 431435.2 | 9733929.8746 | 1770.1066 | 853.3738 | 0.76147
Model 11 | EUn | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ06 | ChlrCap | 2324.592 | 1964248 | 422973.9 | 9542764.8757 | 1763.9291 | 844.9861 | 0.75881
Model 11 | EUn | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ06 | ChlrCap | 2311.588 | 1966616 | 422328.4 | 9486799.5569 | 1759.6289 | 850.7641 | 0.76122
Model 11 | EUn | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ06 | ChlrCap | 2120.4177 | 1750977 | 397777.7 | 8627443.6295 | 1634.4722 | 825.7699 | 0.77083
Model 11 | EUn | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ06 | ChlrCap | 2007.927 | 1653083 | 343452.3 | 7983954.9238 | 1509.0833 | 823.2784 | 0.75156
Model 11 | Hsp | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ06 | ChlrCap | 819.8385 | 629444.3 | 39939.26 | 4169309.483 | 624.3984 | 767.7662 | 0.76161
Model 11 | Hsp | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ06 | ChlrCap | 819.8385 | 628092.1 | 39930.06 | 4153743.0797 | 623.9854 | 766.1169 | 0.76111
Model 11 | Hsp | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ06 | ChlrCap | 819.8385 | 628092.1 | 39930.06 | 4153743.0797 | 623.9854 | 766.1169 | 0.76111
Model 11 | Hsp | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ06 | ChlrCap | 830.9227 | 577499.3 | 29670.66 | 4011521.2896 | 596.9383 | 695.0096 | 0.7184
Model 11 | Hsp | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ06 | ChlrCap | 839.0405 | 551525.6 | 28659.4 | 3777878.3857 | 538.705 | 657.3289 | 0.64205
Model 11 | Htl | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ06 | ChlrCap | 200.1557 | 295283.1 | 33039.92 | 1400921.2401 | 188.559 | 1475.2673 | 0.94206
Model 11 | Htl | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ06 | ChlrCap | 193.5773 | 265087.4 | 28475.94 | 1071247.2261 | 174.7223 | 1369.4134 | 0.9026
Model 11 | Htl | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ06 | ChlrCap | 187.4983 | 263817.4 | 28983.04 | 1046507.4348 | 172.7255 | 1407.0386 | 0.92121
Model 11 | Htl | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ06 | ChlrCap | 162.3686 | 219245.5 | 25896.05 | 956080.6607 | 153.7277 | 1350.2952 | 0.94678
Model 11 | Htl | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ06 | ChlrCap | 160.0203 | 216450.2 | 25264.39 | 940162.8483 | 148.8067 | 1352.6426 | 0.92992
Model 11 | MBT | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ06 | ChlrCap | 347.5739 | 392764.8 | 40691.2 | 2336598.5698 | 324.2654 | 1130.0181 | 0.93294
Model 11 | MBT | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ06 | ChlrCap | 345.009 | 350747.6 | 40592.44 | 2083202.7163 | 299.4609 | 1016.6332 | 0.86798
Model 11 | MBT | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ06 | ChlrCap | 339.1993 | 347849.3 | 40557.11 | 2050907.2157 | 295.8737 | 1025.5011 | 0.87227
Model 11 | MBT | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ06 | ChlrCap | 328.0163 | 313824.9 | 13904.48 | 1933338.3306 | 275.4247 | 956.7356 | 0.83967
Model 11 | MBT | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ06 | ChlrCap | 301.4822 | 293312.8 | 11806.81 | 1780921.6389 | 251.5255 | 972.9027 | 0.8343
Model 11 | Nrs | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ06 | ChlrCap | 121.2249 | 135450.5 | 33128.51 | 1271851.7769 | 160.3757 | 1117.3492 | 1.323
Model 11 | Nrs | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ06 | ChlrCap | 116.4832 | 148315.4 | 29710.42 | 1085083.1011 | 154.4811 | 1273.2774 | 1.3262
Model 11 | Nrs | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ06 | ChlrCap | 116.4832 | 148315.4 | 29710.42 | 1085083.1011 | 154.4811 | 1273.2774 | 1.3262
Model 11 | Nrs | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ06 | ChlrCap | 101.5529 | 115341.8 | 24998.17 | 1035776.9441 | 144.1192 | 1135.7805 | 1.4192
Model 11 | Nrs | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ06 | ChlrCap | 102.7199 | 107892.1 | 23860.08 | 983375.6868 | 131.0533 | 1050.3526 | 1.2758
Model 11 | OfL | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ06 | ChlrCap | 403.3772 | 454307.6 | 81745.6 | 2135220.4525 | 355.7343 | 1126.2601 | 0.88189
Model 11 | OfL | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ06 | ChlrCap | 402.7988 | 411784.2 | 78654.23 | 1959562.7679 | 339.3655 | 1022.3073 | 0.84252
Model 11 | OfL | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ06 | ChlrCap | 397.1907 | 408683.3 | 82013.96 | 1920162.8499 | 334.7435 | 1028.9348 | 0.84278
Model 11 | OfL | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ06 | ChlrCap | 375.7237 | 372996.5 | 77047.73 | 1848103.3962 | 315.843 | 992.7416 | 0.84063
Model 11 | OfL | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ06 | ChlrCap | 360.4377 | 355995 | 31698.93 | 1728417.9543 | 292.6271 | 987.6742 | 0.81187
Model 11 | OfS | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ06 | ChlrCap | 27.2141 | 31097.17 | 2015.504 | 135203.6546 | 20.1801 | 1142.686 | 0.74153
Model 11 | OfS | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ06 | ChlrCap | 27.4273 | 28321.61 | 1844.877 | 124590.1062 | 18.4998 | 1032.6056 | 0.6745
Model 11 | OfS | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ06 | ChlrCap | 27.3397 | 28200.22 | 1842.163 | 123713.9033 | 18.3539 | 1031.4754 | 0.67133
Model 11 | OfS | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ06 | ChlrCap | 23.3383 | 23316.63 | 2159.434 | 106174.7297 | 16.0076 | 999.0718 | 0.68589
Model 11 | OfS | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ06 | ChlrCap | 22.3434 | 22176.45 | 1610.047 | 100034.5708 | 14.9219 | 992.5276 | 0.66784
Model 11 | Rt3 | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ06 | ChlrCap | 262.2133 | 331480.6 | 91536.97 | 1684805.3277 | 378.2231 | 1264.1638 | 1.4424
Model 11 | Rt3 | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ06 | ChlrCap | 261.834 | 305442.7 | 91422 | 1602006.837 | 366.9808 | 1166.5509 | 1.4016
Model 11 | Rt3 | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ06 | ChlrCap | 261.834 | 305442.7 | 91422 | 1602006.837 | 366.9808 | 1166.5509 | 1.4016
Model 11 | Rt3 | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ06 | ChlrCap | 249.733 | 278108.8 | 79655.43 | 1446239.602 | 325.9473 | 1113.6246 | 1.3052
Model 11 | Rt3 | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ06 | ChlrCap | 237.0563 | 259387.4 | 62668.52 | 1321432.4865 | 301.5949 | 1094.2015 | 1.2723
Model 11 | ECC | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ07 | ChlrCap | 647.4993 | 602577.3 | 95358.03 | 3010395.0703 | 584.3517 | 930.6223 | 0.90247
Model 11 | ECC | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ07 | ChlrCap | 647.4993 | 600117.4 | 94965.87 | 2974103.2567 | 583.6163 | 926.8232 | 0.90134
Model 11 | ECC | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ07 | ChlrCap | 645.558 | 599370.7 | 94799.3 | 2971864.558 | 582.8265 | 928.4537 | 0.90283
Model 11 | ECC | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ07 | ChlrCap | 594.6627 | 552068.5 | 91313.16 | 2815554.0094 | 551.4993 | 928.3726 | 0.92742
Model 11 | ECC | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ07 | ChlrCap | 563.0487 | 519751.9 | 71795.37 | 2575550.1735 | 502.3183 | 923.103 | 0.89214
Model 11 | ESe | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ07 | ChlrCap | 359.7787 | 208559.2 | 27467.33 | 1284446.0633 | 172.0551 | 579.6875 | 0.47822
Model 11 | ESe | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ07 | ChlrCap | 355.0423 | 245080.4 | 27696.02 | 1177622.9845 | 166.0327 | 690.285 | 0.46764
Model 11 | ESe | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ07 | ChlrCap | 353.4058 | 244630.1 | 27604.4 | 1175041.8366 | 165.7207 | 692.2073 | 0.46892
Model 11 | ESe | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ07 | ChlrCap | 324.8455 | 188550.5 | 12495.9 | 1060660.3735 | 137.7941 | 580.4313 | 0.42418
Model 11 | ESe | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ07 | ChlrCap | 305.3152 | 175642.4 | 11567.09 | 972931.2216 | 128.5777 | 575.2823 | 0.42113
Model 11 | EUn | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ07 | ChlrCap | 2258.639 | 1656073 | 396102.3 | 9093831.6166 | 1942.5984 | 733.2172 | 0.86007
Model 11 | EUn | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ07 | ChlrCap | 2258.639 | 1641483 | 387770.3 | 8936539.2145 | 1935.696 | 726.7576 | 0.85702
Model 11 | EUn | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ07 | ChlrCap | 2235.6347 | 1641967 | 386933 | 8861227.3693 | 1930.0581 | 734.4523 | 0.86332
Model 11 | EUn | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ07 | ChlrCap | 2054.759 | 1466289 | 381147.1 | 8136224.6155 | 1839.3283 | 713.6063 | 0.89516
Model 11 | EUn | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ07 | ChlrCap | 1946.593 | 1381276 | 322735.5 | 7507132.1887 | 1672.2405 | 709.5864 | 0.85906
Model 11 | Hsp | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ07 | ChlrCap | 832.1303 | 573147.9 | 41402.62 | 4045293.0141 | 588.4581 | 688.7719 | 0.70717
Model 11 | Hsp | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ07 | ChlrCap | 832.1303 | 572009.4 | 41373.71 | 4029346.1172 | 587.9301 | 687.4037 | 0.70654
Model 11 | Hsp | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ07 | ChlrCap | 831.5077 | 571722.9 | 41373.62 | 4028374.5592 | 587.7565 | 687.5737 | 0.70686
Model 11 | Hsp | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ07 | ChlrCap | 852.4405 | 530838.4 | 31718.57 | 3904464.9824 | 563.9364 | 622.7278 | 0.66156
Model 11 | Hsp | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ07 | ChlrCap | 869.8048 | 509963 | 30140.59 | 3669852.449 | 512.0213 | 586.2959 | 0.58866
Model 11 | Htl | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ07 | ChlrCap | 184.6582 | 259360.8 | 31383.03 | 1306920.7642 | 175.9263 | 1404.5455 | 0.95271
Model 11 | Htl | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ07 | ChlrCap | 178.6828 | 232959 | 27012.12 | 997275.2597 | 161.2269 | 1303.757 | 0.90231
Model 11 | Htl | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ07 | ChlrCap | 172.9687 | 231956.6 | 27579.09 | 976595.8421 | 160.7199 | 1341.0325 | 0.92918
Model 11 | Htl | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ07 | ChlrCap | 148.3056 | 191346.5 | 25160.35 | 899104.9655 | 146.7664 | 1290.2175 | 0.98962
Model 11 | Htl | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ07 | ChlrCap | 146.3167 | 188476.3 | 24531.48 | 881567.2129 | 141.7427 | 1288.1391 | 0.96874
Model 11 | MBT | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ07 | ChlrCap | 339.01 | 249903.7 | 37526.22 | 2160178.8406 | 227.4936 | 737.1573 | 0.67105
Model 11 | MBT | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ07 | ChlrCap | 336.4773 | 294538.3 | 37407.05 | 2001507.007 | 226.1943 | 875.3585 | 0.67224
Model 11 | MBT | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ07 | ChlrCap | 329.6443 | 291317.3 | 37157.46 | 1964364.3247 | 223.5322 | 883.7322 | 0.6781
Model 11 | MBT | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ07 | ChlrCap | 322.342 | 264356.4 | 13126.59 | 1861836.9812 | 195.3764 | 820.1116 | 0.60612
Model 11 | MBT | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ07 | ChlrCap | 301.1313 | 249766.1 | 11325.33 | 1720114.7737 | 178.8967 | 829.4258 | 0.59408
Model 11 | Nrs | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ07 | ChlrCap | 112.809 | 117201.9 | 32734.5 | 1211842.1539 | 154.8754 | 1038.941 | 1.3729
Model 11 | Nrs | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ07 | ChlrCap | 108.3649 | 129772.8 | 29184.95 | 1027698.641 | 149.6717 | 1197.5542 | 1.3812
Model 11 | Nrs | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ07 | ChlrCap | 107.9223 | 129686.7 | 29269.88 | 1025839.2118 | 149.5534 | 1201.6669 | 1.3858
Model 11 | Nrs | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ07 | ChlrCap | 102.4046 | 102087.9 | 24377.31 | 985391.0644 | 140.3992 | 996.9072 | 1.371
Model 11 | Nrs | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ07 | ChlrCap | 103.4304 | 95556.03 | 22996.32 | 936408.6692 | 128.3785 | 923.8676 | 1.2412
Model 11 | OfL | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ07 | ChlrCap | 404.6611 | 384106 | 79236.49 | 2048453.034 | 272.3904 | 949.2042 | 0.67313
Model 11 | OfL | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ07 | ChlrCap | 396.2667 | 348258 | 75110.93 | 1869941.9461 | 263.8422 | 878.8476 | 0.66582
Model 11 | OfL | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ07 | ChlrCap | 383.357 | 346120.6 | 79164.09 | 1839122.3435 | 260.1602 | 902.8676 | 0.67864
Model 11 | OfL | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ07 | ChlrCap | 371.1488 | 314370.8 | 74033.3 | 1768465.2831 | 250.0478 | 847.0208 | 0.67371
Model 11 | OfL | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ07 | ChlrCap | 361.6918 | 299079.9 | 30935.74 | 1649906.9273 | 236.6486 | 826.8915 | 0.65428
Model 11 | OfS | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ07 | ChlrCap | 25.9215 | 26723.54 | 1870.408 | 127036.4737 | 14.8253 | 1030.9424 | 0.57193
Model 11 | OfS | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ07 | ChlrCap | 25.8807 | 24249.14 | 1668.181 | 116521.4424 | 13.8834 | 936.9578 | 0.53644
Model 11 | OfS | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ07 | ChlrCap | 25.8991 | 24150.72 | 1658.986 | 115617.6538 | 13.781 | 932.4923 | 0.5321
Model 11 | OfS | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ07 | ChlrCap | 22.1743 | 19937.06 | 2033.133 | 100468.3856 | 12.1898 | 899.108 | 0.54973
Model 11 | OfS | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ07 | ChlrCap | 21.3755 | 18941.07 | 1486.714 | 94182.2999 | 11.4224 | 886.1098 | 0.53437
Model 11 | Rt3 | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ07 | ChlrCap | 256.6523 | 289557.4 | 96065.01 | 1637322.4842 | 363.4964 | 1128.2087 | 1.4163
Model 11 | Rt3 | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ07 | ChlrCap | 256.176 | 260953.7 | 95943.14 | 1552491.7849 | 340.3153 | 1018.6501 | 1.3284
Model 11 | Rt3 | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ07 | ChlrCap | 255.3507 | 260874.8 | 96510.48 | 1552454.3546 | 339.9597 | 1021.6335 | 1.3313
Model 11 | Rt3 | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ07 | ChlrCap | 243.3345 | 238869.6 | 84618.02 | 1400276.9906 | 312.4868 | 981.6512 | 1.2842
Model 11 | Rt3 | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ07 | ChlrCap | 231.2522 | 219894 | 65605.85 | 1267308.017 | 286.4665 | 950.8841 | 1.2388
Model 11 | ECC | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ08 | ChlrCap | 739.8653 | 852294.6 | 122971.3 | 3343227.4467 | 704.3141 | 1151.9591 | 0.95195
Model 11 | ECC | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ08 | ChlrCap | 739.8653 | 848405.8 | 122684.8 | 3291377.8593 | 702.5078 | 1146.703 | 0.94951
Model 11 | ECC | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ08 | ChlrCap | 737.3122 | 846521.4 | 122367.2 | 3287703.4314 | 700.8494 | 1148.118 | 0.95055
Model 11 | ECC | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ08 | ChlrCap | 687.023 | 771647.3 | 110788.1 | 3077228.5428 | 651.6913 | 1123.1754 | 0.94857
Model 11 | ECC | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ08 | ChlrCap | 651.0408 | 730678.6 | 90529.89 | 2819654.4549 | 596.7177 | 1122.3238 | 0.91656
Model 11 | ESe | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ08 | ChlrCap | 400.83 | 327817.2 | 39124.01 | 1453795.1067 | 247.803 | 817.846 | 0.61822
Model 11 | ESe | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ08 | ChlrCap | 393.9603 | 368518.7 | 39479.13 | 1335458.7714 | 233.9871 | 935.4208 | 0.59394
Model 11 | ESe | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ08 | ChlrCap | 392.0157 | 367161.8 | 39317.61 | 1331737.551 | 233.159 | 936.5998 | 0.59477
Model 11 | ESe | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ08 | ChlrCap | 367.1202 | 294338 | 22001.07 | 1196557.6471 | 185.6009 | 801.7484 | 0.50556
Model 11 | ESe | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ08 | ChlrCap | 346.614 | 276739.2 | 21986.91 | 1098135.3052 | 175.1811 | 798.4075 | 0.50541
Model 11 | EUn | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ08 | ChlrCap | 2528.2237 | 2524609 | 537678.4 | 10205911.9707 | 2421.0465 | 998.5703 | 0.95761
Model 11 | EUn | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ08 | ChlrCap | 2528.2237 | 2506417 | 528979.6 | 10020110.6284 | 2417.3517 | 991.3747 | 0.95615
Model 11 | EUn | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ08 | ChlrCap | 2501.0723 | 2493467 | 525600.8 | 9926129.0598 | 2401.3225 | 996.9592 | 0.96012
Model 11 | EUn | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ08 | ChlrCap | 2335.5727 | 2199932 | 463008.7 | 8978164.5967 | 2215.8049 | 941.924 | 0.94872
Model 11 | EUn | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ08 | ChlrCap | 2222.945 | 2086429 | 411577.9 | 8290455.0234 | 2047.2972 | 938.5878 | 0.92098
Model 11 | Hsp | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ08 | ChlrCap | 896.2405 | 746890.3 | 43117.42 | 4278360.2732 | 670.8864 | 833.3592 | 0.74856
Model 11 | Hsp | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ08 | ChlrCap | 896.2405 | 745483.6 | 43088.15 | 4262082.1407 | 670.3961 | 831.7897 | 0.74801
Model 11 | Hsp | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ08 | ChlrCap | 895.5942 | 744945.4 | 43045.29 | 4262024.2943 | 670.0457 | 831.7889 | 0.74816
Model 11 | Hsp | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ08 | ChlrCap | 920.3975 | 683141.7 | 31888.83 | 4093278.4502 | 651.0816 | 742.2246 | 0.70739
Model 11 | Hsp | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ08 | ChlrCap | 939.6933 | 648487.9 | 30609.64 | 3836589.6166 | 596.6011 | 690.1059 | 0.63489
Model 11 | Htl | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ08 | ChlrCap | 212.3743 | 356198.2 | 37474.35 | 1467715.0324 | 232.7941 | 1677.2187 | 1.0961
Model 11 | Htl | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ08 | ChlrCap | 205.637 | 323395.4 | 32925.05 | 1128495.9318 | 216.7923 | 1572.6518 | 1.0542
Model 11 | Htl | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ08 | ChlrCap | 198.3377 | 318562.4 | 33040.85 | 1100108.1334 | 211.8827 | 1606.1619 | 1.0683
Model 11 | Htl | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ08 | ChlrCap | 171.8435 | 267781.8 | 29831.49 | 1001884.1154 | 191.2019 | 1558.2888 | 1.1127
Model 11 | Htl | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ08 | ChlrCap | 170.0543 | 264439.7 | 29187.17 | 983907.1892 | 186.7519 | 1555.0306 | 1.0982
Model 11 | MBT | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ08 | ChlrCap | 379.9615 | 366639.5 | 45764.18 | 2319098.7046 | 276.3001 | 964.9386 | 0.72718
Model 11 | MBT | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ08 | ChlrCap | 376.9867 | 412810.6 | 45648.46 | 2143411.6096 | 270.2677 | 1095.0271 | 0.71692
Model 11 | MBT | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ08 | ChlrCap | 364.483 | 404740.9 | 45136.37 | 2092779.5768 | 263.0019 | 1110.4521 | 0.72158
Model 11 | MBT | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ08 | ChlrCap | 359.3745 | 357943.6 | 16579.75 | 1960690.1032 | 238.1472 | 996.0184 | 0.66267
Model 11 | MBT | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ08 | ChlrCap | 334.8858 | 334523.9 | 14218.11 | 1814445.6014 | 218.8125 | 998.9192 | 0.65339
Model 11 | Nrs | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ08 | ChlrCap | 127.9944 | 175728.3 | 37246.52 | 1315099.0373 | 192.984 | 1372.9376 | 1.5078
Model 11 | Nrs | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ08 | ChlrCap | 125.2755 | 189694.2 | 33900.64 | 1122201.0145 | 185.9206 | 1514.2169 | 1.4841
Model 11 | Nrs | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ08 | ChlrCap | 122.6344 | 189023.2 | 33933.43 | 1119748.6579 | 185.5638 | 1541.355 | 1.5131
Model 11 | Nrs | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ08 | ChlrCap | 110.3115 | 152695.4 | 29213.45 | 1063731.2172 | 171.2013 | 1384.2195 | 1.552
Model 11 | Nrs | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ08 | ChlrCap | 112.0452 | 143695 | 28146.54 | 1010141.7137 | 159.5067 | 1282.4729 | 1.4236
Model 11 | OfL | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ08 | ChlrCap | 444.1263 | 532492.8 | 97519.02 | 2234415.7491 | 348.0983 | 1198.967 | 0.78378
Model 11 | OfL | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ08 | ChlrCap | 443.49 | 484906.9 | 94170.15 | 2044729.2532 | 329.0109 | 1093.3886 | 0.74187
Model 11 | OfL | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ08 | ChlrCap | 429.6913 | 475800.8 | 100382.6 | 1988442.857 | 312.2866 | 1107.3083 | 0.72677
Model 11 | OfL | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ08 | ChlrCap | 410.6412 | 435483.8 | 93618.41 | 1912094.646 | 290.9175 | 1060.4972 | 0.70845
Model 11 | OfL | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ08 | ChlrCap | 397.5578 | 417333.2 | 53636.85 | 1799063.1454 | 279.5381 | 1049.7421 | 0.70314
Model 11 | OfS | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ08 | ChlrCap | 28.1286 | 36999.02 | 3325.511 | 141614.0811 | 20.1157 | 1315.3547 | 0.71514
Model 11 | OfS | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ08 | ChlrCap | 28.0379 | 33479.61 | 3167.066 | 129645.9753 | 18.4883 | 1194.0841 | 0.6594
Model 11 | OfS | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ08 | ChlrCap | 27.8237 | 33240.74 | 3151.007 | 128597.2546 | 18.3281 | 1194.6905 | 0.65872
Model 11 | OfS | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ08 | ChlrCap | 24.0346 | 27498.09 | 3146.293 | 110735.7553 | 15.9551 | 1144.1043 | 0.66384
Model 11 | OfS | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ08 | ChlrCap | 23.315 | 26317.42 | 2598.063 | 104462.8735 | 15.0925 | 1128.7747 | 0.64733
Model 11 | Rt3 | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ08 | ChlrCap | 281.8822 | 321288.4 | 107190.1 | 1687975.0258 | 384.1634 | 1139.7968 | 1.3629
Model 11 | Rt3 | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ08 | ChlrCap | 281.3125 | 362029.1 | 107985.3 | 1671876.4754 | 387.9525 | 1286.9286 | 1.3791
Model 11 | Rt3 | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ08 | ChlrCap | 280.447 | 361249.9 | 108243.8 | 1670849.3646 | 387.3405 | 1288.1218 | 1.3812
Model 11 | Rt3 | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ08 | ChlrCap | 269.9647 | 337351.8 | 95342.38 | 1516645.2626 | 358.8503 | 1249.6146 | 1.3292
Model 11 | Rt3 | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ08 | ChlrCap | 258.647 | 315523.9 | 78662.98 | 1384377.5744 | 331.2019 | 1219.9016 | 1.2805
Model 11 | ECC | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ09 | ChlrCap | 893.031 | 834922.1 | 115186.2 | 3383230.6284 | 820.1565 | 934.9307 | 0.9184
Model 11 | ECC | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ09 | ChlrCap | 893.031 | 830456.9 | 114630 | 3330630.6835 | 818.0114 | 929.9307 | 0.91599
Model 11 | ECC | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ09 | ChlrCap | 882.3562 | 822434.9 | 114095.6 | 3313907.5358 | 809.9025 | 932.0895 | 0.91789
Model 11 | ECC | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ09 | ChlrCap | 816.2587 | 744805.8 | 102555.5 | 3086480.0363 | 749.0267 | 912.463 | 0.91763
Model 11 | ECC | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ09 | ChlrCap | 783.4162 | 708646.8 | 82330.13 | 2839368.0399 | 693.0366 | 904.5598 | 0.88463
Model 11 | ESe | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ09 | ChlrCap | 485.9148 | 408045.8 | 38389.41 | 1584528.823 | 319.8859 | 839.7476 | 0.65832
Model 11 | ESe | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ09 | ChlrCap | 481.3325 | 364945.9 | 38416.04 | 1372795.2872 | 281.8965 | 758.1992 | 0.58566
Model 11 | ESe | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ09 | ChlrCap | 472.9107 | 359651.6 | 37804.27 | 1356627.2943 | 281.1979 | 760.5064 | 0.59461
Model 11 | ESe | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ09 | ChlrCap | 427.1442 | 280544.9 | 21742.27 | 1215439.4445 | 226.8101 | 656.7921 | 0.53099
Model 11 | ESe | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ09 | ChlrCap | 411.9728 | 265533.1 | 21131.12 | 1123610.8333 | 216.2193 | 644.5403 | 0.52484
Model 11 | EUn | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ09 | ChlrCap | 2988.2497 | 2518012 | 518286.2 | 10513038.4642 | 2775.9483 | 842.6378 | 0.92895
Model 11 | EUn | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ09 | ChlrCap | 2988.2497 | 2499184 | 510233.9 | 10334010.993 | 2774.0258 | 836.3371 | 0.92831
Model 11 | EUn | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ09 | ChlrCap | 2909.579 | 2463457 | 500008.1 | 10101553.3318 | 2745.625 | 846.6713 | 0.94365
Model 11 | EUn | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ09 | ChlrCap | 2676.6887 | 2143916 | 432239.7 | 9045994.7151 | 2492.2236 | 800.9583 | 0.93108
Model 11 | EUn | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ09 | ChlrCap | 2584.4677 | 2047346 | 385628.2 | 8405302.5756 | 2331.3189 | 792.1732 | 0.90205
Model 11 | Hsp | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ09 | ChlrCap | 1019.3813 | 726054.6 | 39210.41 | 4314940.245 | 758.7003 | 712.2503 | 0.74428
Model 11 | Hsp | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ09 | ChlrCap | 1019.3813 | 724612.3 | 39160.51 | 4299015.3634 | 758.0879 | 710.8354 | 0.74367
Model 11 | Hsp | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ09 | ChlrCap | 1015.938 | 722470.7 | 39057.35 | 4296771.1852 | 756.2818 | 711.1366 | 0.74442
Model 11 | Hsp | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ09 | ChlrCap | 1046.3467 | 665781.4 | 28976.36 | 4131422.3001 | 732.2336 | 636.2914 | 0.6998
Model 11 | Hsp | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ09 | ChlrCap | 1074.036 | 635601.9 | 27950.98 | 3889216.3423 | 677.0309 | 591.7883 | 0.63036
Model 11 | Htl | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ09 | ChlrCap | 270.7573 | 359853 | 36333.47 | 1506116.5821 | 274.0267 | 1329.061 | 1.0121
Model 11 | Htl | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ09 | ChlrCap | 263.948 | 328472.3 | 32000.42 | 1166387.1774 | 256.7595 | 1244.4584 | 0.97277
Model 11 | Htl | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ09 | ChlrCap | 253.1615 | 322196.6 | 32112.57 | 1131491.3926 | 249.4749 | 1272.6919 | 0.98544
Model 11 | Htl | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ09 | ChlrCap | 222.526 | 272046.8 | 28061.45 | 1028510.9169 | 222.9198 | 1222.5394 | 1.0018
Model 11 | Htl | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ09 | ChlrCap | 220.8133 | 269141.3 | 27495.4 | 1011404.1094 | 218.5811 | 1218.8634 | 0.98989
Model 11 | MBT | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ09 | ChlrCap | 441.9422 | 354367.9 | 44251.19 | 2333225.6999 | 329.0753 | 801.8422 | 0.74461
Model 11 | MBT | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ09 | ChlrCap | 437.8058 | 389202.1 | 44105.13 | 2130220.0692 | 310.7187 | 888.9834 | 0.70972
Model 11 | MBT | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ09 | ChlrCap | 400.1697 | 369162 | 42302.91 | 2048205.8253 | 286.1149 | 922.5137 | 0.71498
Model 11 | MBT | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ09 | ChlrCap | 383.7025 | 329996.3 | 15288.26 | 1928121.7737 | 268.1109 | 860.0317 | 0.69875
Model 11 | MBT | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ09 | ChlrCap | 365.1895 | 310259.7 | 13220.06 | 1788799.6436 | 244.2733 | 849.5855 | 0.66889
Model 11 | Nrs | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ09 | ChlrCap | 161.1163 | 181345.1 | 35202.09 | 1360893.0116 | 223.3277 | 1125.554 | 1.3861
Model 11 | Nrs | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ09 | ChlrCap | 155.7269 | 194824.2 | 32585.6 | 1159367.8612 | 214.1885 | 1251.0636 | 1.3754
Model 11 | Nrs | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ09 | ChlrCap | 149.6776 | 191802.9 | 32692.06 | 1130729.4751 | 210.0833 | 1281.4401 | 1.4036
Model 11 | Nrs | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ09 | ChlrCap | 127.8184 | 151630.7 | 28123.58 | 1071315.4277 | 192.2331 | 1186.2977 | 1.504
Model 11 | Nrs | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ09 | ChlrCap | 128.7526 | 142806.5 | 27114.69 | 1019864.6762 | 180.5475 | 1109.1547 | 1.4023
Model 11 | OfL | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ09 | ChlrCap | 488.7008 | 509453.3 | 85131.22 | 2227295.6495 | 382.2495 | 1042.4646 | 0.78217
Model 11 | OfL | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ09 | ChlrCap | 488.0035 | 457652.7 | 82068.8 | 2023459.5217 | 360.4398 | 937.8062 | 0.7386
Model 11 | OfL | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ09 | ChlrCap | 469.4777 | 445585.9 | 90306.05 | 1959290.8159 | 349.7975 | 949.1099 | 0.74508
Model 11 | OfL | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ09 | ChlrCap | 449.6365 | 409768.6 | 87740.77 | 1886621.6776 | 327.9363 | 911.333 | 0.72934
Model 11 | OfL | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ09 | ChlrCap | 440.7675 | 390229.4 | 28566.87 | 1774281.0457 | 311.9035 | 885.3407 | 0.70764
Model 11 | OfS | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ09 | ChlrCap | 34.1601 | 36822 | 3106.906 | 144058.4722 | 23.8268 | 1077.9237 | 0.6975
Model 11 | OfS | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ09 | ChlrCap | 34.0647 | 35429.01 | 2973.926 | 134295.1803 | 22.5873 | 1040.0493 | 0.66307
Model 11 | OfS | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ09 | ChlrCap | 32.8268 | 34589.01 | 3014.569 | 130564.7653 | 21.5776 | 1053.681 | 0.65732
Model 11 | OfS | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ09 | ChlrCap | 28.4866 | 28464.41 | 2990.515 | 111509.3478 | 18.0093 | 999.2219 | 0.6322
Model 11 | OfS | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ09 | ChlrCap | 27.6906 | 27207.56 | 2529.295 | 105108.1852 | 17.1203 | 982.5561 | 0.61827
Model 11 | Rt3 | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ09 | ChlrCap | 342.2205 | 388047.4 | 96417.6 | 1767378.7005 | 449.193 | 1133.9104 | 1.3126
Model 11 | Rt3 | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ09 | ChlrCap | 341.589 | 353508.4 | 96483.12 | 1658629.9156 | 429.3631 | 1034.894 | 1.257
Model 11 | Rt3 | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ09 | ChlrCap | 336.846 | 350949.5 | 97421.2 | 1655012.3154 | 426.3877 | 1041.8693 | 1.2658
Model 11 | Rt3 | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ09 | ChlrCap | 325.614 | 327475.8 | 85626.31 | 1504268.1125 | 395.2127 | 1005.7178 | 1.2137
Model 11 | Rt3 | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ09 | ChlrCap | 315.9945 | 307357.5 | 72380.96 | 1374672.5627 | 366.0637 | 972.6672 | 1.1584
Model 11 | ECC | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ10 | ChlrCap | 770.1527 | 901712.1 | 122614.5 | 3485945.9015 | 671.0393 | 1170.8225 | 0.87131
Model 11 | ECC | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ10 | ChlrCap | 767.3098 | 894990.9 | 121942.7 | 3429877.8335 | 668.1959 | 1166.4009 | 0.87083
Model 11 | ECC | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ10 | ChlrCap | 764.3988 | 892323.3 | 121509.1 | 3424869.5463 | 666.0619 | 1167.353 | 0.87135
Model 11 | ECC | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ10 | ChlrCap | 729.7298 | 828803.5 | 107165.4 | 3266504.4795 | 621.4639 | 1135.7676 | 0.85164
Model 11 | ECC | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ10 | ChlrCap | 696.4335 | 789263.1 | 87001.13 | 3018599.4478 | 579.025 | 1133.2928 | 0.83141
Model 11 | ESe | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ10 | ChlrCap | 401.8207 | 318992.2 | 31859.74 | 1482831.6377 | 155.5826 | 793.8671 | 0.38719
Model 11 | ESe | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ10 | ChlrCap | 393.7185 | 346098 | 32064.86 | 1373801.9801 | 140.5761 | 879.0494 | 0.35705
Model 11 | ESe | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ10 | ChlrCap | 391.5958 | 344432.2 | 31886.96 | 1369473.5487 | 139.035 | 879.5604 | 0.35505
Model 11 | ESe | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ10 | ChlrCap | 378.9832 | 316768.1 | 23157.74 | 1295507.0246 | 127.4314 | 835.8369 | 0.33625
Model 11 | ESe | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ10 | ChlrCap | 362.4922 | 300866.9 | 23333.29 | 1208524.2103 | 114.5568 | 829.9956 | 0.31603
Model 11 | EUn | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ10 | ChlrCap | 2629.0233 | 2744378 | 566816.3 | 10673618.4232 | 2483.0462 | 1043.8774 | 0.94447
Model 11 | EUn | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ10 | ChlrCap | 2613.854 | 2719955 | 559153.6 | 10483887.5428 | 2474.455 | 1040.5918 | 0.94667
Model 11 | EUn | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ10 | ChlrCap | 2586.9427 | 2704555 | 555796.1 | 10388637.755 | 2458.7751 | 1045.4638 | 0.95046
Model 11 | EUn | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ10 | ChlrCap | 2453.7317 | 2447434 | 448374.1 | 9616328.5955 | 2274.4151 | 997.4334 | 0.92692
Model 11 | EUn | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ10 | ChlrCap | 2358.0787 | 2344105 | 403905.5 | 8991397.578 | 2166.488 | 994.0741 | 0.91875
Model 11 | Hsp | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ10 | ChlrCap | 920.6743 | 759626.5 | 39039.57 | 4405619.4654 | 761.7876 | 825.0763 | 0.82742
Model 11 | Hsp | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ10 | ChlrCap | 919.9765 | 757210.2 | 38992.46 | 4387928.3529 | 760.6536 | 823.0756 | 0.82682
Model 11 | Hsp | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ10 | ChlrCap | 919.2605 | 756547.4 | 38992.39 | 4387440.0445 | 760.1366 | 822.9957 | 0.8269
Model 11 | Hsp | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ10 | ChlrCap | 930.4465 | 735106.5 | 28734.95 | 4295003.354 | 742.9535 | 790.0578 | 0.79849
Model 11 | Hsp | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ10 | ChlrCap | 948.8985 | 699137.2 | 27877.95 | 4052739.1079 | 686.6383 | 736.7882 | 0.72362
Model 11 | Htl | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ10 | ChlrCap | 233.4468 | 378550.8 | 37016.27 | 1539048.0938 | 261.8847 | 1621.5718 | 1.1218
Model 11 | Htl | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ10 | ChlrCap | 226.0702 | 343970.6 | 32405.02 | 1201462.7492 | 244.5671 | 1521.5214 | 1.0818
Model 11 | Htl | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ10 | ChlrCap | 219.7372 | 339011.4 | 32428.56 | 1174927.3748 | 239.9517 | 1542.8041 | 1.092
Model 11 | Htl | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ10 | ChlrCap | 201.0175 | 301589.4 | 29781.95 | 1095411.568 | 223.2738 | 1500.3142 | 1.1107
Model 11 | Htl | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ10 | ChlrCap | 199.322 | 298470.3 | 29218.57 | 1078549.9286 | 218.7889 | 1497.4278 | 1.0977
Model 11 | MBT | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ10 | ChlrCap | 386.5875 | 462078.2 | 39464 | 2398371.2708 | 412.6063 | 1195.2745 | 1.0673
Model 11 | MBT | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ10 | ChlrCap | 377.0093 | 410081.9 | 38842.45 | 2130361.4666 | 381.6926 | 1087.7235 | 1.0124
Model 11 | MBT | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ10 | ChlrCap | 362.7243 | 397747.9 | 37485.2 | 2071578.163 | 369.6473 | 1096.557 | 1.0191
Model 11 | MBT | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ10 | ChlrCap | 361 | 371540.4 | 15945.78 | 1984957.6319 | 349.7213 | 1029.1978 | 0.96876
Model 11 | MBT | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ10 | ChlrCap | 339.4217 | 348249.2 | 14029.81 | 1842437.6671 | 323.9062 | 1026.0076 | 0.95429
Model 11 | Nrs | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ10 | ChlrCap | 129.92 | 179461.9 | 33148.67 | 1363138.5209 | 203.8067 | 1381.3262 | 1.5687
Model 11 | Nrs | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ10 | ChlrCap | 124.8427 | 187761.4 | 30621.01 | 1180779.3334 | 195.4303 | 1503.9832 | 1.5654
Model 11 | Nrs | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ10 | ChlrCap | 121.976 | 185877.7 | 30865.83 | 1165116.6171 | 193.7425 | 1523.8871 | 1.5884
Model 11 | Nrs | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ10 | ChlrCap | 116.8715 | 172967.8 | 29007.84 | 1132707.9155 | 187.2357 | 1479.9827 | 1.6021
Model 11 | Nrs | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ10 | ChlrCap | 116.0286 | 163603.1 | 28142.13 | 1080849.6792 | 175.5689 | 1410.0235 | 1.5132
Model 11 | OfL | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ10 | ChlrCap | 439.3667 | 548698.3 | 104913.6 | 2214631.803 | 441.3699 | 1248.8392 | 1.0046
Model 11 | OfL | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ10 | ChlrCap | 438.1183 | 500200.6 | 101993.3 | 2033394.0809 | 417.9122 | 1141.7021 | 0.95388
Model 11 | OfL | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ10 | ChlrCap | 424.4277 | 489305.5 | 107707.2 | 1981696.5182 | 400.6516 | 1152.8596 | 0.94398
Model 11 | OfL | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ10 | ChlrCap | 427.0532 | 466672.7 | 92420.28 | 1960638.4947 | 389.2489 | 1092.7742 | 0.91148
Model 11 | OfL | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ10 | ChlrCap | 413.0813 | 448617.1 | 38850.25 | 1853781.6377 | 370.9999 | 1086.0261 | 0.89813
Model 11 | OfS | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ10 | ChlrCap | 29.0807 | 37473.24 | 3806.044 | 137347.9239 | 25.3059 | 1288.5956 | 0.8702
Model 11 | OfS | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ10 | ChlrCap | 28.9033 | 36180.96 | 3600.271 | 128765.158 | 24.259 | 1251.7927 | 0.83932
Model 11 | OfS | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ10 | ChlrCap | 28.1904 | 35658.76 | 3654.499 | 125986.0388 | 23.8387 | 1264.9253 | 0.84563
Model 11 | OfS | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ10 | ChlrCap | 26.0697 | 29819.76 | 3404.698 | 114307.8835 | 20.5423 | 1143.8475 | 0.78798
Model 11 | OfS | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ10 | ChlrCap | 25.2521 | 28606.92 | 2984.146 | 107944.0668 | 19.0442 | 1132.8527 | 0.75416
Model 11 | Rt3 | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ10 | ChlrCap | 299.8245 | 436198.3 | 100309.4 | 1822740.0891 | 487.4831 | 1454.8454 | 1.6259
Model 11 | Rt3 | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ10 | ChlrCap | 298.227 | 400535.9 | 100409 | 1724569.6612 | 461.5456 | 1343.0571 | 1.5476
Model 11 | Rt3 | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ10 | ChlrCap | 297.162 | 399617.7 | 100563.9 | 1723276.7128 | 460.4015 | 1344.7806 | 1.5493
Model 11 | Rt3 | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ10 | ChlrCap | 287.1245 | 368748.9 | 89225.25 | 1568594.8617 | 421.1817 | 1284.2823 | 1.4669
Model 11 | Rt3 | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ10 | ChlrCap | 276.7787 | 346835.6 | 76250.77 | 1443373.837 | 391.4097 | 1253.1154 | 1.4142
Model 11 | ECC | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ11 | ChlrCap | 732.3215 | 919831.3 | 104815.9 | 3950245.9613 | 488.2348 | 1256.0485 | 0.66669
Model 11 | ECC | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ11 | ChlrCap | 729.7727 | 911565 | 103997.6 | 3878914.2263 | 483.6308 | 1249.1082 | 0.66271
Model 11 | ECC | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ11 | ChlrCap | 709.2598 | 873310.1 | 106277.7 | 3702341.4256 | 429.2995 | 1231.2978 | 0.60528
Model 11 | ECC | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ11 | ChlrCap | 670.3255 | 804665.6 | 95981.37 | 3502679.3623 | 407.9461 | 1200.4102 | 0.60858
Model 11 | ECC | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ11 | ChlrCap | 638.1592 | 769403.6 | 76785.32 | 3289102.9988 | 376.6751 | 1205.661 | 0.59025
Model 11 | ESe | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ11 | ChlrCap | 372.733 | 386724.9 | 33687.46 | 1797094.7644 | 252.7681 | 1037.5387 | 0.67815
Model 11 | ESe | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ11 | ChlrCap | 361.6988 | 352363.9 | 33476.28 | 1637956.0762 | 226.8643 | 974.1914 | 0.62722
Model 11 | ESe | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ11 | ChlrCap | 355.1192 | 328450.7 | 29434.96 | 1521394.1618 | 199.1957 | 924.9028 | 0.56093
Model 11 | ESe | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ11 | ChlrCap | 345.2653 | 297893.6 | 21710.7 | 1419444.041 | 191.6345 | 862.7961 | 0.55504
Model 11 | ESe | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ11 | ChlrCap | 328.088 | 282867.2 | 21690.08 | 1344852.3367 | 175.1594 | 862.1687 | 0.53388
Model 11 | EUn | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ11 | ChlrCap | 2478.8097 | 2818507 | 520757.2 | 12264735.3798 | 1327.8355 | 1137.0405 | 0.53567
Model 11 | EUn | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ11 | ChlrCap | 2465.2163 | 2795009 | 512922.3 | 12061304.1934 | 1317.4899 | 1133.7784 | 0.53443
Model 11 | EUn | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ11 | ChlrCap | 2374.959 | 2725540 | 515827 | 11482227.5346 | 1206.2014 | 1147.6156 | 0.50788
Model 11 | EUn | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ11 | ChlrCap | 2239.9477 | 2452784 | 422357.9 | 10519710.0481 | 1094.5752 | 1095.0184 | 0.48866
Model 11 | EUn | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ11 | ChlrCap | 2146.914 | 2363197 | 388119.7 | 10000970.8136 | 1009.7025 | 1100.7413 | 0.4703
Model 11 | Hsp | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ11 | ChlrCap | 908.8632 | 809644.5 | 35547.93 | 4792763.2157 | 1040.4987 | 890.832 | 1.1448
Model 11 | Hsp | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ11 | ChlrCap | 907.9913 | 806920.8 | 35344.09 | 4768034.5475 | 1038.6493 | 888.6879 | 1.1439
Model 11 | Hsp | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ11 | ChlrCap | 928.6185 | 782362.5 | 35291.44 | 4638362.5803 | 1007.2457 | 842.5015 | 1.0847
Model 11 | Hsp | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ11 | ChlrCap | 942.108 | 761614.2 | 25948.36 | 4535381.1395 | 972.2462 | 808.415 | 1.032
Model 11 | Hsp | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ11 | ChlrCap | 964.2135 | 727964.5 | 25181.91 | 4327289.0481 | 910.36 | 754.9827 | 0.94415
Model 11 | Htl | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ11 | ChlrCap | 240.8033 | 401662.6 | 35720.31 | 1744103.3411 | 425.2845 | 1668.011 | 1.7661
Model 11 | Htl | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ11 | ChlrCap | 233.1243 | 368105.3 | 31520.04 | 1423348.0717 | 399.2223 | 1579.0085 | 1.7125
Model 11 | Htl | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ11 | ChlrCap | 224.8557 | 359460.9 | 31223.96 | 1361856.8953 | 386.2906 | 1598.6295 | 1.7179
Model 11 | Htl | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ11 | ChlrCap | 206.8593 | 321260.9 | 28774.2 | 1263265.5719 | 358.9631 | 1553.0404 | 1.7353
Model 11 | Htl | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ11 | ChlrCap | 204.9697 | 318055.8 | 28159.63 | 1248080.154 | 353.6483 | 1551.7213 | 1.7254
Model 11 | MBT | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ11 | ChlrCap | 399.3067 | 459982.7 | 34940.61 | 2480047.8406 | 495.6881 | 1151.9535 | 1.2414
Model 11 | MBT | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ11 | ChlrCap | 388.7318 | 411339 | 34429.57 | 2212564.0281 | 457.8987 | 1058.1562 | 1.1779
Model 11 | MBT | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ11 | ChlrCap | 370.9093 | 394859.3 | 33057.84 | 2130599.7808 | 431.6101 | 1064.5709 | 1.1637
Model 11 | MBT | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ11 | ChlrCap | 367.482 | 369207.5 | 15034.26 | 2040452.8628 | 410.8405 | 1004.6955 | 1.118
Model 11 | MBT | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ11 | ChlrCap | 345.7538 | 346332 | 13545.96 | 1903293.3599 | 387.366 | 1001.6722 | 1.1204
Model 11 | Nrs | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ11 | ChlrCap | 138.1275 | 203138 | 29773.23 | 1518778.3945 | 301.8311 | 1470.6559 | 2.1852
Model 11 | Nrs | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ11 | ChlrCap | 132.5941 | 208473.9 | 27694.49 | 1343732.6008 | 284.0737 | 1572.2709 | 2.1424
Model 11 | Nrs | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ11 | ChlrCap | 129.4259 | 205892.8 | 27881.21 | 1319935.1767 | 280.3455 | 1590.8159 | 2.1661
Model 11 | Nrs | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ11 | ChlrCap | 122.7176 | 192281.9 | 26198.76 | 1277298.7061 | 268.676 | 1566.8653 | 2.1894
Model 11 | Nrs | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ11 | ChlrCap | 118.8625 | 182771.5 | 25660.97 | 1220791.1992 | 254.2101 | 1537.671 | 2.1387
Model 11 | OfL | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ11 | ChlrCap | 437.5503 | 533078.8 | 92512.76 | 2271537.1653 | 553.5418 | 1218.3257 | 1.2651
Model 11 | OfL | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ11 | ChlrCap | 436.2393 | 491284.3 | 90817.2 | 2109133.8535 | 523.5605 | 1126.1807 | 1.2002
Model 11 | OfL | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ11 | ChlrCap | 418.8508 | 474932.2 | 93394.98 | 2020352.8077 | 503.4929 | 1133.8934 | 1.2021
Model 11 | OfL | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ11 | ChlrCap | 422.9555 | 458372.5 | 83648.84 | 2045227.5733 | 503.7199 | 1083.7369 | 1.191
Model 11 | OfL | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ11 | ChlrCap | 411.7397 | 443166.5 | 27735.18 | 1959050.1735 | 477.4834 | 1076.327 | 1.1597
Model 11 | OfS | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ11 | ChlrCap | 29.0447 | 36878.13 | 4375.315 | 148753.7306 | 35.582 | 1269.7007 | 1.2251
Model 11 | OfS | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ11 | ChlrCap | 28.8082 | 33976.32 | 4262.479 | 138855.3822 | 32.75 | 1179.3982 | 1.1368
Model 11 | OfS | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ11 | ChlrCap | 28.0648 | 33350.84 | 4290.674 | 135298.9273 | 32.0756 | 1188.3516 | 1.1429
Model 11 | OfS | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ11 | ChlrCap | 26.2097 | 29420.99 | 3974.574 | 123933.9502 | 28.6334 | 1122.5247 | 1.0925
Model 11 | OfS | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ11 | ChlrCap | 25.2603 | 28128.63 | 3507.058 | 117144.3445 | 26.8067 | 1113.5498 | 1.0612
Model 11 | Rt3 | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ11 | ChlrCap | 317.8452 | 439513.4 | 85587.52 | 1921424.1688 | 627.9624 | 1382.7909 | 1.9757
Model 11 | Rt3 | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ11 | ChlrCap | 315.9692 | 410380 | 85852.29 | 1825027.6846 | 609.5488 | 1298.7976 | 1.9291
Model 11 | Rt3 | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ11 | ChlrCap | 297.2928 | 395130 | 87460.95 | 1750569.0621 | 579.316 | 1329.0936 | 1.9486
Model 11 | Rt3 | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ11 | ChlrCap | 287.5838 | 371563.3 | 77488.61 | 1613833.2392 | 544.2277 | 1292.0173 | 1.8924
Model 11 | Rt3 | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ11 | ChlrCap | 276.9912 | 350632.8 | 65562.46 | 1501541.9097 | 511.0715 | 1265.8628 | 1.8451
Model 11 | ECC | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ12 | ChlrCap | 662.3168 | 667699.7 | 91843.2 | 3614429.4361 | 771.6562 | 1008.1273 | 1.1651
Model 11 | ECC | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ12 | ChlrCap | 660.0962 | 662318 | 91282.71 | 3547200.8628 | 767.265 | 1003.3659 | 1.1624
Model 11 | ECC | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ12 | ChlrCap | 648.0275 | 652026.1 | 92116.88 | 3488247.5088 | 758.5328 | 1006.1704 | 1.1705
Model 11 | ECC | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ12 | ChlrCap | 613.3367 | 603793.4 | 79968.37 | 3325863.3517 | 701.6295 | 984.4404 | 1.144
Model 11 | ECC | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ12 | ChlrCap | 583.5185 | 575566.1 | 64873.65 | 3121271.347 | 661.0685 | 986.3716 | 1.1329
Model 11 | ESe | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ12 | ChlrCap | 334.4787 | 229398.1 | 25517.06 | 1578961.5147 | 178.1505 | 685.8376 | 0.53262
Model 11 | ESe | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ12 | ChlrCap | 331.1757 | 249542.4 | 25630.12 | 1481845.2285 | 169.2497 | 753.5046 | 0.51106
Model 11 | ESe | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ12 | ChlrCap | 328.879 | 243493.2 | 24274.93 | 1442035.0154 | 156.5515 | 740.3732 | 0.47602
Model 11 | ESe | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ12 | ChlrCap | 319.1893 | 221618.2 | 17526.13 | 1359226.0335 | 151.4792 | 694.3158 | 0.47457
Model 11 | ESe | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ12 | ChlrCap | 302.8257 | 209627.1 | 17666.88 | 1287305.8503 | 142.2614 | 692.2369 | 0.46978
Model 11 | EUn | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ12 | ChlrCap | 2285.9947 | 2119164 | 454736.8 | 11341528.8007 | 2878.5491 | 927.0205 | 1.2592
Model 11 | EUn | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ12 | ChlrCap | 2294.4407 | 2097050 | 445196.5 | 11116718.4596 | 2849.5707 | 913.97 | 1.2419
Model 11 | EUn | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ12 | ChlrCap | 2243.6113 | 2077378 | 448031.7 | 10857503.4654 | 2805.8007 | 925.9081 | 1.2506
Model 11 | EUn | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ12 | ChlrCap | 2114.4723 | 1875503 | 376086.8 | 10030676.4689 | 2584.8223 | 886.9839 | 1.2224
Model 11 | EUn | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ12 | ChlrCap | 2018.7463 | 1796518 | 336044.4 | 9517266.9918 | 2471.9863 | 889.9177 | 1.2245
Model 11 | Hsp | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ12 | ChlrCap | 874.059 | 575663.2 | 28957.99 | 4478544.3072 | 837.3276 | 658.6091 | 0.95798
Model 11 | Hsp | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ12 | ChlrCap | 873.2853 | 573693.9 | 28837.31 | 4454324.3142 | 835.6475 | 656.9376 | 0.9569
Model 11 | Hsp | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ12 | ChlrCap | 879.031 | 567136 | 28808.47 | 4412443.2614 | 824.8077 | 645.1832 | 0.93831
Model 11 | Hsp | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ12 | ChlrCap | 889.8155 | 551643.4 | 21065.19 | 4320034.4959 | 808.5159 | 619.9526 | 0.90863
Model 11 | Hsp | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ12 | ChlrCap | 908.701 | 526466.2 | 20281.05 | 4121807.0633 | 748.7879 | 579.3613 | 0.82402
Model 11 | Htl | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ12 | ChlrCap | 219.0595 | 311742.5 | 31164.16 | 1624052.0131 | 309.8001 | 1423.0951 | 1.4142
Model 11 | Htl | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ12 | ChlrCap | 211.378 | 282125.5 | 27223.21 | 1307969.5532 | 289.3561 | 1334.6966 | 1.3689
Model 11 | Htl | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ12 | ChlrCap | 204.8895 | 277608.4 | 27174.36 | 1261487.5002 | 282.6335 | 1354.9177 | 1.3794
Model 11 | Htl | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ12 | ChlrCap | 187.9173 | 245291.2 | 24760.72 | 1174763.6715 | 262.5217 | 1305.3144 | 1.397
Model 11 | Htl | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ12 | ChlrCap | 186.1508 | 242979.6 | 24262.93 | 1161032.4148 | 257.6861 | 1305.2834 | 1.3843
Model 11 | MBT | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ12 | ChlrCap | 372.7475 | 347935 | 31175.29 | 2349502.6553 | 467.1618 | 933.4335 | 1.2533
Model 11 | MBT | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ12 | ChlrCap | 362.977 | 309773.3 | 30857.49 | 2103066.9379 | 433.3829 | 853.424 | 1.194
Model 11 | MBT | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ12 | ChlrCap | 350.5465 | 298658.4 | 29503.32 | 2025190.8722 | 417.345 | 851.9794 | 1.1906
Model 11 | MBT | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ12 | ChlrCap | 347.0127 | 279511.3 | 12171.35 | 1942624.4068 | 391.7135 | 805.4787 | 1.1288
Model 11 | MBT | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ12 | ChlrCap | 325.3683 | 262734.9 | 10793.17 | 1814012.837 | 368.0013 | 807.4999 | 1.131
Model 11 | Nrs | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ12 | ChlrCap | 125.9374 | 139209.6 | 25314.08 | 1442901.8484 | 229.8217 | 1105.3875 | 1.8249
Model 11 | Nrs | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ12 | ChlrCap | 120.5391 | 144294.5 | 23352.2 | 1269256.7483 | 219.6086 | 1197.0765 | 1.8219
Model 11 | Nrs | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ12 | ChlrCap | 117.7088 | 142790.6 | 23564.06 | 1247068.5155 | 217.3291 | 1213.0833 | 1.8463
Model 11 | Nrs | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ12 | ChlrCap | 111.6158 | 131629.6 | 21885.33 | 1208501.9076 | 208.9868 | 1179.3094 | 1.8724
Model 11 | Nrs | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ12 | ChlrCap | 110.2839 | 124315.2 | 21066.93 | 1164406.0342 | 196.5994 | 1127.2286 | 1.7827
Model 11 | OfL | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ12 | ChlrCap | 418.6502 | 421969.8 | 82883.71 | 2142592.823 | 503.193 | 1007.9294 | 1.2019
Model 11 | OfL | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ12 | ChlrCap | 417.4628 | 384237.3 | 79749.7 | 1980962.3341 | 474.0507 | 920.4108 | 1.1356
Model 11 | OfL | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ12 | ChlrCap | 403.19 | 374519.1 | 85862.27 | 1904559.8113 | 458.9939 | 928.8899 | 1.1384
Model 11 | OfL | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ12 | ChlrCap | 401.5918 | 356274.8 | 73750.84 | 1917887.6049 | 454.9915 | 887.1565 | 1.133
Model 11 | OfL | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ12 | ChlrCap | 390.1103 | 342701.8 | 14537.74 | 1824871.0703 | 435.1207 | 878.474 | 1.1154
Model 11 | OfS | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ12 | ChlrCap | 27.0139 | 29175.51 | 3064.733 | 139349.3156 | 29.3485 | 1080.0188 | 1.0864
Model 11 | OfS | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ12 | ChlrCap | 26.6977 | 26598.01 | 2964.69 | 129635.8569 | 26.877 | 996.2647 | 1.0067
Model 11 | OfS | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ12 | ChlrCap | 26.1792 | 26204.01 | 3006.326 | 126463.5142 | 26.3655 | 1000.9467 | 1.0071
Model 11 | OfS | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ12 | ChlrCap | 24.359 | 22988.31 | 2743.475 | 116274.9039 | 24.1993 | 943.729 | 0.99344
Model 11 | OfS | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ12 | ChlrCap | 23.6061 | 22075.49 | 2103.371 | 111042.1038 | 23.0646 | 935.1621 | 0.97706
Model 11 | Rt3 | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ12 | ChlrCap | 294.7187 | 337466 | 79853.87 | 1777975.0668 | 521.9701 | 1145.0445 | 1.7711
Model 11 | Rt3 | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ12 | ChlrCap | 292.9947 | 311509.4 | 79912.37 | 1689762.6753 | 505.4758 | 1063.1914 | 1.7252
Model 11 | Rt3 | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ12 | ChlrCap | 286.6217 | 308254.1 | 80855.83 | 1667569.3916 | 495.7067 | 1075.4738 | 1.7295
Model 11 | Rt3 | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ12 | ChlrCap | 276.5603 | 289121.4 | 71415.84 | 1536655.939 | 462.7332 | 1045.4189 | 1.6732
Model 11 | Rt3 | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ12 | ChlrCap | 265.7432 | 272258.4 | 59988.79 | 1437865.4713 | 431.8189 | 1024.517 | 1.6249
Model 11 | ECC | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ13 | ChlrCap | 780.354 | 1017701 | 124850.1 | 3902173.4619 | 926.8907 | 1304.153 | 1.1878
Model 11 | ECC | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ13 | ChlrCap | 778.095 | 1008540 | 123971.7 | 3830967.687 | 921.9721 | 1296.1656 | 1.1849
Model 11 | ECC | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ13 | ChlrCap | 758.2678 | 968709.1 | 124400.6 | 3709786.381 | 889.9374 | 1277.5289 | 1.1736
Model 11 | ECC | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ13 | ChlrCap | 724.1292 | 900233.1 | 112680.6 | 3530033.5088 | 815.8695 | 1243.1941 | 1.1267
Model 11 | ECC | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ13 | ChlrCap | 689.718 | 855067.5 | 92362.04 | 3288629.4889 | 766.272 | 1239.7349 | 1.111
Model 11 | ESe | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ13 | ChlrCap | 405.9537 | 424875.4 | 37274.56 | 1760565.1934 | 222.3647 | 1046.6106 | 0.54776
Model 11 | ESe | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ13 | ChlrCap | 399.7133 | 385991.5 | 37106.08 | 1583974.3834 | 194.661 | 965.6708 | 0.487
Model 11 | ESe | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ13 | ChlrCap | 393.3575 | 361647.4 | 33623.93 | 1505416.0516 | 181.8581 | 919.3861 | 0.46232
Model 11 | ESe | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ13 | ChlrCap | 380.471 | 331048.1 | 25363.69 | 1413882.4947 | 170.0349 | 870.1007 | 0.44691
Model 11 | ESe | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ13 | ChlrCap | 365.916 | 315858.8 | 25689.42 | 1332992.6762 | 158.9928 | 863.2003 | 0.43451
Model 11 | EUn | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ13 | ChlrCap | 2548.0427 | 3110772 | 599266.5 | 11925390.0996 | 3365.1527 | 1220.8477 | 1.3207
Model 11 | EUn | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ13 | ChlrCap | 2603.7117 | 3087448 | 590703.4 | 11733550.4771 | 3358.4203 | 1185.7872 | 1.2899
Model 11 | EUn | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ13 | ChlrCap | 2532.0783 | 3021909 | 588884.6 | 11340506.1196 | 3274.2248 | 1193.45 | 1.2931
Model 11 | EUn | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ13 | ChlrCap | 2391.7757 | 2732910 | 483802.6 | 10453086.4725 | 3005.0987 | 1142.6281 | 1.2564
Model 11 | EUn | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ13 | ChlrCap | 2296.1407 | 2632005 | 446389.2 | 9879769.0059 | 2877.4993 | 1146.2734 | 1.2532
Model 11 | Hsp | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ13 | ChlrCap | 922.8818 | 891749 | 41365.29 | 4743587.3951 | 954.4134 | 966.2657 | 1.0342
Model 11 | Hsp | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ13 | ChlrCap | 924.1015 | 888877.8 | 41107.33 | 4719123.3505 | 952.5729 | 961.8833 | 1.0308
Model 11 | Hsp | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ13 | ChlrCap | 939.1933 | 866054.6 | 40880.23 | 4631017.7995 | 933.7212 | 922.1261 | 0.99417
Model 11 | Hsp | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ13 | ChlrCap | 952.4823 | 842619.6 | 30274.36 | 4528422.2052 | 901.2172 | 884.6565 | 0.94618
Model 11 | Hsp | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ13 | ChlrCap | 967.7355 | 804276.8 | 29388.96 | 4301481.1735 | 830.3341 | 831.0916 | 0.85802
Model 11 | Htl | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ13 | ChlrCap | 239.844 | 437842.9 | 40104.96 | 1707797.7538 | 360.7062 | 1825.532 | 1.5039
Model 11 | Htl | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ13 | ChlrCap | 232.1605 | 401820.5 | 35488.14 | 1378035.2547 | 337.1228 | 1730.7875 | 1.4521
Model 11 | Htl | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ13 | ChlrCap | 224.3243 | 392285.7 | 35064.23 | 1329279.9032 | 327.9711 | 1748.7434 | 1.462
Model 11 | Htl | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ13 | ChlrCap | 206.0013 | 351975.6 | 32386.97 | 1238921.441 | 304.4626 | 1708.6084 | 1.478
Model 11 | Htl | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ13 | ChlrCap | 204.4572 | 348595.2 | 31765.75 | 1222375.253 | 299.2641 | 1704.9791 | 1.4637
Model 11 | MBT | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ13 | ChlrCap | 406.2655 | 498760.7 | 38591.67 | 2497392.313 | 540.7863 | 1227.6718 | 1.3311
Model 11 | MBT | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ13 | ChlrCap | 395.2757 | 445558.4 | 37841.77 | 2226683.6717 | 504.3865 | 1127.2093 | 1.276
Model 11 | MBT | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ13 | ChlrCap | 378.4635 | 426147.4 | 36194.75 | 2144955.8652 | 483.1134 | 1125.9934 | 1.2765
Model 11 | MBT | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ13 | ChlrCap | 375.0285 | 406445.6 | 16605.56 | 2061809.313 | 458.5309 | 1083.7726 | 1.2227
Model 11 | MBT | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ13 | ChlrCap | 353.691 | 374254.3 | 15160.41 | 1913202.7878 | 428.3688 | 1058.1392 | 1.2111
Model 11 | Nrs | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ13 | ChlrCap | 138.3341 | 223039.3 | 33747.89 | 1483913.2579 | 262.1187 | 1612.3234 | 1.8948
Model 11 | Nrs | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ13 | ChlrCap | 132.7963 | 229718.6 | 31545.83 | 1303145.3497 | 248.6893 | 1729.8565 | 1.8727
Model 11 | Nrs | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ13 | ChlrCap | 129.6282 | 226512.6 | 31646.46 | 1282099.0421 | 245.86 | 1747.4022 | 1.8967
Model 11 | Nrs | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ13 | ChlrCap | 122.481 | 212145.7 | 29897.33 | 1242613.6351 | 235.8203 | 1732.0705 | 1.9254
Model 11 | Nrs | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ13 | ChlrCap | 118.2186 | 202501.3 | 29162.76 | 1192114.5407 | 222.9744 | 1712.9394 | 1.8861
Model 11 | OfL | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ13 | ChlrCap | 429.9983 | 564376.8 | 109222.9 | 2272471.1196 | 555.0202 | 1312.5093 | 1.2907
Model 11 | OfL | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ13 | ChlrCap | 428.8553 | 522084.8 | 106216.7 | 2119329.3271 | 524.634 | 1217.3914 | 1.2233
Model 11 | OfL | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ13 | ChlrCap | 414.733 | 504241.2 | 109475.8 | 2036364.8054 | 507.5941 | 1215.8213 | 1.2239
Model 11 | OfL | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ13 | ChlrCap | 416.0417 | 488594.1 | 97229.52 | 2049864.4725 | 504.1163 | 1174.3874 | 1.2117
Model 11 | OfL | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ13 | ChlrCap | 404.4273 | 472308.1 | 51965.9 | 1959621.8453 | 470.5023 | 1167.8442 | 1.1634
Model 11 | OfS | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ13 | ChlrCap | 29.1718 | 39216.8 | 4940.481 | 145966.2939 | 33.2927 | 1344.3379 | 1.1413
Model 11 | OfS | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ13 | ChlrCap | 28.9361 | 37964.54 | 4822.125 | 138269.7122 | 31.6429 | 1312.0119 | 1.0935
Model 11 | OfS | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ13 | ChlrCap | 29.0007 | 37343.95 | 4825.172 | 135051.8931 | 30.9837 | 1287.6932 | 1.0684
Model 11 | OfS | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ13 | ChlrCap | 26.3782 | 32885.57 | 4539.344 | 124131.2498 | 28.1105 | 1246.6934 | 1.0657
Model 11 | OfS | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ13 | ChlrCap | 25.6917 | 31640.84 | 4121.502 | 118331.2989 | 26.4301 | 1231.5584 | 1.0287
Model 11 | Rt3 | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ13 | ChlrCap | 321.207 | 481180.3 | 96756.16 | 1933847.7362 | 595.1963 | 1498.038 | 1.853
Model 11 | Rt3 | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ13 | ChlrCap | 319.3022 | 449131.3 | 96987.04 | 1841298.2544 | 574.1668 | 1406.6027 | 1.7982
Model 11 | Rt3 | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ13 | ChlrCap | 305.8862 | 434177.6 | 96739.72 | 1792650.0317 | 555.0614 | 1419.4091 | 1.8146
Model 11 | Rt3 | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ13 | ChlrCap | 295.795 | 409906.9 | 86147.77 | 1652820.7421 | 521.3172 | 1385.7804 | 1.7624
Model 11 | Rt3 | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ13 | ChlrCap | 284.9072 | 387162.5 | 75841.06 | 1536171.6893 | 487.912 | 1358.9076 | 1.7125
Model 11 | ECC | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ14 | ChlrCap | 842.3122 | 941564.1 | 112369.5 | 3900892.796 | 898.6392 | 1117.8327 | 1.0669
Model 11 | ECC | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ14 | ChlrCap | 839.8307 | 934050.3 | 111693.8 | 3828425.714 | 893.1145 | 1112.1888 | 1.0634
Model 11 | ECC | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ14 | ChlrCap | 815.9963 | 903821.6 | 112911.3 | 3679230.1594 | 871.0731 | 1107.6295 | 1.0675
Model 11 | ECC | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ14 | ChlrCap | 777.5993 | 833223.8 | 100018 | 3493297.422 | 795.8975 | 1071.5336 | 1.0235
Model 11 | ECC | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ14 | ChlrCap | 742.634 | 793264.9 | 79060.55 | 3264099.9988 | 747.9605 | 1068.1775 | 1.0072
Model 11 | ESe | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ14 | ChlrCap | 443.2102 | 391208.3 | 31168.25 | 1767318.585 | 219.0431 | 882.67 | 0.49422
Model 11 | ESe | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ14 | ChlrCap | 436.6147 | 356223 | 30996.01 | 1591583.3411 | 188.8658 | 815.875 | 0.43257
Model 11 | ESe | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ14 | ChlrCap | 431.0297 | 337418.6 | 28084.51 | 1486188.7925 | 167.8682 | 782.8199 | 0.38946
Model 11 | ESe | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ14 | ChlrCap | 416.4333 | 303894 | 20183.97 | 1390288.1372 | 148.5919 | 729.7543 | 0.35682
Model 11 | ESe | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ14 | ChlrCap | 398.6307 | 287492.8 | 20103.34 | 1309243.6658 | 137.6427 | 721.2009 | 0.34529
Model 11 | EUn | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ14 | ChlrCap | 2765.1257 | 2864592 | 535548.9 | 12038996.17 | 3252.5639 | 1035.9717 | 1.1763
Model 11 | EUn | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ14 | ChlrCap | 2751.5513 | 2840086 | 526564.9 | 11819488.5252 | 3239.0601 | 1032.1763 | 1.1772
Model 11 | EUn | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ14 | ChlrCap | 2661.1527 | 2783382 | 534578.3 | 11306428.5615 | 3139.6095 | 1045.931 | 1.1798
Model 11 | EUn | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ14 | ChlrCap | 2534.953 | 2539186 | 447926.9 | 10455897.7608 | 2935.0744 | 1001.6699 | 1.1578
Model 11 | EUn | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ14 | ChlrCap | 2442.6647 | 2446209 | 406768.3 | 9901157.0352 | 2805.4154 | 1001.451 | 1.1485
Model 11 | Hsp | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ14 | ChlrCap | 966.1242 | 800551.5 | 35551.26 | 4849343.6565 | 923.0461 | 828.6217 | 0.95541
Model 11 | Hsp | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ14 | ChlrCap | 965.485 | 797482.8 | 35357.66 | 4821104.5826 | 920.9069 | 825.9919 | 0.95383
Model 11 | Hsp | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ14 | ChlrCap | 989.8152 | 775895.6 | 35347.99 | 4705443.3095 | 889.2603 | 783.8792 | 0.89841
Model 11 | Hsp | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ14 | ChlrCap | 1006.211 | 754333.1 | 25628.51 | 4604411.9918 | 875.0629 | 749.6769 | 0.86966
Model 11 | Hsp | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ14 | ChlrCap | 1033.492 | 721570.8 | 24905.89 | 4398816.4889 | 812.3913 | 698.1871 | 0.78606
Model 11 | Htl | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ14 | ChlrCap | 254.5663 | 389932 | 35507.38 | 1791802.2966 | 347.9913 | 1531.7501 | 1.367
Model 11 | Htl | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ14 | ChlrCap | 246.2812 | 357129.1 | 31543.99 | 1475587.7367 | 324.9103 | 1450.0869 | 1.3193
Model 11 | Htl | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ14 | ChlrCap | 238.4502 | 348876.8 | 31135.83 | 1413925.7021 | 315.2861 | 1463.1015 | 1.3222
Model 11 | Htl | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ14 | ChlrCap | 213.8892 | 319066.9 | 30072.12 | 1246320.4032 | 288.7482 | 1491.7394 | 1.35
Model 11 | Htl | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ14 | ChlrCap | 212.2535 | 316014.9 | 29504.06 | 1230839.8338 | 284.0027 | 1488.856 | 1.338
Model 11 | MBT | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ14 | ChlrCap | 416.1008 | 466591.8 | 36039.64 | 2500795.796 | 522.5568 | 1121.3431 | 1.2558
Model 11 | MBT | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ14 | ChlrCap | 405.316 | 419476.3 | 35623.94 | 2235795.5193 | 486.9501 | 1034.9364 | 1.2014
Model 11 | MBT | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ14 | ChlrCap | 392.189 | 403135.8 | 34160.6 | 2145953.626 | 469.4475 | 1027.9121 | 1.197
Model 11 | MBT | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ14 | ChlrCap | 386.476 | 376058.5 | 15115.27 | 2056341.9508 | 437.1035 | 973.0449 | 1.131
Model 11 | MBT | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ14 | ChlrCap | 365.1983 | 354199.7 | 13616.97 | 1918746.9355 | 410.8172 | 969.8831 | 1.1249
Model 11 | Nrs | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ14 | ChlrCap | 137.3265 | 202511.7 | 31326.6 | 1550945.5937 | 259.6017 | 1474.6733 | 1.8904
Model 11 | Nrs | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ14 | ChlrCap | 131.5436 | 208697.4 | 29224.19 | 1363336.8641 | 246.2039 | 1586.526 | 1.8717
Model 11 | Nrs | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ14 | ChlrCap | 128.4714 | 206551.7 | 29398.07 | 1340842.0993 | 243.337 | 1607.7641 | 1.8941
Model 11 | Nrs | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ14 | ChlrCap | 122.4209 | 191344.5 | 27515.87 | 1299022.3347 | 233.4973 | 1563.0058 | 1.9073
Model 11 | Nrs | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ14 | ChlrCap | 121.6014 | 182188.2 | 26825.02 | 1249282.8701 | 220.8002 | 1498.241 | 1.8158
Model 11 | OfL | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ14 | ChlrCap | 449.7138 | 543690.8 | 95127.07 | 2259084.7538 | 529.3046 | 1208.9706 | 1.177
Model 11 | OfL | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ14 | ChlrCap | 448.4922 | 502667.3 | 93055.36 | 2097362.4185 | 502.1747 | 1120.7939 | 1.1197
Model 11 | OfL | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ14 | ChlrCap | 434.1887 | 487646.2 | 94886.69 | 2016883.4572 | 475.5361 | 1123.1205 | 1.0952
Model 11 | OfL | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ14 | ChlrCap | 438.5937 | 471145.8 | 86552.88 | 2033173.5909 | 472.5397 | 1074.2193 | 1.0774
Model 11 | OfL | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ14 | ChlrCap | 426.4855 | 455903.5 | 42317.16 | 1946227.9355 | 453.1196 | 1068.9777 | 1.0625
Model 11 | OfS | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ14 | ChlrCap | 30.8227 | 37550.49 | 4327.548 | 146242.7081 | 31.5569 | 1218.2722 | 1.0238
Model 11 | OfS | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ14 | ChlrCap | 30.6523 | 36336.83 | 4193.925 | 138311.7046 | 29.9775 | 1185.4523 | 0.97799
Model 11 | OfS | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ14 | ChlrCap | 29.9938 | 35775 | 4220.375 | 135001.2061 | 29.3653 | 1192.7465 | 0.97905
Model 11 | OfS | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ14 | ChlrCap | 28.0533 | 31896.29 | 4071.552 | 123890.145 | 26.4612 | 1136.9885 | 0.94325
Model 11 | OfS | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ14 | ChlrCap | 27.2422 | 30647.11 | 3548.493 | 117959.2682 | 25.0897 | 1124.9859 | 0.92099
Model 11 | Rt3 | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ14 | ChlrCap | 328.0502 | 430977.8 | 86710.65 | 1888908.7819 | 565.6766 | 1313.7558 | 1.7244
Model 11 | Rt3 | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ14 | ChlrCap | 326.0978 | 402860.2 | 87011.73 | 1790040.9707 | 546.555 | 1235.3967 | 1.676
Model 11 | Rt3 | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ14 | ChlrCap | 307.0428 | 390342.9 | 89691.98 | 1731256.1911 | 523.4993 | 1271.2979 | 1.705
Model 11 | Rt3 | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ14 | ChlrCap | 298.3908 | 360150.3 | 78699.38 | 1584000.129 | 478.0689 | 1206.9751 | 1.6022
Model 11 | Rt3 | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ14 | ChlrCap | 286.5403 | 339577.4 | 64943.04 | 1473561.6776 | 446.2429 | 1185.0946 | 1.5573
Model 11 | ECC | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ15 | ChlrCap | 1071.5732 | 1955341 | 187341.4 | 4371168.6131 | 1399.3234 | 1824.7387 | 1.3059
Model 11 | ECC | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ15 | ChlrCap | 1067.7025 | 1942020 | 186445.8 | 4314106.5123 | 1392.5723 | 1818.8774 | 1.3043
Model 11 | ECC | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ15 | ChlrCap | 1039.5275 | 1847047 | 182020 | 4170447.5639 | 1303.9171 | 1776.814 | 1.2543
Model 11 | ECC | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ15 | ChlrCap | 999.8655 | 1719790 | 164156.1 | 3955543.2403 | 1212.5408 | 1720.0213 | 1.2127
Model 11 | ECC | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ15 | ChlrCap | 966.2553 | 1650819 | 148370.6 | 3634270.9918 | 1156.6109 | 1708.4708 | 1.197
Model 11 | ESe | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ15 | ChlrCap | 571.8747 | 856488 | 65574.95 | 2004524.6506 | 342.1391 | 1497.6848 | 0.59828
Model 11 | ESe | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ15 | ChlrCap | 563.4945 | 781693.5 | 64996.14 | 1715469.7866 | 298.2324 | 1387.2247 | 0.52926
Model 11 | ESe | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ15 | ChlrCap | 548.3095 | 717382.4 | 55050.76 | 1613888.6882 | 272.025 | 1308.353 | 0.49612
Model 11 | ESe | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ15 | ChlrCap | 531.334 | 661281.5 | 40336.6 | 1516859.3693 | 248.6565 | 1244.5684 | 0.46799
Model 11 | ESe | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ15 | ChlrCap | 512.9195 | 632546.8 | 37572.2 | 1400692.7409 | 232.9702 | 1233.2282 | 0.4542
Model 11 | EUn | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ15 | ChlrCap | 3491.2633 | 5860873 | 861058.9 | 12941741.5006 | 4974.2699 | 1678.7256 | 1.4248
Model 11 | EUn | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ15 | ChlrCap | 3472.33 | 5823819 | 852403.5 | 12789759.5897 | 4952.8503 | 1677.2078 | 1.4264
Model 11 | EUn | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ15 | ChlrCap | 3357.4867 | 5626999 | 836905.3 | 12436154.1501 | 4752.1605 | 1675.9557 | 1.4154
Model 11 | EUn | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ15 | ChlrCap | 3229.451 | 5149118 | 672441.8 | 11549713.0481 | 4352.246 | 1594.4252 | 1.3477
Model 11 | EUn | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ15 | ChlrCap | 3124.6453 | 4972136 | 629504.4 | 10738547.1981 | 4200.5819 | 1591.2641 | 1.3443
Model 11 | Hsp | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ15 | ChlrCap | 1138.0515 | 1672752 | 59077.69 | 5162697.5193 | 1284.0081 | 1469.8386 | 1.1283
Model 11 | Hsp | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ15 | ChlrCap | 1137.3063 | 1668234 | 58793.79 | 5145959.0352 | 1281.7651 | 1466.8292 | 1.127
Model 11 | Hsp | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ15 | ChlrCap | 1170.9917 | 1602614 | 58326.25 | 5033995.0739 | 1211.5172 | 1368.5955 | 1.0346
Model 11 | Hsp | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ15 | ChlrCap | 1192.3815 | 1559089 | 42957.69 | 4918017.993 | 1184.9318 | 1307.5421 | 0.99375
Model 11 | Hsp | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ15 | ChlrCap | 1221.3843 | 1493202 | 42073.1 | 4610233.8617 | 1116.894 | 1222.5489 | 0.91445
Model 11 | Htl | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ15 | ChlrCap | 320.6793 | 765976.9 | 55960.8 | 1889261.2462 | 541.6455 | 2388.607 | 1.6891
Model 11 | Htl | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ15 | ChlrCap | 312.4632 | 710494.6 | 50305.4 | 1494216.3904 | 508.2091 | 2273.8507 | 1.6265
Model 11 | Htl | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ15 | ChlrCap | 302.4662 | 689632.9 | 48615.45 | 1457703.3118 | 490.9105 | 2280.0332 | 1.623
Model 11 | Htl | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ15 | ChlrCap | 275.608 | 626130.6 | 45829 | 1338588.7573 | 445.9465 | 2271.8158 | 1.618
Model 11 | Htl | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ15 | ChlrCap | 273.3932 | 619957.2 | 44902.66 | 1314556.9859 | 439.6633 | 2267.6397 | 1.6082
Model 11 | MBT | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ15 | ChlrCap | 513.0728 | 937224.7 | 57730.31 | 2899219.0375 | 763.2157 | 1826.6894 | 1.4875
Model 11 | MBT | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ15 | ChlrCap | 501.2435 | 846272.3 | 56394.44 | 2545307.7948 | 714.1432 | 1688.3457 | 1.4247
Model 11 | MBT | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ15 | ChlrCap | 481.6768 | 807170.1 | 53702.32 | 2469859.939 | 670.8521 | 1675.7503 | 1.3927
Model 11 | MBT | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ15 | ChlrCap | 475.9037 | 759823.7 | 26349.02 | 2358756.7351 | 630.4779 | 1596.5914 | 1.3248
Model 11 | MBT | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ15 | ChlrCap | 453.7342 | 714578.6 | 24438.48 | 2184750.5979 | 591.2841 | 1574.8838 | 1.3032
Model 11 | Nrs | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ15 | ChlrCap | 182.887 | 440925.3 | 48932.39 | 1542734.9062 | 378.2023 | 2410.9166 | 2.068
Model 11 | Nrs | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ15 | ChlrCap | 176.6895 | 446183.8 | 46471.85 | 1319486.3927 | 354.4153 | 2525.2423 | 2.0059
Model 11 | Nrs | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ15 | ChlrCap | 169.2027 | 434397.5 | 46485.57 | 1295345.1172 | 344.225 | 2567.3206 | 2.0344
Model 11 | Nrs | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ15 | ChlrCap | 159.5154 | 410261.4 | 44393.04 | 1255356.5147 | 329.8237 | 2571.9229 | 2.0677
Model 11 | Nrs | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ15 | ChlrCap | 156.3556 | 394105.7 | 43632.94 | 1187924.66 | 314.5351 | 2520.573 | 2.0117
Model 11 | OfL | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ15 | ChlrCap | 550.1308 | 996517.2 | 150192.4 | 2687601.8253 | 685.7295 | 1811.4186 | 1.2465
Model 11 | OfL | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ15 | ChlrCap | 548.4895 | 931259.6 | 147957.1 | 2482403.0023 | 652.3569 | 1697.8622 | 1.1894
Model 11 | OfL | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ15 | ChlrCap | 508.8343 | 893480.4 | 148816.7 | 2410614.5692 | 628.0551 | 1755.9358 | 1.2343
Model 11 | OfL | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ15 | ChlrCap | 536.7805 | 887888.6 | 137610.6 | 2399252.2878 | 635.5249 | 1654.1 | 1.184
Model 11 | OfL | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ15 | ChlrCap | 522.6575 | 860278.1 | 96970.95 | 2280129.4431 | 613.0905 | 1645.9691 | 1.173
Model 11 | OfS | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ15 | ChlrCap | 36.3228 | 70070.77 | 7769.45 | 166861.1365 | 46.5577 | 1929.1135 | 1.2818
Model 11 | OfS | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ15 | ChlrCap | 36.0697 | 65724.3 | 7642.452 | 154237.303 | 43.3296 | 1822.1488 | 1.2013
Model 11 | OfS | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ15 | ChlrCap | 34.8143 | 63457.96 | 7592.521 | 149316.1857 | 41.127 | 1822.7569 | 1.1813
Model 11 | OfS | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ15 | ChlrCap | 32.9766 | 57401.8 | 7121.402 | 138571.4544 | 36.7039 | 1740.6801 | 1.113
Model 11 | OfS | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ15 | ChlrCap | 32.0845 | 55481 | 6710.865 | 131078.1045 | 35.0881 | 1729.2137 | 1.0936
Model 11 | Rt3 | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ15 | ChlrCap | 400.5612 | 874125.4 | 137005.7 | 2292176.2151 | 801.0937 | 2182.252 | 1.9999
Model 11 | Rt3 | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ15 | ChlrCap | 399.2927 | 827176.5 | 136899.5 | 2169386.2855 | 781.2709 | 2071.6045 | 1.9566
Model 11 | Rt3 | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ15 | ChlrCap | 381.8447 | 779813.5 | 131815.6 | 2111285.4569 | 731.9501 | 2042.227 | 1.9169
Model 11 | Rt3 | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ15 | ChlrCap | 370.6765 | 733059.1 | 117934.3 | 1931487.6149 | 683.4545 | 1977.625 | 1.8438
Model 11 | Rt3 | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ15 | ChlrCap | 360.4552 | 699010.6 | 106055 | 1770023.0123 | 646.7206 | 1939.2442 | 1.7942
Model 11 | ECC | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2003-CZ16 | ChlrCap | 457.4017 | 297875.7 | 57873.91 | 4348730.8195 | 235.9644 | 651.2344 | 0.51588
Model 11 | ECC | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2007-CZ16 | ChlrCap | 455.6992 | 295234.1 | 57486.77 | 4281952.0621 | 234.3478 | 647.8706 | 0.51426
Model 11 | ECC | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2011-CZ16 | ChlrCap | 435.1002 | 284826.9 | 60547.22 | 3976019.0914 | 213.1295 | 654.6237 | 0.48984
Model 11 | ECC | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2015-CZ16 | ChlrCap | 409.0627 | 259640.6 | 53266.61 | 3759247.0832 | 182.4205 | 634.7208 | 0.44595
Model 11 | ECC | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ECC-2020-CZ16 | ChlrCap | 382.9705 | 245302.3 | 39426.63 | 3642929.5475 | 157.0637 | 640.5253 | 0.41012
Model 11 | ESe | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2003-CZ16 | ChlrCap | 234.3245 | 98377.87 | 18472.17 | 2049181.3891 | 105.6831 | 419.836 | 0.45101
Model 11 | ESe | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2007-CZ16 | ChlrCap | 230.2368 | 112108.9 | 18443.59 | 1964370.4224 | 105.1149 | 486.9286 | 0.45655
Model 11 | ESe | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2011-CZ16 | ChlrCap | 225.8828 | 105857.4 | 16531.19 | 1760587.3437 | 93.1748 | 468.6385 | 0.41249
Model 11 | ESe | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2015-CZ16 | ChlrCap | 217.4782 | 92304.52 | 12346.75 | 1661352.4611 | 80.4652 | 424.4312 | 0.36999
Model 11 | ESe | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-ESe-2020-CZ16 | ChlrCap | 202.1828 | 85684.86 | 12175.13 | 1622240.0451 | 73.4986 | 423.7989 | 0.36353
Model 11 | EUn | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2003-CZ16 | ChlrCap | 1624.4567 | 967572.7 | 287270.9 | 14157643.5932 | 523.273 | 595.6285 | 0.32212
Model 11 | EUn | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2007-CZ16 | ChlrCap | 1615.792 | 954141.1 | 279614.1 | 13904362.272 | 520.3007 | 590.5099 | 0.32201
Model 11 | EUn | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2011-CZ16 | ChlrCap | 1564.3213 | 947760.8 | 295417 | 12870992.9402 | 477.0432 | 605.8607 | 0.30495
Model 11 | EUn | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2015-CZ16 | ChlrCap | 1441.557 | 791807.6 | 251867.8 | 11800157.7902 | 387.4101 | 549.2725 | 0.26874
Model 11 | EUn | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-EUn-2020-CZ16 | ChlrCap | 1356.255 | 751357.4 | 218023.6 | 11441372.1454 | 352.9117 | 553.9942 | 0.26021
Model 11 | Hsp | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2003-CZ16 | ChlrCap | 642.4422 | 275067 | 20897.5 | 5179704.0481 | 608.5651 | 428.1583 | 0.94727
Model 11 | Hsp | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2007-CZ16 | ChlrCap | 641.734 | 273710.5 | 20870.44 | 5145876.9086 | 609.4357 | 426.5171 | 0.94967
Model 11 | Hsp | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2011-CZ16 | ChlrCap | 645.7175 | 264906.5 | 20865.19 | 4915342.6671 | 594.9187 | 410.2514 | 0.92133
Model 11 | Hsp | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2015-CZ16 | ChlrCap | 648.9835 | 257845.3 | 15693.12 | 4800142.1137 | 583.7217 | 397.3064 | 0.89944
Model 11 | Hsp | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Hsp-2020-CZ16 | ChlrCap | 655.2332 | 245197.3 | 15123.2 | 4669300.2743 | 529.1321 | 374.2138 | 0.80755
Model 11 | Htl | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2003-CZ16 | ChlrCap | 148.4864 | 178693.1 | 24448.58 | 1922017.7804 | 205.7815 | 1203.4309 | 1.3859
Model 11 | Htl | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2007-CZ16 | ChlrCap | 142.3047 | 160710.1 | 21406.24 | 1667524.8965 | 189.2999 | 1129.3378 | 1.3302
Model 11 | Htl | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2011-CZ16 | ChlrCap | 137.1796 | 158919.5 | 21531.01 | 1571089.4098 | 185.6724 | 1158.4781 | 1.3535
Model 11 | Htl | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2015-CZ16 | ChlrCap | 119.3118 | 129799.2 | 18890.01 | 1415133.0782 | 168.2259 | 1087.8994 | 1.41
Model 11 | Htl | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Htl-2020-CZ16 | ChlrCap | 118.4843 | 128710.7 | 18494.51 | 1406428.5859 | 164.5951 | 1086.3103 | 1.3892
Model 11 | MBT | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2003-CZ16 | ChlrCap | 263.6658 | 152392.2 | 18147.91 | 2455613.8851 | 252.8609 | 577.9748 | 0.95902
Model 11 | MBT | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2007-CZ16 | ChlrCap | 255.6078 | 135468.4 | 17957.42 | 2249243.0094 | 234.0498 | 529.9853 | 0.91566
Model 11 | MBT | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2011-CZ16 | ChlrCap | 242.0863 | 130476 | 17446.91 | 2110620.0504 | 228.0015 | 538.9647 | 0.94182
Model 11 | MBT | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2015-CZ16 | ChlrCap | 240.6683 | 120228.6 | 7139.078 | 2018132.592 | 208.7509 | 499.5614 | 0.86738
Model 11 | MBT | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-MBT-2020-CZ16 | ChlrCap | 224.0473 | 112274.1 | 5979.604 | 1905361.6026 | 188.6856 | 501.1178 | 0.84217
Model 11 | Nrs | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2003-CZ16 | ChlrCap | 83.2297 | 60630.52 | 17198.33 | 1730375.2664 | 162.6243 | 728.4725 | 1.9539
Model 11 | Nrs | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2007-CZ16 | ChlrCap | 79.3774 | 64251.53 | 15601.93 | 1583269.4436 | 156.3692 | 809.4436 | 1.9699
Model 11 | Nrs | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2011-CZ16 | ChlrCap | 78.7542 | 63789.28 | 15795.1 | 1544954.4798 | 155.3275 | 809.9792 | 1.9723
Model 11 | Nrs | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2015-CZ16 | ChlrCap | 78.6215 | 57488.47 | 14476.85 | 1496253.7523 | 150.6627 | 731.2055 | 1.9163
Model 11 | Nrs | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Nrs-2020-CZ16 | ChlrCap | 78.647 | 53729.68 | 13913.99 | 1463172.2807 | 140.2241 | 683.1756 | 1.783
Model 11 | OfL | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2003-CZ16 | ChlrCap | 320.445 | 210615.3 | 51530.82 | 2142796.6436 | 327.2858 | 657.2588 | 1.0213
Model 11 | OfL | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2007-CZ16 | ChlrCap | 319.4318 | 189659 | 47083.79 | 2041657.7409 | 303.9567 | 593.7386 | 0.95155
Model 11 | OfL | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2011-CZ16 | ChlrCap | 302.0675 | 185771.5 | 47786.28 | 1906685.4631 | 290.1254 | 615 | 0.96047
Model 11 | OfL | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2015-CZ16 | ChlrCap | 305.7612 | 171495.7 | 46890.8 | 1972319.3564 | 282.1427 | 560.8812 | 0.92276
Model 11 | OfL | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfL-2020-CZ16 | ChlrCap | 292.609 | 163985 | 8699.677 | 1900329.5264 | 268.002 | 560.4236 | 0.9159
Model 11 | OfS | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2003-CZ16 | ChlrCap | 20.1187 | 14288.26 | 1969.783 | 151612.1309 | 18.4747 | 710.1994 | 0.91829
Model 11 | OfS | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2007-CZ16 | ChlrCap | 19.935 | 12801.12 | 1865.541 | 144687.1348 | 16.964 | 642.1427 | 0.85097
Model 11 | OfS | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2011-CZ16 | ChlrCap | 19.4755 | 12632.3 | 1904.536 | 140032.9124 | 16.7 | 648.6249 | 0.85749
Model 11 | OfS | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2015-CZ16 | ChlrCap | 17.6336 | 10701.55 | 1482.58 | 126149.6187 | 14.399 | 606.884 | 0.81657
Model 11 | OfS | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-OfS-2020-CZ16 | ChlrCap | 17.013 | 10245.56 | 1309.511 | 121848.5767 | 13.6871 | 602.2207 | 0.80451
Model 11 | Rt3 | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2003-CZ16 | ChlrCap | 217.8227 | 147104.5 | 53605.86 | 1883148.4256 | 368.5885 | 675.3406 | 1.6921
Model 11 | Rt3 | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2007-CZ16 | ChlrCap | 216.4523 | 134391.6 | 53650.77 | 1826056.2251 | 356.62 | 620.8831 | 1.6476
Model 11 | Rt3 | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2011-CZ16 | ChlrCap | 199.7127 | 131058 | 57076.79 | 1670967.3482 | 343.5817 | 656.2328 | 1.7204
Model 11 | Rt3 | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2015-CZ16 | ChlrCap | 188.7828 | 120665.8 | 50426.13 | 1575094.823 | 316.406 | 639.1778 | 1.676
Model 11 | Rt3 | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model11-1.24kwpton-Rt3-2020-CZ16 | ChlrCap | 178.089 | 111746.9 | 38315.18 | 1512800.6038 | 290.7574 | 627.4778 | 1.6327
Model 17 | ECC | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ01 | ChlrCap | 363.0903 | 49248.14 | 13191.63 | 3497045.6436 | 446.6919 | 135.6361 | 1.2302
Model 17 | ECC | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ01 | ChlrCap | 362.3947 | 48755.79 | 13128.86 | 3451148.9156 | 444.9026 | 134.5378 | 1.2277
Model 17 | ECC | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ01 | ChlrCap | 358.621 | 49157.24 | 14694.4 | 3377788.0152 | 444.7508 | 137.073 | 1.2402
Model 17 | ECC | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ01 | ChlrCap | 337.2 | 47174.7 | 13961.43 | 3266572.0352 | 427.1861 | 139.9012 | 1.2669
Model 17 | ECC | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ01 | ChlrCap | 308.2373 | 43837.34 | 4634.174 | 3183895.925 | 383.8791 | 142.2194 | 1.2454
Model 17 | ESe | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ01 | ChlrCap | 177.9213 | 20566.73 | 950.8166 | 1628113.1524 | 120.2685 | 115.5945 | 0.67596
Model 17 | ESe | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ01 | ChlrCap | 172.2432 | 16900.63 | 979.5164 | 1551112.0729 | 111.6547 | 98.1208 | 0.64824
Model 17 | ESe | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ01 | ChlrCap | 171.2935 | 17183.57 | 1103.1 | 1507432.0862 | 111.2717 | 100.3165 | 0.6496
Model 17 | ESe | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ01 | ChlrCap | 162.6435 | 16287.63 | 604.3058 | 1462464.0318 | 105.3239 | 100.1431 | 0.64758
Model 17 | ESe | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ01 | ChlrCap | 147.6032 | 15088.94 | 411.2522 | 1429818.6131 | 97.8678 | 102.2264 | 0.66305
Model 17 | EUn | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ01 | ChlrCap | 1393.3897 | 174755.9 | 67173.32 | 11750873.5275 | 1534.176 | 125.4178 | 1.101
Model 17 | EUn | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ01 | ChlrCap | 1386.448 | 170372.4 | 62261.34 | 11562988.9894 | 1530.3759 | 122.8841 | 1.1038
Model 17 | EUn | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ01 | ChlrCap | 1376.0627 | 174999.7 | 68029.63 | 11219421.7644 | 1529.7449 | 127.1742 | 1.1117
Model 17 | EUn | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ01 | ChlrCap | 1253.919 | 141929.3 | 58698.44 | 10549227.2345 | 1449.2296 | 113.1886 | 1.1558
Model 17 | EUn | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ01 | ChlrCap | 1169.1157 | 127372.9 | 37439.65 | 10176064.4115 | 1303.5377 | 108.9481 | 1.115
Model 17 | Hsp | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ01 | ChlrCap | 534.269 | 20338.31 | 1086.875 | 4287978.5768 | 450.6649 | 38.0675 | 0.84352
Model 17 | Hsp | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ01 | ChlrCap | 533.8913 | 20319.75 | 1084.233 | 4271679.0938 | 450.305 | 38.0597 | 0.84344
Model 17 | Hsp | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ01 | ChlrCap | 533.2168 | 20240.44 | 1107.53 | 4220395.5487 | 449.3101 | 37.9591 | 0.84264
Model 17 | Hsp | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ01 | ChlrCap | 532.3435 | 20036.35 | 829.3415 | 4140043.2532 | 441.5508 | 37.638 | 0.82945
Model 17 | Hsp | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ01 | ChlrCap | 528.477 | 19473.65 | 660.4197 | 4041455.993 | 396.2071 | 36.8486 | 0.74971
Model 17 | Htl | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ01 | ChlrCap | 121.6717 | 42418.21 | 8764.943 | 1537142.2204 | 131.3719 | 348.6285 | 1.0797
Model 17 | Htl | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ01 | ChlrCap | 115.4313 | 35034.83 | 7115.562 | 1324944.8754 | 119.6581 | 303.5123 | 1.0366
Model 17 | Htl | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ01 | ChlrCap | 112.9238 | 35784.89 | 7415.443 | 1256975.102 | 119.5618 | 316.8941 | 1.0588
Model 17 | Htl | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ01 | ChlrCap | 95.2545 | 25997.28 | 5723.393 | 1142689.2565 | 109.1923 | 272.9245 | 1.1463
Model 17 | Htl | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ01 | ChlrCap | 93.868 | 25683.02 | 5644.067 | 1138741.9372 | 105.9517 | 273.6078 | 1.1287
Model 17 | MBT | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ01 | ChlrCap | 197.4575 | 32669.16 | 3894.1 | 2082731.4138 | 180.9087 | 165.4491 | 0.91619
Model 17 | MBT | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ01 | ChlrCap | 192.24 | 28272.8 | 4266.294 | 1902699.0703 | 169.27 | 147.0703 | 0.88051
Model 17 | MBT | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ01 | ChlrCap | 189.7313 | 28072.57 | 4257.489 | 1857012.925 | 166.6937 | 147.9596 | 0.87858
Model 17 | MBT | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ01 | ChlrCap | 189.4815 | 29140.91 | 1646.272 | 1799785.2521 | 159.72 | 153.7929 | 0.84293
Model 17 | MBT | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ01 | ChlrCap | 173.0733 | 28664.26 | 1739.916 | 1669677.8113 | 146.2125 | 165.6192 | 0.8448
Model 17 | Nrs | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ01 | ChlrCap | 65.0155 | 7992.651 | 2526.695 | 1512900.3505 | 128.0228 | 122.9345 | 1.9691
Model 17 | Nrs | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ01 | ChlrCap | 64.0681 | 4716.836 | 1811.591 | 1396841.3434 | 115.9148 | 73.6222 | 1.8092
Model 17 | Nrs | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ01 | ChlrCap | 64.0681 | 4716.836 | 1811.591 | 1396841.3434 | 115.9148 | 73.6222 | 1.8092
Model 17 | Nrs | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ01 | ChlrCap | 63.8031 | 3516.337 | 1217.931 | 1363721.2641 | 112.0861 | 55.1123 | 1.7568
Model 17 | Nrs | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ01 | ChlrCap | 62.0487 | 3021.484 | 995.0484 | 1338361.5732 | 101.5837 | 48.6954 | 1.6372
Model 17 | OfL | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ01 | ChlrCap | 267.187 | 43067.66 | 3926.175 | 1730630.9355 | 243.9153 | 161.1892 | 0.9129
Model 17 | OfL | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ01 | ChlrCap | 262.4838 | 36191.17 | 3233.338 | 1624379.7245 | 231.2293 | 137.8796 | 0.88093
Model 17 | OfL | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ01 | ChlrCap | 258.7623 | 36393.36 | 4154.209 | 1577629.1372 | 228.5605 | 140.644 | 0.88328
Model 17 | OfL | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ01 | ChlrCap | 251.6 | 32409.23 | 3814.408 | 1616732.4256 | 218.5575 | 128.8125 | 0.86867
Model 17 | OfL | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ01 | ChlrCap | 239.618 | 29896.01 | 165.0933 | 1500543.3693 | 201.4313 | 124.7653 | 0.84064
Model 17 | OfS | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ01 | ChlrCap | 16.798 | 2492.016 | 256.0124 | 120914.9477 | 12.6838 | 148.3522 | 0.75508
Model 17 | OfS | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ01 | ChlrCap | 16.4158 | 2138.95 | 218.1973 | 115655.7708 | 11.8217 | 130.2982 | 0.72014
Model 17 | OfS | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ01 | ChlrCap | 16.3121 | 2118.049 | 216.8951 | 115041.1971 | 11.7249 | 129.8455 | 0.71879
Model 17 | OfS | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ01 | ChlrCap | 14.6981 | 1838.212 | 117.0017 | 104410.9499 | 10.4987 | 125.0645 | 0.71429
Model 17 | OfS | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ01 | ChlrCap | 13.954 | 1605.798 | 90.2619 | 100157.9608 | 9.7929 | 115.0778 | 0.7018
Model 17 | Rt3 | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ01 | ChlrCap | 153.7271 | 23134.07 | 21212.68 | 1523854.4162 | 263.9675 | 150.4879 | 1.7171
Model 17 | Rt3 | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ01 | ChlrCap | 152.8906 | 20642.13 | 20308.05 | 1441498.4959 | 259.8836 | 135.0124 | 1.6998
Model 17 | Rt3 | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ01 | ChlrCap | 150.8586 | 21862.15 | 22718.61 | 1412650.1817 | 259.303 | 144.9182 | 1.7188
Model 17 | Rt3 | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ01 | ChlrCap | 139.6182 | 18388.14 | 18718.46 | 1322568.9226 | 235.4827 | 131.703 | 1.6866
Model 17 | Rt3 | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ01 | ChlrCap | 128.2081 | 15391.85 | 13578.44 | 1250282.1231 | 212.9743 | 120.0537 | 1.6612
Model 17 | ECC | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ02 | ChlrCap | 622.7143 | 333170 | 59003.07 | 3343537.2274 | 660.67 | 535.0286 | 1.061
Model 17 | ECC | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ02 | ChlrCap | 620.6888 | 330552.9 | 58594.28 | 3284689.0528 | 656.6553 | 532.5582 | 1.0579
Model 17 | ECC | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ02 | ChlrCap | 618.5397 | 329875.7 | 58534.99 | 3279643.0023 | 655.3401 | 533.3137 | 1.0595
Model 17 | ECC | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ02 | ChlrCap | 589.2032 | 304934.9 | 51019.9 | 3137371.4009 | 626.3501 | 517.5378 | 1.063
Model 17 | ECC | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ02 | ChlrCap | 557.0718 | 290018.6 | 35147.46 | 2978143.5487 | 570.0581 | 520.6126 | 1.0233
Model 17 | ESe | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ02 | ChlrCap | 318.2727 | 141316.6 | 14852.03 | 1520422.8839 | 220.9215 | 444.0111 | 0.69413
Model 17 | ESe | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ02 | ChlrCap | 309.8685 | 120104.9 | 15006.12 | 1393435.4664 | 195.5824 | 387.5996 | 0.63118
Model 17 | ESe | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ02 | ChlrCap | 308.0745 | 119724.5 | 14964.26 | 1388639.9443 | 195.1107 | 388.6219 | 0.63332
Model 17 | ESe | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ02 | ChlrCap | 300.8848 | 108398.1 | 10234.08 | 1321711.713 | 175.2395 | 360.2644 | 0.58241
Model 17 | ESe | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ02 | ChlrCap | 285.2343 | 102599 | 10187.84 | 1269742.4434 | 167.1801 | 359.7007 | 0.58611
Model 17 | EUn | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ02 | ChlrCap | 2222.8973 | 1101897 | 326349.3 | 10808284.7292 | 2241.4569 | 495.7031 | 1.0083
Model 17 | EUn | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ02 | ChlrCap | 2209.6417 | 1086022 | 316433 | 10579118.2544 | 2222.8971 | 491.4924 | 1.006
Model 17 | EUn | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ02 | ChlrCap | 2186.6183 | 1082280 | 315140.9 | 10431999.2708 | 2222.664 | 494.9561 | 1.0165
Model 17 | EUn | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ02 | ChlrCap | 2065.393 | 974959.6 | 262349.7 | 9709573.0094 | 2094.0667 | 472.0456 | 1.0139
Model 17 | EUn | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ02 | ChlrCap | 1962.3893 | 923837.9 | 220585.9 | 9278245.8253 | 1941.1965 | 470.772 | 0.9892
Model 17 | Hsp | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ02 | ChlrCap | 819.109 | 237539.7 | 16193.16 | 4222955.381 | 597.4171 | 289.9977 | 0.72935
Model 17 | Hsp | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ02 | ChlrCap | 818.5588 | 236574.6 | 16180.47 | 4202417.6928 | 596.3179 | 289.0136 | 0.7285
Model 17 | Hsp | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ02 | ChlrCap | 818.008 | 236465.8 | 16180.47 | 4199197.5428 | 596.0481 | 289.0752 | 0.72866
Model 17 | Hsp | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ02 | ChlrCap | 827.012 | 227614.9 | 10796.77 | 4113052.8394 | 587.5993 | 275.2256 | 0.71051
Model 17 | Hsp | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ02 | ChlrCap | 844.9847 | 213111.5 | 10247.04 | 3950718.8781 | 534.278 | 252.2075 | 0.63229
Model 17 | Htl | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ02 | ChlrCap | 192.1052 | 149908.4 | 23431.3 | 1487672.0374 | 194.2159 | 780.3455 | 1.011
Model 17 | Htl | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ02 | ChlrCap | 183.6192 | 132411 | 20283.9 | 1207992.5598 | 178.9107 | 721.1175 | 0.97436
Model 17 | Htl | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ02 | ChlrCap | 179.1558 | 131556.2 | 20418.19 | 1164008.3195 | 176.5457 | 734.3116 | 0.98543
Model 17 | Htl | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ02 | ChlrCap | 162.5328 | 113095.9 | 18109.27 | 1086923.4123 | 165.7159 | 695.8342 | 1.0196
Model 17 | Htl | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ02 | ChlrCap | 161.267 | 111585.8 | 17821.7 | 1076688.515 | 161.7415 | 691.9321 | 1.0029
Model 17 | MBT | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ02 | ChlrCap | 321.5922 | 187092 | 23032.04 | 2195335.8441 | 266.0821 | 581.7679 | 0.82739
Model 17 | MBT | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ02 | ChlrCap | 311.943 | 161024.2 | 22850.61 | 1971048.5311 | 238.4954 | 516.1975 | 0.76455
Model 17 | MBT | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ02 | ChlrCap | 307.7235 | 158267 | 21971.37 | 1896257.1758 | 234.6342 | 514.3156 | 0.76248
Model 17 | MBT | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ02 | ChlrCap | 305.3705 | 154948.7 | 8169.578 | 1834262.7585 | 218.1116 | 507.4121 | 0.71425
Model 17 | MBT | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ02 | ChlrCap | 285.5302 | 145699.7 | 7364.584 | 1715363.6038 | 197.6903 | 510.2778 | 0.69236
Model 17 | Nrs | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ02 | ChlrCap | 105.7102 | 82130.64 | 17907.3 | 1445797.9614 | 178.6154 | 776.9414 | 1.6897
Model 17 | Nrs | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ02 | ChlrCap | 101.8806 | 60933.86 | 16429.56 | 1266315.6546 | 156.5479 | 598.0907 | 1.5366
Model 17 | Nrs | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ02 | ChlrCap | 100.7931 | 60509.72 | 16594.82 | 1240663.3977 | 155.0909 | 600.3361 | 1.5387
Model 17 | Nrs | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ02 | ChlrCap | 98.5594 | 53982.23 | 15159.05 | 1204991.0129 | 149.8683 | 547.7126 | 1.5206
Model 17 | Nrs | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ02 | ChlrCap | 100.1231 | 49677.4 | 14471.78 | 1169262.4093 | 138.594 | 496.1633 | 1.3842
Model 17 | OfL | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ02 | ChlrCap | 380.9968 | 221601.3 | 55718.27 | 1935047.0785 | 305.9097 | 581.6355 | 0.80292
Model 17 | OfL | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ02 | ChlrCap | 380.0078 | 209033.7 | 51998.26 | 1789441.9074 | 294.1691 | 550.0773 | 0.77411
Model 17 | OfL | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ02 | ChlrCap | 367.1977 | 207388.3 | 60554.43 | 1721076.5826 | 282.8128 | 564.7865 | 0.77019
Model 17 | OfL | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ02 | ChlrCap | 366.8677 | 192741.5 | 47311.21 | 1739996.095 | 278.9757 | 525.3706 | 0.76043
Model 17 | OfL | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ02 | ChlrCap | 355.431 | 183337.7 | 4563.705 | 1644697.6038 | 266.1479 | 515.818 | 0.7488
Model 17 | OfS | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ02 | ChlrCap | 23.8356 | 13479.6 | 1691.125 | 124838.0177 | 17.6176 | 565.5234 | 0.73913
Model 17 | OfS | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ02 | ChlrCap | 23.5463 | 13106.59 | 1577.193 | 117801.4715 | 16.8564 | 556.6313 | 0.71588
Model 17 | OfS | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ02 | ChlrCap | 23.1363 | 12997.15 | 1639.146 | 114643.9551 | 16.2357 | 561.764 | 0.70174
Model 17 | OfS | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ02 | ChlrCap | 21.2725 | 11264.2 | 1338.68 | 105871.377 | 14.6575 | 529.5204 | 0.68904
Model 17 | OfS | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ02 | ChlrCap | 20.6019 | 10695.44 | 1132.597 | 100804.5953 | 13.9303 | 519.1476 | 0.67617
Model 17 | Rt3 | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ02 | ChlrCap | 247.1868 | 161536.2 | 65293.9 | 1591712.6413 | 353.6107 | 653.4984 | 1.4305
Model 17 | Rt3 | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ02 | ChlrCap | 245.7843 | 154967.1 | 65224.45 | 1519723.4771 | 348.4143 | 630.5003 | 1.4176
Model 17 | Rt3 | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ02 | ChlrCap | 244.856 | 154826.1 | 65518.82 | 1518592.8218 | 348.0454 | 632.3149 | 1.4214
Model 17 | Rt3 | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ02 | ChlrCap | 235.4288 | 143793.9 | 57211.45 | 1400924.9965 | 323.2166 | 610.7744 | 1.3729
Model 17 | Rt3 | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ02 | ChlrCap | 224.1828 | 133148.4 | 43870.46 | 1316849.7362 | 298.7157 | 593.9277 | 1.3325
Model 17 | ECC | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ03 | ChlrCap | 509.1507 | 215448.1 | 47100.36 | 3118216.2122 | 542.9637 | 423.152 | 1.0664
Model 17 | ECC | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ03 | ChlrCap | 507.977 | 213566.3 | 46734.77 | 3057485.9226 | 540.2791 | 420.4251 | 1.0636
Model 17 | ECC | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ03 | ChlrCap | 506.7695 | 213495.6 | 46772.94 | 3054650.7198 | 539.5048 | 421.2874 | 1.0646
Model 17 | ECC | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ03 | ChlrCap | 456.682 | 197761.7 | 46357.55 | 2874624.3751 | 512.8874 | 433.0403 | 1.1231
Model 17 | ECC | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ03 | ChlrCap | 427.4718 | 186943.6 | 27423.67 | 2722001.0234 | 468.3752 | 437.3238 | 1.0957
Model 17 | ESe | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ03 | ChlrCap | 268.731 | 103224.2 | 13741.71 | 1381997.0666 | 179.5118 | 384.1172 | 0.668
Model 17 | ESe | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ03 | ChlrCap | 265.0458 | 87701.74 | 13839.75 | 1263397.4059 | 158.3039 | 330.8927 | 0.59727
Model 17 | ESe | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ03 | ChlrCap | 264.0397 | 87582.84 | 13838.28 | 1259403.5736 | 158.0223 | 331.7033 | 0.59848
Model 17 | ESe | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ03 | ChlrCap | 235.9863 | 66606.7 | 4932.655 | 1186725.2791 | 127.8831 | 282.2481 | 0.54191
Model 17 | ESe | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ03 | ChlrCap | 220.4452 | 62453.66 | 4248.156 | 1134621.5635 | 120.8761 | 283.307 | 0.54833
Model 17 | EUn | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ03 | ChlrCap | 1824.8797 | 685124.8 | 217744.7 | 10068917.9836 | 1874.8837 | 375.4356 | 1.0274
Model 17 | EUn | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ03 | ChlrCap | 1815.8227 | 670530.6 | 207240.5 | 9818600.8136 | 1869.3387 | 369.271 | 1.0295
Model 17 | EUn | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ03 | ChlrCap | 1794.5313 | 673179.6 | 207276.1 | 9657231.3447 | 1864.9082 | 375.1284 | 1.0392
Model 17 | EUn | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ03 | ChlrCap | 1622.691 | 601183.6 | 222947.9 | 8774555.0176 | 1760.5665 | 370.4856 | 1.085
Model 17 | EUn | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ03 | ChlrCap | 1524.3833 | 560036.4 | 176815.4 | 8303891.0188 | 1604.3312 | 367.3855 | 1.0524
Model 17 | Hsp | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ03 | ChlrCap | 647.9992 | 150368.1 | 13571.25 | 3917485.9941 | 534.1414 | 232.0498 | 0.82429
Model 17 | Hsp | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ03 | ChlrCap | 647.6155 | 149746.3 | 13567.33 | 3897983.1946 | 533.3107 | 231.2272 | 0.8235
Model 17 | Hsp | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ03 | ChlrCap | 647.2195 | 149688.7 | 13567.32 | 3894247.6026 | 533.1397 | 231.2797 | 0.82374
Model 17 | Hsp | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ03 | ChlrCap | 581.0735 | 131423.4 | 9872.73 | 3799983.1536 | 503.9637 | 226.1735 | 0.8673
Model 17 | Hsp | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ03 | ChlrCap | 577.2075 | 123511 | 9032.592 | 3631996.2544 | 456.3034 | 213.9802 | 0.79054
Model 17 | Htl | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ03 | ChlrCap | 159.5386 | 108338.8 | 20436.72 | 1338047.1111 | 156.8002 | 679.0756 | 0.98284
Model 17 | Htl | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ03 | ChlrCap | 152.7626 | 93122.83 | 17017.43 | 1058903.9156 | 144.3915 | 609.5918 | 0.9452
Model 17 | Htl | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ03 | ChlrCap | 147.5439 | 94231.47 | 17759.04 | 1011822.9334 | 141.6391 | 638.6675 | 0.95998
Model 17 | Htl | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ03 | ChlrCap | 127.486 | 75177.98 | 15206.1 | 942514.0721 | 133.1568 | 589.6962 | 1.0445
Model 17 | Htl | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ03 | ChlrCap | 126.2083 | 73715.44 | 14930.59 | 931512.7775 | 129.2744 | 584.0774 | 1.0243
Model 17 | MBT | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ03 | ChlrCap | 259.136 | 117211.5 | 20682.01 | 2080513.6061 | 216.4203 | 452.3165 | 0.83516
Model 17 | MBT | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ03 | ChlrCap | 252.9723 | 112322 | 21127.99 | 1885265.2474 | 202.5584 | 444.009 | 0.80071
Model 17 | MBT | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ03 | ChlrCap | 244.9833 | 112883.8 | 21740.42 | 1830245.5592 | 199.4763 | 460.7815 | 0.81424
Model 17 | MBT | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ03 | ChlrCap | 237.1992 | 107107.3 | 6608.244 | 1755516.2298 | 178.0151 | 451.5501 | 0.75049
Model 17 | MBT | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ03 | ChlrCap | 222.3173 | 102026.6 | 6173.849 | 1640741.51 | 160.7414 | 458.9233 | 0.72303
Model 17 | Nrs | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ03 | ChlrCap | 95.3464 | 56740.62 | 15922 | 1319354.0749 | 155.2525 | 595.1 | 1.6283
Model 17 | Nrs | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ03 | ChlrCap | 90.3487 | 40715 | 13893.3 | 1141480.8687 | 138.817 | 450.6428 | 1.5365
Model 17 | Nrs | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ03 | ChlrCap | 89.974 | 40736.86 | 13951.68 | 1137444.5855 | 138.7005 | 452.7627 | 1.5416
Model 17 | Nrs | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ03 | ChlrCap | 79.6068 | 26992.39 | 10161.75 | 1104461.2356 | 129.2247 | 339.0713 | 1.6233
Model 17 | Nrs | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ03 | ChlrCap | 79.9441 | 24087.51 | 9187.981 | 1071584.2525 | 118.1157 | 301.3045 | 1.4775
Model 17 | OfL | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ03 | ChlrCap | 328.7545 | 151292.6 | 33205.82 | 1868651.9203 | 270.2539 | 460.1993 | 0.82205
Model 17 | OfL | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ03 | ChlrCap | 336.8908 | 142907.4 | 30409.72 | 1737219.8417 | 257.264 | 424.195 | 0.76364
Model 17 | OfL | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ03 | ChlrCap | 329.1995 | 142904.5 | 33921.33 | 1680602.1301 | 253.03 | 434.097 | 0.76862
Model 17 | OfL | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ03 | ChlrCap | 303.0842 | 127831.4 | 39931.14 | 1628516.0539 | 237.439 | 421.7687 | 0.78341
Model 17 | OfL | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ03 | ChlrCap | 290.8142 | 120406.6 | 3185.337 | 1530330.7397 | 224.9445 | 414.0328 | 0.7735
Model 17 | OfS | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ03 | ChlrCap | 22.1567 | 9179.929 | 963.34 | 123657.6517 | 14.6237 | 414.3181 | 0.66001
Model 17 | OfS | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ03 | ChlrCap | 22.0175 | 8708.896 | 886.4683 | 116578.7959 | 13.8217 | 395.545 | 0.62776
Model 17 | OfS | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ03 | ChlrCap | 21.8341 | 8648.801 | 882.0974 | 115766.5778 | 13.7042 | 396.1139 | 0.62765
Model 17 | OfS | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ03 | ChlrCap | 18.6829 | 7192.618 | 762.4254 | 97893.4827 | 11.9922 | 384.9842 | 0.64188
Model 17 | OfS | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ03 | ChlrCap | 17.9189 | 6703.871 | 670.6345 | 92712.1582 | 11.1239 | 374.1236 | 0.62079
Model 17 | Rt3 | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ03 | ChlrCap | 200.361 | 100819 | 59987.24 | 1486247.8605 | 316.1847 | 503.1867 | 1.5781
Model 17 | Rt3 | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ03 | ChlrCap | 199.5548 | 97083.5 | 59782.48 | 1419510.8769 | 309.1048 | 486.5004 | 1.549
Model 17 | Rt3 | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ03 | ChlrCap | 199.4083 | 97256.38 | 60047.32 | 1418974.5217 | 309.037 | 487.7248 | 1.5498
Model 17 | Rt3 | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ03 | ChlrCap | 188.1127 | 86447.09 | 52151.1 | 1297817.075 | 281.7705 | 459.5495 | 1.4979
Model 17 | Rt3 | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ03 | ChlrCap | 178.2805 | 77769.61 | 39764.66 | 1207674.0317 | 258.4076 | 436.2205 | 1.4494
Model 17 | ECC | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ04 | ChlrCap | 650.4283 | 432080.8 | 83732.7 | 3237383.2966 | 730.8073 | 664.3019 | 1.1236
Model 17 | ECC | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ04 | ChlrCap | 648.8233 | 427888.8 | 83135.55 | 3171683.034 | 726.9827 | 659.4843 | 1.1205
Model 17 | ECC | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ04 | ChlrCap | 647.1595 | 427172.8 | 82936.42 | 3167837.3447 | 725.1021 | 660.0734 | 1.1204
Model 17 | ECC | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ04 | ChlrCap | 587.8033 | 388954.8 | 73765.58 | 2961170.3587 | 694.0147 | 661.7091 | 1.1807
Model 17 | ECC | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ04 | ChlrCap | 554.5638 | 371752.3 | 56954.31 | 2771433.5123 | 641.9798 | 670.3508 | 1.1576
Model 17 | ESe | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ04 | ChlrCap | 337.8123 | 208153.9 | 26776.76 | 1473286.9437 | 267.5061 | 616.1821 | 0.79188
Model 17 | ESe | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ04 | ChlrCap | 333.9507 | 177929.8 | 26797.51 | 1317744.5897 | 237.1486 | 532.8026 | 0.71013
Model 17 | ESe | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ04 | ChlrCap | 332.8495 | 177503.3 | 26741.47 | 1313723.6307 | 236.4939 | 533.284 | 0.71051
Model 17 | ESe | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ04 | ChlrCap | 300.5353 | 139606.3 | 14079.45 | 1206006.0671 | 200.7798 | 464.5254 | 0.66807
Model 17 | ESe | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ04 | ChlrCap | 285.7465 | 131844.2 | 13950.85 | 1137153.9027 | 187.186 | 461.4027 | 0.65508
Model 17 | EUn | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ04 | ChlrCap | 2256.9483 | 1412588 | 384527.7 | 10354121.3294 | 2543.7427 | 625.8841 | 1.1271
Model 17 | EUn | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ04 | ChlrCap | 2245.425 | 1392284 | 374135.2 | 10095315.2509 | 2535.4527 | 620.0537 | 1.1292
Model 17 | EUn | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ04 | ChlrCap | 2217.3363 | 1386890 | 372483.6 | 9948837.6952 | 2520.7797 | 625.4757 | 1.1369
Model 17 | EUn | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ04 | ChlrCap | 2015.395 | 1215240 | 341670.5 | 8935570.3517 | 2306.2063 | 602.9786 | 1.1443
Model 17 | EUn | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ04 | ChlrCap | 1919.6637 | 1154084 | 299219.3 | 8427137.9215 | 2157.3719 | 601.1907 | 1.1238
Model 17 | Hsp | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ04 | ChlrCap | 779.1722 | 346299.9 | 29434.04 | 4100782.9519 | 658.3701 | 444.4459 | 0.84496
Model 17 | Hsp | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ04 | ChlrCap | 778.4675 | 345001.4 | 29406.78 | 4077352.0035 | 657.1664 | 443.1802 | 0.84418
Model 17 | Hsp | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ04 | ChlrCap | 780.4422 | 344879.3 | 29406.62 | 4075114.9402 | 656.7003 | 441.9024 | 0.84145
Model 17 | Hsp | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ04 | ChlrCap | 797.7558 | 306148.1 | 22087.41 | 3944246.0223 | 631.391 | 383.7617 | 0.79146
Model 17 | Hsp | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ04 | ChlrCap | 809.9295 | 287146.5 | 21211.66 | 3743340.3623 | 580.7137 | 354.5327 | 0.71699
Model 17 | Htl | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ04 | ChlrCap | 205.5478 | 192133.4 | 29342.52 | 1422237.8845 | 225.1789 | 934.7381 | 1.0955
Model 17 | Htl | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ04 | ChlrCap | 197.8562 | 171586.5 | 25406.2 | 1118036.2947 | 208.7374 | 867.2285 | 1.055
Model 17 | Htl | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ04 | ChlrCap | 190.3282 | 169691.3 | 25681.04 | 1069571.2198 | 204.244 | 891.5722 | 1.0731
Model 17 | Htl | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ04 | ChlrCap | 169.797 | 141592 | 22878.89 | 992167.8506 | 189.3061 | 833.8899 | 1.1149
Model 17 | Htl | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ04 | ChlrCap | 168.1872 | 139859.1 | 22430.06 | 979946.573 | 185.3545 | 831.5682 | 1.1021
Model 17 | MBT | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ04 | ChlrCap | 322.3633 | 243627.1 | 32766.01 | 2225061.9379 | 293.8981 | 755.7531 | 0.9117
Model 17 | MBT | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ04 | ChlrCap | 314.02 | 211549 | 32420.17 | 1983658.2954 | 262.6643 | 673.68 | 0.83646
Model 17 | MBT | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ04 | ChlrCap | 299.6248 | 207581.9 | 32137.84 | 1917842.4127 | 254.0571 | 692.8061 | 0.84792
Model 17 | MBT | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ04 | ChlrCap | 297.989 | 191020.1 | 11034.52 | 1822157.7128 | 233.1273 | 641.0307 | 0.78234
Model 17 | MBT | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ04 | ChlrCap | 278.5123 | 179856.5 | 9664.832 | 1696517.9215 | 216.292 | 645.7757 | 0.7766
Model 17 | Nrs | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ04 | ChlrCap | 123.1325 | 123468.5 | 26261.91 | 1373365.4318 | 206.0325 | 1002.7288 | 1.6733
Model 17 | Nrs | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ04 | ChlrCap | 117.7474 | 94025.31 | 23761.27 | 1154853.6377 | 182.084 | 798.5338 | 1.5464
Model 17 | Nrs | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ04 | ChlrCap | 114.654 | 93781.24 | 24029.19 | 1128705.9982 | 180.2532 | 817.9496 | 1.5721
Model 17 | Nrs | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ04 | ChlrCap | 97.6834 | 72107.63 | 20781.66 | 1084055.8774 | 166.0743 | 738.1767 | 1.7001
Model 17 | Nrs | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ04 | ChlrCap | 96.34 | 66343.7 | 19800.91 | 1040996.5481 | 154.8905 | 688.6414 | 1.6077
Model 17 | OfL | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ04 | ChlrCap | 390.6946 | 274161.3 | 66210.09 | 2019778.6964 | 341.7533 | 701.7279 | 0.87473
Model 17 | OfL | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ04 | ChlrCap | 389.5658 | 261150.2 | 62661.86 | 1880852.381 | 329.2884 | 670.3622 | 0.84527
Model 17 | OfL | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ04 | ChlrCap | 376.0428 | 256707.3 | 68863.76 | 1808540.9637 | 309.9552 | 682.6544 | 0.82426
Model 17 | OfL | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ04 | ChlrCap | 356.0055 | 232129.7 | 67917.67 | 1741603.2896 | 293.2263 | 652.0396 | 0.82366
Model 17 | OfL | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ04 | ChlrCap | 355.2392 | 222436.6 | 11490.07 | 1645762.9062 | 279.8213 | 626.1601 | 0.7877
Model 17 | OfS | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ04 | ChlrCap | 26.9893 | 17294.58 | 2255.009 | 131434.784 | 20.089 | 640.793 | 0.74433
Model 17 | OfS | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ04 | ChlrCap | 26.8214 | 16925.44 | 2132.048 | 123868.9959 | 19.3883 | 631.0412 | 0.72287
Model 17 | OfS | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ04 | ChlrCap | 26.1455 | 16768.66 | 2182.958 | 120527.8929 | 19.0557 | 641.3595 | 0.72883
Model 17 | OfS | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ04 | ChlrCap | 22.0493 | 13745.84 | 2184.425 | 102295.6621 | 16.0021 | 623.4134 | 0.72574
Model 17 | OfS | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ04 | ChlrCap | 21.4147 | 12831.82 | 1655.161 | 96743.4179 | 14.9973 | 599.2055 | 0.70032
Model 17 | Rt3 | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ04 | ChlrCap | 250.458 | 203957.4 | 80787.95 | 1592904.9543 | 385.4469 | 814.3377 | 1.539
Model 17 | Rt3 | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ04 | ChlrCap | 249.161 | 200647.4 | 80850.2 | 1526959.2626 | 390.9121 | 805.2922 | 1.5689
Model 17 | Rt3 | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ04 | ChlrCap | 248.2993 | 200327 | 81050.85 | 1526030.286 | 390.3461 | 806.7964 | 1.5721
Model 17 | Rt3 | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ04 | ChlrCap | 237.1232 | 184383.2 | 71092.4 | 1392074.9144 | 361.6135 | 777.5841 | 1.525
Model 17 | Rt3 | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ04 | ChlrCap | 226.1252 | 171258.7 | 56914.31 | 1293429.068 | 335.8115 | 757.3624 | 1.4851
Model 17 | ECC | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ05 | ChlrCap | 447.8013 | 260531.2 | 53760.32 | 3087181.3517 | 450.559 | 581.8009 | 1.0062
Model 17 | ECC | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ05 | ChlrCap | 446.702 | 258670 | 53381.3 | 3030901.0809 | 447.4743 | 579.0661 | 1.0017
Model 17 | ECC | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ05 | ChlrCap | 446.6988 | 258686.9 | 53286.64 | 3031242.8312 | 447.2519 | 579.1081 | 1.0012
Model 17 | ECC | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ05 | ChlrCap | 399.244 | 238187.4 | 52631.85 | 2858135.3646 | 433.1546 | 596.5961 | 1.0849
Model 17 | ECC | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ05 | ChlrCap | 371.7423 | 226185.6 | 31668.37 | 2700829.0152 | 387.8415 | 608.4472 | 1.0433
Model 17 | ESe | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ05 | ChlrCap | 236.3515 | 130941.3 | 16354.22 | 1366022.8725 | 135.8185 | 554.0109 | 0.57465
Model 17 | ESe | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ05 | ChlrCap | 231.9907 | 112458.8 | 16301.5 | 1244622.8129 | 122.8661 | 484.7557 | 0.52962
Model 17 | ESe | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ05 | ChlrCap | 231.9883 | 112464.3 | 16291.51 | 1244837.8712 | 122.8455 | 484.7843 | 0.52953
Model 17 | ESe | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ05 | ChlrCap | 204.1847 | 88172.13 | 6274.5 | 1176936.7694 | 108.6315 | 431.8254 | 0.53203
Model 17 | ESe | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ05 | ChlrCap | 186.52 | 82939.11 | 5620.689 | 1111658.8955 | 99.6977 | 444.666 | 0.53451
Model 17 | EUn | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ05 | ChlrCap | 1621.1973 | 838322.2 | 252931 | 10000006.2016 | 1576.8411 | 517.1007 | 0.97264
Model 17 | EUn | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ05 | ChlrCap | 1613.4453 | 822510.6 | 242438.3 | 9750770.8066 | 1573.3637 | 509.7852 | 0.97516
Model 17 | EUn | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ05 | ChlrCap | 1604.207 | 823469.6 | 242208.9 | 9634087.2896 | 1571.1665 | 513.3188 | 0.9794
Model 17 | EUn | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ05 | ChlrCap | 1441.5957 | 730843.6 | 249285.9 | 8804090.8945 | 1496.3041 | 506.9685 | 1.0379
Model 17 | EUn | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ05 | ChlrCap | 1337.6327 | 679836.2 | 192145.1 | 8241372.4631 | 1344.9978 | 508.2383 | 1.0055
Model 17 | Hsp | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ05 | ChlrCap | 631.9267 | 173555.5 | 14304.9 | 3969042.1747 | 474.0026 | 274.645 | 0.75009
Model 17 | Hsp | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ05 | ChlrCap | 631.3238 | 172993.9 | 14290.42 | 3951354.7186 | 473.5383 | 274.0177 | 0.75007
Model 17 | Hsp | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ05 | ChlrCap | 631.3238 | 172993.9 | 14290.42 | 3951354.7186 | 473.5383 | 274.0177 | 0.75007
Model 17 | Hsp | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ05 | ChlrCap | 647.081 | 152650.5 | 9726.686 | 3852730.0891 | 460.2355 | 235.9063 | 0.71125
Model 17 | Hsp | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ05 | ChlrCap | 642.7437 | 143127.6 | 8870.13 | 3678606.1946 | 412.2643 | 222.6822 | 0.64141
Model 17 | Htl | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ05 | ChlrCap | 139.7557 | 120843.2 | 22571.93 | 1350366.9912 | 129.9744 | 864.6744 | 0.93001
Model 17 | Htl | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ05 | ChlrCap | 133.036 | 104466.2 | 19173.98 | 1067169.9516 | 117.7445 | 785.2476 | 0.88506
Model 17 | Htl | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ05 | ChlrCap | 129.0901 | 105209.6 | 19754.95 | 1020630.6587 | 117.0914 | 815.0089 | 0.90705
Model 17 | Htl | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ05 | ChlrCap | 108.9339 | 82762.45 | 16820.95 | 947205.2354 | 110.0641 | 759.749 | 1.0104
Model 17 | Htl | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ05 | ChlrCap | 107.2058 | 81264.02 | 16574.62 | 936015.171 | 106.6924 | 758.0185 | 0.99521
Model 17 | MBT | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ05 | ChlrCap | 250.9265 | 157336.6 | 24725.91 | 2131784.177 | 194.3301 | 627.0227 | 0.77445
Model 17 | MBT | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ05 | ChlrCap | 243.1638 | 137714.5 | 24911.02 | 1917940.5733 | 177.3023 | 566.3445 | 0.72915
Model 17 | MBT | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ05 | ChlrCap | 240.6907 | 137237.5 | 24998.31 | 1862693.0856 | 174.9655 | 570.1821 | 0.72693
Model 17 | MBT | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ05 | ChlrCap | 238.0023 | 128282.3 | 7610.977 | 1778729.0821 | 159.1441 | 538.996 | 0.66867
Model 17 | MBT | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ05 | ChlrCap | 214.5538 | 123114.2 | 7116.193 | 1657467.6589 | 145.0383 | 573.815 | 0.676
Model 17 | Nrs | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ05 | ChlrCap | 83.5064 | 67305.85 | 18438.15 | 1346871.2999 | 137.2931 | 805.9965 | 1.6441
Model 17 | Nrs | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ05 | ChlrCap | 81.0218 | 48564.01 | 16350.3 | 1164720.4982 | 121.6149 | 599.3946 | 1.501
Model 17 | Nrs | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ05 | ChlrCap | 81.0218 | 48564.01 | 16350.3 | 1164720.4982 | 121.6149 | 599.3946 | 1.501
Model 17 | Nrs | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ05 | ChlrCap | 77.6435 | 32741.91 | 12490.44 | 1131775.6155 | 114.9812 | 421.6956 | 1.4809
Model 17 | Nrs | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ05 | ChlrCap | 77.4103 | 29120.66 | 11478.85 | 1092981.2927 | 104.6896 | 376.186 | 1.3524
Model 17 | OfL | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ05 | ChlrCap | 334.4605 | 188560.3 | 36096.56 | 1898525.7081 | 235.9755 | 563.7745 | 0.70554
Model 17 | OfL | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ05 | ChlrCap | 333.5467 | 178694 | 32493.44 | 1760630.9414 | 226.5073 | 535.7391 | 0.67909
Model 17 | OfL | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ05 | ChlrCap | 325.9472 | 178320.5 | 40287.81 | 1695741.483 | 222.8669 | 547.0841 | 0.68375
Model 17 | OfL | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ05 | ChlrCap | 299.6537 | 160401.8 | 42852.5 | 1639661.2849 | 214.4081 | 535.2906 | 0.71552
Model 17 | OfL | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ05 | ChlrCap | 286.4257 | 151213.4 | 2898.552 | 1537850.3189 | 202.3602 | 527.9324 | 0.7065
Model 17 | OfS | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ05 | ChlrCap | 20.0139 | 12265.82 | 1051.739 | 125724.2894 | 12.1197 | 612.8638 | 0.60556
Model 17 | OfS | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ05 | ChlrCap | 19.4836 | 10879.8 | 997.5093 | 117536.4164 | 11.4047 | 558.4079 | 0.58535
Model 17 | OfS | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ05 | ChlrCap | 19.3847 | 10809.18 | 991.8775 | 116757.7661 | 11.3085 | 557.614 | 0.58337
Model 17 | OfS | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ05 | ChlrCap | 16.6051 | 8885.562 | 787.8894 | 98104.4825 | 10.4348 | 535.1107 | 0.62841
Model 17 | OfS | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ05 | ChlrCap | 15.8386 | 8332.646 | 689.386 | 92936.0932 | 9.7228 | 526.0963 | 0.61387
Model 17 | Rt3 | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ05 | ChlrCap | 191.4887 | 118631.7 | 67221.8 | 1495970.0715 | 280.8125 | 619.5233 | 1.4665
Model 17 | Rt3 | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ05 | ChlrCap | 190.3688 | 114021.5 | 67250.45 | 1424499.2016 | 271.6387 | 598.9505 | 1.4269
Model 17 | Rt3 | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ05 | ChlrCap | 190.3688 | 114021.5 | 67250.45 | 1424499.2016 | 271.6387 | 598.9505 | 1.4269
Model 17 | Rt3 | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ05 | ChlrCap | 179.1423 | 102596.9 | 58295.68 | 1296622.8335 | 247.9167 | 572.7116 | 1.3839
Model 17 | Rt3 | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ05 | ChlrCap | 167.5133 | 92019.2 | 43839.07 | 1194755.524 | 223.6271 | 549.3246 | 1.335
Model 17 | ECC | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ06 | ChlrCap | 690.1455 | 555807.2 | 97022.34 | 3066700.4947 | 426.7169 | 805.3479 | 0.6183
Model 17 | ECC | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ06 | ChlrCap | 690.1455 | 552445.2 | 96501.79 | 3016845.4115 | 425.8292 | 800.4764 | 0.61701
Model 17 | ECC | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ06 | ChlrCap | 690.1378 | 552397 | 96455.38 | 3016624.9977 | 425.6561 | 800.4155 | 0.61677
Model 17 | ECC | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ06 | ChlrCap | 634.5987 | 505840.4 | 88576.3 | 2828882.6354 | 383.3936 | 797.1028 | 0.60415
Model 17 | ECC | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ06 | ChlrCap | 598.1787 | 479705.7 | 69682.76 | 2599015.0246 | 346.7229 | 801.9438 | 0.57963
Model 17 | ESe | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ06 | ChlrCap | 377.0638 | 261644.1 | 29755.34 | 1380514.3822 | 111.0148 | 693.8987 | 0.29442
Model 17 | ESe | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ06 | ChlrCap | 372.102 | 224515.5 | 29978.27 | 1200960.2516 | 86.4098 | 603.3708 | 0.23222
Model 17 | ESe | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ06 | ChlrCap | 372.0698 | 224519.7 | 29920.62 | 1200792.3802 | 86.3809 | 603.4343 | 0.23216
Model 17 | ESe | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ06 | ChlrCap | 342.9848 | 174186.4 | 12681.8 | 1088650.04 | 63.5069 | 507.8545 | 0.18516
Model 17 | ESe | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ06 | ChlrCap | 322.4653 | 162783.6 | 12078.88 | 1000869.8978 | 54.2875 | 504.8096 | 0.16835
Model 17 | EUn | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ06 | ChlrCap | 2324.592 | 1665721 | 431399.3 | 9410024.3904 | 1701.9544 | 716.5649 | 0.73215
Model 17 | EUn | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ06 | ChlrCap | 2324.592 | 1646501 | 422931.9 | 9219526.5909 | 1685.6392 | 708.2968 | 0.72513
Model 17 | EUn | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ06 | ChlrCap | 2311.588 | 1647302 | 422293.6 | 9161822.728 | 1682.0796 | 712.6279 | 0.72767
Model 17 | EUn | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ06 | ChlrCap | 2120.4177 | 1472342 | 397751.2 | 8343292.5592 | 1519.075 | 694.3641 | 0.7164
Model 17 | EUn | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ06 | ChlrCap | 2007.927 | 1383992 | 343350.1 | 7709974.6143 | 1406.8714 | 689.2641 | 0.70066
Model 17 | Hsp | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ06 | ChlrCap | 819.8385 | 442222.4 | 39939.26 | 3981630.1899 | 593.3509 | 539.4018 | 0.72374
Model 17 | Hsp | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ06 | ChlrCap | 819.8385 | 440825.4 | 39930.06 | 3966060.4936 | 592.7759 | 537.6979 | 0.72304
Model 17 | Hsp | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ06 | ChlrCap | 819.8385 | 440825.4 | 39930.06 | 3966060.4936 | 592.7759 | 537.6979 | 0.72304
Model 17 | Hsp | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ06 | ChlrCap | 830.9227 | 386545.1 | 29670.66 | 3820567.2896 | 555.5194 | 465.1998 | 0.66856
Model 17 | Hsp | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ06 | ChlrCap | 839.0405 | 363471.8 | 28659.4 | 3589825.3857 | 499.0899 | 433.1994 | 0.59483
Model 17 | Htl | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ06 | ChlrCap | 200.1557 | 221597.5 | 33031.31 | 1326827.0069 | 171.7681 | 1107.1258 | 0.85817
Model 17 | Htl | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ06 | ChlrCap | 193.5773 | 198083.8 | 28467.88 | 1003843.272 | 157.3709 | 1023.2799 | 0.81296
Model 17 | Htl | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ06 | ChlrCap | 187.4983 | 197408.1 | 28973.84 | 979680.2117 | 156.264 | 1052.8526 | 0.83342
Model 17 | Htl | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ06 | ChlrCap | 162.3686 | 161785.9 | 25886.13 | 898355.4497 | 142.0775 | 996.4115 | 0.87503
Model 17 | Htl | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ06 | ChlrCap | 160.0203 | 159046.2 | 25253.29 | 882505.3392 | 137.7221 | 993.913 | 0.86065
Model 17 | MBT | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ06 | ChlrCap | 347.5739 | 291815.7 | 40691.2 | 2235649.5698 | 297.5417 | 839.5788 | 0.85605
Model 17 | MBT | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ06 | ChlrCap | 345.009 | 276718.9 | 40593.38 | 2007093.4572 | 276.8183 | 802.0628 | 0.80235
Model 17 | MBT | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ06 | ChlrCap | 339.1993 | 274849.7 | 40555.73 | 1975876.1032 | 274.5252 | 810.2896 | 0.80933
Model 17 | MBT | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ06 | ChlrCap | 328.0163 | 251644.4 | 13904.48 | 1868834.4267 | 253.0405 | 767.1703 | 0.77143
Model 17 | MBT | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ06 | ChlrCap | 301.4822 | 239003.4 | 11789.64 | 1724302.4103 | 229.3254 | 792.7613 | 0.76066
Model 17 | Nrs | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ06 | ChlrCap | 121.2249 | 144924.4 | 33128.51 | 1281325.4769 | 164.1665 | 1195.5007 | 1.3542
Model 17 | Nrs | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ06 | ChlrCap | 116.4832 | 109414.5 | 29710.42 | 1045393.858 | 145.441 | 939.3158 | 1.2486
Model 17 | Nrs | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ06 | ChlrCap | 116.4832 | 109414.5 | 29710.42 | 1045393.858 | 145.441 | 939.3158 | 1.2486
Model 17 | Nrs | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ06 | ChlrCap | 101.5529 | 82462.34 | 24998.17 | 1002543.57 | 134.7819 | 812.0136 | 1.3272
Model 17 | Nrs | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ06 | ChlrCap | 102.7199 | 74996.38 | 23860.08 | 950392.1816 | 122.8155 | 730.1058 | 1.1956
Model 17 | OfL | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ06 | ChlrCap | 403.3772 | 347395.5 | 81745.6 | 2028308.4525 | 327.4647 | 861.2176 | 0.81181
Model 17 | OfL | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ06 | ChlrCap | 402.7988 | 328162 | 78675.6 | 1871874.2591 | 311.5719 | 814.7044 | 0.77352
Model 17 | OfL | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ06 | ChlrCap | 397.1907 | 325931.4 | 81981.49 | 1833375.8429 | 307.3185 | 820.5918 | 0.77373
Model 17 | OfL | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ06 | ChlrCap | 375.7237 | 298382.3 | 77022.86 | 1770016.9273 | 292.6667 | 794.1536 | 0.77894
Model 17 | OfL | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ06 | ChlrCap | 360.4377 | 284443.3 | 31673.83 | 1653558.2145 | 271.5373 | 789.1609 | 0.75335
Model 17 | OfS | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ06 | ChlrCap | 27.2141 | 20698.5 | 2015.504 | 124804.9546 | 17.8459 | 760.58 | 0.65576
Model 17 | OfS | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ06 | ChlrCap | 27.4273 | 20235.4 | 1844.878 | 116503.9562 | 17.1187 | 737.7825 | 0.62415
Model 17 | OfS | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ06 | ChlrCap | 27.3397 | 20133.49 | 1842.163 | 115647.3162 | 16.9771 | 736.4198 | 0.62097
Model 17 | OfS | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ06 | ChlrCap | 23.3383 | 16959.33 | 2159.434 | 99818.2297 | 15.0513 | 726.674 | 0.64492
Model 17 | OfS | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ06 | ChlrCap | 22.3434 | 16111.36 | 1610.047 | 93968.9608 | 13.9964 | 721.0789 | 0.62642
Model 17 | Rt3 | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ06 | ChlrCap | 262.2133 | 250311.1 | 91536.98 | 1603635.3277 | 348.9829 | 954.6086 | 1.3309
Model 17 | Rt3 | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ06 | ChlrCap | 261.834 | 242033.4 | 91407.7 | 1535959.837 | 336.8676 | 924.3773 | 1.2866
Model 17 | Rt3 | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ06 | ChlrCap | 261.834 | 242033.4 | 91407.7 | 1535959.837 | 336.8676 | 924.3773 | 1.2866
Model 17 | Rt3 | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ06 | ChlrCap | 249.733 | 223683.9 | 79644.72 | 1389316.602 | 313.2843 | 895.6922 | 1.2545
Model 17 | Rt3 | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ06 | ChlrCap | 237.0563 | 205998.2 | 62664.83 | 1265608.3869 | 285.2862 | 868.9842 | 1.2035
Model 17 | ECC | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ07 | ChlrCap | 647.4993 | 462697.1 | 95358.03 | 2867734.898 | 559.3707 | 714.5909 | 0.86389
Model 17 | ECC | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ07 | ChlrCap | 647.4993 | 460544.5 | 94965.87 | 2831760.0844 | 558.4817 | 711.2664 | 0.86252
Model 17 | ECC | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ07 | ChlrCap | 645.558 | 460095.1 | 94799.3 | 2829855.3857 | 557.8653 | 712.7092 | 0.86416
Model 17 | ECC | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ07 | ChlrCap | 594.6627 | 421455.2 | 91313.16 | 2682696.7163 | 530.743 | 708.7299 | 0.89251
Model 17 | ECC | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ07 | ChlrCap | 563.0487 | 397944.7 | 71795.38 | 2451651.2943 | 479.1391 | 706.7679 | 0.85097
Model 17 | ESe | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ07 | ChlrCap | 359.7787 | 215363.8 | 27467.33 | 1291251.0633 | 177.4361 | 598.6008 | 0.49318
Model 17 | ESe | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ07 | ChlrCap | 355.0423 | 181682.2 | 27696.02 | 1113363.7087 | 152.7854 | 511.7198 | 0.43033
Model 17 | ESe | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ07 | ChlrCap | 353.4058 | 181426.5 | 27604.4 | 1110969.7728 | 152.5903 | 513.3659 | 0.43177
Model 17 | ESe | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ07 | ChlrCap | 324.8455 | 139932.4 | 12495.9 | 1011389.727 | 127.1486 | 430.766 | 0.39141
Model 17 | ESe | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ07 | ChlrCap | 305.3152 | 130689.4 | 11567.09 | 927334.2285 | 118.3614 | 428.0475 | 0.38767
Model 17 | EUn | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ07 | ChlrCap | 2258.639 | 1344152 | 396112.2 | 8778105.9437 | 1889.3676 | 595.1159 | 0.83651
Model 17 | EUn | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ07 | ChlrCap | 2258.639 | 1330773 | 387804.8 | 8622117.4021 | 1886.4377 | 589.1924 | 0.83521
Model 17 | EUn | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ07 | ChlrCap | 2235.6347 | 1330625 | 386970 | 8546163.6448 | 1883.2653 | 595.1889 | 0.84239
Model 17 | EUn | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ07 | ChlrCap | 2054.759 | 1186497 | 381085.3 | 7852879.3787 | 1794.0552 | 577.4385 | 0.87312
Model 17 | EUn | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ07 | ChlrCap | 1946.593 | 1109263 | 322748.2 | 7231889.8593 | 1627.7461 | 569.8484 | 0.8362
Model 17 | Hsp | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ07 | ChlrCap | 832.1303 | 379846.2 | 41402.62 | 3851931.0141 | 553.7667 | 456.4745 | 0.66548
Model 17 | Hsp | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ07 | ChlrCap | 832.1303 | 378848.6 | 41373.71 | 3836113.8242 | 553.1793 | 455.2756 | 0.66477
Model 17 | Hsp | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ07 | ChlrCap | 831.5077 | 378602.8 | 41373.62 | 3835194.2661 | 553.0363 | 455.3208 | 0.6651
Model 17 | Hsp | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ07 | ChlrCap | 852.4405 | 337804.9 | 31718.57 | 3711429.9824 | 523.7993 | 396.2797 | 0.61447
Model 17 | Hsp | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ07 | ChlrCap | 869.8048 | 318843.8 | 30140.59 | 3478733.449 | 471.9829 | 366.5694 | 0.54263
Model 17 | Htl | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ07 | ChlrCap | 184.6582 | 190782.3 | 31376.22 | 1237834.0913 | 157.5703 | 1033.1647 | 0.85331
Model 17 | Htl | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ07 | ChlrCap | 178.6828 | 169615.7 | 27007.52 | 933506.4266 | 145.0119 | 949.2557 | 0.81156
Model 17 | Htl | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ07 | ChlrCap | 172.9687 | 169474.8 | 27573.45 | 913642.309 | 143.8804 | 979.8006 | 0.83183
Model 17 | Htl | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ07 | ChlrCap | 148.3056 | 137706.9 | 25157.17 | 845225.0774 | 133.5187 | 928.5346 | 0.90029
Model 17 | Htl | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ07 | ChlrCap | 146.3167 | 134575.5 | 24528.74 | 827447.9334 | 128.8774 | 919.7547 | 0.88081
Model 17 | MBT | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ07 | ChlrCap | 339.01 | 264880.6 | 37526.22 | 2175155.8406 | 232.0087 | 781.3357 | 0.68437
Model 17 | MBT | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ07 | ChlrCap | 336.4773 | 227517.3 | 37407.05 | 1932623.5826 | 205.5259 | 676.1742 | 0.61082
Model 17 | MBT | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ07 | ChlrCap | 329.6443 | 226067.9 | 37157.45 | 1897287.2227 | 203.6663 | 685.7934 | 0.61784
Model 17 | MBT | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ07 | ChlrCap | 322.342 | 209902.7 | 13126.59 | 1805451.9707 | 179.9492 | 651.1801 | 0.55826
Model 17 | MBT | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ07 | ChlrCap | 301.1313 | 198341.4 | 11325.33 | 1666811.4373 | 163.6241 | 658.6541 | 0.54336
Model 17 | Nrs | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ07 | ChlrCap | 112.809 | 124615.5 | 32734.5 | 1219255.6539 | 159.243 | 1104.6592 | 1.4116
Model 17 | Nrs | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ07 | ChlrCap | 108.3649 | 91614.21 | 29184.95 | 988969.3342 | 139.5766 | 845.4235 | 1.288
Model 17 | Nrs | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ07 | ChlrCap | 107.9223 | 91566.5 | 29269.88 | 987158.905 | 139.5036 | 848.4481 | 1.2926
Model 17 | Nrs | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ07 | ChlrCap | 102.4046 | 69348.55 | 24377.31 | 952519.6834 | 131.9585 | 677.2014 | 1.2886
Model 17 | Nrs | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ07 | ChlrCap | 103.4304 | 63229.37 | 22996.32 | 904068.8692 | 120.2717 | 611.3227 | 1.1628
Model 17 | OfL | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ07 | ChlrCap | 404.6611 | 288947.9 | 79236.45 | 1953294.1219 | 255.2535 | 714.0491 | 0.63078
Model 17 | OfL | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ07 | ChlrCap | 396.2667 | 273945.8 | 75089.19 | 1791914.3646 | 245.4378 | 691.3168 | 0.61938
Model 17 | OfL | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ07 | ChlrCap | 383.357 | 272304.7 | 79165.18 | 1761200.2415 | 242.3405 | 710.3162 | 0.63215
Model 17 | OfL | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ07 | ChlrCap | 371.1488 | 248125 | 73997.16 | 1699158.1143 | 233.3329 | 668.5323 | 0.62868
Model 17 | OfL | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ07 | ChlrCap | 361.6918 | 235622.3 | 30925.46 | 1583664.493 | 222.6414 | 651.4449 | 0.61556
Model 17 | OfS | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ07 | ChlrCap | 25.9215 | 17250.1 | 1870.408 | 117562.9837 | 13.2694 | 665.4755 | 0.51191
Model 17 | OfS | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ07 | ChlrCap | 25.8807 | 16745.65 | 1668.181 | 109018.7224 | 12.8556 | 647.0319 | 0.49673
Model 17 | OfS | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ07 | ChlrCap | 25.8991 | 16639.5 | 1658.987 | 108106.9538 | 12.7436 | 642.4739 | 0.49205
Model 17 | OfS | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ07 | ChlrCap | 22.1743 | 13867.88 | 2033.133 | 94399.6856 | 11.4279 | 625.4042 | 0.51537
Model 17 | OfS | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ07 | ChlrCap | 21.3755 | 13112.65 | 1486.714 | 88353.5299 | 10.6292 | 613.442 | 0.49726
Model 17 | Rt3 | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ07 | ChlrCap | 256.6523 | 213439.8 | 96064.85 | 1561203.4842 | 339.7555 | 831.6301 | 1.3238
Model 17 | Rt3 | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ07 | ChlrCap | 256.176 | 208015 | 95938.07 | 1497165.7849 | 325.9987 | 812.0003 | 1.2726
Model 17 | Rt3 | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ07 | ChlrCap | 255.3507 | 208033.6 | 96505.3 | 1497121.3576 | 325.8677 | 814.6977 | 1.2762
Model 17 | Rt3 | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ07 | ChlrCap | 243.3345 | 190528.5 | 84618.08 | 1349937.9906 | 299.7551 | 782.9901 | 1.2319
Model 17 | Rt3 | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ07 | ChlrCap | 231.2522 | 174217 | 65605.95 | 1219739.0141 | 274.1488 | 753.3638 | 1.1855
Model 17 | ECC | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ08 | ChlrCap | 739.8653 | 663345.4 | 122971.4 | 3151102.2743 | 631.6029 | 896.5759 | 0.85367
Model 17 | ECC | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ08 | ChlrCap | 739.8653 | 659301.1 | 122684.8 | 3099232.3939 | 629.5012 | 891.1096 | 0.85083
Model 17 | ECC | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ08 | ChlrCap | 737.3122 | 658214.1 | 122367.2 | 3096315.2591 | 628.0773 | 892.7211 | 0.85185
Model 17 | ECC | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ08 | ChlrCap | 687.023 | 598299.3 | 110788.1 | 2901040.6635 | 587.9669 | 870.8577 | 0.85582
Model 17 | ECC | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ08 | ChlrCap | 651.0408 | 566812.8 | 90529.88 | 2653288.9894 | 536.1125 | 870.6256 | 0.82347
Model 17 | ESe | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ08 | ChlrCap | 400.83 | 328056.8 | 39124.01 | 1454035.1067 | 232.6093 | 818.4437 | 0.58032
Model 17 | ESe | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ08 | ChlrCap | 393.9603 | 279934.1 | 39479.13 | 1245841.3318 | 198.6703 | 710.5642 | 0.50429
Model 17 | ESe | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ08 | ChlrCap | 392.0157 | 279130.2 | 39317.61 | 1242684.0528 | 198.0804 | 712.0384 | 0.50529
Model 17 | ESe | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ08 | ChlrCap | 367.1202 | 223996.2 | 22001.07 | 1125461.0834 | 159.2258 | 610.1441 | 0.43372
Model 17 | ESe | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ08 | ChlrCap | 346.614 | 211205.3 | 21986.91 | 1031922.2121 | 149.7199 | 609.3386 | 0.43195
Model 17 | EUn | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ08 | ChlrCap | 2528.2237 | 2064748 | 537745.1 | 9741024.1336 | 2207.5605 | 816.6793 | 0.87317
Model 17 | EUn | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ08 | ChlrCap | 2528.2237 | 2046157 | 528982.8 | 9554948.9109 | 2206.7079 | 809.3259 | 0.87283
Model 17 | EUn | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ08 | ChlrCap | 2501.0723 | 2035041 | 525605.8 | 9463008.0422 | 2193.6098 | 813.6674 | 0.87707
Model 17 | EUn | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ08 | ChlrCap | 2335.5727 | 1789749 | 463008 | 8564169.1653 | 2034.7935 | 766.2999 | 0.87122
Model 17 | EUn | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ08 | ChlrCap | 2222.945 | 1687129 | 411573.7 | 7887723.3505 | 1869.5827 | 758.9612 | 0.84104
Model 17 | Hsp | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ08 | ChlrCap | 896.2405 | 529630.3 | 43117.42 | 4060854.687 | 618.0575 | 590.9466 | 0.68961
Model 17 | Hsp | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ08 | ChlrCap | 896.2405 | 528314.9 | 43088.15 | 4044647.2614 | 617.4814 | 589.4789 | 0.68897
Model 17 | Hsp | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ08 | ChlrCap | 895.5942 | 527904.5 | 43045.29 | 4044718.415 | 617.1516 | 589.4461 | 0.6891
Model 17 | Hsp | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ08 | ChlrCap | 920.3975 | 458866.8 | 31888.83 | 3868997.4502 | 582.9467 | 498.5529 | 0.63336
Model 17 | Hsp | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ08 | ChlrCap | 939.6933 | 427509 | 30609.64 | 3615613.6166 | 529.0745 | 454.9453 | 0.56303
Model 17 | Htl | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ08 | ChlrCap | 212.3743 | 265541.4 | 37468.06 | 1376499.7154 | 195.8975 | 1250.346 | 0.92242
Model 17 | Htl | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ08 | ChlrCap | 205.637 | 240235.1 | 32920.1 | 1044821.2245 | 181.3669 | 1168.2484 | 0.88198
Model 17 | Htl | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ08 | ChlrCap | 198.3377 | 236510.1 | 33036.8 | 1017533.021 | 178.0393 | 1192.4618 | 0.89766
Model 17 | Htl | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ08 | ChlrCap | 171.8435 | 198371.7 | 29827.85 | 932100.5805 | 162.6575 | 1154.3742 | 0.94654
Model 17 | Htl | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ08 | ChlrCap | 170.0543 | 195452.3 | 29183.56 | 914558.6716 | 158.5915 | 1149.3521 | 0.93259
Model 17 | MBT | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ08 | ChlrCap | 379.9615 | 374177.1 | 45764.18 | 2326635.7046 | 266.3866 | 984.7764 | 0.70109
Model 17 | MBT | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ08 | ChlrCap | 376.9867 | 323606.8 | 45648.46 | 2052285.8335 | 234.6919 | 858.4038 | 0.62255
Model 17 | MBT | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ08 | ChlrCap | 364.483 | 316603.8 | 45136.37 | 2002772.0938 | 228.9696 | 868.638 | 0.6282
Model 17 | MBT | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ08 | ChlrCap | 359.3745 | 291383.5 | 16579.75 | 1892175.2427 | 209.3959 | 810.8074 | 0.58267
Model 17 | MBT | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ08 | ChlrCap | 334.8858 | 273389.3 | 14218.28 | 1751608.8875 | 192.7113 | 816.3657 | 0.57545
Model 17 | Nrs | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ08 | ChlrCap | 127.9944 | 181206.2 | 37246.52 | 1320576.7373 | 189.8165 | 1415.7356 | 1.483
Model 17 | Nrs | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ08 | ChlrCap | 125.2755 | 139194.3 | 33900.64 | 1070928.644 | 164.7053 | 1111.106 | 1.3147
Model 17 | Nrs | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ08 | ChlrCap | 122.6344 | 138866.1 | 33933.43 | 1068811.0477 | 164.6548 | 1132.3581 | 1.3426
Model 17 | Nrs | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ08 | ChlrCap | 110.3115 | 110054 | 29213.45 | 1020637.8277 | 152.1159 | 997.6652 | 1.379
Model 17 | Nrs | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ08 | ChlrCap | 112.0452 | 101881 | 28146.54 | 968081.6862 | 140.8094 | 909.2844 | 1.2567
Model 17 | OfL | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ08 | ChlrCap | 444.1263 | 401006.3 | 97519.48 | 2102929.7198 | 309.0616 | 902.9104 | 0.69589
Model 17 | OfL | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ08 | ChlrCap | 443.49 | 381455.1 | 94151.37 | 1937660.5428 | 285.8532 | 860.1211 | 0.64455
Model 17 | OfL | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ08 | ChlrCap | 429.6913 | 375300 | 100360.6 | 1884136.8535 | 275.4281 | 873.4177 | 0.64099
Model 17 | OfL | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ08 | ChlrCap | 410.6412 | 343721.5 | 93601.22 | 1817079.9215 | 258.9337 | 837.0361 | 0.63056
Model 17 | OfL | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ08 | ChlrCap | 397.5578 | 328835.7 | 53610.21 | 1707458.6764 | 246.399 | 827.1393 | 0.61978
Model 17 | OfS | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ08 | ChlrCap | 28.1286 | 24910.14 | 3325.511 | 129525.1811 | 16.8589 | 885.5821 | 0.59935
Model 17 | OfS | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ08 | ChlrCap | 28.0379 | 24490.89 | 3167.066 | 120657.4753 | 16.2255 | 873.4923 | 0.5787
Model 17 | OfS | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ08 | ChlrCap | 27.8237 | 24318.24 | 3151.007 | 119674.9546 | 16.0841 | 874.0109 | 0.57807
Model 17 | OfS | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ08 | ChlrCap | 24.0346 | 20073.74 | 3146.293 | 103311.7683 | 14.0201 | 835.2018 | 0.58333
Model 17 | OfS | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ08 | ChlrCap | 23.315 | 19139.28 | 2598.063 | 97285.6364 | 13.208 | 820.8987 | 0.5665
Model 17 | Rt3 | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ08 | ChlrCap | 281.8822 | 330909.8 | 107190.1 | 1697597.0258 | 371.2192 | 1173.9295 | 1.3169
Model 17 | Rt3 | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ08 | ChlrCap | 281.3125 | 295959.8 | 107985.6 | 1603371.4754 | 356.1297 | 1052.0677 | 1.266
Model 17 | Rt3 | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ08 | ChlrCap | 280.447 | 295468.7 | 108244.2 | 1602727.3646 | 355.5912 | 1053.5634 | 1.2679
Model 17 | Rt3 | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ08 | ChlrCap | 269.9647 | 274454 | 95342.7 | 1451578.2626 | 328.7863 | 1016.6293 | 1.2179
Model 17 | Rt3 | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ08 | ChlrCap | 258.647 | 255275.7 | 78663.22 | 1322258.5451 | 301.7329 | 986.9656 | 1.1666
Model 17 | ECC | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ09 | ChlrCap | 893.031 | 610686.5 | 115186.2 | 3158319.3353 | 694.6863 | 683.8357 | 0.7779
Model 17 | ECC | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ09 | ChlrCap | 893.031 | 607222.5 | 114630 | 3106762.3904 | 692.5733 | 679.9568 | 0.77553
Model 17 | ECC | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ09 | ChlrCap | 882.3562 | 601584.8 | 114095.7 | 3092414.5358 | 686.3609 | 681.7936 | 0.77787
Model 17 | ECC | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ09 | ChlrCap | 816.2587 | 544201.3 | 102555.5 | 2885417.7433 | 641.4355 | 666.702 | 0.78582
Model 17 | ECC | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ09 | ChlrCap | 783.4162 | 515818.8 | 82330.13 | 2646197.0399 | 589.2741 | 658.4225 | 0.75219
Model 17 | ESe | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ09 | ChlrCap | 485.9148 | 280985.2 | 38389.41 | 1457468.823 | 259.0834 | 578.2602 | 0.53319
Model 17 | ESe | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ09 | ChlrCap | 481.3325 | 262225.2 | 38416.04 | 1269817.8734 | 226.3273 | 544.7901 | 0.47021
Model 17 | ESe | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ09 | ChlrCap | 472.9107 | 259018.6 | 37794.68 | 1255650.6307 | 223.6023 | 547.7115 | 0.47282
Model 17 | ESe | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ09 | ChlrCap | 427.1442 | 203896.1 | 21742.27 | 1138626.0152 | 185.4767 | 477.3473 | 0.43423
Model 17 | ESe | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ09 | ChlrCap | 411.9728 | 192352.9 | 21131.12 | 1050292.3333 | 176.6016 | 466.9068 | 0.42867
Model 17 | EUn | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ09 | ChlrCap | 2988.2497 | 1957129 | 518291 | 9949382.4056 | 2392.2419 | 654.9416 | 0.80055
Model 17 | EUn | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ09 | ChlrCap | 2988.2497 | 1942309 | 510230.5 | 9774200.6647 | 2390.3519 | 649.9822 | 0.79992
Model 17 | EUn | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ09 | ChlrCap | 2909.579 | 1914326 | 500007.8 | 9549623.4865 | 2361.1722 | 657.9392 | 0.81152
Model 17 | EUn | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ09 | ChlrCap | 2676.6887 | 1664448 | 432237.6 | 8564117.9531 | 2178.3923 | 621.831 | 0.81384
Model 17 | EUn | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ09 | ChlrCap | 2584.4677 | 1580878 | 385648.7 | 7936240.7304 | 2039.7257 | 611.6842 | 0.78922
Model 17 | Hsp | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ09 | ChlrCap | 1019.3813 | 492804.6 | 39210.41 | 4081741.245 | 662.0725 | 483.435 | 0.64948
Model 17 | Hsp | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ09 | ChlrCap | 1019.3813 | 491484.7 | 39160.51 | 4065941.3634 | 661.4284 | 482.1402 | 0.64885
Model 17 | Hsp | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ09 | ChlrCap | 1015.938 | 489957.3 | 39057.35 | 4064309.4783 | 659.9231 | 482.2709 | 0.64957
Model 17 | Hsp | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ09 | ChlrCap | 1046.3467 | 434420.1 | 28976.36 | 3900061.3001 | 627.3111 | 415.178 | 0.59953
Model 17 | Hsp | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ09 | ChlrCap | 1074.036 | 407990.4 | 27950.98 | 3661603.3423 | 572.6995 | 379.8666 | 0.53322
Model 17 | Htl | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ09 | ChlrCap | 270.7573 | 261211.5 | 36332.09 | 1407278.9336 | 216.1117 | 964.744 | 0.79817
Model 17 | Htl | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ09 | ChlrCap | 263.948 | 235518.9 | 31999.68 | 1073321.1049 | 200.7131 | 892.2928 | 0.76043
Model 17 | Htl | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ09 | ChlrCap | 253.1615 | 230836.7 | 32111.88 | 1039996.2495 | 195.7351 | 911.816 | 0.77316
Model 17 | Htl | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ09 | ChlrCap | 222.526 | 191032.4 | 28061.09 | 947430.8048 | 176.976 | 858.4723 | 0.7953
Model 17 | Htl | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ09 | ChlrCap | 220.8133 | 188527 | 27495.06 | 930734.2025 | 173.0767 | 853.7845 | 0.78381
Model 17 | MBT | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ09 | ChlrCap | 441.9422 | 353548.5 | 44251.19 | 2332405.6999 | 303.849 | 799.9882 | 0.68753
Model 17 | MBT | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ09 | ChlrCap | 437.8058 | 299706.8 | 44102.09 | 2040008.5416 | 260.8125 | 684.5656 | 0.59573
Model 17 | MBT | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ09 | ChlrCap | 400.1697 | 288313.5 | 42302.91 | 1966418.415 | 243.3061 | 720.4781 | 0.60801
Model 17 | MBT | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ09 | ChlrCap | 383.7025 | 261934.1 | 15288.26 | 1858836.8617 | 224.9955 | 682.6489 | 0.58638
Model 17 | MBT | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ09 | ChlrCap | 365.1895 | 246204.2 | 13220.07 | 1723755.585 | 204.8444 | 674.182 | 0.56093
Model 17 | Nrs | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ09 | ChlrCap | 161.1163 | 182232.7 | 35202.09 | 1361780.9116 | 206.0089 | 1131.0631 | 1.2786
Model 17 | Nrs | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ09 | ChlrCap | 155.7269 | 137896.2 | 32586.33 | 1102241.844 | 178.9751 | 885.5005 | 1.1493
Model 17 | Nrs | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ09 | ChlrCap | 149.6776 | 136013.5 | 32692.06 | 1074710.0114 | 176.0781 | 908.7097 | 1.1764
Model 17 | Nrs | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ09 | ChlrCap | 127.8184 | 105916.8 | 28124.24 | 1025445.9553 | 162.7312 | 828.6505 | 1.2731
Model 17 | Nrs | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ09 | ChlrCap | 128.7526 | 98307.61 | 27114.69 | 975326.3124 | 151.3663 | 763.5391 | 1.1756
Model 17 | OfL | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ09 | ChlrCap | 488.7008 | 375631.8 | 85131.22 | 2093473.6495 | 323.2461 | 768.6334 | 0.66144
Model 17 | OfL | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ09 | ChlrCap | 488.0035 | 360230.5 | 82061.27 | 1924574.1372 | 305.5283 | 738.172 | 0.62608
Model 17 | OfL | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ09 | ChlrCap | 469.4777 | 352387.3 | 90296.98 | 1864440.1383 | 294.8014 | 750.5944 | 0.62793
Model 17 | OfL | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ09 | ChlrCap | 449.6365 | 319395.8 | 87735.98 | 1794933.6483 | 277.8526 | 710.3422 | 0.61795
Model 17 | OfL | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ09 | ChlrCap | 440.7675 | 305918.5 | 28563.61 | 1688887.3388 | 263.9822 | 694.0587 | 0.59891
Model 17 | OfS | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ09 | ChlrCap | 34.1601 | 23861.14 | 3106.906 | 131097.6722 | 18.8899 | 698.5087 | 0.55298
Model 17 | OfS | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ09 | ChlrCap | 34.0647 | 22961.62 | 2973.926 | 121827.7803 | 17.857 | 674.0582 | 0.52421
Model 17 | OfS | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ09 | ChlrCap | 32.8268 | 22451.71 | 3014.569 | 118427.4553 | 17.1317 | 683.9438 | 0.52188
Model 17 | OfS | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ09 | ChlrCap | 28.4866 | 18410.92 | 2990.515 | 101455.8678 | 14.5501 | 646.3016 | 0.51077
Model 17 | OfS | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ09 | ChlrCap | 27.6906 | 17591.34 | 2529.295 | 95491.9552 | 13.7586 | 635.2822 | 0.49687
Model 17 | Rt3 | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ09 | ChlrCap | 342.2205 | 279417.8 | 96417.6 | 1658748.7005 | 394.8011 | 816.4847 | 1.1536
Model 17 | Rt3 | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ09 | ChlrCap | 341.589 | 271411.9 | 96483.51 | 1575959.9156 | 375.9187 | 794.5569 | 1.1005
Model 17 | Rt3 | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ09 | ChlrCap | 336.846 | 269847.5 | 97421.54 | 1573308.3183 | 373.6177 | 801.1005 | 1.1092
Model 17 | Rt3 | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ09 | ChlrCap | 325.614 | 249061.9 | 85626.59 | 1425458.1125 | 347.2657 | 764.8992 | 1.0665
Model 17 | Rt3 | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ09 | ChlrCap | 315.9945 | 231350 | 72381.09 | 1298410.5627 | 319.3669 | 732.133 | 1.0107
Model 17 | ECC | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ10 | ChlrCap | 770.1527 | 681469.6 | 122614.5 | 3264118.6084 | 549.338 | 884.85 | 0.71328
Model 17 | ECC | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ10 | ChlrCap | 767.3098 | 675989 | 121942.7 | 3209394.2474 | 546.8546 | 880.9857 | 0.71269
Model 17 | ECC | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ10 | ChlrCap | 764.3988 | 674428.8 | 121509.1 | 3205434.2532 | 545.1239 | 882.2996 | 0.71314
Model 17 | ECC | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ10 | ChlrCap | 729.7298 | 626370.8 | 107165.4 | 3062636.4795 | 499.2433 | 858.3599 | 0.68415
Model 17 | ECC | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ10 | ChlrCap | 696.4335 | 596689.3 | 87001.13 | 2824423.1547 | 462.7213 | 856.7786 | 0.66442
Model 17 | ESe | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ10 | ChlrCap | 401.8207 | 301046.5 | 31859.74 | 1464885.6377 | 137.6845 | 749.2061 | 0.34265
Model 17 | ESe | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ10 | ChlrCap | 393.7185 | 257637.6 | 32064.86 | 1284850.087 | 106.3714 | 654.3701 | 0.27017
Model 17 | ESe | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ10 | ChlrCap | 391.5958 | 256593.7 | 31886.96 | 1281149.1487 | 105.3156 | 655.2514 | 0.26894
Model 17 | ESe | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ10 | ChlrCap | 378.9832 | 236209.3 | 23157.74 | 1214474.8781 | 97.0673 | 623.2712 | 0.25613
Model 17 | ESe | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ10 | ChlrCap | 362.4922 | 224704.6 | 23333.29 | 1131964.0103 | 86.3792 | 619.8882 | 0.23829
Model 17 | EUn | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ10 | ChlrCap | 2629.0233 | 2159447 | 566796.3 | 10085246.9566 | 2143.5505 | 821.3875 | 0.81534
Model 17 | EUn | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ10 | ChlrCap | 2613.854 | 2138939 | 559153.3 | 9899387.3693 | 2143.6163 | 818.3085 | 0.8201
Model 17 | EUn | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ10 | ChlrCap | 2586.9427 | 2127557 | 555789.9 | 9808280.9953 | 2132.2507 | 822.4214 | 0.82424
Model 17 | EUn | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ10 | ChlrCap | 2453.7317 | 1922000 | 448375.1 | 9088124.9297 | 1984.9564 | 783.2967 | 0.80895
Model 17 | EUn | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ10 | ChlrCap | 2358.0787 | 1833353 | 403900.3 | 8477523.8195 | 1865.1219 | 777.4775 | 0.79095
Model 17 | Hsp | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ10 | ChlrCap | 920.6743 | 520986.3 | 39039.57 | 4167025.4654 | 681.9325 | 565.8747 | 0.74069
Model 17 | Hsp | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ10 | ChlrCap | 919.9765 | 519255.6 | 38992.46 | 4150019.939 | 688.2124 | 564.4227 | 0.74808
Model 17 | Hsp | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ10 | ChlrCap | 919.2605 | 518741.5 | 38992.39 | 4149677.3376 | 687.6957 | 564.303 | 0.7481
Model 17 | Hsp | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ10 | ChlrCap | 930.4465 | 497362.7 | 28734.95 | 4057344.6471 | 667.9152 | 534.542 | 0.71784
Model 17 | Hsp | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ10 | ChlrCap | 948.8985 | 465856.7 | 27877.95 | 3819476.1079 | 601.3861 | 490.9447 | 0.63377
Model 17 | Htl | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ10 | ChlrCap | 233.4468 | 271417.4 | 37013.99 | 1431724.4523 | 210.784 | 1162.6519 | 0.90292
Model 17 | Htl | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ10 | ChlrCap | 226.0702 | 245250.6 | 32401.49 | 1102549.6577 | 194.4551 | 1084.8428 | 0.86015
Model 17 | Htl | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ10 | ChlrCap | 219.7372 | 242066.5 | 32426.45 | 1077781.9781 | 191.4834 | 1101.6184 | 0.87142
Model 17 | Htl | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ10 | ChlrCap | 201.0175 | 214690.6 | 29779.87 | 1008326.8592 | 180.0634 | 1068.0195 | 0.89576
Model 17 | Htl | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ10 | ChlrCap | 199.322 | 211910.4 | 29215.33 | 991819.7905 | 175.9135 | 1063.1561 | 0.88256
Model 17 | MBT | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ10 | ChlrCap | 386.5875 | 330166.8 | 39464 | 2266460.2708 | 347.6879 | 854.0545 | 0.89938
Model 17 | MBT | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ10 | ChlrCap | 377.0093 | 310839.8 | 38841.64 | 2029815.163 | 322.0763 | 824.4883 | 0.85429
Model 17 | MBT | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ10 | ChlrCap | 362.7243 | 303126.7 | 37487.78 | 1975657.0645 | 311.3923 | 835.6944 | 0.85848
Model 17 | MBT | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ10 | ChlrCap | 361 | 295243.6 | 15945.78 | 1907367.8921 | 293.9865 | 817.8493 | 0.81437
Model 17 | MBT | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ10 | ChlrCap | 339.4217 | 278108.2 | 14029.82 | 1771149.6635 | 271.9707 | 819.359 | 0.80128
Model 17 | Nrs | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ10 | ChlrCap | 129.92 | 173985.5 | 33148.22 | 1357661.9278 | 193.0505 | 1339.1741 | 1.4859
Model 17 | Nrs | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ10 | ChlrCap | 124.8427 | 133752.7 | 30620.12 | 1126489.4404 | 169.2521 | 1071.3694 | 1.3557
Model 17 | Nrs | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ10 | ChlrCap | 121.976 | 132648.7 | 30864.94 | 1111554.419 | 168.0088 | 1087.4981 | 1.3774
Model 17 | Nrs | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ10 | ChlrCap | 116.8715 | 122089.1 | 29007.84 | 1081563.938 | 162.674 | 1044.6439 | 1.3919
Model 17 | Nrs | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ10 | ChlrCap | 116.0286 | 114081.9 | 28142.13 | 1031173.7414 | 151.3197 | 983.222 | 1.3042
Model 17 | OfL | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ10 | ChlrCap | 439.3667 | 400602.6 | 104913.6 | 2066536.803 | 375.5103 | 911.7729 | 0.85466
Model 17 | OfL | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ10 | ChlrCap | 438.1183 | 381066.9 | 101979.9 | 1912230.374 | 354.1345 | 869.7808 | 0.80831
Model 17 | OfL | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ10 | ChlrCap | 424.4277 | 373742.6 | 107693.4 | 1864193.7321 | 340.9431 | 880.5802 | 0.8033
Model 17 | OfL | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ10 | ChlrCap | 427.0532 | 354943.8 | 92407.46 | 1846901.7585 | 331.9743 | 831.1466 | 0.77736
Model 17 | OfL | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ10 | ChlrCap | 413.0813 | 340268.8 | 38839.69 | 1743553.34 | 315.3459 | 823.7332 | 0.7634
Model 17 | OfS | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ10 | ChlrCap | 29.0807 | 24565.06 | 3806.044 | 124439.7268 | 20.6759 | 844.7209 | 0.71099
Model 17 | OfS | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ10 | ChlrCap | 28.9033 | 23707.66 | 3600.271 | 116291.858 | 19.7954 | 820.2401 | 0.68488
Model 17 | OfS | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ10 | ChlrCap | 28.1904 | 23402.88 | 3654.498 | 113730.1817 | 19.4754 | 830.1717 | 0.69085
Model 17 | OfS | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ10 | ChlrCap | 26.0697 | 21005.37 | 3404.699 | 105493.1664 | 17.8261 | 805.7388 | 0.68379
Model 17 | OfS | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ10 | ChlrCap | 25.2521 | 20097.25 | 2984.148 | 99433.6509 | 16.5315 | 795.8642 | 0.65466
Model 17 | Rt3 | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ10 | ChlrCap | 299.8245 | 314705.8 | 100309.4 | 1701247.0891 | 409.4153 | 1049.6334 | 1.3655
Model 17 | Rt3 | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ10 | ChlrCap | 298.227 | 304617 | 100403.9 | 1627455.6671 | 403.8556 | 1021.4266 | 1.3542
Model 17 | Rt3 | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ10 | ChlrCap | 297.162 | 304175.4 | 100558.7 | 1626618.7128 | 403.0913 | 1023.6013 | 1.3565
Model 17 | Rt3 | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ10 | ChlrCap | 287.1245 | 287293.7 | 89223.38 | 1486206.8617 | 377.2869 | 1000.5893 | 1.314
Model 17 | Rt3 | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ10 | ChlrCap | 276.7787 | 269166.6 | 76250.02 | 1364870.8664 | 349.6175 | 972.4976 | 1.2632
Model 17 | ECC | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ11 | ChlrCap | 732.3215 | 654802.6 | 104816 | 3683766.4783 | 310.2746 | 894.1464 | 0.42369
Model 17 | ECC | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ11 | ChlrCap | 729.7727 | 649061.8 | 103997.7 | 3615006.4502 | 307.3867 | 889.4027 | 0.42121
Model 17 | ECC | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ11 | ChlrCap | 709.2598 | 625457.9 | 106277.7 | 3452919.408 | 271.7772 | 881.8459 | 0.38318
Model 17 | ECC | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ11 | ChlrCap | 670.3255 | 575845.4 | 95981.34 | 3272335.7585 | 260.0941 | 859.0534 | 0.38801
Model 17 | ECC | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ11 | ChlrCap | 638.1592 | 550284.6 | 76785.3 | 3068438.8605 | 235.8377 | 862.2999 | 0.36956
Model 17 | ESe | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ11 | ChlrCap | 372.733 | 258958.8 | 33687.46 | 1669329.0574 | 164.7091 | 694.7568 | 0.4419
Model 17 | ESe | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ11 | ChlrCap | 361.6988 | 243889.3 | 33476.29 | 1528952.1416 | 143.0573 | 674.2883 | 0.39552
Model 17 | ESe | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ11 | ChlrCap | 355.1192 | 229925.6 | 29434.98 | 1422353.2272 | 124.9063 | 647.4604 | 0.35173
Model 17 | ESe | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ11 | ChlrCap | 345.2653 | 208710.8 | 21710.7 | 1329839.0134 | 120.4679 | 604.4939 | 0.34891
Model 17 | ESe | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ11 | ChlrCap | 328.088 | 198116.4 | 21690.08 | 1259683.2021 | 108.5805 | 603.8514 | 0.33095
Model 17 | EUn | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ11 | ChlrCap | 2478.8097 | 2138172 | 520755.8 | 11581886.204 | 806.5108 | 862.5801 | 0.32536
Model 17 | EUn | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ11 | ChlrCap | 2465.2163 | 2119112 | 512927 | 11382896.7093 | 799.6455 | 859.6049 | 0.32437
Model 17 | EUn | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ11 | ChlrCap | 2374.959 | 2079092 | 515845.6 | 10833201.6729 | 736.9314 | 875.4223 | 0.31029
Model 17 | EUn | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ11 | ChlrCap | 2239.9477 | 1869216 | 422361.2 | 9933723.7362 | 646.5219 | 834.4909 | 0.28863
Model 17 | EUn | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ11 | ChlrCap | 2146.914 | 1793016 | 388119.6 | 9428832.864 | 590.7197 | 835.1597 | 0.27515
Model 17 | Hsp | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ11 | ChlrCap | 908.8632 | 552941.2 | 35547.93 | 4536365.5088 | 770.2155 | 608.3877 | 0.84745
Model 17 | Hsp | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ11 | ChlrCap | 907.9913 | 550676.9 | 35344.09 | 4512121.1336 | 772.0704 | 606.4782 | 0.85031
Model 17 | Hsp | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ11 | ChlrCap | 928.6185 | 524866.4 | 35291.44 | 4381081.8734 | 738.124 | 565.2121 | 0.79486
Model 17 | Hsp | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ11 | ChlrCap | 942.108 | 504327.1 | 25948.36 | 4278113.8464 | 710.1135 | 535.3177 | 0.75375
Model 17 | Hsp | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ11 | ChlrCap | 964.2135 | 475621.1 | 25181.91 | 4074954.0481 | 657.6879 | 493.2736 | 0.6821
Model 17 | Htl | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ11 | ChlrCap | 240.8033 | 274361.1 | 35718.91 | 1616680.8273 | 286.5757 | 1139.3576 | 1.1901
Model 17 | Htl | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ11 | ChlrCap | 233.1243 | 250308.8 | 31518.74 | 1305436.4441 | 266.9429 | 1073.7137 | 1.1451
Model 17 | Htl | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ11 | ChlrCap | 224.8557 | 244944.7 | 31222.64 | 1247228.7607 | 258.9454 | 1089.3419 | 1.1516
Model 17 | Htl | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ11 | ChlrCap | 206.8593 | 218228.8 | 28772.95 | 1160151.5442 | 242.2057 | 1054.9623 | 1.1709
Model 17 | Htl | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ11 | ChlrCap | 204.9697 | 215601.3 | 28158.71 | 1145562.8264 | 237.8669 | 1051.8693 | 1.1605
Model 17 | MBT | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ11 | ChlrCap | 399.3067 | 313099.3 | 34941.84 | 2333182.1336 | 337.7217 | 784.1074 | 0.84577
Model 17 | MBT | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ11 | ChlrCap | 388.7318 | 292848.9 | 34431.8 | 2093330.4936 | 315.4957 | 753.3443 | 0.8116
Model 17 | MBT | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ11 | ChlrCap | 370.9093 | 283090.8 | 33055.83 | 2017942.9531 | 298.9352 | 763.2345 | 0.80595
Model 17 | MBT | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ11 | ChlrCap | 367.482 | 273561.5 | 15034.21 | 1943941.9472 | 283.8878 | 744.4215 | 0.77252
Model 17 | MBT | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ11 | ChlrCap | 345.7538 | 257775.9 | 13545.93 | 1814013.2392 | 266.4983 | 745.5475 | 0.77077
Model 17 | Nrs | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ11 | ChlrCap | 138.1275 | 182672.9 | 29773.24 | 1498315.9014 | 243.6999 | 1322.495 | 1.7643
Model 17 | Nrs | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ11 | ChlrCap | 132.5941 | 143159.5 | 27694.49 | 1278233.9423 | 212.7455 | 1079.682 | 1.6045
Model 17 | Nrs | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ11 | ChlrCap | 129.4259 | 141590.6 | 27882.53 | 1255399.1182 | 210.3715 | 1093.9895 | 1.6254
Model 17 | Nrs | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ11 | ChlrCap | 122.7176 | 131062.9 | 26198.76 | 1215917.3268 | 201.5153 | 1068.0044 | 1.6421
Model 17 | Nrs | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ11 | ChlrCap | 118.8625 | 123402 | 25660.97 | 1161328.413 | 188.9413 | 1038.1908 | 1.5896
Model 17 | OfL | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ11 | ChlrCap | 437.5503 | 369054 | 92513.09 | 2107512.1653 | 387.1808 | 843.455 | 0.88488
Model 17 | OfL | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ11 | ChlrCap | 436.2393 | 350296 | 90807.86 | 1966871 | 373.5435 | 802.9904 | 0.85628
Model 17 | OfL | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ11 | ChlrCap | 418.8508 | 340016.9 | 93384.71 | 1884085.9543 | 360.4711 | 811.7852 | 0.86062
Model 17 | OfL | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ11 | ChlrCap | 422.9555 | 326383.8 | 83640.84 | 1912176.6612 | 359.8199 | 771.6741 | 0.85073
Model 17 | OfL | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ11 | ChlrCap | 411.7397 | 315135.4 | 27715.47 | 1830044.4959 | 340.1404 | 765.3754 | 0.82611
Model 17 | OfS | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ11 | ChlrCap | 29.0447 | 23412.18 | 4375.315 | 135287.7306 | 24.1617 | 806.0729 | 0.83188
Model 17 | OfS | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ11 | ChlrCap | 28.8082 | 23083.94 | 4262.479 | 127963.0822 | 23.1374 | 801.298 | 0.80315
Model 17 | OfS | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ11 | ChlrCap | 28.0648 | 22733.51 | 4290.675 | 124681.3373 | 22.7181 | 810.0367 | 0.80949
Model 17 | OfS | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ11 | ChlrCap | 26.2097 | 19948.95 | 3974.575 | 114463.0843 | 20.2949 | 761.1297 | 0.77433
Model 17 | OfS | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ11 | ChlrCap | 25.2603 | 19045.53 | 3507.058 | 108062.2045 | 18.9919 | 753.9701 | 0.75185
Model 17 | Rt3 | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ11 | ChlrCap | 317.8452 | 304160.2 | 85587.52 | 1786071.1688 | 447.6065 | 956.9446 | 1.4083
Model 17 | Rt3 | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ11 | ChlrCap | 315.9692 | 290326.5 | 85849.66 | 1704382.6846 | 446.1081 | 918.8444 | 1.4119
Model 17 | Rt3 | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ11 | ChlrCap | 297.2928 | 280974.6 | 87457.75 | 1635771.0328 | 428.2563 | 945.1106 | 1.4405
Model 17 | Rt3 | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ11 | ChlrCap | 287.5838 | 263911.5 | 77485.88 | 1505558.2392 | 398.8461 | 917.6855 | 1.3869
Model 17 | Rt3 | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ11 | ChlrCap | 276.9912 | 248102.7 | 65555.58 | 1398527.2075 | 371.2199 | 895.7062 | 1.3402
Model 17 | ECC | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ12 | ChlrCap | 662.3168 | 509028.3 | 91843.19 | 3453869.4361 | 604.4662 | 768.5571 | 0.91265
Model 17 | ECC | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ12 | ChlrCap | 660.0962 | 504519.6 | 91282.71 | 3387595.1559 | 600.7625 | 764.3123 | 0.91011
Model 17 | ECC | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ12 | ChlrCap | 648.0275 | 498786.9 | 92116.88 | 3333329.5088 | 594.116 | 769.7002 | 0.91681
Model 17 | ECC | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ12 | ChlrCap | 613.3367 | 461327.7 | 79968.37 | 3181981.3517 | 538.1265 | 752.1606 | 0.87738
Model 17 | ECC | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ12 | ChlrCap | 583.5185 | 439635.3 | 64873.65 | 2983862.0539 | 502.6165 | 753.4214 | 0.86135
Model 17 | ESe | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ12 | ChlrCap | 334.4787 | 215692.7 | 25517.06 | 1565258.5147 | 149.656 | 644.8622 | 0.44743
Model 17 | ESe | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ12 | ChlrCap | 331.1757 | 185693.2 | 25630.27 | 1417457.6216 | 122.1797 | 560.7091 | 0.36893
Model 17 | ESe | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ12 | ChlrCap | 328.879 | 181727.2 | 24274.96 | 1379736.7223 | 112.9156 | 552.5655 | 0.34333
Model 17 | ESe | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ12 | ChlrCap | 319.1893 | 165414 | 17526.13 | 1302594.9266 | 109.5333 | 518.2316 | 0.34316
Model 17 | ESe | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ12 | ChlrCap | 302.8257 | 156762.2 | 17666.93 | 1234121.6434 | 101.7507 | 517.6648 | 0.336
Model 17 | EUn | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ12 | ChlrCap | 2285.9947 | 1669785 | 454697.8 | 10890328.3013 | 2349.8659 | 730.4413 | 1.0279
Model 17 | EUn | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ12 | ChlrCap | 2294.4407 | 1652965 | 445198.5 | 10669776.837 | 2337.3876 | 720.4218 | 1.0187
Model 17 | EUn | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ12 | ChlrCap | 2243.6113 | 1639829 | 448061.8 | 10417296.9121 | 2305.4549 | 730.8882 | 1.0276
Model 17 | EUn | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ12 | ChlrCap | 2114.4723 | 1480731 | 376093.8 | 9633239.5709 | 2128.5433 | 700.2839 | 1.0067
Model 17 | EUn | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ12 | ChlrCap | 2018.7463 | 1412484 | 336060.8 | 9130750.3529 | 2031.0446 | 699.6837 | 1.0061
Model 17 | Hsp | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ12 | ChlrCap | 874.059 | 392206.7 | 28957.99 | 4295147.3072 | 707.2541 | 448.7188 | 0.80916
Model 17 | Hsp | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ12 | ChlrCap | 873.2853 | 390374.8 | 28837.31 | 4271042.0211 | 703.5839 | 447.0187 | 0.80567
Model 17 | Hsp | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ12 | ChlrCap | 879.031 | 383283 | 28808.47 | 4228665.9683 | 700.9727 | 436.029 | 0.79744
Model 17 | Hsp | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ12 | ChlrCap | 889.8155 | 367812.3 | 21065.19 | 4136220.2028 | 681.033 | 413.3579 | 0.76536
Model 17 | Hsp | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ12 | ChlrCap | 908.701 | 345944.1 | 20281.05 | 3941292.0633 | 619.7782 | 380.7018 | 0.68205
Model 17 | Htl | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ12 | ChlrCap | 219.0595 | 218966.9 | 31160.73 | 1531098.9993 | 234.1419 | 999.5773 | 1.0689
Model 17 | Htl | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ12 | ChlrCap | 211.378 | 196934.9 | 27220.68 | 1222620.7841 | 217.3707 | 931.6717 | 1.0284
Model 17 | Htl | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ12 | ChlrCap | 204.8895 | 193892.4 | 27172.3 | 1177614.438 | 212.8668 | 946.3267 | 1.0389
Model 17 | Htl | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ12 | ChlrCap | 187.9173 | 171240.6 | 24758.52 | 1100565.6023 | 198.9973 | 911.2549 | 1.059
Model 17 | Htl | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ12 | ChlrCap | 186.1508 | 169154.5 | 24260.77 | 1087060.9318 | 195.9621 | 908.6959 | 1.0527
Model 17 | MBT | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ12 | ChlrCap | 372.7475 | 245579.8 | 31175.29 | 2247147.6553 | 370.8817 | 658.8369 | 0.99499
Model 17 | MBT | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ12 | ChlrCap | 362.977 | 231673.3 | 30857.51 | 2024057.2825 | 344.6529 | 638.2589 | 0.94952
Model 17 | MBT | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ12 | ChlrCap | 350.5465 | 224838 | 29503.35 | 1950541.51 | 332.2959 | 641.3928 | 0.94794
Model 17 | MBT | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ12 | ChlrCap | 347.0127 | 218351.6 | 12171.34 | 1880400.9308 | 314.6387 | 629.2324 | 0.90671
Model 17 | MBT | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ12 | ChlrCap | 325.3683 | 205656.1 | 10793.17 | 1755915.5955 | 291.5518 | 632.0717 | 0.89607
Model 17 | Nrs | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ12 | ChlrCap | 125.9374 | 133069 | 25314.08 | 1436762.5484 | 207.4088 | 1056.6283 | 1.6469
Model 17 | Nrs | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ12 | ChlrCap | 120.5391 | 101553.4 | 23350.16 | 1226245.4967 | 181.9448 | 842.4935 | 1.5094
Model 17 | Nrs | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ12 | ChlrCap | 117.7088 | 100615.1 | 23564.06 | 1204601.8708 | 180.345 | 854.7796 | 1.5321
Model 17 | Nrs | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ12 | ChlrCap | 111.6158 | 91796.08 | 21885.33 | 1168459.1422 | 173.9591 | 822.4288 | 1.5586
Model 17 | Nrs | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ12 | ChlrCap | 110.2839 | 85774.2 | 21066.93 | 1125754.055 | 161.9029 | 777.7579 | 1.4681
Model 17 | OfL | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ12 | ChlrCap | 418.6502 | 303333.5 | 82883.63 | 2023955.8523 | 401.99 | 724.5512 | 0.96021
Model 17 | OfL | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ12 | ChlrCap | 417.4628 | 287331.4 | 79777.98 | 1882368.6882 | 383.4133 | 688.2802 | 0.91844
Model 17 | OfL | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ12 | ChlrCap | 403.19 | 281278.1 | 85855.4 | 1809656.2216 | 372.2485 | 697.6316 | 0.92326
Model 17 | OfL | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ12 | ChlrCap | 401.5918 | 266564.9 | 73737.79 | 1826654.1032 | 368.9249 | 663.7707 | 0.91866
Model 17 | OfL | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ12 | ChlrCap | 390.1103 | 255856.1 | 14533.27 | 1736697.6565 | 351.3653 | 655.8557 | 0.90068
Model 17 | OfS | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ12 | ChlrCap | 27.0139 | 18935.54 | 3064.733 | 129109.3656 | 22.8826 | 700.9557 | 0.84707
Model 17 | OfS | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ12 | ChlrCap | 26.6977 | 18552.54 | 2964.69 | 121591.2069 | 21.8685 | 694.9107 | 0.81912
Model 17 | OfS | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ12 | ChlrCap | 26.1792 | 18313.44 | 3006.326 | 118573.6142 | 21.4767 | 699.541 | 0.82037
Model 17 | OfS | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ12 | ChlrCap | 24.359 | 16013.58 | 2743.475 | 109300.5039 | 19.8047 | 657.3985 | 0.81303
Model 17 | OfS | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ12 | ChlrCap | 23.6061 | 15335.87 | 2103.375 | 104302.4738 | 18.7969 | 649.6582 | 0.79627
Model 17 | Rt3 | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ12 | ChlrCap | 294.7187 | 240509.3 | 79853.87 | 1681018.0668 | 423.3311 | 816.064 | 1.4364
Model 17 | Rt3 | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ12 | ChlrCap | 292.9947 | 231085.7 | 79909.22 | 1608595.6753 | 411.6603 | 788.7028 | 1.405
Model 17 | Rt3 | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ12 | ChlrCap | 286.6217 | 229009.2 | 80852.2 | 1587538.3916 | 406.4725 | 798.9947 | 1.4181
Model 17 | Rt3 | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ12 | ChlrCap | 276.5603 | 214070.2 | 71412.69 | 1460934.939 | 376.1026 | 774.0452 | 1.3599
Model 17 | Rt3 | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ12 | ChlrCap | 265.7432 | 200455.7 | 59986.19 | 1365389.5885 | 348.878 | 754.3212 | 1.3128
Model 17 | ECC | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ13 | ChlrCap | 780.354 | 730329.2 | 124850 | 3613101.2204 | 672.3986 | 935.8947 | 0.86166
Model 17 | ECC | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ13 | ChlrCap | 778.095 | 723611.8 | 123971.6 | 3544468.4455 | 668.7128 | 929.9787 | 0.85942
Model 17 | ECC | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ13 | ChlrCap | 758.2678 | 703899.7 | 124400.6 | 3443147.8464 | 651.1927 | 928.2996 | 0.85879
Model 17 | ECC | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ13 | ChlrCap | 724.1292 | 648486.9 | 112680.6 | 3276708.8535 | 583.5141 | 895.5404 | 0.80581
Model 17 | ECC | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ13 | ChlrCap | 689.718 | 620281.4 | 92362.03 | 3052243.2474 | 544.2314 | 899.3261 | 0.78906
Model 17 | ESe | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ13 | ChlrCap | 405.9537 | 287459.6 | 37274.56 | 1623149.1934 | 154.7907 | 708.1094 | 0.3813
Model 17 | ESe | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ13 | ChlrCap | 399.7133 | 268538.5 | 37106.07 | 1466059.9695 | 130.8961 | 671.8277 | 0.32747
Model 17 | ESe | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ13 | ChlrCap | 393.3575 | 255560.8 | 33623.93 | 1398959.9377 | 122.5152 | 649.6909 | 0.31146
Model 17 | ESe | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ13 | ChlrCap | 380.471 | 234584 | 25363.69 | 1317052.0878 | 115.162 | 616.5621 | 0.30268
Model 17 | ESe | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ13 | ChlrCap | 365.916 | 222319.4 | 25688.32 | 1239030.1555 | 106.2174 | 607.5695 | 0.29028
Model 17 | EUn | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ13 | ChlrCap | 2548.0427 | 2375312 | 599272.6 | 11187582.0645 | 2606.8695 | 932.2104 | 1.0231
Model 17 | EUn | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ13 | ChlrCap | 2603.7117 | 2353132 | 590684.6 | 10996766.3212 | 2612.5957 | 903.7606 | 1.0034
Model 17 | EUn | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ13 | ChlrCap | 2532.0783 | 2306850 | 588887.1 | 10622956.4982 | 2546.2339 | 911.05 | 1.0056
Model 17 | EUn | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ13 | ChlrCap | 2391.7757 | 2081448 | 483789.8 | 9799523.9543 | 2343.2321 | 870.2522 | 0.9797
Model 17 | EUn | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ13 | ChlrCap | 2296.1407 | 1997329 | 446391.1 | 9242832.0399 | 2237.5401 | 869.8635 | 0.97448
Model 17 | Hsp | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ13 | ChlrCap | 922.8818 | 615504.2 | 41365.28 | 4467890.5674 | 751.7495 | 666.9372 | 0.81457
Model 17 | Hsp | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ13 | ChlrCap | 924.1015 | 612977.3 | 41107.33 | 4443783.5229 | 754.3322 | 663.3225 | 0.81629
Model 17 | Hsp | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ13 | ChlrCap | 939.1933 | 590032.8 | 40880.23 | 4355303.7995 | 742.6715 | 628.2336 | 0.79075
Model 17 | Hsp | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ13 | ChlrCap | 952.4823 | 566008.6 | 30274.36 | 4251867.2052 | 716.6541 | 594.2458 | 0.75241
Model 17 | Hsp | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ13 | ChlrCap | 967.7355 | 533517.6 | 29388.96 | 4030721.1735 | 652.4829 | 551.3052 | 0.67424
Model 17 | Htl | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ13 | ChlrCap | 239.844 | 304783.7 | 40102.05 | 1574548.0331 | 259.5679 | 1270.7581 | 1.0822
Model 17 | Htl | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ13 | ChlrCap | 232.1605 | 278517.3 | 35486.34 | 1254583.7202 | 241.1232 | 1199.6757 | 1.0386
Model 17 | Htl | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ13 | ChlrCap | 224.3243 | 272444.7 | 35062.13 | 1209283.9617 | 235.242 | 1214.5125 | 1.0487
Model 17 | Htl | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ13 | ChlrCap | 206.0013 | 243718.2 | 32385.09 | 1130546.6064 | 219.8231 | 1183.0904 | 1.0671
Model 17 | Htl | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ13 | ChlrCap | 204.4572 | 240972.9 | 31763.93 | 1114645.7115 | 215.2207 | 1178.5985 | 1.0526
Model 17 | MBT | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ13 | ChlrCap | 406.2655 | 342931.7 | 38590.45 | 2341545.0199 | 405.743 | 844.1074 | 0.99871
Model 17 | MBT | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ13 | ChlrCap | 395.2757 | 320574.8 | 37844.44 | 2100840.7233 | 375.9793 | 811.0158 | 0.95118
Model 17 | MBT | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ13 | ChlrCap | 378.4635 | 308015.2 | 36193.42 | 2026098.7116 | 361.7903 | 813.8571 | 0.95594
Model 17 | MBT | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ13 | ChlrCap | 375.0285 | 295469.9 | 16605.62 | 1949919.1594 | 342.3489 | 787.8599 | 0.91286
Model 17 | MBT | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ13 | ChlrCap | 353.691 | 280343.5 | 15160.27 | 1818551.6084 | 320.1887 | 792.6227 | 0.90528
Model 17 | Nrs | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ13 | ChlrCap | 138.3341 | 203083.4 | 33747.89 | 1463957.6648 | 225.1603 | 1468.0646 | 1.6277
Model 17 | Nrs | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ13 | ChlrCap | 132.7963 | 159873.9 | 31546.28 | 1233068.9843 | 197.5075 | 1203.903 | 1.4873
Model 17 | Nrs | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ13 | ChlrCap | 129.6282 | 157676 | 31646.9 | 1213005.2767 | 195.6067 | 1216.3711 | 1.509
Model 17 | Nrs | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ13 | ChlrCap | 122.481 | 146586.7 | 29897.98 | 1176837.8627 | 187.7192 | 1196.8119 | 1.5326
Model 17 | Nrs | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ13 | ChlrCap | 118.2186 | 138768.4 | 29162.76 | 1128225.5614 | 175.73 | 1173.8288 | 1.4865
Model 17 | OfL | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ13 | ChlrCap | 429.9983 | 393697 | 109222.1 | 2101791.1196 | 422.2753 | 915.578 | 0.98204
Model 17 | OfL | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ13 | ChlrCap | 428.8553 | 376830.4 | 106204.6 | 1972081.5909 | 408.4381 | 878.6889 | 0.95239
Model 17 | OfL | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ13 | ChlrCap | 414.733 | 364766.2 | 109463.1 | 1894937.3669 | 396.2519 | 879.5206 | 0.95544
Model 17 | OfL | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ13 | ChlrCap | 416.0417 | 352345.9 | 97219.45 | 1911969.7655 | 393.0191 | 846.9005 | 0.94466
Model 17 | OfL | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ13 | ChlrCap | 404.4273 | 340438.3 | 51954.38 | 1826244.3435 | 367.2861 | 841.7787 | 0.90816
Model 17 | OfS | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ13 | ChlrCap | 29.1718 | 25222.07 | 4940.481 | 131971.5939 | 24.7525 | 864.6035 | 0.84851
Model 17 | OfS | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ13 | ChlrCap | 28.9361 | 24427.3 | 4822.125 | 124732.5122 | 23.4461 | 844.1801 | 0.81027
Model 17 | OfS | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ13 | ChlrCap | 29.0007 | 23969.69 | 4825.172 | 121677.6031 | 22.9491 | 826.5223 | 0.79133
Model 17 | OfS | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ13 | ChlrCap | 26.3782 | 21126.43 | 4539.344 | 112372.0798 | 21.036 | 800.9039 | 0.79748
Model 17 | OfS | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ13 | ChlrCap | 25.6917 | 20316.54 | 4121.502 | 107006.9889 | 19.6365 | 790.782 | 0.76431
Model 17 | Rt3 | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ13 | ChlrCap | 321.207 | 335440.9 | 96756.16 | 1788106.7362 | 449.8641 | 1044.3138 | 1.4005
Model 17 | Rt3 | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ13 | ChlrCap | 319.3022 | 321130.1 | 96984.36 | 1712661.2544 | 447.3167 | 1005.7248 | 1.4009
Model 17 | Rt3 | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ13 | ChlrCap | 305.8862 | 311552 | 96736.27 | 1669286.0317 | 433.8039 | 1018.5227 | 1.4182
Model 17 | Rt3 | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ13 | ChlrCap | 295.795 | 293287 | 86144.9 | 1535584.7421 | 404.4503 | 991.5212 | 1.3673
Model 17 | Rt3 | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ13 | ChlrCap | 284.9072 | 276141 | 75838.76 | 1424640.7186 | 375.7033 | 969.2315 | 1.3187
Model 17 | ECC | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ14 | ChlrCap | 842.3122 | 671599.1 | 112369.5 | 3630263.796 | 643.6821 | 797.328 | 0.76418
Model 17 | ECC | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ14 | ChlrCap | 839.8307 | 665407.4 | 111693.8 | 3559108.007 | 638.9151 | 792.3114 | 0.76077
Model 17 | ECC | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ14 | ChlrCap | 815.9963 | 646659.8 | 112911.3 | 3421292.4525 | 621.1083 | 792.4788 | 0.76117
Model 17 | ECC | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ14 | ChlrCap | 777.5993 | 594539.3 | 100018 | 3254226.422 | 566.2663 | 764.5831 | 0.72822
Model 17 | ECC | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ14 | ChlrCap | 742.634 | 569109.1 | 79060.55 | 3039457.9988 | 526.7603 | 766.3386 | 0.70931
Model 17 | ESe | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ14 | ChlrCap | 443.2102 | 265283.3 | 31168.25 | 1641393.585 | 152.1395 | 598.5497 | 0.34327
Model 17 | ESe | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ14 | ChlrCap | 436.6147 | 246165.1 | 30996.01 | 1481380.9342 | 126.3038 | 563.804 | 0.28928
Model 17 | ESe | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ14 | ChlrCap | 431.0297 | 234249.8 | 28084.51 | 1382745.8925 | 113.0269 | 543.4656 | 0.26223
Model 17 | ESe | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ14 | ChlrCap | 416.4333 | 211606.2 | 20183.97 | 1297888.5302 | 101.108 | 508.1394 | 0.2428
Model 17 | ESe | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ14 | ChlrCap | 398.6307 | 200845 | 20103.34 | 1222525.8658 | 92.2073 | 503.8373 | 0.23131
Model 17 | EUn | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ14 | ChlrCap | 2765.1257 | 2128874 | 535562.6 | 11302266.3283 | 2499.8255 | 769.9014 | 0.90405
Model 17 | EUn | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ14 | ChlrCap | 2751.5513 | 2108764 | 526537.6 | 11086977.3177 | 2489.9465 | 766.3909 | 0.90492
Model 17 | EUn | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ14 | ChlrCap | 2661.1527 | 2076587 | 534580.6 | 10597966.9226 | 2418.5157 | 780.3337 | 0.90882
Model 17 | EUn | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ14 | ChlrCap | 2534.953 | 1891655 | 447926.2 | 9806801.6565 | 2229.0671 | 746.2288 | 0.87933
Model 17 | EUn | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ14 | ChlrCap | 2442.6647 | 1814981 | 406793.4 | 9268795.6108 | 2120.2805 | 743.0332 | 0.86802
Model 17 | Hsp | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ14 | ChlrCap | 966.1242 | 549671.7 | 35551.25 | 4598642.2427 | 744.8037 | 568.9451 | 0.77092
Model 17 | Hsp | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ14 | ChlrCap | 965.485 | 547043.4 | 35357.66 | 4570836.8757 | 742.9757 | 566.5996 | 0.76954
Model 17 | Hsp | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ14 | ChlrCap | 989.8152 | 522034.7 | 35347.99 | 4451647.3095 | 719.8866 | 527.4062 | 0.72729
Model 17 | Hsp | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ14 | ChlrCap | 1006.211 | 502081.9 | 25628.51 | 4352160.9918 | 703.5811 | 498.9827 | 0.69924
Model 17 | Hsp | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ14 | ChlrCap | 1033.492 | 473972.3 | 24905.89 | 4151217.4889 | 648.0288 | 458.6125 | 0.62703
Model 17 | Htl | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ14 | ChlrCap | 254.5663 | 270178.1 | 35506.23 | 1671935.562 | 250.2177 | 1061.3269 | 0.98292
Model 17 | Htl | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ14 | ChlrCap | 246.2812 | 246517.7 | 31543.5 | 1364932.4229 | 233.2405 | 1000.9604 | 0.94705
Model 17 | Htl | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ14 | ChlrCap | 238.4502 | 241048.5 | 31135.42 | 1306062.1952 | 226.4887 | 1010.8968 | 0.94984
Model 17 | Htl | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ14 | ChlrCap | 213.8892 | 220340 | 30071.6 | 1147559.2893 | 210.7109 | 1030.1597 | 0.98514
Model 17 | Htl | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ14 | ChlrCap | 212.2535 | 217983.3 | 29503.59 | 1132780.8268 | 206.3591 | 1026.9951 | 0.97223
Model 17 | MBT | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ14 | ChlrCap | 416.1008 | 323743.1 | 36039.64 | 2357946.5029 | 395.6689 | 778.04 | 0.9509
Model 17 | MBT | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ14 | ChlrCap | 405.316 | 301588.6 | 35623 | 2117373.1055 | 366.6259 | 744.0826 | 0.90454
Model 17 | MBT | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ14 | ChlrCap | 392.189 | 291582.7 | 34160.97 | 2033790.5053 | 351.9734 | 743.475 | 0.89746
Model 17 | MBT | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ14 | ChlrCap | 386.476 | 280495.1 | 15115.27 | 1960192.2732 | 334.2724 | 725.7762 | 0.86492
Model 17 | MBT | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ14 | ChlrCap | 365.1983 | 264002.9 | 13616.97 | 1827988.2286 | 309.3687 | 722.9028 | 0.84713
Model 17 | Nrs | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ14 | ChlrCap | 137.3265 | 186213.9 | 31326.6 | 1534647.5937 | 221.7957 | 1355.9941 | 1.6151
Model 17 | Nrs | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ14 | ChlrCap | 131.5436 | 144432 | 29224.19 | 1298817.9849 | 193.2851 | 1097.9779 | 1.4694
Model 17 | Nrs | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ14 | ChlrCap | 128.4714 | 142931.3 | 29398.07 | 1276929.3339 | 191.399 | 1112.5535 | 1.4898
Model 17 | Nrs | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ14 | ChlrCap | 122.4209 | 131644 | 27515.87 | 1239133.3762 | 183.8619 | 1075.3397 | 1.5019
Model 17 | Nrs | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ14 | ChlrCap | 121.6014 | 124631.9 | 26825.02 | 1191633.1978 | 172.3841 | 1024.9216 | 1.4176
Model 17 | OfL | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ14 | ChlrCap | 449.7138 | 384063.7 | 95126.55 | 2099457.871 | 402.9626 | 854.018 | 0.89604
Model 17 | OfL | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ14 | ChlrCap | 448.4922 | 363847.3 | 93050.05 | 1957303.5358 | 389.6627 | 811.2679 | 0.86883
Model 17 | OfL | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ14 | ChlrCap | 434.1887 | 354091.8 | 94851.5 | 1882115.5158 | 372.3029 | 815.5252 | 0.85747
Model 17 | OfL | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ14 | ChlrCap | 438.5937 | 341307.1 | 86547.84 | 1902231.2063 | 369.354 | 778.1852 | 0.84213
Model 17 | OfL | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ14 | ChlrCap | 426.4855 | 329681.8 | 42273.18 | 1818893.1407 | 352.4276 | 773.02 | 0.82635
Model 17 | OfS | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ14 | ChlrCap | 30.8227 | 23889.34 | 4327.549 | 132581.6081 | 23.3884 | 775.0556 | 0.7588
Model 17 | OfS | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ14 | ChlrCap | 30.6523 | 23120.94 | 4193.925 | 125095.7046 | 22.1471 | 754.2973 | 0.72253
Model 17 | OfS | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ14 | ChlrCap | 29.9938 | 22780.4 | 4220.375 | 122006.639 | 21.7256 | 759.5036 | 0.72434
Model 17 | OfS | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ14 | ChlrCap | 28.0533 | 20277.95 | 4071.552 | 112271.735 | 19.7367 | 722.8363 | 0.70354
Model 17 | OfS | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ14 | ChlrCap | 27.2422 | 19491.23 | 3548.493 | 106803.3682 | 18.5768 | 715.4789 | 0.68191
Model 17 | Rt3 | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ14 | ChlrCap | 328.0502 | 304489.5 | 86710.65 | 1762420.7819 | 435.6367 | 928.1797 | 1.328
Model 17 | Rt3 | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ14 | ChlrCap | 326.0978 | 288725.9 | 87011.41 | 1675833.9707 | 427.6323 | 885.3966 | 1.3114
Model 17 | Rt3 | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ14 | ChlrCap | 307.0428 | 280942.9 | 89691.09 | 1621545.1618 | 411.2943 | 914.9958 | 1.3395
Model 17 | Rt3 | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ14 | ChlrCap | 298.3908 | 265060.5 | 78699.41 | 1488774.129 | 383.734 | 888.2997 | 1.286
Model 17 | Rt3 | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ14 | ChlrCap | 286.5403 | 249138.7 | 64943.03 | 1383021.6483 | 355.6155 | 869.4717 | 1.2411
Model 17 | ECC | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ15 | ChlrCap | 1071.5732 | 1315904 | 187341.5 | 3734204.0785 | 837.5715 | 1228.0113 | 0.78163
Model 17 | ECC | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ15 | ChlrCap | 1067.7025 | 1306417 | 186445.9 | 3680990.9777 | 833.5689 | 1223.5777 | 0.78071
Model 17 | ECC | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ15 | ChlrCap | 1039.5275 | 1246976 | 182020 | 3572558.0586 | 778.2987 | 1199.5604 | 0.7487
Model 17 | ECC | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ15 | ChlrCap | 999.8655 | 1154974 | 164177.3 | 3392659.8148 | 715.358 | 1155.1294 | 0.71545
Model 17 | ECC | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ15 | ChlrCap | 966.2553 | 1103519 | 148370.6 | 3088960.4314 | 667.554 | 1142.0573 | 0.69087
Model 17 | ESe | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ15 | ChlrCap | 571.8747 | 551786.5 | 65574.96 | 1699823.5334 | 196.7545 | 964.8731 | 0.34405
Model 17 | ESe | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ15 | ChlrCap | 563.4945 | 509791.6 | 64994.7 | 1444173.1454 | 162.2203 | 904.6967 | 0.28788
Model 17 | ESe | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ15 | ChlrCap | 548.3095 | 476230 | 55050.91 | 1373466.1278 | 148.4657 | 868.5423 | 0.27077
Model 17 | ESe | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ15 | ChlrCap | 531.334 | 439317 | 40336.45 | 1295582.6038 | 136.2413 | 826.8189 | 0.25641
Model 17 | ESe | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ15 | ChlrCap | 512.9195 | 419980.2 | 37572.21 | 1188735.034 | 125.6034 | 818.8033 | 0.24488
Model 17 | EUn | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ15 | ChlrCap | 3491.2633 | 4094540 | 861071.3 | 11177332.8605 | 3181.9572 | 1172.7961 | 0.91141
Model 17 | EUn | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ15 | ChlrCap | 3472.33 | 4066250 | 852403.9 | 11033751.3482 | 3169.8681 | 1171.0437 | 0.91289
Model 17 | EUn | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ15 | ChlrCap | 3357.4867 | 3933196 | 836910.3 | 10744227.6671 | 3043.4993 | 1171.4703 | 0.90648
Model 17 | EUn | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ15 | ChlrCap | 3229.451 | 3599496 | 672454.7 | 10001306.4619 | 2788.4277 | 1114.5845 | 0.86344
Model 17 | EUn | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ15 | ChlrCap | 3124.6453 | 3469599 | 629488.4 | 9236117.8417 | 2659.086 | 1110.3977 | 0.851
Model 17 | Hsp | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ15 | ChlrCap | 1138.0515 | 1103435 | 59077.68 | 4594873.1571 | 868.0389 | 969.5827 | 0.76274
Model 17 | Hsp | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ15 | ChlrCap | 1137.3063 | 1100390 | 58793.78 | 4579597.6729 | 866.4989 | 967.5406 | 0.76189
Model 17 | Hsp | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ15 | ChlrCap | 1170.9917 | 1040035 | 58326.24 | 4472023.66 | 837.6736 | 888.1659 | 0.71535
Model 17 | Hsp | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ15 | ChlrCap | 1192.3815 | 997535.4 | 42957.69 | 4356586.993 | 833.3249 | 836.5908 | 0.69887
Model 17 | Hsp | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ15 | ChlrCap | 1221.3843 | 943371.6 | 42073.1 | 4060420.8617 | 772.6323 | 772.379 | 0.63259
Model 17 | Htl | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ15 | ChlrCap | 320.6793 | 496776.8 | 55962.49 | 1620288.9015 | 320.2235 | 1549.1388 | 0.99858
Model 17 | Htl | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ15 | ChlrCap | 312.4632 | 459797.4 | 50307.2 | 1243842.5698 | 297.8973 | 1471.5251 | 0.95338
Model 17 | Htl | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ15 | ChlrCap | 302.4662 | 447450.1 | 48617.03 | 1215811.6377 | 288.7981 | 1479.3393 | 0.95481
Model 17 | Htl | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ15 | ChlrCap | 275.608 | 407615.5 | 45830.87 | 1120416.8539 | 264.1556 | 1478.9683 | 0.95845
Model 17 | Htl | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ15 | ChlrCap | 273.3932 | 403471.4 | 44904.5 | 1098406.3239 | 259.3777 | 1475.7918 | 0.94874
Model 17 | MBT | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ15 | ChlrCap | 513.0728 | 608779.1 | 57730.32 | 2570773.0375 | 485.5441 | 1186.5354 | 0.94635
Model 17 | MBT | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ15 | ChlrCap | 501.2435 | 562137.3 | 56396.73 | 2261719.8242 | 448.2036 | 1121.4855 | 0.89418
Model 17 | MBT | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ15 | ChlrCap | 481.6768 | 538753.1 | 53702.2 | 2201894.7339 | 422.9629 | 1118.4949 | 0.87811
Model 17 | MBT | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ15 | ChlrCap | 475.9037 | 519151.6 | 26349.02 | 2118700.6178 | 400.8548 | 1090.8754 | 0.8423
Model 17 | MBT | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ15 | ChlrCap | 453.7342 | 488764.1 | 24439.39 | 1959740.3927 | 369.0255 | 1077.2036 | 0.81331
Model 17 | Nrs | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ15 | ChlrCap | 182.887 | 362065.6 | 48932.39 | 1463874.5838 | 268.219 | 1979.723 | 1.4666
Model 17 | Nrs | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ15 | ChlrCap | 176.6895 | 288286.4 | 46471.4 | 1161712.2169 | 232.0503 | 1631.5989 | 1.3133
Model 17 | Nrs | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ15 | ChlrCap | 169.2027 | 281135 | 46485.57 | 1142208.5604 | 226.3273 | 1661.5282 | 1.3376
Model 17 | Nrs | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ15 | ChlrCap | 159.5154 | 264513.9 | 44393.04 | 1109687.0233 | 217.7284 | 1658.2339 | 1.3649
Model 17 | Nrs | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ15 | ChlrCap | 156.3556 | 252835.2 | 43632.94 | 1046697.8808 | 204.9518 | 1617.0524 | 1.3108
Model 17 | OfL | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ15 | ChlrCap | 550.1308 | 661024.6 | 150192.9 | 2352111.6788 | 452.4705 | 1201.5771 | 0.82248
Model 17 | OfL | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ15 | ChlrCap | 548.4895 | 627803.8 | 147956.2 | 2179180.0258 | 435.6571 | 1144.605 | 0.79429
Model 17 | OfL | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ15 | ChlrCap | 508.8343 | 603604.1 | 148813.4 | 2120522.5985 | 422.6439 | 1186.2488 | 0.83061
Model 17 | OfL | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ15 | ChlrCap | 536.7805 | 598206.9 | 137611.1 | 2109976.3259 | 424.6791 | 1114.4349 | 0.79116
Model 17 | OfL | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ15 | ChlrCap | 522.6575 | 578498.1 | 96978.36 | 1998902.5428 | 406.9847 | 1106.8398 | 0.77868
Model 17 | OfS | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ15 | ChlrCap | 36.3228 | 42562.46 | 7769.448 | 139352.8365 | 28.9069 | 1171.7841 | 0.79583
Model 17 | OfS | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ15 | ChlrCap | 36.0697 | 41966.79 | 7642.452 | 130480.306 | 27.5857 | 1163.4926 | 0.76479
Model 17 | OfS | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ15 | ChlrCap | 34.8143 | 40630.14 | 7592.519 | 126488.2857 | 26.3646 | 1167.054 | 0.75729
Model 17 | OfS | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ15 | ChlrCap | 32.9766 | 36628.51 | 7121.402 | 117798.8544 | 23.8536 | 1110.7408 | 0.72335
Model 17 | OfS | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ15 | ChlrCap | 32.0845 | 35330.79 | 6710.866 | 110928.6045 | 22.6052 | 1101.1785 | 0.70455
Model 17 | Rt3 | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ15 | ChlrCap | 400.5612 | 573371.1 | 137005.5 | 1991421.2151 | 523.2378 | 1431.4196 | 1.3063
Model 17 | Rt3 | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ15 | ChlrCap | 399.2927 | 544477.8 | 136901.6 | 1887889.2855 | 515.8729 | 1363.6058 | 1.292
Model 17 | Rt3 | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ15 | ChlrCap | 381.8447 | 514583.4 | 131818.6 | 1847727.4569 | 486.3753 | 1347.625 | 1.2738
Model 17 | Rt3 | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ15 | ChlrCap | 370.6765 | 491783.2 | 117934.9 | 1692135.6266 | 461.6422 | 1326.718 | 1.2454
Model 17 | Rt3 | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ15 | ChlrCap | 360.4552 | 464735.8 | 106057.3 | 1537648.0006 | 431.0084 | 1289.3026 | 1.1957
Model 17 | ECC | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2003-CZ16 | ChlrCap | 457.4017 | 237026.6 | 57873.9 | 4286079.3189 | 199.1614 | 518.2023 | 0.43542
Model 17 | ECC | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2007-CZ16 | ChlrCap | 455.6992 | 234725.5 | 57486.75 | 4219657.2685 | 197.8302 | 515.0887 | 0.43412
Model 17 | ECC | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2011-CZ16 | ChlrCap | 435.1002 | 227594.3 | 60547.2 | 3917143.4701 | 180.3987 | 523.0848 | 0.41461
Model 17 | ECC | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2015-CZ16 | ChlrCap | 409.0627 | 206521.5 | 53266.6 | 3704528.9965 | 156.3346 | 504.8652 | 0.38218
Model 17 | ECC | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ECC-2020-CZ16 | ChlrCap | 382.9705 | 196912.5 | 39426.63 | 3593070.5639 | 133.6139 | 514.1715 | 0.34889
Model 17 | ESe | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2003-CZ16 | ChlrCap | 234.3245 | 100569.6 | 18472.17 | 2051371.7891 | 103.7263 | 429.1894 | 0.44266
Model 17 | ESe | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2007-CZ16 | ChlrCap | 230.2368 | 86195.67 | 18443.54 | 1938149.4878 | 87.8809 | 374.3783 | 0.3817
Model 17 | ESe | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2011-CZ16 | ChlrCap | 225.8828 | 81152.02 | 16531.15 | 1735487.2884 | 78.1641 | 359.266 | 0.34604
Model 17 | ESe | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2015-CZ16 | ChlrCap | 217.4782 | 72756.41 | 12346.7 | 1641454.3127 | 68.1861 | 334.5458 | 0.31353
Model 17 | ESe | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-ESe-2020-CZ16 | ChlrCap | 202.1828 | 68619.48 | 12175.1 | 1604838.5313 | 61.7991 | 339.3932 | 0.30566
Model 17 | EUn | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2003-CZ16 | ChlrCap | 1624.4567 | 811671.3 | 287264.8 | 13998286.2474 | 442.4648 | 499.6571 | 0.27238
Model 17 | EUn | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2007-CZ16 | ChlrCap | 1615.792 | 798960.6 | 279618.5 | 13745709.8687 | 440.0145 | 494.47 | 0.27232
Model 17 | EUn | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2011-CZ16 | ChlrCap | 1564.3213 | 795050.4 | 295389 | 12715283.0434 | 399.4091 | 508.2398 | 0.25532
Model 17 | EUn | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2015-CZ16 | ChlrCap | 1441.557 | 665331.1 | 251866.8 | 11671181.9285 | 324.6578 | 461.5364 | 0.22521
Model 17 | EUn | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-EUn-2020-CZ16 | ChlrCap | 1356.255 | 631317.3 | 217961.6 | 11318756.8687 | 290.642 | 465.4857 | 0.2143
Model 17 | Hsp | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2003-CZ16 | ChlrCap | 642.4422 | 197214.1 | 20897.5 | 5101637.0481 | 569.6818 | 306.9756 | 0.88674
Model 17 | Hsp | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2007-CZ16 | ChlrCap | 641.734 | 195789.6 | 20870.44 | 5067749.9086 | 566.7391 | 305.0946 | 0.88314
Model 17 | Hsp | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2011-CZ16 | ChlrCap | 645.7175 | 186113.3 | 20865.19 | 4836516.6671 | 558.5625 | 288.2271 | 0.86503
Model 17 | Hsp | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2015-CZ16 | ChlrCap | 648.9835 | 179142.6 | 15693.12 | 4721439.1137 | 543.4587 | 276.0357 | 0.8374
Model 17 | Hsp | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Hsp-2020-CZ16 | ChlrCap | 655.2332 | 167461.5 | 15123.2 | 4591565.2743 | 489.8635 | 255.5754 | 0.74762
Model 17 | Htl | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2003-CZ16 | ChlrCap | 148.4864 | 132058.3 | 24439.7 | 1875132.8873 | 182.2325 | 889.363 | 1.2273
Model 17 | Htl | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2007-CZ16 | ChlrCap | 142.3047 | 118580.5 | 21399.52 | 1625156.8443 | 167.2791 | 833.2858 | 1.1755
Model 17 | Htl | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2011-CZ16 | ChlrCap | 137.1796 | 117451.5 | 21526.17 | 1529380.9508 | 163.2737 | 856.1881 | 1.1902
Model 17 | Htl | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2015-CZ16 | ChlrCap | 119.3118 | 95836.89 | 18885.93 | 1380990.3116 | 149.0719 | 803.2476 | 1.2494
Model 17 | Htl | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Htl-2020-CZ16 | ChlrCap | 118.4843 | 94744.87 | 18489.38 | 1372280.7753 | 145.6033 | 799.6408 | 1.2289
Model 17 | MBT | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2003-CZ16 | ChlrCap | 263.6658 | 113121.7 | 18147.91 | 2416343.8851 | 227.7551 | 429.0344 | 0.8638
Model 17 | MBT | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2007-CZ16 | ChlrCap | 255.6078 | 107135.7 | 17957.42 | 2220214.6471 | 211.5726 | 419.1409 | 0.82772
Model 17 | MBT | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2011-CZ16 | ChlrCap | 242.0863 | 104119.2 | 17446.91 | 2083603.3951 | 206.6016 | 430.0912 | 0.85342
Model 17 | MBT | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2015-CZ16 | ChlrCap | 240.6683 | 101658.2 | 7139.077 | 1998767.7644 | 192.3637 | 422.3996 | 0.79929
Model 17 | MBT | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-MBT-2020-CZ16 | ChlrCap | 224.0473 | 94801.91 | 5979.604 | 1887126.7749 | 172.0221 | 423.1334 | 0.76779
Model 17 | Nrs | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2003-CZ16 | ChlrCap | 83.2297 | 64225.6 | 17198.33 | 1733970.1664 | 165.1875 | 771.6672 | 1.9847
Model 17 | Nrs | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2007-CZ16 | ChlrCap | 79.3774 | 47721.73 | 15601.93 | 1566420.9574 | 145.8436 | 601.2005 | 1.8373
Model 17 | Nrs | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2011-CZ16 | ChlrCap | 78.7542 | 47364.45 | 15795.1 | 1528203.0937 | 145.1753 | 601.4211 | 1.8434
Model 17 | Nrs | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2015-CZ16 | ChlrCap | 78.6215 | 42298.29 | 14477.5 | 1480827.5661 | 140.1342 | 537.999 | 1.7824
Model 17 | Nrs | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Nrs-2020-CZ16 | ChlrCap | 78.647 | 38974.04 | 13913.99 | 1448305.9807 | 129.944 | 495.5569 | 1.6522
Model 17 | OfL | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2003-CZ16 | ChlrCap | 320.445 | 157278 | 51530.82 | 2089459.6436 | 291.5248 | 490.8112 | 0.90975
Model 17 | OfL | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2007-CZ16 | ChlrCap | 319.4318 | 149273.9 | 47079.54 | 1999970.2427 | 275.1341 | 467.3107 | 0.86132
Model 17 | OfL | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2011-CZ16 | ChlrCap | 302.0675 | 145991.2 | 47777.51 | 1865553.0785 | 264.0592 | 483.3065 | 0.87417
Model 17 | OfL | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2015-CZ16 | ChlrCap | 305.7612 | 134751.6 | 46882.71 | 1934470.2356 | 256.8615 | 440.7087 | 0.84007
Model 17 | OfL | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfL-2020-CZ16 | ChlrCap | 292.609 | 128809.4 | 8703.141 | 1864057.5264 | 245.0785 | 440.21 | 0.83756
Model 17 | OfS | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2003-CZ16 | ChlrCap | 20.1187 | 9581.365 | 1969.783 | 146905.2509 | 16.1597 | 476.2427 | 0.80322
Model 17 | OfS | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2007-CZ16 | ChlrCap | 19.935 | 9460.146 | 1865.541 | 141345.9948 | 15.6123 | 474.5494 | 0.78316
Model 17 | OfS | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2011-CZ16 | ChlrCap | 19.4755 | 9370.526 | 1904.536 | 136771.3724 | 15.3856 | 481.1441 | 0.79
Model 17 | OfS | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2015-CZ16 | ChlrCap | 17.6336 | 7900.497 | 1482.58 | 123348.0094 | 13.3353 | 448.0365 | 0.75624
Model 17 | OfS | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-OfS-2020-CZ16 | ChlrCap | 17.013 | 7543.696 | 1309.511 | 119147.0767 | 12.6765 | 443.4086 | 0.74511
Model 17 | Rt3 | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2003-CZ16 | ChlrCap | 217.8227 | 110623.5 | 53605.86 | 1846667.4256 | 332.7947 | 507.8604 | 1.5278
Model 17 | Rt3 | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2007-CZ16 | ChlrCap | 216.4523 | 107570.6 | 53645.22 | 1798074.2251 | 326.3477 | 496.9713 | 1.5077
Model 17 | Rt3 | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2011-CZ16 | ChlrCap | 199.7127 | 105281.5 | 57069.29 | 1643911.3482 | 315.0631 | 527.1649 | 1.5776
Model 17 | Rt3 | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2015-CZ16 | ChlrCap | 188.7828 | 96962.82 | 50419.35 | 1550152.823 | 289.398 | 513.621 | 1.533
Model 17 | Rt3 | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model17-1.16kwpton-Rt3-2020-CZ16 | ChlrCap | 178.089 | 89775.52 | 38310.19 | 1489749.1899 | 265.2717 | 504.1048 | 1.4895
Model 7 | ECC | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ01 | ChlrCap | 363.0903 | 25329.31 | 13191.63 | 3473282.7644 | 418.5157 | 69.7604 | 1.1526
Model 7 | ECC | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ01 | ChlrCap | 362.3947 | 25079.47 | 13128.86 | 3427628.7433 | 417.3629 | 69.2049 | 1.1517
Model 7 | ECC | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ01 | ChlrCap | 358.621 | 25422.81 | 14694.4 | 3354206.136 | 416.8385 | 70.8905 | 1.1623
Model 7 | ECC | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ01 | ChlrCap | 337.2 | 24622.8 | 13961.43 | 3244187.8628 | 403.0633 | 73.0214 | 1.1953
Model 7 | ECC | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ01 | ChlrCap | 308.2373 | 23355.01 | 4634.174 | 3163553.4596 | 359.8411 | 75.7696 | 1.1674
Model 7 | ESe | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ01 | ChlrCap | 177.9213 | 9696.205 | 950.8166 | 1617242.5524 | 112.4331 | 54.4971 | 0.63193
Model 7 | ESe | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ01 | ChlrCap | 172.2432 | 8888.606 | 979.5164 | 1543227.5757 | 105.2137 | 51.605 | 0.61084
Model 7 | ESe | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ01 | ChlrCap | 171.2935 | 9021.132 | 1103.1 | 1499327.1862 | 104.704 | 52.6648 | 0.61125
Model 7 | ESe | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ01 | ChlrCap | 162.6435 | 8669.147 | 604.3058 | 1454900.4318 | 99.7951 | 53.3015 | 0.61358
Model 7 | ESe | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ01 | ChlrCap | 147.6032 | 8155.214 | 411.2522 | 1422947.92 | 92.1489 | 55.2509 | 0.6243
Model 7 | EUn | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ01 | ChlrCap | 1393.3897 | 80324.95 | 67189.05 | 11657039.2192 | 1417.8464 | 57.6472 | 1.0176
Model 7 | EUn | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ01 | ChlrCap | 1386.448 | 78169.21 | 62268.79 | 11471354.6811 | 1415.1825 | 56.3809 | 1.0207
Model 7 | EUn | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ01 | ChlrCap | 1376.0627 | 80278.91 | 68036.88 | 11125279.456 | 1414.0571 | 58.3396 | 1.0276
Model 7 | EUn | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ01 | ChlrCap | 1253.919 | 69520.09 | 58726.94 | 10477242.7878 | 1349.6942 | 55.4422 | 1.0764
Model 7 | EUn | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ01 | ChlrCap | 1169.1157 | 61471.13 | 37437.43 | 10110518.8265 | 1207.9509 | 52.5792 | 1.0332
Model 7 | Hsp | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ01 | ChlrCap | 534.269 | 8134.483 | 1086.875 | 4275773.5768 | 431.0148 | 15.2254 | 0.80674
Model 7 | Hsp | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ01 | ChlrCap | 533.8913 | 8113.932 | 1084.233 | 4259474.0938 | 430.7391 | 15.1977 | 0.80679
Model 7 | Hsp | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ01 | ChlrCap | 533.2168 | 8127.108 | 1107.53 | 4208282.2556 | 429.9528 | 15.2417 | 0.80634
Model 7 | Hsp | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ01 | ChlrCap | 532.3435 | 7910.608 | 829.343 | 4127917.5463 | 423.9412 | 14.86 | 0.79637
Model 7 | Hsp | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ01 | ChlrCap | 528.477 | 7265.639 | 660.42 | 4029247.993 | 378.6884 | 13.7483 | 0.71657
Model 7 | Htl | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ01 | ChlrCap | 121.6717 | 20697.31 | 8765.026 | 1515424.4342 | 118.0134 | 170.1079 | 0.96993
Model 7 | Htl | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ01 | ChlrCap | 115.4313 | 16586.07 | 7115.595 | 1306499.0961 | 107.6167 | 143.6878 | 0.9323
Model 7 | Htl | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ01 | ChlrCap | 112.9238 | 17061.08 | 7417.798 | 1238254.8158 | 107.476 | 151.0849 | 0.95176
Model 7 | Htl | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ01 | ChlrCap | 95.2545 | 11405.27 | 5723.375 | 1128097.7565 | 100.0662 | 119.7348 | 1.0505
Model 7 | Htl | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ01 | ChlrCap | 93.868 | 11306.74 | 5644.045 | 1124366.0372 | 96.9128 | 120.4536 | 1.0324
Model 7 | MBT | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ01 | ChlrCap | 197.4575 | 15032.05 | 3894.1 | 2065094.4138 | 173.2684 | 76.128 | 0.8775
Model 7 | MBT | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ01 | ChlrCap | 192.24 | 14240.55 | 4266.294 | 1888731.4842 | 160.1995 | 74.0769 | 0.83333
Model 7 | MBT | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ01 | ChlrCap | 189.7313 | 14157.86 | 4257.489 | 1843162.0457 | 157.7746 | 74.6206 | 0.83157
Model 7 | MBT | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ01 | ChlrCap | 189.4815 | 14997.2 | 1646.272 | 1785744.6659 | 151.0513 | 79.1486 | 0.79718
Model 7 | MBT | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ01 | ChlrCap | 173.0733 | 15082.62 | 1739.916 | 1656252.932 | 137.8194 | 87.1458 | 0.79631
Model 7 | Nrs | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ01 | ChlrCap | 65.0155 | 3289.704 | 2526.695 | 1508197.5505 | 121.3085 | 50.5987 | 1.8658
Model 7 | Nrs | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ01 | ChlrCap | 64.0681 | 1963.971 | 1811.591 | 1394099.2503 | 111.5843 | 30.6544 | 1.7417
Model 7 | Nrs | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ01 | ChlrCap | 64.0681 | 1963.971 | 1811.591 | 1394099.2503 | 111.5843 | 30.6544 | 1.7417
Model 7 | Nrs | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ01 | ChlrCap | 63.8031 | 1367.098 | 1217.931 | 1361571.9641 | 108.3994 | 21.4268 | 1.699
Model 7 | Nrs | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ01 | ChlrCap | 62.0487 | 1113.284 | 995.0484 | 1336453.3732 | 98.2505 | 17.9421 | 1.5834
Model 7 | OfL | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ01 | ChlrCap | 267.187 | 20136.13 | 3926.175 | 1707699.9355 | 230.7596 | 75.3634 | 0.86366
Model 7 | OfL | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ01 | ChlrCap | 262.4838 | 18855.07 | 3233.354 | 1607177.6952 | 221.2135 | 71.8333 | 0.84277
Model 7 | OfL | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ01 | ChlrCap | 258.7623 | 19045.6 | 4154.229 | 1560405.1079 | 218.5816 | 73.6027 | 0.84472
Model 7 | OfL | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ01 | ChlrCap | 251.6 | 16824.49 | 3814.42 | 1601257.3376 | 210.8633 | 66.87 | 0.83809
Model 7 | OfL | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ01 | ChlrCap | 239.618 | 15495.08 | 165.0933 | 1486238.2814 | 194.0892 | 64.6658 | 0.80999
Model 7 | OfS | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ01 | ChlrCap | 16.798 | 716.2567 | 256.0124 | 119139.1777 | 11.6427 | 42.6395 | 0.6931
Model 7 | OfS | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ01 | ChlrCap | 16.4158 | 755.9978 | 218.1972 | 114272.7308 | 10.9543 | 46.053 | 0.6673
Model 7 | OfS | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ01 | ChlrCap | 16.3121 | 747.8095 | 216.8951 | 113670.9471 | 10.8616 | 45.8439 | 0.66586
Model 7 | OfS | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ01 | ChlrCap | 14.6981 | 642.671 | 117.0017 | 103215.2499 | 9.9623 | 43.7247 | 0.67779
Model 7 | OfS | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ01 | ChlrCap | 13.954 | 570.2164 | 90.2619 | 99122.2308 | 9.2757 | 40.864 | 0.66474
Model 7 | Rt3 | 2003 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ01 | ChlrCap | 153.7271 | 10866.02 | 21212.68 | 1511586.4162 | 247.0735 | 70.6838 | 1.6072
Model 7 | Rt3 | 2007 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ01 | ChlrCap | 152.8906 | 9810.231 | 20308.6 | 1430778.4666 | 250.178 | 64.165 | 1.6363
Model 7 | Rt3 | 2011 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ01 | ChlrCap | 150.8586 | 10525.25 | 22719.39 | 1401429.1524 | 249.2129 | 69.769 | 1.652
Model 7 | Rt3 | 2015 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ01 | ChlrCap | 139.6182 | 8819.749 | 18718.63 | 1313090.9226 | 226.7601 | 63.1705 | 1.6241
Model 7 | Rt3 | 2020 | CZ01 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ01 | ChlrCap | 128.2081 | 7338.206 | 13578.82 | 1242311.3645 | 204.5505 | 57.2367 | 1.5955
Model 7 | ECC | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ02 | ChlrCap | 622.7143 | 251768.3 | 59003.07 | 3262900.2274 | 669.8109 | 404.3079 | 1.0756
Model 7 | ECC | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ02 | ChlrCap | 620.6888 | 249351.7 | 58594.29 | 3204325.3458 | 665.7769 | 401.7338 | 1.0726
Model 7 | ECC | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ02 | ChlrCap | 618.5397 | 248861.8 | 58534.98 | 3199461.2954 | 664.391 | 402.3377 | 1.0741
Model 7 | ECC | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ02 | ChlrCap | 589.2032 | 228647.5 | 51019.9 | 3061812.694 | 633.8799 | 388.0622 | 1.0758
Model 7 | ECC | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ02 | ChlrCap | 557.0718 | 218498.7 | 35147.46 | 2907307.721 | 580.7312 | 392.2272 | 1.0425
Model 7 | ESe | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ02 | ChlrCap | 318.2727 | 106920.2 | 14852.03 | 1486026.4839 | 234.2274 | 335.939 | 0.73593
Model 7 | ESe | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ02 | ChlrCap | 309.8685 | 88389.61 | 15006.12 | 1361936.1664 | 197.3164 | 285.2488 | 0.63677
Model 7 | ESe | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ02 | ChlrCap | 308.0745 | 88174.76 | 14964.26 | 1357282.6374 | 196.8301 | 286.2125 | 0.6389
Model 7 | ESe | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ02 | ChlrCap | 300.8848 | 79621.54 | 10234.08 | 1293118.4061 | 177.6971 | 264.6246 | 0.59058
Model 7 | ESe | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ02 | ChlrCap | 285.2343 | 75798.4 | 10187.84 | 1243150.4434 | 169.9159 | 265.7408 | 0.59571
Model 7 | EUn | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ02 | ChlrCap | 2222.8973 | 823900.7 | 326360.4 | 10532056.2825 | 2193.8229 | 370.6427 | 0.98692
Model 7 | EUn | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ02 | ChlrCap | 2209.6417 | 810917.5 | 316429.2 | 10306040.0152 | 2186.5098 | 366.9905 | 0.98953
Model 7 | EUn | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ02 | ChlrCap | 2186.6183 | 807544.6 | 315142 | 10159030.8242 | 2177.8854 | 369.3121 | 0.99601
Model 7 | EUn | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ02 | ChlrCap | 2065.393 | 727518.6 | 262350.4 | 9463768.4936 | 2060.9775 | 352.2422 | 0.99786
Model 7 | EUn | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ02 | ChlrCap | 1962.3893 | 688165.9 | 220597.3 | 9044256.3787 | 1902.1019 | 350.6776 | 0.96928
Model 7 | Hsp | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ02 | ChlrCap | 819.109 | 164681 | 16193.16 | 4150104.381 | 580.2192 | 201.0489 | 0.70835
Model 7 | Hsp | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ02 | ChlrCap | 818.5588 | 163812.4 | 16180.47 | 4129667.6928 | 579.1365 | 200.123 | 0.70751
Model 7 | Hsp | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ02 | ChlrCap | 818.008 | 163696.2 | 16180.47 | 4126452.5428 | 578.8913 | 200.1156 | 0.70768
Model 7 | Hsp | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ02 | ChlrCap | 827.012 | 155554.3 | 10796.77 | 4041002.1325 | 562.5424 | 188.092 | 0.68021
Model 7 | Hsp | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ02 | ChlrCap | 844.9847 | 142608 | 10247.04 | 3880214.8781 | 512.0979 | 168.7699 | 0.60604
Model 7 | Htl | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ02 | ChlrCap | 192.1052 | 102509.9 | 23433.33 | 1440372.8512 | 183.9255 | 533.6134 | 0.95742
Model 7 | Htl | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ02 | ChlrCap | 183.6192 | 91195.85 | 20284.8 | 1166858.629 | 169.6691 | 496.6576 | 0.92403
Model 7 | Htl | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ02 | ChlrCap | 179.1558 | 90385.05 | 20419.6 | 1122928.6955 | 167.5339 | 504.5052 | 0.93513
Model 7 | Htl | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ02 | ChlrCap | 162.5328 | 77533.2 | 18110.35 | 1051425.5676 | 157.6961 | 477.031 | 0.97024
Model 7 | Htl | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ02 | ChlrCap | 161.267 | 76442.54 | 17822.77 | 1041606.5634 | 153.7884 | 474.0123 | 0.95363
Model 7 | MBT | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ02 | ChlrCap | 321.5922 | 140340.7 | 23032.04 | 2148583.8441 | 279.6731 | 436.3934 | 0.86965
Model 7 | MBT | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ02 | ChlrCap | 311.943 | 116866.1 | 22850.62 | 1927504.1172 | 231.8351 | 374.6393 | 0.7432
Model 7 | MBT | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ02 | ChlrCap | 307.7235 | 114055.5 | 21971.36 | 1852611.0551 | 226.0336 | 370.6428 | 0.73453
Model 7 | MBT | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ02 | ChlrCap | 305.3705 | 115415 | 8169.577 | 1795443.6377 | 212.6055 | 377.9507 | 0.69622
Model 7 | MBT | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ02 | ChlrCap | 285.5302 | 108924.9 | 7364.583 | 1679232.6553 | 192.3847 | 381.483 | 0.67378
Model 7 | Nrs | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ02 | ChlrCap | 105.7102 | 61087.69 | 17907.3 | 1424755.0614 | 178.3109 | 577.8788 | 1.6868
Model 7 | Nrs | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ02 | ChlrCap | 101.8806 | 44664.46 | 16429.56 | 1250222.727 | 152.1395 | 438.3999 | 1.4933
Model 7 | Nrs | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ02 | ChlrCap | 100.7931 | 44332.09 | 16594.82 | 1224661.57 | 151.1089 | 439.8327 | 1.4992
Model 7 | Nrs | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ02 | ChlrCap | 98.5594 | 39153.16 | 15159.05 | 1190251.4991 | 146.0393 | 397.2544 | 1.4817
Model 7 | Nrs | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ02 | ChlrCap | 100.1231 | 35321.97 | 14471.78 | 1154955.0093 | 134.7039 | 352.7855 | 1.3454
Model 7 | OfL | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ02 | ChlrCap | 380.9968 | 146897.1 | 55718.3 | 1860342.9906 | 288.261 | 385.5599 | 0.7566
Model 7 | OfL | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ02 | ChlrCap | 380.0078 | 151567.4 | 51990.31 | 1733027.5147 | 285.8836 | 398.8534 | 0.75231
Model 7 | OfL | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ02 | ChlrCap | 367.1977 | 149453.2 | 60527.36 | 1664503.8511 | 273.9843 | 407.0102 | 0.74615
Model 7 | OfL | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ02 | ChlrCap | 366.8677 | 140187.7 | 47314.91 | 1688219.3623 | 270.3655 | 382.1206 | 0.73696
Model 7 | OfL | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ02 | ChlrCap | 355.431 | 133737.5 | 4563.786 | 1595786.5487 | 257.5736 | 376.2685 | 0.72468
Model 7 | OfS | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ02 | ChlrCap | 23.8356 | 8588.821 | 1691.14 | 119947.2084 | 16.7386 | 360.3356 | 0.70225
Model 7 | OfS | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ02 | ChlrCap | 23.5463 | 9027.69 | 1577.193 | 113722.2815 | 16.7266 | 383.4022 | 0.71037
Model 7 | OfS | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ02 | ChlrCap | 23.1363 | 8970.261 | 1639.146 | 110616.041 | 16.1819 | 387.7134 | 0.69942
Model 7 | OfS | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ02 | ChlrCap | 21.2725 | 7742.443 | 1338.68 | 102349.657 | 14.4793 | 363.9656 | 0.68066
Model 7 | OfS | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ02 | ChlrCap | 20.6019 | 7353.246 | 1132.597 | 97462.5153 | 13.7615 | 356.9203 | 0.66797
Model 7 | Rt3 | 2003 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ02 | ChlrCap | 247.1868 | 108884.6 | 65294.07 | 1539061.6413 | 326.849 | 440.4951 | 1.3223
Model 7 | Rt3 | 2007 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ02 | ChlrCap | 245.7843 | 116448.2 | 65226.96 | 1481824.4771 | 340.89 | 473.782 | 1.3869
Model 7 | Rt3 | 2011 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ02 | ChlrCap | 244.856 | 116319.4 | 65521.31 | 1480703.7925 | 340.5874 | 475.0523 | 1.391
Model 7 | Rt3 | 2015 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ02 | ChlrCap | 235.4288 | 111166.2 | 57212.5 | 1368849.9672 | 326.1747 | 472.186 | 1.3854
Model 7 | Rt3 | 2020 | CZ02 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ02 | ChlrCap | 224.1828 | 102015.1 | 43871.68 | 1286221.5897 | 300.8816 | 455.0531 | 1.3421
Model 7 | ECC | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ03 | ChlrCap | 509.1507 | 131605.7 | 47100.38 | 3035535.075 | 504.7205 | 258.4809 | 0.9913
Model 7 | ECC | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ03 | ChlrCap | 507.977 | 130557 | 46734.78 | 2975626.1993 | 502.4655 | 257.0136 | 0.98915
Model 7 | ECC | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ03 | ChlrCap | 506.7695 | 130496.9 | 46772.95 | 2972807.9965 | 501.7577 | 257.5074 | 0.99011
Model 7 | ECC | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ03 | ChlrCap | 456.682 | 120771.3 | 46357.56 | 2798690.6518 | 479.0693 | 264.4538 | 1.049
Model 7 | ECC | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ03 | ChlrCap | 427.4718 | 116390.2 | 27423.67 | 2652484.0762 | 443.0251 | 272.2757 | 1.0364
Model 7 | ESe | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ03 | ChlrCap | 268.731 | 60448.21 | 13741.71 | 1339221.2666 | 165.8756 | 224.9395 | 0.61726
Model 7 | ESe | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ03 | ChlrCap | 265.0458 | 52647.69 | 13839.75 | 1228738.0958 | 141.1787 | 198.6362 | 0.53266
Model 7 | ESe | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ03 | ChlrCap | 264.0397 | 52647.7 | 13838.29 | 1224845.1635 | 140.9234 | 199.3931 | 0.53372
Model 7 | ESe | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ03 | ChlrCap | 235.9863 | 40886.75 | 4932.657 | 1161243.1552 | 120.6347 | 173.259 | 0.51119
Model 7 | ESe | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ03 | ChlrCap | 220.4452 | 39025.69 | 4248.158 | 1111450.8604 | 114.5998 | 177.0313 | 0.51986
Model 7 | EUn | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ03 | ChlrCap | 1824.8797 | 434380.9 | 217727.4 | 9820627.5369 | 1742.8454 | 238.0326 | 0.95505
Model 7 | EUn | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ03 | ChlrCap | 1815.8227 | 425315.2 | 207239.3 | 9575656.5744 | 1737.7848 | 234.2273 | 0.95702
Model 7 | EUn | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ03 | ChlrCap | 1794.5313 | 425313.9 | 207228.6 | 9411900.898 | 1723.4488 | 237.0056 | 0.96039
Model 7 | EUn | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ03 | ChlrCap | 1622.691 | 380824.1 | 223027.3 | 8556209.8054 | 1632.9858 | 234.6868 | 1.0063
Model 7 | EUn | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ03 | ChlrCap | 1524.3833 | 353459.5 | 176847.3 | 8099311.0903 | 1480.5485 | 231.8705 | 0.97124
Model 7 | Hsp | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ03 | ChlrCap | 647.9992 | 83912.11 | 13571.25 | 3851161.5803 | 504.8592 | 129.4941 | 0.7791
Model 7 | Hsp | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ03 | ChlrCap | 647.6155 | 83546.03 | 13567.33 | 3831887.7808 | 504.2001 | 129.0056 | 0.77855
Model 7 | Hsp | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ03 | ChlrCap | 647.2195 | 83522.16 | 13567.32 | 3828187.4818 | 504.0675 | 129.0477 | 0.77882
Model 7 | Hsp | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ03 | ChlrCap | 581.0735 | 72055.25 | 9872.727 | 3740616.1536 | 474.6691 | 124.0037 | 0.81688
Model 7 | Hsp | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ03 | ChlrCap | 577.2075 | 66273.17 | 9032.592 | 3574759.2544 | 427.5945 | 114.8169 | 0.7408
Model 7 | Htl | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ03 | ChlrCap | 159.5386 | 62648.54 | 20438.42 | 1292413.5011 | 140.2509 | 392.6857 | 0.8791
Model 7 | Htl | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ03 | ChlrCap | 152.7626 | 53591.48 | 17023.08 | 1019425.4986 | 129.0421 | 350.8154 | 0.84472
Model 7 | Htl | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ03 | ChlrCap | 147.5439 | 54177.79 | 17760.52 | 971826.8164 | 127.7283 | 367.1978 | 0.8657
Model 7 | Htl | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ03 | ChlrCap | 127.486 | 42508.37 | 15207.66 | 909881.0413 | 120.2336 | 333.4357 | 0.94311
Model 7 | Htl | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ03 | ChlrCap | 126.2083 | 41603.16 | 14932.01 | 899435.9328 | 116.5243 | 329.6387 | 0.92327
Model 7 | MBT | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ03 | ChlrCap | 259.136 | 66568.02 | 20682.01 | 2029870.6061 | 195.7534 | 256.8845 | 0.75541
Model 7 | MBT | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ03 | ChlrCap | 252.9723 | 68456.81 | 21129.2 | 1842102.0234 | 189.4796 | 270.6099 | 0.74901
Model 7 | MBT | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ03 | ChlrCap | 244.9833 | 70163.51 | 21740.42 | 1788209.9215 | 186.8266 | 286.4012 | 0.76261
Model 7 | MBT | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ03 | ChlrCap | 237.1992 | 67512.68 | 6608.244 | 1716654.442 | 166.9962 | 284.6244 | 0.70403
Model 7 | MBT | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ03 | ChlrCap | 222.3173 | 64714.64 | 6173.85 | 1604090.0445 | 151.671 | 291.0913 | 0.68223
Model 7 | Nrs | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ03 | ChlrCap | 95.3464 | 30927.19 | 15922 | 1293540.9749 | 144.4849 | 324.3667 | 1.5154
Model 7 | Nrs | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ03 | ChlrCap | 90.3487 | 24071.14 | 13893.3 | 1125005.2618 | 130.6632 | 266.4248 | 1.4462
Model 7 | Nrs | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ03 | ChlrCap | 89.974 | 24091.53 | 13951.68 | 1120973.4785 | 130.5663 | 267.7611 | 1.4512
Model 7 | Nrs | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ03 | ChlrCap | 79.6068 | 15285.28 | 10161.75 | 1092815.0356 | 122.7839 | 192.0097 | 1.5424
Model 7 | Nrs | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ03 | ChlrCap | 79.9441 | 13069.92 | 9187.981 | 1060591.5594 | 111.7379 | 163.4883 | 1.3977
Model 7 | OfL | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ03 | ChlrCap | 328.7545 | 87556.17 | 33205.82 | 1804915.9203 | 245.4715 | 266.3269 | 0.74667
Model 7 | OfL | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ03 | ChlrCap | 336.8908 | 87895.65 | 30449.33 | 1683387.9988 | 240.5725 | 260.9025 | 0.7141
Model 7 | OfL | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ03 | ChlrCap | 329.1995 | 87842.56 | 33892.12 | 1626876.9027 | 236.7085 | 266.8369 | 0.71904
Model 7 | OfL | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ03 | ChlrCap | 303.0842 | 78797.84 | 39937.63 | 1580617.5299 | 223.3003 | 259.9867 | 0.73676
Model 7 | OfL | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ03 | ChlrCap | 290.8142 | 74359.07 | 3185.453 | 1485345.7468 | 211.1971 | 255.6927 | 0.72623
Model 7 | OfS | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ03 | ChlrCap | 22.1567 | 4574.851 | 963.34 | 119052.5717 | 13.1727 | 206.4769 | 0.59453
Model 7 | OfS | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ03 | ChlrCap | 22.0175 | 4328.719 | 886.4683 | 112198.6059 | 12.3688 | 196.6039 | 0.56177
Model 7 | OfS | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ03 | ChlrCap | 21.8341 | 4302.229 | 882.0974 | 111419.9978 | 12.2623 | 197.0415 | 0.56161
Model 7 | OfS | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ03 | ChlrCap | 18.6829 | 3575.301 | 762.4254 | 94276.1727 | 10.9955 | 191.3676 | 0.58853
Model 7 | OfS | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ03 | ChlrCap | 17.9189 | 3344.929 | 670.6345 | 89353.1982 | 10.2911 | 186.6708 | 0.57431
Model 7 | Rt3 | 2003 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ03 | ChlrCap | 200.361 | 58773.94 | 59987.23 | 1444202.8605 | 283.6572 | 293.3402 | 1.4157
Model 7 | Rt3 | 2007 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ03 | ChlrCap | 199.5548 | 60493.57 | 59785.44 | 1383441.8476 | 289.2809 | 303.1426 | 1.4496
Model 7 | Rt3 | 2011 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ03 | ChlrCap | 199.4083 | 60608.69 | 60050.43 | 1382890.4924 | 288.9897 | 303.9426 | 1.4492
Model 7 | Rt3 | 2015 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ03 | ChlrCap | 188.1127 | 53680.43 | 52153.08 | 1265449.0457 | 263.5205 | 285.3632 | 1.4009
Model 7 | Rt3 | 2020 | CZ03 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ03 | ChlrCap | 178.2805 | 48291.53 | 39765.75 | 1178531.8851 | 240.1955 | 270.8739 | 1.3473
Model 7 | ECC | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ04 | ChlrCap | 650.4283 | 315797.8 | 83732.7 | 3122522.6764 | 745.4373 | 485.5228 | 1.1461
Model 7 | ECC | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ04 | ChlrCap | 648.8233 | 312809.9 | 83135.56 | 3057981.1208 | 741.0243 | 482.1188 | 1.1421
Model 7 | ECC | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ04 | ChlrCap | 647.1595 | 312087.8 | 82936.43 | 3054155.1383 | 738.6911 | 482.2425 | 1.1414
Model 7 | ECC | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ04 | ChlrCap | 587.8033 | 283354.2 | 73765.59 | 2856708.4971 | 717.7249 | 482.0561 | 1.221
Model 7 | ECC | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ04 | ChlrCap | 554.5638 | 275166.8 | 56954.32 | 2675955.1161 | 669.9196 | 496.186 | 1.208
Model 7 | ESe | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ04 | ChlrCap | 337.8123 | 154250.9 | 26776.76 | 1419383.9437 | 291.4137 | 456.6171 | 0.86265
Model 7 | ESe | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ04 | ChlrCap | 333.9507 | 126100 | 26797.51 | 1266431.545 | 246.6929 | 377.6007 | 0.73871
Model 7 | ESe | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ04 | ChlrCap | 332.8495 | 125937.2 | 26741.47 | 1262683.886 | 246.2159 | 378.3608 | 0.73972
Model 7 | ESe | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ04 | ChlrCap | 300.5353 | 102098.1 | 14079.45 | 1168712.5671 | 208.6597 | 339.7208 | 0.69429
Model 7 | ESe | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ04 | ChlrCap | 285.7465 | 96965.11 | 13950.86 | 1102540.3027 | 195.6863 | 339.3396 | 0.68482
Model 7 | EUn | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ04 | ChlrCap | 2256.9483 | 1058833 | 384537.9 | 10003196.8828 | 2542.5709 | 469.1437 | 1.1266
Model 7 | EUn | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ04 | ChlrCap | 2245.425 | 1043253 | 374136.6 | 9748980.3658 | 2533.9699 | 464.6127 | 1.1285
Model 7 | EUn | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ04 | ChlrCap | 2217.3363 | 1037674 | 372468.7 | 9602602.7655 | 2518.6143 | 467.9822 | 1.1359
Model 7 | EUn | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ04 | ChlrCap | 2015.395 | 904045.1 | 341676.8 | 8627102.1805 | 2309.1623 | 448.5697 | 1.1458
Model 7 | EUn | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ04 | ChlrCap | 1919.6637 | 856877.7 | 299222.3 | 8132724.5088 | 2155.5364 | 446.3687 | 1.1229
Model 7 | Hsp | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ04 | ChlrCap | 779.1722 | 239660.3 | 29434.04 | 3994348.245 | 658.8485 | 307.5832 | 0.84557
Model 7 | Hsp | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ04 | ChlrCap | 778.4675 | 238366.3 | 29406.78 | 3970936.2966 | 657.6427 | 306.1994 | 0.84479
Model 7 | Hsp | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ04 | ChlrCap | 780.4422 | 238023.4 | 29406.62 | 3968506.2333 | 657.1827 | 304.9853 | 0.84206
Model 7 | Hsp | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ04 | ChlrCap | 797.7558 | 201923.5 | 22087.41 | 3840036.0223 | 613.9936 | 253.1144 | 0.76965
Model 7 | Hsp | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ04 | ChlrCap | 809.9295 | 185437.5 | 21211.66 | 3641626.0692 | 560.8389 | 228.9551 | 0.69245
Model 7 | Htl | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ04 | ChlrCap | 205.5478 | 131613.4 | 29344.85 | 1361825.926 | 216.1818 | 640.3055 | 1.0517
Model 7 | Htl | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ04 | ChlrCap | 197.8562 | 117877.2 | 25408.34 | 1064425.0708 | 200.6029 | 595.7722 | 1.0139
Model 7 | Htl | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ04 | ChlrCap | 190.3282 | 116321.5 | 25683.57 | 1016305.789 | 196.3805 | 611.1628 | 1.0318
Model 7 | Htl | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ04 | ChlrCap | 169.797 | 96702.17 | 22880.45 | 947333.106 | 182.6132 | 569.5164 | 1.0755
Model 7 | Htl | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ04 | ChlrCap | 168.1872 | 95448.96 | 22431.6 | 935586.9284 | 178.5845 | 567.5163 | 1.0618
Model 7 | MBT | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ04 | ChlrCap | 322.3633 | 181523.9 | 32766.01 | 2162958.9379 | 314.8989 | 563.1034 | 0.97684
Model 7 | MBT | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ04 | ChlrCap | 314.02 | 157779.5 | 32421.01 | 1931065.5369 | 260.0769 | 502.4505 | 0.82822
Model 7 | MBT | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ04 | ChlrCap | 299.6248 | 153176 | 32137.84 | 1864649.8628 | 252.0233 | 511.226 | 0.84113
Model 7 | MBT | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ04 | ChlrCap | 297.989 | 142116.4 | 11034.52 | 1774450.1301 | 230.1955 | 476.9183 | 0.7725
Model 7 | MBT | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ04 | ChlrCap | 278.5123 | 134270.5 | 9664.833 | 1652071.5147 | 213.424 | 482.0989 | 0.7663
Model 7 | Nrs | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ04 | ChlrCap | 123.1325 | 88415.87 | 26261.91 | 1338312.3318 | 213.2805 | 718.0547 | 1.7321
Model 7 | Nrs | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ04 | ChlrCap | 117.7474 | 67626.85 | 23761.27 | 1128713.5308 | 181.6715 | 574.3382 | 1.5429
Model 7 | Nrs | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ04 | ChlrCap | 114.654 | 67467.43 | 24029.19 | 1102670.3913 | 179.6163 | 588.4435 | 1.5666
Model 7 | Nrs | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ04 | ChlrCap | 97.6834 | 50969.66 | 20781.66 | 1063072.0635 | 163.4421 | 521.7841 | 1.6732
Model 7 | Nrs | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ04 | ChlrCap | 96.34 | 46156.7 | 19800.91 | 1020859.5411 | 152.1756 | 479.1022 | 1.5796
Model 7 | OfL | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ04 | ChlrCap | 390.6946 | 180443 | 66210.09 | 1926060.6964 | 321.687 | 461.8518 | 0.82337
Model 7 | OfL | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ04 | ChlrCap | 389.5658 | 187764.9 | 62699.67 | 1809180.2122 | 325.8715 | 481.985 | 0.8365
Model 7 | OfL | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ04 | ChlrCap | 376.0428 | 184012.4 | 68828.27 | 1737577.4103 | 304.9255 | 489.3389 | 0.81088
Model 7 | OfL | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ04 | ChlrCap | 356.0055 | 166139.3 | 67927.59 | 1677078.3224 | 287.6405 | 466.6762 | 0.80797
Model 7 | OfL | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ04 | ChlrCap | 355.2392 | 159467.5 | 11445.45 | 1584141.789 | 274.5411 | 448.9018 | 0.77283
Model 7 | OfS | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ04 | ChlrCap | 26.9893 | 10847.56 | 2255.009 | 124987.774 | 19.2227 | 401.9201 | 0.71223
Model 7 | OfS | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ04 | ChlrCap | 26.8214 | 11441.48 | 2132.048 | 118385.1359 | 19.6553 | 426.5795 | 0.73282
Model 7 | OfS | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ04 | ChlrCap | 26.1455 | 11403.09 | 2182.958 | 115162.6358 | 19.3126 | 436.1398 | 0.73866
Model 7 | OfS | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ04 | ChlrCap | 22.0493 | 9392.929 | 2184.425 | 97942.4021 | 16.2783 | 425.9964 | 0.73827
Model 7 | OfS | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ04 | ChlrCap | 21.4147 | 8055.526 | 1655.161 | 91967.1279 | 14.3707 | 376.1676 | 0.67106
Model 7 | Rt3 | 2003 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ04 | ChlrCap | 250.458 | 135797.4 | 80787.95 | 1524744.9543 | 354.2766 | 542.1963 | 1.4145
Model 7 | Rt3 | 2007 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ04 | ChlrCap | 249.161 | 157840.5 | 80850.27 | 1485035.2626 | 405.7925 | 633.488 | 1.6286
Model 7 | Rt3 | 2011 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ04 | ChlrCap | 248.2993 | 157664 | 81050.88 | 1484202.286 | 405.172 | 634.9755 | 1.6318
Model 7 | Rt3 | 2015 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ04 | ChlrCap | 237.1232 | 145163.1 | 71092.46 | 1353620.9144 | 375.8039 | 612.1844 | 1.5848
Model 7 | Rt3 | 2020 | CZ04 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ04 | ChlrCap | 226.1252 | 135247.1 | 56908.39 | 1258057.8839 | 349.3225 | 598.1072 | 1.5448
Model 7 | ECC | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ05 | ChlrCap | 447.8013 | 172965.1 | 53762.48 | 3001362.5252 | 418.4016 | 386.2541 | 0.93435
Model 7 | ECC | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ05 | ChlrCap | 446.702 | 171832.5 | 53383.36 | 2945812.2544 | 416.2024 | 384.6692 | 0.93172
Model 7 | ECC | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ05 | ChlrCap | 446.6988 | 171859.6 | 53288.7 | 2946164.0047 | 415.9929 | 384.7326 | 0.93126
Model 7 | ECC | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ05 | ChlrCap | 399.244 | 161130.6 | 52635.84 | 2782276.4338 | 407.6717 | 403.5893 | 1.0211
Model 7 | ECC | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ05 | ChlrCap | 371.7423 | 153572.8 | 31672.98 | 2629392.9812 | 363.5927 | 413.1163 | 0.97808
Model 7 | ESe | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ05 | ChlrCap | 236.3515 | 82889.83 | 16354.38 | 1317964.0725 | 123.6187 | 350.7057 | 0.52303
Model 7 | ESe | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ05 | ChlrCap | 231.9907 | 73059.43 | 16301.69 | 1205846.2066 | 111.3178 | 314.924 | 0.47984
Model 7 | ESe | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ05 | ChlrCap | 231.9883 | 73068.72 | 16291.7 | 1206064.4717 | 111.2973 | 314.9672 | 0.47975
Model 7 | ESe | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ05 | ChlrCap | 204.1847 | 60511.13 | 6274.518 | 1149708.7694 | 101.1047 | 296.3549 | 0.49516
Model 7 | ESe | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ05 | ChlrCap | 186.52 | 57394.78 | 5620.709 | 1086521.4131 | 93.0298 | 307.7138 | 0.49877
Model 7 | EUn | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ05 | ChlrCap | 1621.1973 | 557793 | 252944.6 | 9722460.1008 | 1455.7333 | 344.0624 | 0.89794
Model 7 | EUn | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ05 | ChlrCap | 1613.4453 | 547580.8 | 242444.8 | 9478743.7749 | 1452.9452 | 339.386 | 0.90052
Model 7 | EUn | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ05 | ChlrCap | 1604.207 | 546580.2 | 242203.9 | 9360093.7737 | 1451.0225 | 340.7168 | 0.90451
Model 7 | EUn | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ05 | ChlrCap | 1441.5957 | 485950.7 | 249329.2 | 8561911.966 | 1392.9979 | 337.0922 | 0.96629
Model 7 | EUn | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ05 | ChlrCap | 1337.6327 | 450714.2 | 192187.4 | 8014371.6577 | 1251.6517 | 336.9492 | 0.93572
Model 7 | Hsp | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ05 | ChlrCap | 631.9267 | 105361.1 | 14304.9 | 3900919.4678 | 448.5501 | 166.7299 | 0.70981
Model 7 | Hsp | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ05 | ChlrCap | 631.3238 | 104904.2 | 14290.42 | 3883344.0117 | 448.1958 | 166.1655 | 0.70993
Model 7 | Hsp | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ05 | ChlrCap | 631.3238 | 104904.2 | 14290.42 | 3883344.0117 | 448.1958 | 166.1655 | 0.70993
Model 7 | Hsp | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ05 | ChlrCap | 647.081 | 88594.42 | 9726.669 | 3788671.0891 | 436.9764 | 136.914 | 0.6753
Model 7 | Hsp | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ05 | ChlrCap | 642.7437 | 81125.71 | 8870.126 | 3616605.1946 | 390.8239 | 126.2178 | 0.60806
Model 7 | Htl | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ05 | ChlrCap | 139.7557 | 73247.95 | 22574.86 | 1302961.861 | 117.3257 | 524.1141 | 0.83951
Model 7 | Htl | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ05 | ChlrCap | 133.036 | 63646.3 | 19179.05 | 1026493.6314 | 106.54 | 478.4141 | 0.80084
Model 7 | Htl | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ05 | ChlrCap | 129.0901 | 63842.99 | 19757.05 | 979426.9732 | 106.0595 | 494.5614 | 0.82159
Model 7 | Htl | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ05 | ChlrCap | 108.9339 | 49810.43 | 16827.7 | 914275.2216 | 100.7504 | 457.2536 | 0.92488
Model 7 | Htl | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ05 | ChlrCap | 107.2058 | 48963.48 | 16575.54 | 903730.7264 | 97.5129 | 456.724 | 0.90959
Model 7 | MBT | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ05 | ChlrCap | 250.9265 | 99394.13 | 24725.91 | 2073842.177 | 181.8659 | 396.1085 | 0.72478
Model 7 | MBT | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ05 | ChlrCap | 243.1638 | 89977.43 | 24911.02 | 1871274.3494 | 166.1547 | 370.028 | 0.6833
Model 7 | MBT | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ05 | ChlrCap | 240.6907 | 88420.18 | 24998.31 | 1814798.5686 | 163.475 | 367.3602 | 0.67919
Model 7 | MBT | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ05 | ChlrCap | 238.0023 | 84479.22 | 7610.977 | 1735994.6202 | 150.4629 | 354.9512 | 0.63219
Model 7 | MBT | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ05 | ChlrCap | 214.5538 | 82708.55 | 7116.194 | 1618035.9004 | 136.8416 | 385.4909 | 0.6378
Model 7 | Nrs | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ05 | ChlrCap | 83.5064 | 38755.47 | 18438.81 | 1318321.8206 | 127.1989 | 464.1019 | 1.5232
Model 7 | Nrs | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ05 | ChlrCap | 81.0218 | 30691.97 | 16350.3 | 1147100.4706 | 115.4635 | 378.8114 | 1.4251
Model 7 | Nrs | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ05 | ChlrCap | 81.0218 | 30691.97 | 16350.3 | 1147100.4706 | 115.4635 | 378.8114 | 1.4251
Model 7 | Nrs | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ05 | ChlrCap | 77.6435 | 19962.4 | 12490.44 | 1119072.9086 | 109.9147 | 257.1034 | 1.4156
Model 7 | Nrs | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ05 | ChlrCap | 77.4103 | 17281.27 | 11478.85 | 1081160.0996 | 99.6084 | 223.2426 | 1.2868
Model 7 | OfL | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ05 | ChlrCap | 334.4605 | 113463.4 | 36096.56 | 1823428.7081 | 217.3911 | 339.243 | 0.64998
Model 7 | OfL | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ05 | ChlrCap | 333.5467 | 115529.7 | 32453.08 | 1699349.6635 | 212.9849 | 346.3674 | 0.63855
Model 7 | OfL | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ05 | ChlrCap | 325.9472 | 115417.2 | 40300.59 | 1634659.197 | 209.738 | 354.0979 | 0.64347
Model 7 | OfL | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ05 | ChlrCap | 299.6537 | 104064.6 | 42861.23 | 1585035.7655 | 202.9731 | 347.2829 | 0.67736
Model 7 | OfL | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ05 | ChlrCap | 286.4257 | 98175.44 | 2898.608 | 1486340.2966 | 191.4303 | 342.7606 | 0.66834
Model 7 | OfS | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ05 | ChlrCap | 20.0139 | 7192.441 | 1051.739 | 120650.9094 | 11.2732 | 359.3715 | 0.56327
Model 7 | OfS | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ05 | ChlrCap | 19.4836 | 6681.29 | 997.5093 | 113337.9264 | 10.663 | 342.9185 | 0.54728
Model 7 | OfS | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ05 | ChlrCap | 19.3847 | 6634.229 | 991.8774 | 112582.7461 | 10.5701 | 342.2405 | 0.54528
Model 7 | OfS | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ05 | ChlrCap | 16.6051 | 5466.442 | 787.8894 | 94685.4284 | 9.8142 | 329.2028 | 0.59104
Model 7 | OfS | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ05 | ChlrCap | 15.8386 | 5120.597 | 689.386 | 89724.1002 | 9.1273 | 323.2979 | 0.57627
Model 7 | Rt3 | 2003 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ05 | ChlrCap | 191.4887 | 71888.03 | 67221.67 | 1449226.0715 | 259.719 | 375.4166 | 1.3563
Model 7 | Rt3 | 2007 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ05 | ChlrCap | 190.3688 | 74143.54 | 67254.49 | 1385443.2603 | 256.9875 | 389.4731 | 1.3499
Model 7 | Rt3 | 2011 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ05 | ChlrCap | 190.3688 | 74143.54 | 67254.49 | 1385443.2603 | 256.9875 | 389.4731 | 1.3499
Model 7 | Rt3 | 2015 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ05 | ChlrCap | 179.1423 | 67371.34 | 58298.14 | 1262096.8042 | 235.6663 | 376.0772 | 1.3155
Model 7 | Rt3 | 2020 | CZ05 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ05 | ChlrCap | 167.5133 | 59989.45 | 43841.14 | 1163276.3482 | 211.8647 | 358.1175 | 1.2648
Model 7 | ECC | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ06 | ChlrCap | 690.1455 | 368458.9 | 97022.4 | 2882784.1688 | 383.9169 | 533.8858 | 0.55628
Model 7 | ECC | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ06 | ChlrCap | 690.1455 | 366499.6 | 96501.83 | 2834299.3095 | 383.1644 | 531.0469 | 0.55519
Model 7 | ECC | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ06 | ChlrCap | 690.1378 | 366491 | 96455.5 | 2834130.4467 | 382.9916 | 531.0403 | 0.55495
Model 7 | ECC | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ06 | ChlrCap | 634.5987 | 333865 | 88576.35 | 2659999.8957 | 344.2692 | 526.1042 | 0.5425
Model 7 | ECC | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ06 | ChlrCap | 598.1787 | 317127.8 | 69682.8 | 2439267.2333 | 312.9561 | 530.1557 | 0.52318
Model 7 | ESe | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ06 | ChlrCap | 377.0638 | 170176.9 | 29755.34 | 1289047.0822 | 98.9603 | 451.3212 | 0.26245
Model 7 | ESe | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ06 | ChlrCap | 372.102 | 143569.8 | 29978.27 | 1121224.4227 | 71.7747 | 385.8345 | 0.19289
Model 7 | ESe | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ06 | ChlrCap | 372.0698 | 143582.1 | 29920.63 | 1121065.1807 | 71.7471 | 385.9009 | 0.19283
Model 7 | ESe | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ06 | ChlrCap | 342.9848 | 111919.3 | 12681.8 | 1027187.5869 | 54.4 | 326.3098 | 0.15861
Model 7 | ESe | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ06 | ChlrCap | 322.4653 | 104974.4 | 12078.88 | 943827.3293 | 46.5663 | 325.537 | 0.14441
Model 7 | EUn | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ06 | ChlrCap | 2324.592 | 1141335 | 431436.4 | 8890538.1161 | 1538.3611 | 490.9829 | 0.66178
Model 7 | EUn | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ06 | ChlrCap | 2324.592 | 1128052 | 422968.3 | 8706019.1172 | 1531.7437 | 485.2688 | 0.65893
Model 7 | EUn | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ06 | ChlrCap | 2311.588 | 1126324 | 422335.4 | 8645756.5569 | 1528.6826 | 487.2512 | 0.66131
Model 7 | EUn | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ06 | ChlrCap | 2120.4177 | 1002996 | 397777.2 | 7878776.6295 | 1372.6115 | 473.0181 | 0.64733
Model 7 | EUn | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ06 | ChlrCap | 2007.927 | 941044.3 | 343427 | 7271239.925 | 1262.1587 | 468.6646 | 0.62859
Model 7 | Hsp | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ06 | ChlrCap | 819.8385 | 277464.7 | 39939.26 | 3817196.6038 | 550.7805 | 338.4382 | 0.67182
Model 7 | Hsp | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ06 | ChlrCap | 819.8385 | 276524.4 | 39930.06 | 3802076.2005 | 550.2753 | 337.2913 | 0.6712
Model 7 | Hsp | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ06 | ChlrCap | 819.8385 | 276524.4 | 39930.06 | 3802076.2005 | 550.2753 | 337.2913 | 0.6712
Model 7 | Hsp | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ06 | ChlrCap | 830.9227 | 234351.7 | 29670.66 | 3668374.2896 | 517.2345 | 282.0379 | 0.62248
Model 7 | Hsp | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ06 | ChlrCap | 839.0405 | 215939.2 | 28659.4 | 3442292.3857 | 464.7853 | 257.3645 | 0.55395
Model 7 | Htl | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ06 | ChlrCap | 200.1557 | 139273.8 | 33039.49 | 1244867.4124 | 146.6995 | 695.8274 | 0.73293
Model 7 | Htl | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ06 | ChlrCap | 193.5773 | 124088.5 | 28475.35 | 930200.9985 | 134.9867 | 641.028 | 0.69733
Model 7 | Htl | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ06 | ChlrCap | 187.4983 | 123777.5 | 28982.39 | 906428.4727 | 133.9685 | 660.1525 | 0.71451
Model 7 | Htl | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ06 | ChlrCap | 162.3686 | 101043.8 | 25895.11 | 837846.6503 | 123.003 | 622.3113 | 0.75755
Model 7 | Htl | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ06 | ChlrCap | 160.0203 | 99190.66 | 25262.37 | 822878.1448 | 119.0016 | 619.8632 | 0.74367
Model 7 | MBT | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ06 | ChlrCap | 347.5739 | 174930.3 | 40691.2 | 2118764.5698 | 261.2438 | 503.2895 | 0.75162
Model 7 | MBT | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ06 | ChlrCap | 345.009 | 180974.5 | 40593.38 | 1913123.5955 | 253.4033 | 524.5501 | 0.73448
Model 7 | MBT | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ06 | ChlrCap | 339.1993 | 179803.7 | 40557.11 | 1882620.8605 | 251.0982 | 530.0827 | 0.74027
Model 7 | MBT | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ06 | ChlrCap | 328.0163 | 166156.5 | 13904.48 | 1785325.2392 | 232.8555 | 506.5495 | 0.70989
Model 7 | MBT | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ06 | ChlrCap | 301.4822 | 159670.4 | 11806.81 | 1647019.3716 | 210.6569 | 529.6181 | 0.69874
Model 7 | Nrs | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ06 | ChlrCap | 121.2249 | 87175.59 | 33128.51 | 1223576.6769 | 150.9304 | 719.1231 | 1.245
Model 7 | Nrs | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ06 | ChlrCap | 116.4832 | 69720.63 | 29710.42 | 1006344.9717 | 135.5608 | 598.5467 | 1.1638
Model 7 | Nrs | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ06 | ChlrCap | 116.4832 | 69720.63 | 29710.42 | 1006344.9717 | 135.5608 | 598.5467 | 1.1638
Model 7 | Nrs | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ06 | ChlrCap | 101.5529 | 51473.82 | 24998.17 | 971814.8975 | 126.7793 | 506.8671 | 1.2484
Model 7 | Nrs | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ06 | ChlrCap | 102.7199 | 45927.63 | 23860.08 | 921377.9057 | 114.4469 | 447.1153 | 1.1142
Model 7 | OfL | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ06 | ChlrCap | 403.3772 | 211712.2 | 81745.6 | 1892624.4525 | 291.5765 | 524.8492 | 0.72284
Model 7 | OfL | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ06 | ChlrCap | 402.7988 | 218724.9 | 78646.94 | 1765971.061 | 287.7386 | 543.0127 | 0.71435
Model 7 | OfL | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ06 | ChlrCap | 397.1907 | 217146.4 | 82005.88 | 1728126.2603 | 283.7997 | 546.7057 | 0.71452
Model 7 | OfL | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ06 | ChlrCap | 375.7237 | 199119 | 77045.84 | 1673813.5135 | 271.0981 | 529.9613 | 0.72154
Model 7 | OfL | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ06 | ChlrCap | 360.4377 | 190200 | 31698.23 | 1562233.0129 | 250.5569 | 527.6918 | 0.69515
Model 7 | OfS | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ06 | ChlrCap | 27.2141 | 12505.08 | 2015.504 | 116611.5046 | 16.0439 | 459.5074 | 0.58954
Model 7 | OfS | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ06 | ChlrCap | 27.4273 | 12892.74 | 1844.878 | 109161.6091 | 15.7216 | 470.0692 | 0.57321
Model 7 | OfS | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ06 | ChlrCap | 27.3397 | 12816.9 | 1842.163 | 108331.1333 | 15.5829 | 468.8019 | 0.56997
Model 7 | OfS | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ06 | ChlrCap | 23.3383 | 10945 | 2159.433 | 93802.9226 | 13.9365 | 468.9718 | 0.59715
Model 7 | OfS | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ06 | ChlrCap | 22.3434 | 10409.92 | 1610.047 | 88267.9608 | 12.9271 | 465.9056 | 0.57857
Model 7 | Rt3 | 2003 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ06 | ChlrCap | 262.2133 | 154243.4 | 91537.12 | 1507568.3277 | 308.4983 | 588.2363 | 1.1765
Model 7 | Rt3 | 2007 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ06 | ChlrCap | 261.834 | 161677.3 | 91420.94 | 1458000.837 | 310.9017 | 617.4802 | 1.1874
Model 7 | Rt3 | 2011 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ06 | ChlrCap | 261.834 | 161677.3 | 91420.94 | 1458000.837 | 310.9017 | 617.4802 | 1.1874
Model 7 | Rt3 | 2015 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ06 | ChlrCap | 249.733 | 152151.6 | 79654.38 | 1320023.6079 | 292.2399 | 609.2571 | 1.1702
Model 7 | Rt3 | 2020 | CZ06 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ06 | ChlrCap | 237.0563 | 138900.4 | 62667.39 | 1200600.5158 | 264.0794 | 585.9384 | 1.114
Model 7 | ECC | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ07 | ChlrCap | 647.4993 | 295698 | 95358.03 | 2703049.4842 | 515.3273 | 456.6769 | 0.79587
Model 7 | ECC | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ07 | ChlrCap | 647.4993 | 294133.3 | 94965.86 | 2667702.9637 | 514.5879 | 454.2604 | 0.79473
Model 7 | ECC | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ07 | ChlrCap | 645.558 | 293980.7 | 94799.3 | 2666079.2649 | 513.9795 | 455.3901 | 0.79618
Model 7 | ECC | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ07 | ChlrCap | 594.6627 | 268207 | 91313.16 | 2531474.7163 | 490.9721 | 451.0238 | 0.82563
Model 7 | ECC | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ07 | ChlrCap | 563.0487 | 254920.4 | 71795.37 | 2310506.5873 | 445.4029 | 452.7502 | 0.79106
Model 7 | ESe | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ07 | ChlrCap | 359.7787 | 128901.1 | 27467.33 | 1204788.3633 | 159.6949 | 358.2789 | 0.44387
Model 7 | ESe | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ07 | ChlrCap | 355.0423 | 112293.8 | 27696.02 | 1044689.7552 | 138.0537 | 316.2828 | 0.38884
Model 7 | ESe | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ07 | ChlrCap | 353.4058 | 112239.7 | 27604.4 | 1042489.4193 | 137.8632 | 317.5944 | 0.3901
Model 7 | ESe | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ07 | ChlrCap | 324.8455 | 86895.16 | 12495.9 | 958889.9442 | 116.3971 | 267.4969 | 0.35832
Model 7 | ESe | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ07 | ChlrCap | 305.3152 | 81607.46 | 11567.09 | 878819.963 | 108.4729 | 267.2892 | 0.35528
Model 7 | EUn | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ07 | ChlrCap | 2258.639 | 880502.1 | 396114.1 | 8317779.3236 | 1718.3377 | 389.8375 | 0.76078
Model 7 | EUn | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ07 | ChlrCap | 2258.639 | 871359.3 | 387856.5 | 8166085.3353 | 1716.4187 | 385.7895 | 0.75993
Model 7 | EUn | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ07 | ChlrCap | 2235.6347 | 870219.8 | 386933 | 8088918.0762 | 1716.2661 | 389.2496 | 0.76769
Model 7 | EUn | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ07 | ChlrCap | 2054.759 | 772415.4 | 381144.9 | 7442132.7362 | 1633.91 | 375.9153 | 0.79518
Model 7 | EUn | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ07 | ChlrCap | 1946.593 | 721684.2 | 322738.9 | 6847101.3611 | 1477.6823 | 370.7422 | 0.75911
Model 7 | Hsp | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ07 | ChlrCap | 832.1303 | 218477.8 | 41402.62 | 3690597.5487 | 512.7316 | 262.5524 | 0.61617
Model 7 | Hsp | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ07 | ChlrCap | 832.1303 | 217679 | 41373.71 | 3674979.9449 | 512.3331 | 261.5925 | 0.61569
Model 7 | Hsp | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ07 | ChlrCap | 831.5077 | 217590.6 | 41373.62 | 3674206.3869 | 512.2267 | 261.682 | 0.61602
Model 7 | Hsp | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ07 | ChlrCap | 852.4405 | 184795.8 | 31718.57 | 3558420.9824 | 489.6652 | 216.7844 | 0.57443
Model 7 | Hsp | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ07 | ChlrCap | 869.8048 | 167360.2 | 30140.59 | 3327249.449 | 440.7224 | 192.4112 | 0.50669
Model 7 | Htl | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ07 | ChlrCap | 184.6582 | 115464.7 | 31382.35 | 1162951.4504 | 138.5839 | 625.2889 | 0.75049
Model 7 | Htl | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ07 | ChlrCap | 178.6828 | 102187 | 27010.44 | 866438.9924 | 128.0089 | 571.8904 | 0.7164
Model 7 | Htl | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ07 | ChlrCap | 172.9687 | 102149.2 | 27578.68 | 846722.6403 | 127.0499 | 590.5648 | 0.73453
Model 7 | Htl | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ07 | ChlrCap | 148.3056 | 83076.32 | 25159.84 | 790800.5638 | 118.4913 | 560.1697 | 0.79897
Model 7 | Htl | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ07 | ChlrCap | 146.3167 | 80871.81 | 24531.1 | 773933.2525 | 114.2448 | 552.7174 | 0.7808
Model 7 | MBT | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ07 | ChlrCap | 339.01 | 160109.4 | 37526.22 | 2070384.8406 | 214.8609 | 472.2852 | 0.63379
Model 7 | MBT | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ07 | ChlrCap | 336.4773 | 142282.3 | 37407.05 | 1849002.3294 | 187.7828 | 422.8585 | 0.55808
Model 7 | MBT | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ07 | ChlrCap | 329.6443 | 141145.8 | 37157.46 | 1814006.6764 | 185.7844 | 428.176 | 0.56359
Model 7 | MBT | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ07 | ChlrCap | 322.342 | 133069.9 | 13126.59 | 1730429.0692 | 165.8929 | 412.8221 | 0.51465
Model 7 | MBT | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ07 | ChlrCap | 301.1313 | 125898.3 | 11325.34 | 1596015.0961 | 150.5782 | 418.0844 | 0.50004
Model 7 | Nrs | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ07 | ChlrCap | 112.809 | 69087.44 | 32734.5 | 1163727.6539 | 145.8651 | 612.4284 | 1.293
Model 7 | Nrs | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ07 | ChlrCap | 108.3649 | 54466.57 | 29184.95 | 952277.6066 | 130.0159 | 502.622 | 1.1998
Model 7 | Nrs | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ07 | ChlrCap | 107.9223 | 54481.08 | 29269.88 | 950523.6481 | 129.7699 | 504.8175 | 1.2024
Model 7 | Nrs | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ07 | ChlrCap | 102.4046 | 39628.07 | 24377.31 | 922892.4592 | 122.8689 | 386.9754 | 1.1998
Model 7 | Nrs | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ07 | ChlrCap | 103.4304 | 35180.63 | 22996.32 | 876030.4399 | 111.7691 | 340.1381 | 1.0806
Model 7 | OfL | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ07 | ChlrCap | 404.6611 | 173357.5 | 79236.49 | 1837704.034 | 231.229 | 428.4017 | 0.57141
Model 7 | OfL | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ07 | ChlrCap | 396.2667 | 175182.9 | 75109.19 | 1696426.0926 | 228.8109 | 442.0834 | 0.57742
Model 7 | OfL | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ07 | ChlrCap | 383.357 | 173895.9 | 79145.98 | 1666321.3916 | 225.7592 | 453.6135 | 0.5889
Model 7 | OfL | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ07 | ChlrCap | 371.1488 | 159229.6 | 74013.27 | 1612964.3329 | 219.1929 | 429.0182 | 0.59058
Model 7 | OfL | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ07 | ChlrCap | 361.6918 | 151522.4 | 30935.03 | 1501891.0035 | 206.8231 | 418.9268 | 0.57182
Model 7 | OfS | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ07 | ChlrCap | 25.9215 | 9654.223 | 1870.408 | 109967.1037 | 11.9869 | 372.4412 | 0.46243
Model 7 | OfS | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ07 | ChlrCap | 25.8807 | 9856.495 | 1668.181 | 102129.0794 | 11.8396 | 380.8432 | 0.45747
Model 7 | OfS | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ07 | ChlrCap | 25.8991 | 9760.911 | 1658.986 | 101227.8338 | 11.7304 | 376.8821 | 0.45293
Model 7 | OfS | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ07 | ChlrCap | 22.1743 | 8178.793 | 2033.133 | 88709.9756 | 10.8172 | 368.8416 | 0.48783
Model 7 | OfS | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ07 | ChlrCap | 21.3755 | 7711.025 | 1486.714 | 82952.0499 | 10.0154 | 360.7407 | 0.46855
Model 7 | Rt3 | 2003 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ07 | ChlrCap | 256.6523 | 128800 | 96065.01 | 1476564.4842 | 295.4077 | 501.8462 | 1.151
Model 7 | Rt3 | 2007 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ07 | ChlrCap | 256.176 | 136347.5 | 95942.39 | 1427618.7849 | 307.3294 | 532.2415 | 1.1997
Model 7 | Rt3 | 2011 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ07 | ChlrCap | 255.3507 | 136391.8 | 96509.39 | 1427604.3546 | 307.2476 | 534.1353 | 1.2032
Model 7 | Rt3 | 2015 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ07 | ChlrCap | 243.3345 | 125710.6 | 84618.03 | 1286900.9936 | 282.5811 | 516.6164 | 1.1613
Model 7 | Rt3 | 2020 | CZ07 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ07 | ChlrCap | 231.2522 | 114698.7 | 65605.89 | 1161908.0141 | 257.8338 | 495.9897 | 1.1149
Model 7 | ECC | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ08 | ChlrCap | 739.8653 | 492415.1 | 122971.3 | 2982853.1536 | 618.4973 | 665.5469 | 0.83596
Model 7 | ECC | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ08 | ChlrCap | 739.8653 | 489435.1 | 122684.8 | 2931905.2732 | 616.4094 | 661.5192 | 0.83314
Model 7 | ECC | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ08 | ChlrCap | 737.3122 | 488518.3 | 122367.2 | 2929288.1383 | 615.1063 | 662.5664 | 0.83425
Model 7 | ECC | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ08 | ChlrCap | 687.023 | 441077.7 | 110788.1 | 2745874.2497 | 576.2759 | 642.013 | 0.8388
Model 7 | ECC | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ08 | ChlrCap | 651.0408 | 419043.1 | 90529.89 | 2507314.8687 | 524.8643 | 643.651 | 0.80619
Model 7 | ESe | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ08 | ChlrCap | 400.83 | 242868.8 | 39124.01 | 1368847.1067 | 234.9366 | 605.9147 | 0.58613
Model 7 | ESe | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ08 | ChlrCap | 393.9603 | 202909.9 | 39479.13 | 1169665.0835 | 187.9042 | 515.0516 | 0.47696
Model 7 | ESe | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ08 | ChlrCap | 392.0157 | 202268.9 | 39317.61 | 1166683.4338 | 187.3221 | 515.9715 | 0.47784
Model 7 | ESe | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ08 | ChlrCap | 367.1202 | 162854.8 | 22001.07 | 1064822.6592 | 152.8241 | 443.6008 | 0.41628
Model 7 | ESe | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ08 | ChlrCap | 346.614 | 154462.1 | 21986.91 | 975609.2586 | 144.9195 | 445.6315 | 0.4181
Model 7 | EUn | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ08 | ChlrCap | 2528.2237 | 1555971 | 537694.6 | 9236206.2814 | 2139.0209 | 615.4404 | 0.84606
Model 7 | EUn | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ08 | ChlrCap | 2528.2237 | 1542600 | 528984.6 | 9055047.653 | 2151.2423 | 610.1517 | 0.85089
Model 7 | EUn | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ08 | ChlrCap | 2501.0723 | 1532171 | 525596.4 | 8963740.3529 | 2138.6128 | 612.6056 | 0.85508
Model 7 | EUn | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ08 | ChlrCap | 2335.5727 | 1341107 | 463012.9 | 8118699.4244 | 1961.4142 | 574.2091 | 0.8398
Model 7 | EUn | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ08 | ChlrCap | 2222.945 | 1265828 | 411578.4 | 7469136.075 | 1797.7553 | 569.4374 | 0.80873
Model 7 | Hsp | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ08 | ChlrCap | 896.2405 | 364808.2 | 43117.42 | 3896155.9801 | 591.0277 | 407.0428 | 0.65945
Model 7 | Hsp | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ08 | ChlrCap | 896.2405 | 363672 | 43088.15 | 3880128.8476 | 590.5449 | 405.775 | 0.65891
Model 7 | Hsp | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ08 | ChlrCap | 895.5942 | 363373.7 | 43045.29 | 3880312.0012 | 590.2644 | 405.7347 | 0.65908
Model 7 | Hsp | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ08 | ChlrCap | 920.3975 | 301573.5 | 31888.83 | 3711712.4502 | 555.9583 | 327.6557 | 0.60404
Model 7 | Hsp | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ08 | ChlrCap | 939.6933 | 273687.3 | 30609.64 | 3461791.6166 | 506.0339 | 291.2517 | 0.53851
Model 7 | Htl | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ08 | ChlrCap | 212.3743 | 185219.8 | 37473.59 | 1296637.1047 | 183.7597 | 872.1383 | 0.86526
Model 7 | Htl | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ08 | ChlrCap | 205.637 | 168078.7 | 32924.27 | 973054.3213 | 170.1553 | 817.3563 | 0.82745
Model 7 | Htl | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ08 | ChlrCap | 198.3377 | 165360.8 | 33039.86 | 946779.5351 | 167.3082 | 833.7337 | 0.84355
Model 7 | Htl | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ08 | ChlrCap | 171.8435 | 138579.2 | 29830.78 | 872607.4118 | 153.7572 | 806.4268 | 0.89475
Model 7 | Htl | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ08 | ChlrCap | 170.0543 | 136312.6 | 29186.47 | 855713.7857 | 149.853 | 801.5826 | 0.88121
Model 7 | MBT | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ08 | ChlrCap | 379.9615 | 279341.3 | 45764.18 | 2231800.7046 | 267.6085 | 735.1832 | 0.7043
Model 7 | MBT | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ08 | ChlrCap | 376.9867 | 235615.6 | 45648.46 | 1965897.1372 | 223.6283 | 624.9972 | 0.5932
Model 7 | MBT | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ08 | ChlrCap | 364.483 | 229195 | 45136.37 | 1916749.3681 | 218.3945 | 628.8222 | 0.59919
Model 7 | MBT | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ08 | ChlrCap | 359.3745 | 216166.6 | 16579.75 | 1818557.4256 | 199.7305 | 601.5079 | 0.55577
Model 7 | MBT | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ08 | ChlrCap | 334.8858 | 203329.4 | 14218.1 | 1682975.8652 | 183.4913 | 607.1604 | 0.54792
Model 7 | Nrs | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ08 | ChlrCap | 127.9944 | 128351.3 | 37246.52 | 1267722.0373 | 186.0826 | 1002.7885 | 1.4538
Model 7 | Nrs | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ08 | ChlrCap | 125.2755 | 97937.2 | 33900.64 | 1030284.1456 | 157.9753 | 781.7749 | 1.261
Model 7 | Nrs | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ08 | ChlrCap | 122.6344 | 97840.96 | 33933.43 | 1028421.3252 | 157.732 | 797.8262 | 1.2862
Model 7 | Nrs | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ08 | ChlrCap | 110.3115 | 76442.2 | 29213.45 | 987363.0069 | 146.1575 | 692.9664 | 1.325
Model 7 | Nrs | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ08 | ChlrCap | 112.0452 | 69727.09 | 28146.54 | 936094.5086 | 134.9004 | 622.3119 | 1.204
Model 7 | OfL | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ08 | ChlrCap | 444.1263 | 267844 | 97519.48 | 1969766.7198 | 281.0507 | 603.0807 | 0.63282
Model 7 | OfL | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ08 | ChlrCap | 443.49 | 278356.4 | 94167.09 | 1837476.6049 | 274.8013 | 627.6498 | 0.61963
Model 7 | OfL | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ08 | ChlrCap | 429.6913 | 273039.6 | 100378.8 | 1784831.0621 | 262.5673 | 635.4319 | 0.61106
Model 7 | OfL | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ08 | ChlrCap | 410.6412 | 250447.9 | 93614.62 | 1726304.8218 | 248.4564 | 609.8948 | 0.60505
Model 7 | OfL | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ08 | ChlrCap | 397.5578 | 240236.7 | 53634.46 | 1621275.3212 | 236.1785 | 604.2811 | 0.59407
Model 7 | OfS | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ08 | ChlrCap | 28.1286 | 16594.97 | 3325.511 | 121210.0011 | 15.7799 | 589.9689 | 0.56099
Model 7 | OfS | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ08 | ChlrCap | 28.0379 | 17676.96 | 3167.066 | 113843.1353 | 15.81 | 630.4666 | 0.56388
Model 7 | OfS | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ08 | ChlrCap | 27.8237 | 17557.9 | 3151.008 | 112914.3746 | 15.6738 | 631.0406 | 0.56333
Model 7 | OfS | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ08 | ChlrCap | 24.0346 | 14420.91 | 3146.293 | 97658.6983 | 13.8489 | 600.0062 | 0.57621
Model 7 | OfS | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ08 | ChlrCap | 23.315 | 13722.77 | 2598.063 | 91868.3735 | 13.0464 | 588.5803 | 0.55957
Model 7 | Rt3 | 2003 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ08 | ChlrCap | 281.8822 | 251307 | 107190.1 | 1617993.0258 | 373.9825 | 891.5321 | 1.3267
Model 7 | Rt3 | 2007 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ08 | ChlrCap | 281.3125 | 229503.1 | 107985.5 | 1538705.4754 | 353.593 | 815.8297 | 1.2569
Model 7 | Rt3 | 2011 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ08 | ChlrCap | 280.447 | 229149.7 | 108244.1 | 1538174.3646 | 353.08 | 817.0874 | 1.259
Model 7 | Rt3 | 2015 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ08 | ChlrCap | 269.9647 | 212400.1 | 95342.34 | 1391148.2626 | 324.8346 | 786.77 | 1.2032
Model 7 | Rt3 | 2020 | CZ08 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ08 | ChlrCap | 258.647 | 197969.7 | 78662.95 | 1266309.5744 | 298.5504 | 765.405 | 1.1543
Model 7 | ECC | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ09 | ChlrCap | 893.031 | 447537.5 | 115186.2 | 2995518.6284 | 699.1983 | 501.1444 | 0.78295
Model 7 | ECC | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ09 | ChlrCap | 893.031 | 444720.2 | 114630 | 2944662.6835 | 697.0041 | 497.9897 | 0.78049
Model 7 | ECC | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ09 | ChlrCap | 882.3562 | 441231.3 | 114095.6 | 2932368.5358 | 690.516 | 500.0603 | 0.78258
Model 7 | ECC | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ09 | ChlrCap | 816.2587 | 395981.9 | 102555.5 | 2737563.0363 | 646.5269 | 485.1182 | 0.79206
Model 7 | ECC | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ09 | ChlrCap | 783.4162 | 375361.2 | 82330.13 | 2506018.0399 | 593.5924 | 479.1338 | 0.7577
Model 7 | ESe | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ09 | ChlrCap | 485.9148 | 184726.9 | 38389.41 | 1361211.1161 | 232.2523 | 380.1631 | 0.47797
Model 7 | ESe | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ09 | ChlrCap | 481.3325 | 181375.6 | 38416.04 | 1189137.0924 | 216.8279 | 376.8198 | 0.45047
Model 7 | ESe | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ09 | ChlrCap | 472.9107 | 178767.4 | 37794.68 | 1175604.9497 | 210.4155 | 378.0152 | 0.44494
Model 7 | ESe | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ09 | ChlrCap | 427.1442 | 144273.4 | 21742.27 | 1079081.8152 | 179.6179 | 337.7628 | 0.42051
Model 7 | ESe | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ09 | ChlrCap | 411.9728 | 136157.8 | 21131.12 | 994206.6333 | 171.0844 | 330.5019 | 0.41528
Model 7 | EUn | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ09 | ChlrCap | 2988.2497 | 1496416 | 518292.3 | 9490934.5674 | 2400.3325 | 500.7667 | 0.80326
Model 7 | EUn | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ09 | ChlrCap | 2988.2497 | 1483469 | 510233.7 | 9318019.646 | 2398.6826 | 496.4341 | 0.8027
Model 7 | EUn | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ09 | ChlrCap | 2909.579 | 1461383 | 500016.8 | 9099050.8664 | 2377.5532 | 502.2661 | 0.81715
Model 7 | EUn | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ09 | ChlrCap | 2676.6887 | 1264540 | 432240.9 | 8166303.3529 | 2175.413 | 472.427 | 0.81273
Model 7 | EUn | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ09 | ChlrCap | 2584.4677 | 1197171 | 385650.9 | 7554680.2825 | 2008.4301 | 463.2176 | 0.77712
Model 7 | Hsp | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ09 | ChlrCap | 1019.3813 | 338162 | 39210.41 | 3927076.245 | 645.8003 | 331.7326 | 0.63352
Model 7 | Hsp | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ09 | ChlrCap | 1019.3813 | 337106 | 39160.51 | 3911525.3634 | 645.2156 | 330.6967 | 0.63295
Model 7 | Hsp | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ09 | ChlrCap | 1015.938 | 335924.8 | 39057.35 | 3910254.4783 | 643.8129 | 330.6548 | 0.63371
Model 7 | Hsp | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ09 | ChlrCap | 1046.3467 | 283251.2 | 28976.36 | 3748892.3001 | 609.6423 | 270.7049 | 0.58264
Model 7 | Hsp | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ09 | ChlrCap | 1074.036 | 256881.6 | 27950.98 | 3510495.3423 | 558.3113 | 239.1741 | 0.51983
Model 7 | Htl | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ09 | ChlrCap | 270.7573 | 188634 | 36332.82 | 1334814.5613 | 211.3288 | 696.6903 | 0.78051
Model 7 | Htl | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ09 | ChlrCap | 263.948 | 169666 | 32000.12 | 1007534.8291 | 196.2229 | 642.8009 | 0.74342
Model 7 | Htl | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ09 | ChlrCap | 253.1615 | 165712.9 | 32112.36 | 974962.1978 | 191.4107 | 654.5739 | 0.75608
Model 7 | Htl | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ09 | ChlrCap | 222.526 | 135536.8 | 28061.34 | 891968.6583 | 173.4565 | 609.083 | 0.77949
Model 7 | Htl | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ09 | ChlrCap | 220.8133 | 133627.4 | 27495.2 | 875854.3438 | 169.6441 | 605.16 | 0.76827
Model 7 | MBT | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ09 | ChlrCap | 441.9422 | 269068.6 | 44251.19 | 2247925.6999 | 315.9023 | 608.8322 | 0.7148
Model 7 | MBT | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ09 | ChlrCap | 437.8058 | 225723.4 | 44104.45 | 1966536.8347 | 255.8832 | 515.5788 | 0.58447
Model 7 | MBT | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ09 | ChlrCap | 400.1697 | 217721.6 | 42302.91 | 1896376.6202 | 239.0534 | 544.0732 | 0.59738
Model 7 | MBT | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ09 | ChlrCap | 383.7025 | 198091.3 | 15288.26 | 1795775.9203 | 218.8067 | 516.2627 | 0.57025
Model 7 | MBT | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ09 | ChlrCap | 365.1895 | 186200.2 | 13220.06 | 1664433.6729 | 198.6759 | 509.8728 | 0.54404
Model 7 | Nrs | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ09 | ChlrCap | 161.1163 | 133203.3 | 35202.09 | 1312751.3116 | 216.3453 | 826.7525 | 1.3428
Model 7 | Nrs | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ09 | ChlrCap | 155.7269 | 97558.55 | 32585.6 | 1062054.7491 | 175.2088 | 626.4722 | 1.1251
Model 7 | Nrs | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ09 | ChlrCap | 149.6776 | 96374.35 | 32692.06 | 1035229.1631 | 172.3018 | 643.8795 | 1.1512
Model 7 | Nrs | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ09 | ChlrCap | 127.8184 | 74435.36 | 28123.58 | 994051.0294 | 158.7335 | 582.3524 | 1.2419
Model 7 | Nrs | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ09 | ChlrCap | 128.7526 | 68129.81 | 27114.69 | 945175.7297 | 147.7217 | 529.1531 | 1.1473
Model 7 | OfL | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ09 | ChlrCap | 488.7008 | 261642 | 85131.22 | 1979483.6495 | 302.0925 | 535.3828 | 0.61815
Model 7 | OfL | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ09 | ChlrCap | 488.0035 | 273918.8 | 82066.29 | 1839195.6389 | 295.2259 | 561.305 | 0.60497
Model 7 | OfL | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ09 | ChlrCap | 469.4777 | 266550.5 | 90302.95 | 1779653.9039 | 286.8514 | 567.7597 | 0.611
Model 7 | OfL | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ09 | ChlrCap | 449.6365 | 240865.3 | 87738.54 | 1717224.7069 | 269.2833 | 535.6889 | 0.59889
Model 7 | OfL | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ09 | ChlrCap | 440.7675 | 232333 | 28565.59 | 1616003.1923 | 257.4774 | 527.1101 | 0.58416
Model 7 | OfS | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ09 | ChlrCap | 34.1601 | 14941.8 | 3106.906 | 122178.2622 | 17.7175 | 437.4048 | 0.51866
Model 7 | OfS | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ09 | ChlrCap | 34.0647 | 14231.4 | 2973.926 | 113097.6003 | 16.5848 | 417.7751 | 0.48686
Model 7 | OfS | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ09 | ChlrCap | 32.8268 | 14006.66 | 3014.569 | 109982.3953 | 16.1521 | 426.6833 | 0.49204
Model 7 | OfS | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ09 | ChlrCap | 28.4866 | 11379.73 | 2990.515 | 94424.6678 | 14.018 | 399.4769 | 0.49209
Model 7 | OfS | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ09 | ChlrCap | 27.6906 | 10852.92 | 2529.295 | 88753.5152 | 13.2449 | 391.9353 | 0.47832
Model 7 | Rt3 | 2003 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ09 | ChlrCap | 342.2205 | 198492.8 | 96417.41 | 1577823.7005 | 365.6889 | 580.0143 | 1.0686
Model 7 | Rt3 | 2007 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ09 | ChlrCap | 341.589 | 212360.3 | 96483.34 | 1517232.9127 | 379.2148 | 621.6837 | 1.1101
Model 7 | Rt3 | 2011 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ09 | ChlrCap | 336.846 | 211082.7 | 97421.38 | 1514897.3124 | 376.8259 | 626.6445 | 1.1187
Model 7 | Rt3 | 2015 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ09 | ChlrCap | 325.614 | 194208.4 | 85626.4 | 1370878.1096 | 349.5072 | 596.4375 | 1.0734
Model 7 | Rt3 | 2020 | CZ09 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ09 | ChlrCap | 315.9945 | 179976.5 | 72381.02 | 1247159.5627 | 320.2665 | 569.5558 | 1.0135
Model 7 | ECC | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ10 | ChlrCap | 770.1527 | 553311.8 | 122614.5 | 3136959.9015 | 546.9941 | 718.4443 | 0.71024
Model 7 | ECC | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ10 | ChlrCap | 767.3098 | 548373.8 | 121942.7 | 3082863.5404 | 544.2291 | 714.6706 | 0.70927
Model 7 | ECC | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ10 | ChlrCap | 764.3988 | 547071.1 | 121509.1 | 3079168.5463 | 542.3265 | 715.688 | 0.70948
Model 7 | ECC | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ10 | ChlrCap | 729.7298 | 505575.3 | 107165.4 | 2942887.4795 | 488.3618 | 692.8253 | 0.66924
Model 7 | ECC | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ10 | ChlrCap | 696.4335 | 482095.1 | 87001.13 | 2710983.4478 | 453.2212 | 692.2342 | 0.65077
Model 7 | ESe | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ10 | ChlrCap | 401.8207 | 253798 | 31859.74 | 1417636.6377 | 147.0141 | 631.6201 | 0.36587
Model 7 | ESe | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ10 | ChlrCap | 393.7185 | 204949.3 | 32064.86 | 1232542.987 | 98.8836 | 520.5478 | 0.25115
Model 7 | ESe | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ10 | ChlrCap | 391.5958 | 204038.3 | 31886.96 | 1228977.3487 | 97.7873 | 521.0431 | 0.24971
Model 7 | ESe | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ10 | ChlrCap | 378.9832 | 187433.1 | 23157.74 | 1166016.8953 | 88.8991 | 494.5684 | 0.23457
Model 7 | ESe | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ10 | ChlrCap | 362.4922 | 179236.1 | 23333.29 | 1086793.3103 | 78.1377 | 494.4551 | 0.21556
Model 7 | EUn | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ10 | ChlrCap | 2629.0233 | 1761312 | 566815.7 | 9689732.2333 | 2125.5837 | 669.9492 | 0.80851
Model 7 | EUn | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ10 | ChlrCap | 2613.854 | 1745209 | 559154 | 9508156.646 | 2119.2917 | 667.6765 | 0.81079
Model 7 | EUn | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ10 | ChlrCap | 2586.9427 | 1733748 | 555789.6 | 9417197.5651 | 2118.3659 | 670.1919 | 0.81887
Model 7 | EUn | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ10 | ChlrCap | 2453.7317 | 1559254 | 448375.9 | 8727663.6471 | 1922.4951 | 635.4623 | 0.7835
Model 7 | EUn | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ10 | ChlrCap | 2358.0787 | 1487072 | 403905.9 | 8133857.0445 | 1811.1317 | 630.6287 | 0.76805
Model 7 | Hsp | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ10 | ChlrCap | 920.6743 | 385414.4 | 39039.57 | 4031454.4654 | 669.1165 | 418.6219 | 0.72677
Model 7 | Hsp | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ10 | ChlrCap | 919.9765 | 383719.9 | 38992.46 | 4014510.939 | 665.9611 | 417.0975 | 0.72389
Model 7 | Hsp | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ10 | ChlrCap | 919.2605 | 383318.2 | 38992.39 | 4014283.3376 | 665.5147 | 416.9854 | 0.72397
Model 7 | Hsp | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ10 | ChlrCap | 930.4465 | 362059.7 | 28734.95 | 3921991.6471 | 648.5071 | 389.1247 | 0.69698
Model 7 | Hsp | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ10 | ChlrCap | 948.8985 | 332333 | 27877.95 | 3685950.1079 | 576.7016 | 350.2303 | 0.60776
Model 7 | Htl | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ10 | ChlrCap | 233.4468 | 205632.9 | 37015.7 | 1366088.0869 | 202.8487 | 880.8554 | 0.86893
Model 7 | Htl | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ10 | ChlrCap | 226.0702 | 186342.3 | 32404.47 | 1043783.6233 | 186.7961 | 824.2675 | 0.82627
Model 7 | Htl | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ10 | ChlrCap | 219.7372 | 183556.1 | 32427.99 | 1019429.873 | 184.2433 | 835.3439 | 0.83847
Model 7 | Htl | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ10 | ChlrCap | 201.0175 | 163039.9 | 29781.07 | 956795.3386 | 173.7871 | 811.0732 | 0.86454
Model 7 | Htl | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ10 | ChlrCap | 199.322 | 160876.6 | 29217.81 | 940885.2079 | 169.6486 | 807.1191 | 0.85113
Model 7 | MBT | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ10 | ChlrCap | 386.5875 | 231159.2 | 39464 | 2167453.2708 | 317.5604 | 597.9479 | 0.82145
Model 7 | MBT | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ10 | ChlrCap | 377.0093 | 243787.4 | 38842.45 | 1963668.3165 | 313.7893 | 646.6349 | 0.83231
Model 7 | MBT | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ10 | ChlrCap | 362.7243 | 237158 | 37486.48 | 1910555.0129 | 303.2371 | 653.8243 | 0.836
Model 7 | MBT | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ10 | ChlrCap | 361 | 240764.8 | 15945.78 | 1853822.0129 | 288.2264 | 666.9385 | 0.79841
Model 7 | MBT | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ10 | ChlrCap | 339.4217 | 228386.4 | 14029.81 | 1722184.9894 | 266.864 | 672.8692 | 0.78623
Model 7 | Nrs | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ10 | ChlrCap | 129.92 | 142734.8 | 33148.67 | 1326411.3209 | 197.4191 | 1098.6361 | 1.5195
Model 7 | Nrs | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ10 | ChlrCap | 124.8427 | 104203.7 | 30621.01 | 1097135.8249 | 166.1137 | 834.6796 | 1.3306
Model 7 | Nrs | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ10 | ChlrCap | 121.976 | 103210.1 | 30865.83 | 1082353.8034 | 164.792 | 846.1507 | 1.351
Model 7 | Nrs | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ10 | ChlrCap | 116.8715 | 94102.35 | 29007.84 | 1053740.7 | 158.8755 | 805.1779 | 1.3594
Model 7 | Nrs | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ10 | ChlrCap | 116.0286 | 86712.82 | 28142.13 | 1003910.3569 | 146.9109 | 747.3398 | 1.2662
Model 7 | OfL | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ10 | ChlrCap | 439.3667 | 283331.9 | 104913.6 | 1949265.803 | 345.9659 | 644.8644 | 0.78742
Model 7 | OfL | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ10 | ChlrCap | 438.1183 | 299633.1 | 101990.9 | 1832404.1981 | 346.6687 | 683.9091 | 0.79127
Model 7 | OfL | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ10 | ChlrCap | 424.4277 | 293613 | 107704.2 | 1785457.6178 | 332.8351 | 691.7857 | 0.7842
Model 7 | OfL | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ10 | ChlrCap | 427.0532 | 279706.9 | 92433.88 | 1773073.1524 | 323.1227 | 654.9697 | 0.75663
Model 7 | OfL | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ10 | ChlrCap | 413.0813 | 268173.9 | 38860.75 | 1672906.9004 | 306.6763 | 649.2036 | 0.74241
Model 7 | OfS | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ10 | ChlrCap | 29.0807 | 17315.45 | 3806.044 | 117190.1368 | 19.6429 | 595.4279 | 0.67546
Model 7 | OfS | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ10 | ChlrCap | 28.9033 | 16617.51 | 3600.271 | 109201.698 | 18.7006 | 574.9344 | 0.64701
Model 7 | OfS | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ10 | ChlrCap | 28.1904 | 16465.68 | 3654.499 | 106792.9717 | 18.4021 | 584.088 | 0.65278
Model 7 | OfS | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ10 | ChlrCap | 26.0697 | 16165.19 | 3404.699 | 100653.4835 | 17.8183 | 620.0758 | 0.68349
Model 7 | OfS | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ10 | ChlrCap | 25.2521 | 15470.45 | 2984.147 | 94807.4009 | 16.4687 | 612.6399 | 0.65217
Model 7 | Rt3 | 2003 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ10 | ChlrCap | 299.8245 | 227813.8 | 100309.4 | 1614355.0891 | 374.2025 | 759.8238 | 1.2481
Model 7 | Rt3 | 2007 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ10 | ChlrCap | 298.227 | 250471.7 | 100407.1 | 1574027.6641 | 402.3488 | 839.8693 | 1.3491
Model 7 | Rt3 | 2011 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ10 | ChlrCap | 297.162 | 250019.5 | 100562.1 | 1573224.7157 | 401.7287 | 841.3576 | 1.3519
Model 7 | Rt3 | 2015 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ10 | ChlrCap | 287.1245 | 245206.8 | 89224.66 | 1444794.8617 | 385.6486 | 854.0086 | 1.3431
Model 7 | Rt3 | 2020 | CZ10 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ10 | ChlrCap | 276.7787 | 230672.8 | 76250.48 | 1326926.8664 | 357.8777 | 833.4197 | 1.293
Model 7 | ECC | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ11 | ChlrCap | 732.3215 | 553469.8 | 104815.9 | 3583505.1336 | 327.1357 | 755.7743 | 0.44671
Model 7 | ECC | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ11 | ChlrCap | 729.7727 | 549046.5 | 103997.6 | 3515956.1055 | 324.2785 | 752.3528 | 0.44436
Model 7 | ECC | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ11 | ChlrCap | 709.2598 | 529549.3 | 106277.7 | 3358070.5979 | 285.4912 | 746.6224 | 0.40252
Model 7 | ECC | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ11 | ChlrCap | 670.3255 | 484031.9 | 95981.37 | 3181546.5346 | 273.1621 | 722.0849 | 0.40751
Model 7 | ECC | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ11 | ChlrCap | 638.1592 | 463440.3 | 76785.31 | 2982564.3435 | 248.2261 | 726.2143 | 0.38897
Model 7 | ESe | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ11 | ChlrCap | 372.733 | 196138.8 | 33687.46 | 1606512.0574 | 173.4658 | 526.218 | 0.46539
Model 7 | ESe | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ11 | ChlrCap | 361.6988 | 199882.3 | 33476.26 | 1485270.2624 | 151.5988 | 552.6208 | 0.41913
Model 7 | ESe | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ11 | ChlrCap | 355.1192 | 190563.9 | 29434.96 | 1383369.2549 | 131.6844 | 536.6196 | 0.37082
Model 7 | ESe | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ11 | ChlrCap | 345.2653 | 172853.1 | 21710.7 | 1294297.9341 | 126.987 | 500.6384 | 0.3678
Model 7 | ESe | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ11 | ChlrCap | 328.088 | 163970.5 | 21690.08 | 1225860.9298 | 114.2406 | 499.776 | 0.3482
Model 7 | EUn | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ11 | ChlrCap | 2478.8097 | 1856403 | 520763.4 | 11302354.3107 | 839.3939 | 748.9091 | 0.33863
Model 7 | EUn | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ11 | ChlrCap | 2465.2163 | 1839785 | 512934.1 | 11105832.1934 | 832.5305 | 746.2976 | 0.33771
Model 7 | EUn | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ11 | ChlrCap | 2374.959 | 1799059 | 515860.4 | 10555741.7433 | 769.9307 | 757.5116 | 0.32419
Model 7 | EUn | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ11 | ChlrCap | 2239.9477 | 1616708 | 422362.8 | 9683080.5651 | 696.9746 | 721.7615 | 0.31116
Model 7 | EUn | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ11 | ChlrCap | 2146.914 | 1554191 | 388103.9 | 9191498.9168 | 635.8945 | 723.9186 | 0.29619
Model 7 | Hsp | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ11 | ChlrCap | 908.8632 | 452394.5 | 35547.93 | 4435714.8019 | 817.3687 | 497.7586 | 0.89933
Model 7 | Hsp | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ11 | ChlrCap | 907.9913 | 449775.6 | 35344.09 | 4411158.1336 | 815.5707 | 495.3524 | 0.89821
Model 7 | Hsp | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ11 | ChlrCap | 928.6185 | 420895.2 | 35291.44 | 4276974.8734 | 772.4297 | 453.2488 | 0.83181
Model 7 | Hsp | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ11 | ChlrCap | 942.108 | 396849 | 25948.36 | 4170624.8464 | 735.7147 | 421.2351 | 0.78092
Model 7 | Hsp | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ11 | ChlrCap | 964.2135 | 371478.4 | 25181.91 | 3970808.0481 | 676.4401 | 385.2657 | 0.70155
Model 7 | Htl | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ11 | ChlrCap | 240.8033 | 222768.8 | 35719.99 | 1565176.3204 | 290.708 | 925.1068 | 1.2072
Model 7 | Htl | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ11 | ChlrCap | 233.1243 | 204604.1 | 31519.43 | 1259788.1579 | 271.8848 | 877.6608 | 1.1663
Model 7 | Htl | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ11 | ChlrCap | 224.8557 | 199529.5 | 31223.67 | 1201889.8884 | 263.803 | 887.367 | 1.1732
Model 7 | Htl | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ11 | ChlrCap | 206.8593 | 178405.8 | 28773.63 | 1120375.158 | 246.9953 | 862.4498 | 1.194
Model 7 | Htl | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ11 | ChlrCap | 204.9697 | 176071.5 | 28159.23 | 1106071.7402 | 242.5665 | 859.0125 | 1.1834
Model 7 | MBT | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ11 | ChlrCap | 399.3067 | 231357 | 34941.84 | 2251441.1336 | 326.1987 | 579.3968 | 0.81691
Model 7 | MBT | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ11 | ChlrCap | 388.7318 | 245039.1 | 34431.5 | 2045911.6143 | 327.0513 | 630.3551 | 0.84133
Model 7 | MBT | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ11 | ChlrCap | 370.9093 | 235506.2 | 33057.72 | 1970895.3669 | 310.2287 | 634.9428 | 0.8364
Model 7 | MBT | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ11 | ChlrCap | 367.482 | 236876.1 | 15034.27 | 1907702.449 | 297.0281 | 644.5924 | 0.80828
Model 7 | MBT | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ11 | ChlrCap | 345.7538 | 225194.2 | 13545.95 | 1781799.653 | 279.233 | 651.3137 | 0.80761
Model 7 | Nrs | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ11 | ChlrCap | 138.1275 | 169102.7 | 29773.24 | 1484743.3945 | 276.041 | 1224.2509 | 1.9985
Model 7 | Nrs | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ11 | ChlrCap | 132.5941 | 121110.8 | 27694.49 | 1256301.7216 | 223.734 | 913.3949 | 1.6874
Model 7 | Nrs | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ11 | ChlrCap | 129.4259 | 119535.7 | 27882.53 | 1233490.2974 | 220.6603 | 923.584 | 1.7049
Model 7 | Nrs | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ11 | ChlrCap | 122.7176 | 109690.2 | 26198.76 | 1194646.613 | 209.6792 | 893.8427 | 1.7086
Model 7 | Nrs | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ11 | ChlrCap | 118.8625 | 102130.3 | 25660.97 | 1140110.7061 | 194.8188 | 859.2303 | 1.639
Model 7 | OfL | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ11 | ChlrCap | 437.5503 | 275884.5 | 92513.09 | 2014343.1653 | 376.5981 | 630.5206 | 0.8607
Model 7 | OfL | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ11 | ChlrCap | 436.2393 | 292378.2 | 90814.38 | 1909756.9121 | 383.0323 | 670.2243 | 0.87803
Model 7 | OfL | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ11 | ChlrCap | 418.8508 | 282137.6 | 93392.82 | 1827240.837 | 371.0501 | 673.5992 | 0.88588
Model 7 | OfL | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ11 | ChlrCap | 422.9555 | 272756.8 | 83646.05 | 1859250.6026 | 372.0381 | 644.883 | 0.87962
Model 7 | OfL | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ11 | ChlrCap | 411.7397 | 264082.1 | 27728.06 | 1779599.2907 | 350.4597 | 641.3812 | 0.85117
Model 7 | OfS | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ11 | ChlrCap | 29.0447 | 17716.08 | 4375.314 | 129591.6706 | 24.3389 | 609.9583 | 0.83798
Model 7 | OfS | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ11 | ChlrCap | 28.8082 | 19204.2 | 4262.479 | 124082.8963 | 25.226 | 666.6231 | 0.87565
Model 7 | OfS | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ11 | ChlrCap | 28.0648 | 18956.05 | 4290.675 | 120904.1773 | 24.7481 | 675.4388 | 0.88182
Model 7 | OfS | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ11 | ChlrCap | 26.2097 | 16542.15 | 3974.573 | 111055.6602 | 22.4855 | 631.1471 | 0.85791
Model 7 | OfS | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ11 | ChlrCap | 25.2603 | 15823.4 | 3507.058 | 104839.4016 | 20.9861 | 626.4132 | 0.83079
Model 7 | Rt3 | 2003 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ11 | ChlrCap | 317.8452 | 231533.7 | 85587.52 | 1713444.1688 | 425.4182 | 728.4481 | 1.3384
Model 7 | Rt3 | 2007 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ11 | ChlrCap | 315.9692 | 252235.8 | 85851.2 | 1666626.6846 | 456.7312 | 798.2924 | 1.4455
Model 7 | Rt3 | 2011 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ11 | ChlrCap | 297.2928 | 243207 | 87460.06 | 1598429.0328 | 438.1551 | 818.0722 | 1.4738
Model 7 | Rt3 | 2015 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ11 | ChlrCap | 287.5838 | 229385 | 77487.47 | 1471400.2392 | 408.667 | 797.6283 | 1.421
Model 7 | Rt3 | 2020 | CZ11 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ11 | ChlrCap | 276.9912 | 216507 | 65561.43 | 1367198.939 | 380.7845 | 781.6386 | 1.3747
Model 7 | ECC | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ12 | ChlrCap | 662.3168 | 413229.4 | 91843.2 | 3359415.4361 | 631.4403 | 623.915 | 0.95338
Model 7 | ECC | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ12 | ChlrCap | 660.0962 | 409495.6 | 91282.71 | 3293914.8628 | 627.2483 | 620.3575 | 0.95024
Model 7 | ECC | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ12 | ChlrCap | 648.0275 | 405564.2 | 92116.88 | 3241370.8019 | 619.3349 | 625.8441 | 0.95572
Model 7 | ECC | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ12 | ChlrCap | 613.3367 | 372836.4 | 79968.37 | 3094591.0586 | 548.7802 | 607.8821 | 0.89475
Model 7 | ECC | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ12 | ChlrCap | 583.5185 | 355529 | 64873.65 | 2900724.0539 | 511.4723 | 609.2849 | 0.87653
Model 7 | ESe | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ12 | ChlrCap | 334.4787 | 181478.9 | 25517.06 | 1531043.9147 | 170.0213 | 542.5723 | 0.50832
Model 7 | ESe | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ12 | ChlrCap | 331.1757 | 147411.7 | 25630.12 | 1379490.0285 | 121.1608 | 445.1163 | 0.36585
Model 7 | ESe | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ12 | ChlrCap | 328.879 | 144234.9 | 24274.93 | 1342544.6223 | 111.2831 | 438.5652 | 0.33837
Model 7 | ESe | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ12 | ChlrCap | 319.1893 | 130991.8 | 17526.13 | 1268460.5335 | 107.9447 | 410.389 | 0.33818
Model 7 | ESe | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ12 | ChlrCap | 302.8257 | 124925.4 | 17666.88 | 1202501.4503 | 100.2595 | 412.5324 | 0.33108
Model 7 | EUn | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ12 | ChlrCap | 2285.9947 | 1345688 | 454734.9 | 10567892.7315 | 2402.4679 | 588.6663 | 1.051
Model 7 | EUn | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ12 | ChlrCap | 2294.4407 | 1330579 | 445221.9 | 10349241.6706 | 2391.7031 | 579.9143 | 1.0424
Model 7 | EUn | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ12 | ChlrCap | 2243.6113 | 1318335 | 448065.6 | 10098013.4748 | 2358.1957 | 587.5951 | 1.0511
Model 7 | EUn | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ12 | ChlrCap | 2114.4723 | 1188154 | 376087.1 | 9343133.7444 | 2152.9979 | 561.9151 | 1.0182
Model 7 | EUn | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ12 | ChlrCap | 2018.7463 | 1136990 | 336067.4 | 8857430.2849 | 2050.4683 | 563.2159 | 1.0157
Model 7 | Hsp | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ12 | ChlrCap | 874.059 | 291524.7 | 28957.99 | 4194456.6002 | 707.598 | 333.5298 | 0.80955
Model 7 | Hsp | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ12 | ChlrCap | 873.2853 | 289952 | 28837.31 | 4170612.3142 | 706.0084 | 332.0244 | 0.80845
Model 7 | Hsp | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ12 | ChlrCap | 879.031 | 282901 | 28808.47 | 4128254.9683 | 703.518 | 321.8328 | 0.80033
Model 7 | Hsp | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ12 | ChlrCap | 889.8155 | 266746.3 | 21065.19 | 4035153.4959 | 668.0746 | 299.7771 | 0.7508
Model 7 | Hsp | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ12 | ChlrCap | 908.701 | 246683 | 20281.05 | 3842026.0633 | 613.5005 | 271.4677 | 0.67514
Model 7 | Htl | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ12 | ChlrCap | 219.0595 | 163467.1 | 31163.28 | 1475708.1855 | 229.0914 | 746.2224 | 1.0458
Model 7 | Htl | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ12 | ChlrCap | 211.378 | 147683.2 | 27222.34 | 1173465.8256 | 213.0686 | 698.6687 | 1.008
Model 7 | Htl | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ12 | ChlrCap | 204.8895 | 145103.3 | 27173.88 | 1128927.4795 | 208.7081 | 708.2027 | 1.0186
Model 7 | Htl | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ12 | ChlrCap | 187.9173 | 128063.7 | 24760.2 | 1057504.2577 | 195.4486 | 681.4896 | 1.0401
Model 7 | Htl | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ12 | ChlrCap | 186.1508 | 126357.1 | 24263.55 | 1044370.794 | 191.2079 | 678.7888 | 1.0272
Model 7 | MBT | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ12 | ChlrCap | 372.7475 | 172540.4 | 31175.29 | 2174108.6553 | 341.269 | 462.8881 | 0.91555
Model 7 | MBT | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ12 | ChlrCap | 362.977 | 180305.7 | 30857.5 | 1973397.524 | 342.4236 | 496.7414 | 0.94338
Model 7 | MBT | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ12 | ChlrCap | 350.5465 | 174814.5 | 29503.34 | 1901158.7515 | 331.9007 | 498.6913 | 0.94681
Model 7 | MBT | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ12 | ChlrCap | 347.0127 | 176473 | 12171.35 | 1839271.8464 | 319.5767 | 508.5492 | 0.92094
Model 7 | MBT | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ12 | ChlrCap | 325.3683 | 166261.5 | 10793.17 | 1717255.4232 | 296.7733 | 510.9947 | 0.91211
Model 7 | Nrs | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ12 | ChlrCap | 125.9374 | 109757 | 25314.08 | 1413449.5484 | 219.8778 | 871.5205 | 1.7459
Model 7 | Nrs | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ12 | ChlrCap | 120.5391 | 79307.68 | 23350.16 | 1204197.7691 | 182.0381 | 657.9416 | 1.5102
Model 7 | Nrs | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ12 | ChlrCap | 117.7088 | 78517.52 | 23564.06 | 1182709.4362 | 180.2173 | 667.0488 | 1.531
Model 7 | Nrs | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ12 | ChlrCap | 111.6158 | 71094.71 | 21885.33 | 1147883.3215 | 172.5767 | 636.959 | 1.5462
Model 7 | Nrs | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ12 | ChlrCap | 110.2839 | 65569.64 | 21066.93 | 1105623.8411 | 160.426 | 594.553 | 1.4547
Model 7 | OfL | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ12 | ChlrCap | 418.6502 | 213559.9 | 82883.71 | 1934182.823 | 380.4699 | 510.1154 | 0.9088
Model 7 | OfL | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ12 | ChlrCap | 417.4628 | 223481.9 | 79784.98 | 1819699.4244 | 378.6461 | 535.3336 | 0.90702
Model 7 | OfL | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ12 | ChlrCap | 403.19 | 217910 | 85860.06 | 1747566.0164 | 367.6153 | 540.4648 | 0.91177
Model 7 | OfL | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ12 | ChlrCap | 401.5918 | 207641.3 | 73748.6 | 1768810.7808 | 365.6728 | 517.0456 | 0.91056
Model 7 | OfL | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ12 | ChlrCap | 390.1103 | 199889.5 | 14537.48 | 1681664.2462 | 348.1902 | 512.3922 | 0.89254
Model 7 | OfS | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ12 | ChlrCap | 27.0139 | 13168.44 | 3064.733 | 123342.2556 | 21.9575 | 487.4692 | 0.81282
Model 7 | OfS | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ12 | ChlrCap | 26.6977 | 14051.26 | 2964.69 | 117089.2798 | 22.1515 | 526.3091 | 0.82972
Model 7 | OfS | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ12 | ChlrCap | 26.1792 | 13890.94 | 3006.326 | 114150.4771 | 21.7381 | 530.6093 | 0.83036
Model 7 | OfS | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ12 | ChlrCap | 24.359 | 12068.4 | 2743.475 | 105355.2339 | 20.1178 | 495.4387 | 0.82589
Model 7 | OfS | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ12 | ChlrCap | 23.6061 | 11568.24 | 2103.375 | 100534.6838 | 19.1133 | 490.0539 | 0.80968
Model 7 | Rt3 | 2003 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ12 | ChlrCap | 294.7187 | 173069.4 | 79853.87 | 1613578.0668 | 388.2068 | 587.236 | 1.3172
Model 7 | Rt3 | 2007 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ12 | ChlrCap | 292.9947 | 186852.2 | 79911.54 | 1564874.6753 | 407.6464 | 637.7324 | 1.3913
Model 7 | Rt3 | 2011 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ12 | ChlrCap | 286.6217 | 185227 | 80854.49 | 1544189.3916 | 400.5943 | 646.2421 | 1.3976
Model 7 | Rt3 | 2015 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ12 | ChlrCap | 276.5603 | 173180.9 | 71415.18 | 1420554.939 | 371.5861 | 626.1957 | 1.3436
Model 7 | Rt3 | 2020 | CZ12 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ12 | ChlrCap | 265.7432 | 162455.4 | 59987.94 | 1327816.5006 | 344.4513 | 611.3248 | 1.2962
Model 7 | ECC | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ13 | ChlrCap | 780.354 | 612551.6 | 124850.1 | 3496456.755 | 699.7756 | 784.9663 | 0.89674
Model 7 | ECC | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ13 | ChlrCap | 778.095 | 606598.1 | 123971.7 | 3428549.9801 | 695.7691 | 779.5939 | 0.8942
Model 7 | ECC | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ13 | ChlrCap | 758.2678 | 597390.3 | 124400.6 | 3338035.6741 | 685.595 | 787.8355 | 0.90416
Model 7 | ECC | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ13 | ChlrCap | 724.1292 | 541410.6 | 112680.6 | 3170688.095 | 597.5893 | 747.6713 | 0.82525
Model 7 | ECC | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ13 | ChlrCap | 689.718 | 526112.9 | 92362.03 | 2959040.3681 | 559.4521 | 762.7942 | 0.81113
Model 7 | ESe | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ13 | ChlrCap | 405.9537 | 215459.6 | 37274.56 | 1551150.1934 | 157.4996 | 530.7492 | 0.38797
Model 7 | ESe | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ13 | ChlrCap | 399.7133 | 214677.1 | 37106.07 | 1412547.9834 | 133.2393 | 537.0777 | 0.33334
Model 7 | ESe | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ13 | ChlrCap | 393.3575 | 209426.4 | 33623.93 | 1353014.6447 | 123.9577 | 532.4073 | 0.31513
Model 7 | ESe | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ13 | ChlrCap | 380.471 | 191915.1 | 25363.69 | 1274634.6878 | 115.7731 | 504.4145 | 0.30429
Model 7 | ESe | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ13 | ChlrCap | 365.916 | 180056.9 | 25689.42 | 1197094.9693 | 106.7856 | 492.0717 | 0.29183
Model 7 | EUn | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ13 | ChlrCap | 2548.0427 | 2037591 | 599271.2 | 10852096.6342 | 2717.1125 | 799.6691 | 1.0664
Model 7 | EUn | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ13 | ChlrCap | 2603.7117 | 2021560 | 590680.9 | 10667248.7702 | 2753.9577 | 776.4147 | 1.0577
Model 7 | EUn | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ13 | ChlrCap | 2532.0783 | 1978128 | 588886.1 | 10296101.1196 | 2680.271 | 781.227 | 1.0585
Model 7 | EUn | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ13 | ChlrCap | 2391.7757 | 1772662 | 483804.9 | 9492798.4033 | 2437.1492 | 741.1489 | 1.019
Model 7 | EUn | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ13 | ChlrCap | 2296.1407 | 1704424 | 446390.8 | 8951865.4373 | 2318.0968 | 742.2995 | 1.0096
Model 7 | Hsp | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ13 | ChlrCap | 922.8818 | 503032.7 | 41365.29 | 4355207.2743 | 780.3837 | 545.0673 | 0.84559
Model 7 | Hsp | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ13 | ChlrCap | 924.1015 | 500379.5 | 41107.33 | 4330921.2298 | 778.5522 | 541.4768 | 0.8425
Model 7 | Hsp | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ13 | ChlrCap | 939.1933 | 472799.3 | 40880.23 | 4237923.3857 | 764.7545 | 503.41 | 0.81427
Model 7 | Hsp | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ13 | ChlrCap | 952.4823 | 444654.3 | 30274.36 | 4130493.2052 | 718.2696 | 466.8374 | 0.7541
Model 7 | Hsp | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ13 | ChlrCap | 967.7355 | 415150.6 | 29388.96 | 3912352.1735 | 651.1573 | 428.9918 | 0.67287
Model 7 | Htl | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ13 | ChlrCap | 239.844 | 247274.7 | 40103.72 | 1517155.44 | 256.9487 | 1030.9814 | 1.0713
Model 7 | Htl | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ13 | ChlrCap | 232.1605 | 227066.7 | 35487.57 | 1203230.4409 | 240.7955 | 978.0591 | 1.0372
Model 7 | Htl | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ13 | ChlrCap | 224.3243 | 221799.2 | 35063.41 | 1158734.8824 | 234.9256 | 988.7434 | 1.0473
Model 7 | Htl | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ13 | ChlrCap | 206.0013 | 199206.4 | 32386.23 | 1086107.5272 | 219.8211 | 967.0151 | 1.0671
Model 7 | Htl | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ13 | ChlrCap | 204.4572 | 196560.9 | 31765.22 | 1070309.6392 | 215.2325 | 961.3794 | 1.0527
Model 7 | MBT | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ13 | ChlrCap | 406.2655 | 251560 | 38590.46 | 2250174.0199 | 371.8529 | 619.201 | 0.9153
Model 7 | MBT | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ13 | ChlrCap | 395.2757 | 265464.3 | 37842.48 | 2046256.2579 | 378.4381 | 671.5928 | 0.9574
Model 7 | MBT | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ13 | ChlrCap | 378.4635 | 253419.6 | 36193.42 | 1972076.129 | 369.0796 | 669.6012 | 0.97521
Model 7 | MBT | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ13 | ChlrCap | 375.0285 | 243109.6 | 16605.58 | 1898114.0164 | 346.3463 | 648.243 | 0.92352
Model 7 | MBT | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ13 | ChlrCap | 353.691 | 241641 | 15160.31 | 1780361.0223 | 326.8243 | 683.198 | 0.92404
Model 7 | Nrs | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ13 | ChlrCap | 138.3341 | 186886 | 33747.89 | 1447759.4648 | 246.2507 | 1350.9756 | 1.7801
Model 7 | Nrs | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ13 | ChlrCap | 132.7963 | 134425.1 | 31546.28 | 1207782.2635 | 202.0653 | 1012.2651 | 1.5216
Model 7 | Nrs | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ13 | ChlrCap | 129.6282 | 132429.3 | 31646.9 | 1187921.1628 | 199.7677 | 1021.6087 | 1.5411
Model 7 | Nrs | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ13 | ChlrCap | 122.481 | 121943.4 | 29897.98 | 1152364.5489 | 190.5895 | 995.6109 | 1.5561
Model 7 | Nrs | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ13 | ChlrCap | 118.2186 | 114409.4 | 29162.76 | 1103971.7476 | 177.5074 | 967.7783 | 1.5015
Model 7 | OfL | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ13 | ChlrCap | 429.9983 | 292144.2 | 109222.9 | 2000240.1196 | 401.7713 | 679.4077 | 0.93436
Model 7 | OfL | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ13 | ChlrCap | 428.8553 | 311101.6 | 106214.2 | 1907819.3271 | 406.1267 | 725.4232 | 0.947
Model 7 | OfL | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ13 | ChlrCap | 414.733 | 300252.6 | 109473.5 | 1831907.1911 | 393.9634 | 723.966 | 0.94992
Model 7 | OfL | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ13 | ChlrCap | 416.0417 | 291965.5 | 97226.13 | 1852615.5897 | 392.2925 | 701.7699 | 0.94292
Model 7 | OfL | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ13 | ChlrCap | 404.4273 | 282743.3 | 51952.66 | 1769528.0797 | 366.5125 | 699.1202 | 0.90625
Model 7 | OfS | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ13 | ChlrCap | 29.1718 | 19116.31 | 4940.481 | 125865.8439 | 24.0739 | 655.3003 | 0.82525
Model 7 | OfS | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ13 | ChlrCap | 28.9361 | 18396.69 | 4822.125 | 118701.8422 | 22.6347 | 635.769 | 0.78223
Model 7 | OfS | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ13 | ChlrCap | 29.0007 | 17939.34 | 4825.172 | 115647.2831 | 22.1329 | 618.5839 | 0.76318
Model 7 | OfS | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ13 | ChlrCap | 26.3782 | 15856.51 | 4539.344 | 107102.1698 | 20.5919 | 601.121 | 0.78064
Model 7 | OfS | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ13 | ChlrCap | 25.6917 | 15263.87 | 4121.502 | 101954.2989 | 19.3907 | 594.1166 | 0.75474
Model 7 | Rt3 | 2003 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ13 | ChlrCap | 321.207 | 255369.7 | 96756.16 | 1708035.7362 | 421.8645 | 795.0316 | 1.3134
Model 7 | Rt3 | 2007 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ13 | ChlrCap | 319.3022 | 278026.1 | 96986.25 | 1669979.2544 | 448.1435 | 870.7304 | 1.4035
Model 7 | Rt3 | 2011 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ13 | ChlrCap | 305.8862 | 269611.9 | 96738.55 | 1627821.0317 | 434.7159 | 881.4125 | 1.4212
Model 7 | Rt3 | 2015 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ13 | ChlrCap | 295.795 | 254500.1 | 86146.93 | 1497217.7421 | 405.5597 | 860.3935 | 1.3711
Model 7 | Rt3 | 2020 | CZ13 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ13 | ChlrCap | 284.9072 | 240094.4 | 75840.63 | 1389009.6893 | 377.0042 | 842.711 | 1.3233
Model 7 | ECC | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ14 | ChlrCap | 842.3122 | 554616.1 | 112369.5 | 3513655.796 | 670.4608 | 658.4448 | 0.79598
Model 7 | ECC | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ14 | ChlrCap | 839.8307 | 549411.2 | 111693.8 | 3443397.714 | 664.3741 | 654.1928 | 0.79108
Model 7 | ECC | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ14 | ChlrCap | 815.9963 | 532616.4 | 112911.3 | 3307688.1594 | 631.1125 | 652.7191 | 0.77343
Model 7 | ECC | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ14 | ChlrCap | 777.5993 | 485981.2 | 100018 | 3145936.422 | 577.8377 | 624.9764 | 0.7431
Model 7 | ECC | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ14 | ChlrCap | 742.634 | 470026.8 | 79060.55 | 2940736.9988 | 536.8196 | 632.9185 | 0.72286
Model 7 | ESe | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ14 | ChlrCap | 443.2102 | 197427 | 31168.25 | 1573536.585 | 154.5383 | 445.4478 | 0.34868
Model 7 | ESe | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ14 | ChlrCap | 436.6147 | 193671.6 | 30996.01 | 1428955.3342 | 127.8411 | 443.5756 | 0.2928
Model 7 | ESe | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ14 | ChlrCap | 431.0297 | 184023.5 | 28084.51 | 1332678.5925 | 112.0651 | 426.9393 | 0.25999
Model 7 | ESe | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ14 | ChlrCap | 416.4333 | 167205.5 | 20183.97 | 1253504.2372 | 97.8377 | 401.5181 | 0.23494
Model 7 | ESe | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ14 | ChlrCap | 398.6307 | 159842.5 | 20103.34 | 1181548.3658 | 88.9869 | 400.9789 | 0.22323
Model 7 | EUn | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ14 | ChlrCap | 2765.1257 | 1788825 | 535549.5 | 10962898.17 | 2617.7975 | 646.9236 | 0.94672
Model 7 | EUn | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ14 | ChlrCap | 2751.5513 | 1771149 | 526566.3 | 10750307.5252 | 2607.2807 | 643.6911 | 0.94757
Model 7 | EUn | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ14 | ChlrCap | 2661.1527 | 1735867 | 534616.6 | 10258709.837 | 2493.8409 | 652.2989 | 0.93713
Model 7 | EUn | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ14 | ChlrCap | 2534.953 | 1575262 | 447928.4 | 9491685.4502 | 2290.0539 | 621.4166 | 0.90339
Model 7 | EUn | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ14 | ChlrCap | 2442.6647 | 1514220 | 406767.7 | 8969233.3283 | 2189.5268 | 619.905 | 0.89637
Model 7 | Hsp | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ14 | ChlrCap | 966.1242 | 435433.6 | 35551.25 | 4484288.6565 | 765.7597 | 450.7014 | 0.79261
Model 7 | Hsp | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ14 | ChlrCap | 965.485 | 432958.8 | 35357.66 | 4456637.8757 | 753.0111 | 448.4366 | 0.77993
Model 7 | Hsp | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ14 | ChlrCap | 989.8152 | 406338.7 | 35347.99 | 4335926.0164 | 734.9786 | 410.5197 | 0.74254
Model 7 | Hsp | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ14 | ChlrCap | 1006.211 | 388379.6 | 25628.51 | 4238456.2849 | 693.9493 | 385.9823 | 0.68967
Model 7 | Hsp | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ14 | ChlrCap | 1033.492 | 362186.3 | 24905.89 | 4039431.4889 | 640.1133 | 350.4491 | 0.61937
Model 7 | Htl | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ14 | ChlrCap | 254.5663 | 216826.6 | 35507.04 | 1618664.2828 | 253.657 | 851.7489 | 0.99643
Model 7 | Htl | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ14 | ChlrCap | 246.2812 | 198533.4 | 31543.87 | 1316980.9298 | 236.9738 | 806.125 | 0.96221
Model 7 | Htl | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ14 | ChlrCap | 238.4502 | 194106.8 | 31135.74 | 1259149.0021 | 229.9935 | 814.0351 | 0.96454
Model 7 | Htl | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ14 | ChlrCap | 213.8892 | 176646.7 | 30071.95 | 1103890.4962 | 212.7027 | 825.8796 | 0.99445
Model 7 | Htl | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ14 | ChlrCap | 212.2535 | 174640.2 | 29503.86 | 1089452.5268 | 209.6761 | 822.7907 | 0.98786
Model 7 | MBT | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ14 | ChlrCap | 416.1008 | 239177.8 | 36039.64 | 2273381.5029 | 370.2866 | 574.8073 | 0.8899
Model 7 | MBT | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ14 | ChlrCap | 405.316 | 250353.5 | 35623.02 | 2066453.5193 | 375.7323 | 617.6749 | 0.92701
Model 7 | MBT | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ14 | ChlrCap | 392.189 | 241414.4 | 34161.96 | 1983931.2122 | 357.8755 | 615.5563 | 0.91251
Model 7 | MBT | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ14 | ChlrCap | 386.476 | 241245.7 | 15115.27 | 1921266.1266 | 340.5507 | 624.2191 | 0.88117
Model 7 | MBT | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ14 | ChlrCap | 365.1983 | 226488.5 | 13616.97 | 1790850.9355 | 319.2491 | 620.1794 | 0.87418
Model 7 | Nrs | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ14 | ChlrCap | 137.3265 | 168661 | 31326.6 | 1517094.5937 | 245.3024 | 1228.1753 | 1.7863
Model 7 | Nrs | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ14 | ChlrCap | 131.5436 | 118354.2 | 29224.19 | 1272893.678 | 195.4646 | 899.7334 | 1.4859
Model 7 | Nrs | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ14 | ChlrCap | 128.4714 | 116935.8 | 29398.07 | 1251119.0131 | 193.2866 | 910.2088 | 1.5045
Model 7 | Nrs | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ14 | ChlrCap | 122.4209 | 107155.7 | 27515.87 | 1214768.5555 | 184.9987 | 875.306 | 1.5112
Model 7 | Nrs | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ14 | ChlrCap | 121.6014 | 100652.8 | 26825.02 | 1167706.7839 | 172.5866 | 827.7273 | 1.4193
Model 7 | OfL | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ14 | ChlrCap | 449.7138 | 286770.8 | 95127.07 | 2002165.7538 | 390.1529 | 637.674 | 0.86756
Model 7 | OfL | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ14 | ChlrCap | 448.4922 | 303148 | 93053.44 | 1897332.4478 | 392.1738 | 675.9271 | 0.87443
Model 7 | OfL | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ14 | ChlrCap | 434.1887 | 293917 | 94883.67 | 1822575.4865 | 372.685 | 676.9338 | 0.85835
Model 7 | OfL | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ14 | ChlrCap | 438.5937 | 283974.9 | 86551.21 | 1845674.177 | 372.8612 | 647.4669 | 0.85013
Model 7 | OfL | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ14 | ChlrCap | 426.4855 | 274877.7 | 42275.05 | 1764771.9941 | 355.7587 | 644.5183 | 0.83416
Model 7 | OfS | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ14 | ChlrCap | 30.8227 | 17615.34 | 4327.549 | 126307.5981 | 22.9645 | 571.5046 | 0.74505
Model 7 | OfS | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ14 | ChlrCap | 30.6523 | 16943.71 | 4193.925 | 118918.4846 | 21.5737 | 552.7714 | 0.70382
Model 7 | OfS | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ14 | ChlrCap | 29.9938 | 16713.17 | 4220.375 | 115939.4261 | 21.1549 | 557.2208 | 0.70531
Model 7 | OfS | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ14 | ChlrCap | 28.0533 | 14860.05 | 4071.552 | 106853.845 | 19.7483 | 529.7076 | 0.70396
Model 7 | OfS | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ14 | ChlrCap | 27.2422 | 14311.61 | 3548.493 | 101623.7482 | 18.5865 | 525.3468 | 0.68227
Model 7 | Rt3 | 2003 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ14 | ChlrCap | 328.0502 | 232438.8 | 86710.65 | 1690369.7819 | 413.929 | 708.5465 | 1.2618
Model 7 | Rt3 | 2007 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ14 | ChlrCap | 326.0978 | 249780.8 | 87011.82 | 1636982.9707 | 432.8445 | 765.9689 | 1.3273
Model 7 | Rt3 | 2011 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ14 | ChlrCap | 307.0428 | 242034.3 | 89691.84 | 1582884.1618 | 415.7299 | 788.2754 | 1.354
Model 7 | Rt3 | 2015 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ14 | ChlrCap | 298.3908 | 238727.8 | 78699.37 | 1462524.129 | 407.1255 | 800.0507 | 1.3644
Model 7 | Rt3 | 2020 | CZ14 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ14 | ChlrCap | 286.5403 | 224616.3 | 64943.05 | 1358548.6776 | 377.7883 | 783.8907 | 1.3184
Model 7 | ECC | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ15 | ChlrCap | 1071.5732 | 1205241 | 187341.4 | 3622387.1993 | 964.4507 | 1124.7398 | 0.90003
Model 7 | ECC | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ15 | ChlrCap | 1067.7025 | 1195520 | 186445.8 | 3568986.3916 | 959.6117 | 1119.7127 | 0.89876
Model 7 | ECC | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ15 | ChlrCap | 1039.5275 | 1140036 | 182020 | 3464767.4431 | 890.6369 | 1096.6867 | 0.85677
Model 7 | ECC | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ15 | ChlrCap | 999.8655 | 1039394 | 164155.9 | 3276301.9156 | 785.6318 | 1039.5338 | 0.78574
Model 7 | ECC | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ15 | ChlrCap | 966.2553 | 991572.4 | 148370.6 | 2976169.1676 | 736.4552 | 1026.2012 | 0.76217
Model 7 | ESe | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ15 | ChlrCap | 571.8747 | 441366.1 | 65574.96 | 1589403.5334 | 218.3647 | 771.7882 | 0.38184
Model 7 | ESe | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ15 | ChlrCap | 563.4945 | 435033.3 | 64996.31 | 1369146.6401 | 181.9294 | 772.0276 | 0.32286
Model 7 | ESe | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ15 | ChlrCap | 548.3095 | 417514.2 | 55050.84 | 1314457.9226 | 164.9384 | 761.4572 | 0.30081
Model 7 | ESe | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ15 | ChlrCap | 531.334 | 385502.7 | 40336.48 | 1241569.6038 | 149.4225 | 725.5374 | 0.28122
Model 7 | ESe | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ15 | ChlrCap | 512.9195 | 369474.3 | 37572.2 | 1138037.3461 | 137.961 | 720.3358 | 0.26897
Model 7 | EUn | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ15 | ChlrCap | 3491.2633 | 3778225 | 861056.1 | 10861619.6729 | 3531.8479 | 1082.1942 | 1.0116
Model 7 | EUn | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ15 | ChlrCap | 3472.33 | 3752515 | 852400.6 | 10720828.1758 | 3517.4018 | 1080.6908 | 1.013
Model 7 | EUn | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ15 | ChlrCap | 3357.4867 | 3622695 | 836880.1 | 10434709.0199 | 3373.4587 | 1078.9901 | 1.0048
Model 7 | EUn | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ15 | ChlrCap | 3229.451 | 3310247 | 672443.5 | 9712540.1688 | 3072.381 | 1025.0185 | 0.95136
Model 7 | EUn | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ15 | ChlrCap | 3124.6453 | 3185185 | 629477.9 | 8952744.721 | 2979.0974 | 1019.3749 | 0.95342
Model 7 | Hsp | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ15 | ChlrCap | 1138.0515 | 969299.9 | 59077.69 | 4460072.4502 | 954.5951 | 851.7188 | 0.8388
Model 7 | Hsp | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ15 | ChlrCap | 1137.3063 | 966502.8 | 58793.79 | 4444995.7937 | 952.7675 | 849.8175 | 0.83774
Model 7 | Hsp | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ15 | ChlrCap | 1170.9917 | 895208.7 | 58326.25 | 4326852.3669 | 930.294 | 764.4876 | 0.79445
Model 7 | Hsp | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ15 | ChlrCap | 1192.3815 | 845453.6 | 42957.69 | 4204455.6999 | 881.9641 | 709.0462 | 0.73967
Model 7 | Hsp | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ15 | ChlrCap | 1221.3843 | 793465.9 | 42073.1 | 3910500.7409 | 806.6569 | 649.6448 | 0.66044
Model 7 | Htl | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ15 | ChlrCap | 320.6793 | 447868.3 | 55961.57 | 1571261.0739 | 346.5073 | 1396.6235 | 1.0805
Model 7 | Htl | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ15 | ChlrCap | 312.4632 | 414191.5 | 50306.67 | 1198124.6042 | 324.0171 | 1325.569 | 1.037
Model 7 | Htl | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ15 | ChlrCap | 302.4662 | 403486.7 | 48616.52 | 1171746.6429 | 314.1473 | 1333.9895 | 1.0386
Model 7 | Htl | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ15 | ChlrCap | 275.608 | 368440.8 | 45830.11 | 1081087.4177 | 287.6125 | 1336.8291 | 1.0436
Model 7 | Htl | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ15 | ChlrCap | 273.3932 | 364401.8 | 44903.83 | 1059199.3584 | 282.6505 | 1332.8855 | 1.0339
Model 7 | MBT | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ15 | ChlrCap | 513.0728 | 484124.7 | 57730.32 | 2446120.3306 | 475.2853 | 943.5789 | 0.92635
Model 7 | MBT | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ15 | ChlrCap | 501.2435 | 505667.2 | 56394.45 | 2205014.7362 | 490.9939 | 1008.8255 | 0.97955
Model 7 | MBT | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ15 | ChlrCap | 481.6768 | 483593.3 | 53702.33 | 2146455.8804 | 461.5933 | 1003.9787 | 0.9583
Model 7 | MBT | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ15 | ChlrCap | 475.9037 | 483624.3 | 26349.02 | 2082912.6178 | 434.2001 | 1016.2231 | 0.91237
Model 7 | MBT | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ15 | ChlrCap | 453.7342 | 456638.2 | 24438.44 | 1927251.4513 | 409.514 | 1006.4003 | 0.90254
Model 7 | Nrs | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ15 | ChlrCap | 182.887 | 378482.2 | 48932.39 | 1480291.6424 | 333.7597 | 2069.4866 | 1.825
Model 7 | Nrs | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ15 | ChlrCap | 176.6895 | 258908.8 | 46471.85 | 1132260.6048 | 251.6136 | 1465.3321 | 1.424
Model 7 | Nrs | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ15 | ChlrCap | 169.2027 | 251995.3 | 46485.57 | 1113017.3707 | 244.2253 | 1489.3105 | 1.4434
Model 7 | Nrs | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ15 | ChlrCap | 159.5154 | 235372.3 | 44393.04 | 1080496.9336 | 233.0667 | 1475.5456 | 1.4611
Model 7 | Nrs | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ15 | ChlrCap | 156.3556 | 223532.8 | 43632.94 | 1017362.5497 | 219.0922 | 1429.6437 | 1.4012
Model 7 | OfL | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ15 | ChlrCap | 550.1308 | 536133 | 150192.9 | 2227219.6788 | 454.5442 | 974.5554 | 0.82625
Model 7 | OfL | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ15 | ChlrCap | 548.4895 | 573820.8 | 147957.4 | 2125278.0023 | 458.8402 | 1046.1837 | 0.83655
Model 7 | OfL | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ15 | ChlrCap | 508.8343 | 548929.5 | 148815.3 | 2065980.575 | 443.6984 | 1078.7981 | 0.87199
Model 7 | OfL | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ15 | ChlrCap | 536.7805 | 547948.4 | 137611.3 | 2059711.2907 | 447.2051 | 1020.8053 | 0.83312
Model 7 | OfL | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ15 | ChlrCap | 522.6575 | 530905.6 | 96978.77 | 1951210.5721 | 428.8085 | 1015.7811 | 0.82044
Model 7 | OfS | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ15 | ChlrCap | 36.3228 | 35102.85 | 7769.448 | 131893.2365 | 30.7207 | 966.4141 | 0.84577
Model 7 | OfS | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ15 | ChlrCap | 36.0697 | 37601.19 | 7642.451 | 126114.306 | 31.4099 | 1042.4601 | 0.87081
Model 7 | OfS | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ15 | ChlrCap | 34.8143 | 36534.06 | 7592.514 | 122391.7857 | 29.8159 | 1049.3988 | 0.85643
Model 7 | OfS | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ15 | ChlrCap | 32.9766 | 32809.04 | 7121.401 | 113979.4544 | 26.7478 | 994.9173 | 0.81111
Model 7 | OfS | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ15 | ChlrCap | 32.0845 | 31599.02 | 6710.865 | 107196.3045 | 25.3962 | 984.8679 | 0.79154
Model 7 | Rt3 | 2003 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ15 | ChlrCap | 400.5612 | 471662.5 | 137005.7 | 1889713.2151 | 512.4358 | 1177.5043 | 1.2793
Model 7 | Rt3 | 2007 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ15 | ChlrCap | 399.2927 | 512902.6 | 136900.8 | 1855883.2855 | 550.1445 | 1284.528 | 1.3778
Model 7 | Rt3 | 2011 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ15 | ChlrCap | 381.8447 | 485252.5 | 131817.7 | 1817899.4566 | 519.9631 | 1270.8113 | 1.3617
Model 7 | Rt3 | 2015 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ15 | ChlrCap | 370.6765 | 482765 | 117934.7 | 1682368.6178 | 520.3587 | 1302.389 | 1.4038
Model 7 | Rt3 | 2020 | CZ15 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ15 | ChlrCap | 360.4552 | 450552.4 | 106056.6 | 1522750.0064 | 480.3841 | 1249.9541 | 1.3327
Model 7 | ECC | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2003-CZ16 | ChlrCap | 457.4017 | 162219.1 | 57873.91 | 4212782.9918 | 178.5513 | 354.6535 | 0.39036
Model 7 | ECC | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2007-CZ16 | ChlrCap | 455.6992 | 160920.2 | 57486.77 | 4147308.5275 | 177.4657 | 353.1281 | 0.38944
Model 7 | ECC | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2011-CZ16 | ChlrCap | 435.1002 | 155970.6 | 60547.22 | 3846957.2638 | 162.0099 | 358.4706 | 0.37235
Model 7 | ECC | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2015-CZ16 | ChlrCap | 409.0627 | 140886 | 53266.61 | 3640090.8417 | 142.7081 | 344.4118 | 0.34887
Model 7 | ECC | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ECC-2020-CZ16 | ChlrCap | 382.9705 | 135296.2 | 39426.63 | 3532698.5991 | 121.2197 | 353.281 | 0.31652
Model 7 | ESe | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2003-CZ16 | ChlrCap | 234.3245 | 67765.96 | 18472.17 | 2018565.8891 | 99.8988 | 289.1971 | 0.42633
Model 7 | ESe | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2007-CZ16 | ChlrCap | 230.2368 | 58501.78 | 18443.55 | 1910761.0155 | 78.8465 | 254.0939 | 0.34246
Model 7 | ESe | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2011-CZ16 | ChlrCap | 225.8828 | 54562.92 | 16531.15 | 1709243.3299 | 70.3872 | 241.5541 | 0.31161
Model 7 | ESe | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2015-CZ16 | ChlrCap | 217.4782 | 49691.51 | 12346.72 | 1618735.2472 | 61.7777 | 228.4896 | 0.28406
Model 7 | ESe | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-ESe-2020-CZ16 | ChlrCap | 202.1828 | 47517.95 | 12175.11 | 1584037.6382 | 55.5916 | 235.0247 | 0.27496
Model 7 | EUn | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2003-CZ16 | ChlrCap | 1624.4567 | 547557.5 | 287275.3 | 13737139.524 | 370.9297 | 337.0712 | 0.22834
Model 7 | EUn | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2007-CZ16 | ChlrCap | 1615.792 | 538855.4 | 279613 | 13488662.272 | 369.0033 | 333.493 | 0.22837
Model 7 | EUn | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2011-CZ16 | ChlrCap | 1564.3213 | 535696.6 | 295391.8 | 12458728.2509 | 340.0771 | 342.4466 | 0.2174
Model 7 | EUn | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2015-CZ16 | ChlrCap | 1441.557 | 450503.1 | 251866.7 | 11458494.7902 | 278.5415 | 312.5115 | 0.19322
Model 7 | EUn | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-EUn-2020-CZ16 | ChlrCap | 1356.255 | 427185.3 | 218020.1 | 11116794.1454 | 249.472 | 314.9742 | 0.18394
Model 7 | Hsp | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2003-CZ16 | ChlrCap | 642.4422 | 129931.2 | 20897.5 | 5034507.0481 | 537.4053 | 202.2457 | 0.8365
Model 7 | Hsp | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2007-CZ16 | ChlrCap | 641.734 | 128930.1 | 20870.44 | 5001040.9086 | 535.9611 | 200.9089 | 0.83518
Model 7 | Hsp | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2011-CZ16 | ChlrCap | 645.7175 | 121253.2 | 20865.19 | 4771673.6671 | 521.4121 | 187.7806 | 0.80749
Model 7 | Hsp | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2015-CZ16 | ChlrCap | 648.9835 | 116098.2 | 15693.12 | 4658394.1137 | 509.1528 | 178.8924 | 0.78454
Model 7 | Hsp | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Hsp-2020-CZ16 | ChlrCap | 655.2332 | 107336.9 | 15123.2 | 4531440.2743 | 460.5485 | 163.8148 | 0.70288
Model 7 | Htl | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2003-CZ16 | ChlrCap | 148.4864 | 83051.09 | 24448.23 | 1826355.3597 | 163.2353 | 559.3179 | 1.0993
Model 7 | Htl | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2007-CZ16 | ChlrCap | 142.3047 | 74506.16 | 21403.27 | 1581295.5826 | 151.1612 | 523.5677 | 1.0622
Model 7 | Htl | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2011-CZ16 | ChlrCap | 137.1796 | 73659.8 | 21530.6 | 1485804.9891 | 147.8946 | 536.959 | 1.0781
Model 7 | Htl | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2015-CZ16 | ChlrCap | 119.3118 | 59933.88 | 18889.46 | 1345244.3574 | 136.1576 | 502.33 | 1.1412
Model 7 | Htl | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Htl-2020-CZ16 | ChlrCap | 118.4843 | 59184.04 | 18494.04 | 1336878.0652 | 132.8197 | 499.5096 | 1.121
Model 7 | MBT | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2003-CZ16 | ChlrCap | 263.6658 | 69641.98 | 18147.91 | 2372863.8851 | 205.9757 | 264.1297 | 0.7812
Model 7 | MBT | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2007-CZ16 | ChlrCap | 255.6078 | 72733.29 | 17957.42 | 2186411.3025 | 196.7965 | 284.5503 | 0.76992
Model 7 | MBT | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2011-CZ16 | ChlrCap | 242.0863 | 71034.27 | 17446.91 | 2051129.3435 | 192.2373 | 293.4254 | 0.79409
Model 7 | MBT | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2015-CZ16 | ChlrCap | 240.6683 | 71786.96 | 7139.078 | 1969606.592 | 181.5388 | 298.2817 | 0.75431
Model 7 | MBT | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-MBT-2020-CZ16 | ChlrCap | 224.0473 | 66774.55 | 5979.605 | 1859768.6026 | 161.4509 | 298.0377 | 0.72061
Model 7 | Nrs | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2003-CZ16 | ChlrCap | 83.2297 | 41245.05 | 17198.33 | 1710989.8664 | 155.8097 | 495.5571 | 1.872
Model 7 | Nrs | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2007-CZ16 | ChlrCap | 79.3774 | 32012.43 | 15601.93 | 1550990.2436 | 138.3901 | 403.294 | 1.7434
Model 7 | Nrs | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2011-CZ16 | ChlrCap | 78.7542 | 31725.13 | 15795.1 | 1512858.0798 | 137.5965 | 402.8372 | 1.7472
Model 7 | Nrs | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2015-CZ16 | ChlrCap | 78.6215 | 27900.38 | 14477.5 | 1466621.0592 | 133.4073 | 354.8696 | 1.6968
Model 7 | Nrs | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Nrs-2020-CZ16 | ChlrCap | 78.647 | 25420.01 | 13913.99 | 1434835.2807 | 122.9073 | 323.2167 | 1.5628
Model 7 | OfL | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2003-CZ16 | ChlrCap | 320.445 | 97186.31 | 51530.82 | 2029367.6436 | 266.2004 | 303.2855 | 0.83072
Model 7 | OfL | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2007-CZ16 | ChlrCap | 319.4318 | 101371.6 | 47083.01 | 1953195.034 | 258.7393 | 317.3497 | 0.81
Model 7 | OfL | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2011-CZ16 | ChlrCap | 302.0675 | 98875.97 | 47784.54 | 1819483.6096 | 248.6864 | 327.3307 | 0.82328
Model 7 | OfL | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2015-CZ16 | ChlrCap | 305.7612 | 91530.73 | 46890.21 | 1892228.3564 | 242.6837 | 299.3537 | 0.7937
Model 7 | OfL | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfL-2020-CZ16 | ChlrCap | 292.609 | 87747.19 | 8699.651 | 1823873.8195 | 231.1907 | 299.8786 | 0.7901
Model 7 | OfS | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2003-CZ16 | ChlrCap | 20.1187 | 5927.39 | 1969.783 | 143251.2609 | 14.8865 | 294.6215 | 0.73993
Model 7 | OfS | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2007-CZ16 | ChlrCap | 19.935 | 6307.795 | 1865.542 | 138194.1348 | 14.814 | 316.418 | 0.74311
Model 7 | OfS | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2011-CZ16 | ChlrCap | 19.4755 | 6267.273 | 1904.536 | 133667.8424 | 14.6017 | 321.8028 | 0.74975
Model 7 | OfS | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2015-CZ16 | ChlrCap | 17.6336 | 5251.62 | 1482.58 | 120699.5687 | 12.5655 | 297.8189 | 0.71259
Model 7 | OfS | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-OfS-2020-CZ16 | ChlrCap | 17.013 | 5023.287 | 1309.511 | 116626.6467 | 11.9327 | 295.2623 | 0.70139
Model 7 | Rt3 | 2003 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2003-CZ16 | ChlrCap | 217.8227 | 70556.81 | 53605.86 | 1806601.4256 | 301.7355 | 323.9186 | 1.3852
Model 7 | Rt3 | 2007 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2007-CZ16 | ChlrCap | 216.4523 | 74599.25 | 53649.52 | 1765987.2251 | 309.2343 | 344.6452 | 1.4286
Model 7 | Rt3 | 2011 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2011-CZ16 | ChlrCap | 199.7127 | 72455.91 | 57075.94 | 1612195.3482 | 299.4938 | 362.8008 | 1.4996
Model 7 | Rt3 | 2015 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2015-CZ16 | ChlrCap | 188.7828 | 67069.2 | 50424.71 | 1521223.823 | 274.8128 | 355.2717 | 1.4557
Model 7 | Rt3 | 2020 | CZ16 | cAVVG | AirCldScrewChlr-Model7-1.16kwpton-Rt3-2020-CZ16 | ChlrCap | 178.089 | 62353.33 | 38314.28 | 1463205.6038 | 251.3027 | 350.1245 | 1.4111