## Sensitivity Analysis_CZ6
Month | Day | Average Daily Temperature (deg F) | Size Category | Baseline Heater Size (kW) | New Heater Size (kW) | Baseline Daily kWh | Treatment Daily kWh | Daily kWh Savings | Size Category | Average Energy Savings (kWh/day) | # of Operating Days | Annual Energy Savings (kWh/year) | Original Savings Methodology Savings (kWh/year) | % Difference
1 | 1 | 51.7083 | 1 | 1 | 1 | 20.2037 | 9.7809 | 10.4228 | 1 | 12.0934 | 334 | 4039.1831 | 4037 | -0.05408%
1 | 2 | 55.1667 | 1 | 1 | 1 | 20.2037 | 9.3089 | 10.8948 | 2 | 9.6791 | 334 | 3232.8194 | 3231 | -0.05631%
1 | 3 | 51.4583 | 1 | 1 | 1 | 20.2037 | 9.815 | 10.3887 | 3 | 19.7212 | 334 | 6586.8747 | 6581 | -0.08927%
1 | 4 | 50.0833 | 1 | 1 | 1 | 20.2037 | 10.0027 | 10.201 | 4 | 137.3059 | 334 | 45860.181 | 45819 | -0.08988%
1 | 5 | 53.9583 | 1 | 1 | 1 | 20.2037 | 9.4738 | 10.7299
1 | 6 | 54.8333 | 1 | 1 | 1 | 20.2037 | 9.3544 | 10.8493
1 | 7 | 54.4583 | 1 | 1 | 1 | 20.2037 | 9.4056 | 10.7981
1 | 8 | 53.7083 | 1 | 1 | 1 | 20.2037 | 9.5079 | 10.6958
1 | 9 | 56.75 | 1 | 1 | 1 | 20.2037 | 9.0928 | 11.1109
1 | 10 | 59 | 1 | 1 | 1 | 20.2037 | 8.7857 | 11.418
1 | 11 | 57.875 | 1 | 1 | 1 | 20.2037 | 8.9392 | 11.2645
1 | 12 | 55.875 | 1 | 1 | 1 | 20.2037 | 9.2122 | 10.9915
1 | 13 | 59.2917 | 1 | 1 | 1 | 20.2037 | 8.7459 | 11.4578
1 | 14 | 64.7917 | 1 | 1 | 1 | 20.2037 | 7.9952 | 12.2085
1 | 15 | 57.9167 | 1 | 1 | 1 | 20.2037 | 8.9335 | 11.2702
1 | 16 | 56.7083 | 1 | 1 | 1 | 20.2037 | 9.0985 | 11.1052
1 | 17 | 55.6667 | 1 | 1 | 1 | 20.2037 | 9.2406 | 10.9631
1 | 18 | 55.4583 | 1 | 1 | 1 | 20.2037 | 9.2691 | 10.9346
1 | 19 | 55 | 1 | 1 | 1 | 20.2037 | 9.3316 | 10.8721
1 | 20 | 53.9167 | 1 | 1 | 1 | 20.2037 | 9.4795 | 10.7242
1 | 21 | 56.5833 | 1 | 1 | 1 | 20.2037 | 9.1155 | 11.0882
1 | 22 | 61.75 | 1 | 1 | 1 | 20.2037 | 8.4103 | 11.7934
1 | 23 | 56.0417 | 1 | 1 | 1 | 20.2037 | 9.1895 | 11.0142
1 | 24 | 52.7917 | 1 | 1 | 1 | 20.2037 | 9.6331 | 10.5706
1 | 25 | 54.5 | 1 | 1 | 1 | 20.2037 | 9.3999 | 10.8038
1 | 26 | 53.25 | 1 | 1 | 1 | 20.2037 | 9.5705 | 10.6332
1 | 27 | 54.25 | 1 | 1 | 1 | 20.2037 | 9.434 | 10.7697
1 | 28 | 56.3333 | 1 | 1 | 1 | 20.2037 | 9.1496 | 11.0541
1 | 29 | 55.375 | 1 | 1 | 1 | 20.2037 | 9.2805 | 10.9232
1 | 30 | 53.1667 | 1 | 1 | 1 | 20.2037 | 9.5819 | 10.6218
1 | 31 | 55.875 | 1 | 1 | 1 | 20.2037 | 9.2122 | 10.9915
2 | 1 | 51.4583 | 1 | 1 | 1 | 20.2037 | 9.815 | 10.3887
2 | 2 | 51.2917 | 1 | 1 | 1 | 20.2037 | 9.8378 | 10.3659
2 | 3 | 52.0833 | 1 | 1 | 1 | 20.2037 | 9.7297 | 10.474
2 | 4 | 53.625 | 1 | 1 | 1 | 20.2037 | 9.5193 | 10.6844
2 | 5 | 50.5833 | 1 | 1 | 1 | 20.2037 | 9.9345 | 10.2692
2 | 6 | 49.8333 | 1 | 1 | 1 | 20.2037 | 10.0368 | 10.1669
2 | 7 | 53.5417 | 1 | 1 | 1 | 20.2037 | 9.5307 | 10.673
2 | 8 | 55.9583 | 1 | 1 | 1 | 20.2037 | 9.2008 | 11.0029
2 | 9 | 62.0833 | 1 | 1 | 1 | 20.2037 | 8.3648 | 11.8389
2 | 10 | 59.4167 | 1 | 1 | 1 | 20.2037 | 8.7288 | 11.4749
2 | 11 | 57.8333 | 1 | 1 | 1 | 20.2037 | 8.9449 | 11.2588
2 | 12 | 60 | 1 | 1 | 1 | 20.2037 | 8.6492 | 11.5545
2 | 13 | 52.9583 | 1 | 1 | 1 | 20.2037 | 9.6103 | 10.5934
2 | 14 | 52.375 | 1 | 1 | 1 | 20.2037 | 9.6899 | 10.5138
2 | 15 | 53.375 | 1 | 1 | 1 | 20.2037 | 9.5534 | 10.6503
2 | 16 | 53.375 | 1 | 1 | 1 | 20.2037 | 9.5534 | 10.6503
2 | 17 | 53.125 | 1 | 1 | 1 | 20.2037 | 9.5876 | 10.6161
2 | 18 | 53.625 | 1 | 1 | 1 | 20.2037 | 9.5193 | 10.6844
2 | 19 | 54.75 | 1 | 1 | 1 | 20.2037 | 9.3658 | 10.8379
2 | 20 | 54.75 | 1 | 1 | 1 | 20.2037 | 9.3658 | 10.8379
2 | 21 | 54.5417 | 1 | 1 | 1 | 20.2037 | 9.3942 | 10.8095
2 | 22 | 53.2917 | 1 | 1 | 1 | 20.2037 | 9.5648 | 10.6389
2 | 23 | 52 | 1 | 1 | 1 | 20.2037 | 9.7411 | 10.4626
2 | 24 | 54.3333 | 1 | 1 | 1 | 20.2037 | 9.4226 | 10.7811
2 | 25 | 54.5833 | 1 | 1 | 1 | 20.2037 | 9.3885 | 10.8152
2 | 26 | 61.625 | 1 | 1 | 1 | 20.2037 | 8.4274 | 11.7763
2 | 27 | 63.5417 | 1 | 1 | 1 | 20.2037 | 8.1658 | 12.0379
2 | 28 | 57.5833 | 1 | 1 | 1 | 20.2037 | 8.979 | 11.2247
3 | 1 | 58.4167 | 1 | 1 | 1 | 20.2037 | 8.8653 | 11.3384
3 | 2 | 59.1667 | 1 | 1 | 1 | 20.2037 | 8.7629 | 11.4408
3 | 3 | 59.9167 | 1 | 1 | 1 | 20.2037 | 8.6606 | 11.5431
3 | 4 | 62.625 | 1 | 1 | 1 | 20.2037 | 8.2909 | 11.9128
3 | 5 | 63.0417 | 1 | 1 | 1 | 20.2037 | 8.234 | 11.9697
3 | 6 | 66.0833 | 1 | 1 | 1 | 20.2037 | 7.8189 | 12.3848
3 | 7 | 66.5417 | 1 | 1 | 1 | 20.2037 | 7.7563 | 12.4474
3 | 8 | 69.5417 | 1 | 1 | 1 | 20.2037 | 7.3468 | 12.8569
3 | 9 | 71.5417 | 1 | 1 | 1 | 20.2037 | 7.0738 | 13.1299
3 | 10 | 66.5 | 1 | 1 | 1 | 20.2037 | 7.762 | 12.4417
3 | 11 | 63.9583 | 1 | 1 | 1 | 20.2037 | 8.1089 | 12.0948
3 | 12 | 66.875 | 1 | 1 | 1 | 20.2037 | 7.7108 | 12.4929
3 | 13 | 63.5 | 1 | 1 | 1 | 20.2037 | 8.1715 | 12.0322
3 | 14 | 62.7917 | 1 | 1 | 1 | 20.2037 | 8.2681 | 11.9356
3 | 15 | 66.2083 | 1 | 1 | 1 | 20.2037 | 7.8018 | 12.4019
3 | 16 | 72.4583 | 1 | 1 | 1 | 20.2037 | 6.9487 | 13.255
3 | 17 | 66.625 | 1 | 1 | 1 | 20.2037 | 7.7449 | 12.4588
3 | 18 | 63.9167 | 1 | 1 | 1 | 20.2037 | 8.1146 | 12.0891
3 | 19 | 63.75 | 1 | 1 | 1 | 20.2037 | 8.1373 | 12.0664
3 | 20 | 62.2917 | 1 | 1 | 1 | 20.2037 | 8.3364 | 11.8673
3 | 21 | 62.75 | 1 | 1 | 1 | 20.2037 | 8.2738 | 11.9299
3 | 22 | 61.0833 | 1 | 1 | 1 | 20.2037 | 8.5013 | 11.7024
3 | 23 | 61.8333 | 1 | 1 | 1 | 20.2037 | 8.3989 | 11.8048
3 | 24 | 62.375 | 1 | 1 | 1 | 20.2037 | 8.325 | 11.8787
3 | 25 | 62.2083 | 1 | 1 | 1 | 20.2037 | 8.3478 | 11.8559
3 | 26 | 62.375 | 1 | 1 | 1 | 20.2037 | 8.325 | 11.8787
3 | 27 | 61.2083 | 1 | 1 | 1 | 20.2037 | 8.4843 | 11.7194
3 | 28 | 61.9167 | 1 | 1 | 1 | 20.2037 | 8.3876 | 11.8161
3 | 29 | 63.125 | 1 | 1 | 1 | 20.2037 | 8.2226 | 11.9811
3 | 30 | 62.5417 | 1 | 1 | 1 | 20.2037 | 8.3023 | 11.9014
3 | 31 | 60 | 1 | 1 | 1 | 20.2037 | 8.6492 | 11.5545
4 | 1 | 68.2917 | 1 | 1 | 1 | 20.2037 | 7.5174 | 12.6863
4 | 2 | 61.4583 | 1 | 1 | 1 | 20.2037 | 8.4501 | 11.7536
4 | 3 | 60.25 | 1 | 1 | 1 | 20.2037 | 8.6151 | 11.5886
4 | 4 | 61.25 | 1 | 1 | 1 | 20.2037 | 8.4786 | 11.7251
4 | 5 | 61.2917 | 1 | 1 | 1 | 20.2037 | 8.4729 | 11.7308
4 | 6 | 61.875 | 1 | 1 | 1 | 20.2037 | 8.3933 | 11.8104
4 | 7 | 57.7917 | 1 | 1 | 1 | 20.2037 | 8.9506 | 11.2531
4 | 8 | 52.7083 | 1 | 1 | 1 | 20.2037 | 9.6444 | 10.5593
4 | 9 | 53.25 | 1 | 1 | 1 | 20.2037 | 9.5705 | 10.6332
4 | 10 | 56.7083 | 1 | 1 | 1 | 20.2037 | 9.0985 | 11.1052
4 | 11 | 60.1667 | 1 | 1 | 1 | 20.2037 | 8.6264 | 11.5773
4 | 12 | 59.0833 | 1 | 1 | 1 | 20.2037 | 8.7743 | 11.4294
4 | 13 | 57.9583 | 1 | 1 | 1 | 20.2037 | 8.9278 | 11.2759
4 | 14 | 62.5833 | 1 | 1 | 1 | 20.2037 | 8.2966 | 11.9071
4 | 15 | 70.125 | 1 | 1 | 1 | 20.2037 | 7.2672 | 12.9365
4 | 16 | 72.9167 | 1 | 1 | 1 | 20.2037 | 6.8862 | 13.3175
4 | 17 | 65.7083 | 1 | 1 | 1 | 20.2037 | 7.87 | 12.3337
4 | 18 | 63.1667 | 1 | 1 | 1 | 20.2037 | 8.217 | 11.9867
4 | 19 | 63.4583 | 1 | 1 | 1 | 20.2037 | 8.1771 | 12.0266
4 | 20 | 60.875 | 1 | 1 | 1 | 20.2037 | 8.5298 | 11.6739
4 | 21 | 62.1667 | 1 | 1 | 1 | 20.2037 | 8.3535 | 11.8502
4 | 22 | 61 | 1 | 1 | 1 | 20.2037 | 8.5127 | 11.691
4 | 23 | 61.8333 | 1 | 1 | 1 | 20.2037 | 8.3989 | 11.8048
4 | 24 | 59.9167 | 1 | 1 | 1 | 20.2037 | 8.6606 | 11.5431
4 | 25 | 63.2917 | 1 | 1 | 1 | 20.2037 | 8.1999 | 12.0038
4 | 26 | 65.4167 | 1 | 1 | 1 | 20.2037 | 7.9099 | 12.2938
4 | 27 | 66.875 | 1 | 1 | 1 | 20.2037 | 7.7108 | 12.4929
4 | 28 | 67.2083 | 1 | 1 | 1 | 20.2037 | 7.6653 | 12.5384
4 | 29 | 63.5417 | 1 | 1 | 1 | 20.2037 | 8.1658 | 12.0379
4 | 30 | 67.9583 | 1 | 1 | 1 | 20.2037 | 7.5629 | 12.6408
5 | 1 | 67.0417 | 1 | 1 | 1 | 20.2037 | 7.6881 | 12.5156
5 | 2 | 67.1667 | 1 | 1 | 1 | 20.2037 | 7.671 | 12.5327
5 | 3 | 65.625 | 1 | 1 | 1 | 20.2037 | 7.8814 | 12.3223
5 | 4 | 62.875 | 1 | 1 | 1 | 20.2037 | 8.2568 | 11.9469
5 | 5 | 61.7917 | 1 | 1 | 1 | 20.2037 | 8.4046 | 11.7991
5 | 6 | 58.5417 | 1 | 1 | 1 | 20.2037 | 8.8482 | 11.3555
5 | 7 | 54.9167 | 1 | 1 | 1 | 20.2037 | 9.343 | 10.8607
5 | 8 | 60.3333 | 1 | 1 | 1 | 20.2037 | 8.6037 | 11.6
5 | 9 | 61.6667 | 1 | 1 | 1 | 20.2037 | 8.4217 | 11.782
5 | 10 | 63.25 | 1 | 1 | 1 | 20.2037 | 8.2056 | 11.9981
5 | 11 | 62.625 | 1 | 1 | 1 | 20.2037 | 8.2909 | 11.9128
5 | 12 | 61.7917 | 1 | 1 | 1 | 20.2037 | 8.4046 | 11.7991
5 | 13 | 62.5 | 1 | 1 | 1 | 20.2037 | 8.308 | 11.8957
5 | 14 | 61.0417 | 1 | 1 | 1 | 20.2037 | 8.507 | 11.6967
5 | 15 | 58.875 | 1 | 1 | 1 | 20.2037 | 8.8027 | 11.401
5 | 16 | 59.625 | 1 | 1 | 1 | 20.2037 | 8.7004 | 11.5033
5 | 17 | 60.7083 | 1 | 1 | 1 | 20.2037 | 8.5525 | 11.6512
5 | 18 | 64.375 | 1 | 1 | 1 | 20.2037 | 8.052 | 12.1517
5 | 19 | 69.0833 | 1 | 1 | 1 | 20.2037 | 7.4094 | 12.7943
5 | 20 | 72.1667 | 1 | 1 | 1 | 20.2037 | 6.9885 | 13.2152
5 | 21 | 65.7917 | 1 | 1 | 1 | 20.2037 | 7.8587 | 12.345
5 | 22 | 56.625 | 1 | 1 | 1 | 20.2037 | 9.1098 | 11.0939
5 | 23 | 63.1667 | 1 | 1 | 1 | 20.2037 | 8.217 | 11.9867
5 | 24 | 61.8333 | 1 | 1 | 1 | 20.2037 | 8.3989 | 11.8048
5 | 25 | 62.6667 | 1 | 1 | 1 | 20.2037 | 8.2852 | 11.9185
5 | 26 | 63.9583 | 1 | 1 | 1 | 20.2037 | 8.1089 | 12.0948
5 | 27 | 62.6667 | 1 | 1 | 1 | 20.2037 | 8.2852 | 11.9185
5 | 28 | 64.1667 | 1 | 1 | 1 | 20.2037 | 8.0805 | 12.1232
5 | 29 | 63.2083 | 1 | 1 | 1 | 20.2037 | 8.2113 | 11.9924
5 | 30 | 62.5417 | 1 | 1 | 1 | 20.2037 | 8.3023 | 11.9014
5 | 31 | 62.125 | 1 | 1 | 1 | 20.2037 | 8.3591 | 11.8446
6 | 1 | 70 | 1 | 1 | 1 | 20.2037 | 7.2843 | 12.9194
6 | 2 | 68.0417 | 1 | 1 | 1 | 20.2037 | 7.5516 | 12.6521
6 | 3 | 69.0417 | 1 | 1 | 1 | 20.2037 | 7.4151 | 12.7886
6 | 4 | 68.0833 | 1 | 1 | 1 | 20.2037 | 7.5459 | 12.6578
6 | 5 | 65.7917 | 1 | 1 | 1 | 20.2037 | 7.8587 | 12.345
6 | 6 | 64.7083 | 1 | 1 | 1 | 20.2037 | 8.0065 | 12.1972
6 | 7 | 65.9583 | 1 | 1 | 1 | 20.2037 | 7.8359 | 12.3678
6 | 8 | 66.625 | 1 | 1 | 1 | 20.2037 | 7.7449 | 12.4588
6 | 9 | 66.9583 | 1 | 1 | 1 | 20.2037 | 7.6994 | 12.5043
6 | 10 | 68.5 | 1 | 1 | 1 | 20.2037 | 7.489 | 12.7147
6 | 11 | 69.2917 | 1 | 1 | 1 | 20.2037 | 7.381 | 12.8227
6 | 12 | 66.625 | 1 | 1 | 1 | 20.2037 | 7.7449 | 12.4588
6 | 13 | 67.625 | 1 | 1 | 1 | 20.2037 | 7.6084 | 12.5953
6 | 14 | 68.125 | 1 | 1 | 1 | 20.2037 | 7.5402 | 12.6635
6 | 15 | 67.2917 | 1 | 1 | 1 | 20.2037 | 7.6539 | 12.5498
6 | 16 | 67.875 | 1 | 1 | 1 | 20.2037 | 7.5743 | 12.6294
6 | 17 | 69.7083 | 1 | 1 | 1 | 20.2037 | 7.3241 | 12.8796
6 | 18 | 70.75 | 1 | 1 | 1 | 20.2037 | 7.1819 | 13.0218
6 | 19 | 71.7083 | 1 | 1 | 1 | 20.2037 | 7.0511 | 13.1526
6 | 20 | 73.125 | 1 | 1 | 1 | 20.2037 | 6.8577 | 13.346
6 | 21 | 71.4167 | 1 | 1 | 1 | 20.2037 | 7.0909 | 13.1128
6 | 22 | 70.0833 | 1 | 1 | 1 | 20.2037 | 7.2729 | 12.9308
6 | 23 | 67.9583 | 1 | 1 | 1 | 20.2037 | 7.5629 | 12.6408
6 | 24 | 69.7917 | 1 | 1 | 1 | 20.2037 | 7.3127 | 12.891
6 | 25 | 68.875 | 1 | 1 | 1 | 20.2037 | 7.4378 | 12.7659
6 | 26 | 71.6667 | 1 | 1 | 1 | 20.2037 | 7.0568 | 13.1469
6 | 27 | 72.375 | 1 | 1 | 1 | 20.2037 | 6.9601 | 13.2436
6 | 28 | 72.0833 | 1 | 1 | 1 | 20.2037 | 6.9999 | 13.2038
6 | 29 | 72.375 | 1 | 1 | 1 | 20.2037 | 6.9601 | 13.2436
6 | 30 | 76.1667 | 1 | 1 | 1 | 20.2037 | 6.4426 | 13.7611
7 | 1 | 74.2083 | 1 | 1 | 1 | 20.2037 | 6.7099 | 13.4938
7 | 2 | 70.0417 | 1 | 1 | 1 | 20.2037 | 7.2786 | 12.9251
7 | 3 | 69.25 | 1 | 1 | 1 | 20.2037 | 7.3866 | 12.8171
7 | 4 | 70.5417 | 1 | 1 | 1 | 20.2037 | 7.2103 | 12.9934
7 | 5 | 73.5 | 1 | 1 | 1 | 20.2037 | 6.8066 | 13.3971
7 | 6 | 75.7917 | 1 | 1 | 1 | 20.2037 | 6.4938 | 13.7099
7 | 7 | 74.125 | 1 | 1 | 1 | 20.2037 | 6.7212 | 13.4825
7 | 8 | 72.25 | 1 | 1 | 1 | 20.2037 | 6.9772 | 13.2265
7 | 9 | 69.6667 | 1 | 1 | 1 | 20.2037 | 7.3298 | 12.8739
7 | 10 | 70.0833 | 1 | 1 | 1 | 20.2037 | 7.2729 | 12.9308
7 | 11 | 70.0417 | 1 | 1 | 1 | 20.2037 | 7.2786 | 12.9251
7 | 12 | 69.25 | 1 | 1 | 1 | 20.2037 | 7.3866 | 12.8171
7 | 13 | 69.25 | 1 | 1 | 1 | 20.2037 | 7.3866 | 12.8171
7 | 14 | 66.875 | 1 | 1 | 1 | 20.2037 | 7.7108 | 12.4929
7 | 15 | 67.625 | 1 | 1 | 1 | 20.2037 | 7.6084 | 12.5953
7 | 16 | 68.25 | 1 | 1 | 1 | 20.2037 | 7.5231 | 12.6806
7 | 17 | 69.2917 | 1 | 1 | 1 | 20.2037 | 7.381 | 12.8227
7 | 18 | 71.9583 | 1 | 1 | 1 | 20.2037 | 7.017 | 13.1867
7 | 19 | 71.5417 | 1 | 1 | 1 | 20.2037 | 7.0738 | 13.1299
7 | 20 | 68.5 | 1 | 1 | 1 | 20.2037 | 7.489 | 12.7147
7 | 21 | 67.4167 | 1 | 1 | 1 | 20.2037 | 7.6369 | 12.5668
7 | 22 | 68.1667 | 1 | 1 | 1 | 20.2037 | 7.5345 | 12.6692
7 | 23 | 68.5417 | 1 | 1 | 1 | 20.2037 | 7.4833 | 12.7204
7 | 24 | 67.4167 | 1 | 1 | 1 | 20.2037 | 7.6369 | 12.5668
7 | 25 | 71.5417 | 1 | 1 | 1 | 20.2037 | 7.0738 | 13.1299
7 | 26 | 72.3333 | 1 | 1 | 1 | 20.2037 | 6.9658 | 13.2379
7 | 27 | 71 | 1 | 1 | 1 | 20.2037 | 7.1478 | 13.0559
7 | 28 | 71.6667 | 1 | 1 | 1 | 20.2037 | 7.0568 | 13.1469
7 | 29 | 68.9583 | 1 | 1 | 1 | 20.2037 | 7.4264 | 12.7773
7 | 30 | 67.5 | 1 | 1 | 1 | 20.2037 | 7.6255 | 12.5782
7 | 31 | 69.7917 | 1 | 1 | 1 | 20.2037 | 7.3127 | 12.891
8 | 1 | 69.9167 | 1 | 1 | 1 | 20.2037 | 7.2956 | 12.9081
8 | 2 | 71.125 | 1 | 1 | 1 | 20.2037 | 7.1307 | 13.073
8 | 3 | 71.3333 | 1 | 1 | 1 | 20.2037 | 7.1023 | 13.1014
8 | 4 | 71.125 | 1 | 1 | 1 | 20.2037 | 7.1307 | 13.073
8 | 5 | 72.125 | 1 | 1 | 1 | 20.2037 | 6.9942 | 13.2095
8 | 6 | 72.8333 | 1 | 1 | 1 | 20.2037 | 6.8975 | 13.3062
8 | 7 | 73.3333 | 1 | 1 | 1 | 20.2037 | 6.8293 | 13.3744
8 | 8 | 72.3333 | 1 | 1 | 1 | 20.2037 | 6.9658 | 13.2379
8 | 9 | 71.125 | 1 | 1 | 1 | 20.2037 | 7.1307 | 13.073
8 | 10 | 70.4167 | 1 | 1 | 1 | 20.2037 | 7.2274 | 12.9763
8 | 11 | 69.75 | 1 | 1 | 1 | 20.2037 | 7.3184 | 12.8853
8 | 12 | 69.4167 | 1 | 1 | 1 | 20.2037 | 7.3639 | 12.8398
8 | 13 | 70.75 | 1 | 1 | 1 | 20.2037 | 7.1819 | 13.0218
8 | 14 | 71.9583 | 1 | 1 | 1 | 20.2037 | 7.017 | 13.1867
8 | 15 | 71.125 | 1 | 1 | 1 | 20.2037 | 7.1307 | 13.073
8 | 16 | 71.4583 | 1 | 1 | 1 | 20.2037 | 7.0852 | 13.1185
8 | 17 | 70.8333 | 1 | 1 | 1 | 20.2037 | 7.1705 | 13.0332
8 | 18 | 69.5 | 1 | 1 | 1 | 20.2037 | 7.3525 | 12.8512
8 | 19 | 68.6667 | 1 | 1 | 1 | 20.2037 | 7.4663 | 12.7374
8 | 20 | 68.8333 | 1 | 1 | 1 | 20.2037 | 7.4435 | 12.7602
8 | 21 | 71.0833 | 1 | 1 | 1 | 20.2037 | 7.1364 | 13.0673
8 | 22 | 71.5833 | 1 | 1 | 1 | 20.2037 | 7.0682 | 13.1355
8 | 23 | 69.4583 | 1 | 1 | 1 | 20.2037 | 7.3582 | 12.8455
8 | 24 | 68.9583 | 1 | 1 | 1 | 20.2037 | 7.4264 | 12.7773
8 | 25 | 71.875 | 1 | 1 | 1 | 20.2037 | 7.0284 | 13.1753
8 | 26 | 71.9167 | 1 | 1 | 1 | 20.2037 | 7.0227 | 13.181
8 | 27 | 70.9583 | 1 | 1 | 1 | 20.2037 | 7.1535 | 13.0502
8 | 28 | 68.25 | 1 | 1 | 1 | 20.2037 | 7.5231 | 12.6806
8 | 29 | 70.4583 | 1 | 1 | 1 | 20.2037 | 7.2217 | 12.982
8 | 30 | 71.2917 | 1 | 1 | 1 | 20.2037 | 7.108 | 13.0957
8 | 31 | 70.375 | 1 | 1 | 1 | 20.2037 | 7.2331 | 12.9706
9 | 1 | 71.7083 | 1 | 1 | 1 | 20.2037 | 7.0511 | 13.1526
9 | 2 | 75.75 | 1 | 1 | 1 | 20.2037 | 6.4994 | 13.7043
9 | 3 | 76.5 | 1 | 1 | 1 | 20.2037 | 6.3971 | 13.8066
9 | 4 | 76 | 1 | 1 | 1 | 20.2037 | 6.4653 | 13.7384
9 | 5 | 74.4167 | 1 | 1 | 1 | 20.2037 | 6.6814 | 13.5223
9 | 6 | 73.2083 | 1 | 1 | 1 | 20.2037 | 6.8464 | 13.3573
9 | 7 | 71.3333 | 1 | 1 | 1 | 20.2037 | 7.1023 | 13.1014
9 | 8 | 69.1667 | 1 | 1 | 1 | 20.2037 | 7.398 | 12.8057
9 | 9 | 68.8333 | 1 | 1 | 1 | 20.2037 | 7.4435 | 12.7602
9 | 10 | 68.6667 | 1 | 1 | 1 | 20.2037 | 7.4663 | 12.7374
9 | 11 | 68.2083 | 1 | 1 | 1 | 20.2037 | 7.5288 | 12.6749
9 | 12 | 67.7917 | 1 | 1 | 1 | 20.2037 | 7.5857 | 12.618
9 | 13 | 69.375 | 1 | 1 | 1 | 20.2037 | 7.3696 | 12.8341
9 | 14 | 67.2083 | 1 | 1 | 1 | 20.2037 | 7.6653 | 12.5384
9 | 15 | 66.75 | 1 | 1 | 1 | 20.2037 | 7.7279 | 12.4758
9 | 16 | 66.8333 | 1 | 1 | 1 | 20.2037 | 7.7165 | 12.4872
9 | 17 | 71.625 | 1 | 1 | 1 | 20.2037 | 7.0625 | 13.1412
9 | 18 | 73.125 | 1 | 1 | 1 | 20.2037 | 6.8577 | 13.346
9 | 19 | 69.0417 | 1 | 1 | 1 | 20.2037 | 7.4151 | 12.7886
9 | 20 | 67.0833 | 1 | 1 | 1 | 20.2037 | 7.6824 | 12.5213
9 | 21 | 66.0833 | 1 | 1 | 1 | 20.2037 | 7.8189 | 12.3848
9 | 22 | 67.625 | 1 | 1 | 1 | 20.2037 | 7.6084 | 12.5953
9 | 23 | 69.5 | 1 | 1 | 1 | 20.2037 | 7.3525 | 12.8512
9 | 24 | 67.6667 | 1 | 1 | 1 | 20.2037 | 7.6028 | 12.6009
9 | 25 | 68.25 | 1 | 1 | 1 | 20.2037 | 7.5231 | 12.6806
9 | 26 | 66.5417 | 1 | 1 | 1 | 20.2037 | 7.7563 | 12.4474
9 | 27 | 65.9167 | 1 | 1 | 1 | 20.2037 | 7.8416 | 12.3621
9 | 28 | 66.7917 | 1 | 1 | 1 | 20.2037 | 7.7222 | 12.4815
9 | 29 | 67 | 1 | 1 | 1 | 20.2037 | 7.6937 | 12.51
9 | 30 | 66.7083 | 1 | 1 | 1 | 20.2037 | 7.7336 | 12.4701
10 | 1 | 77.5417 | 1 | 1 | 1 | 20.2037 | 6.2549 | 13.9488
10 | 2 | 78 | 1 | 1 | 1 | 20.2037 | 6.1923 | 14.0114
10 | 3 | 70.0417 | 1 | 1 | 1 | 20.2037 | 7.2786 | 12.9251
10 | 4 | 67.9167 | 1 | 1 | 1 | 20.2037 | 7.5686 | 12.6351
10 | 5 | 69.625 | 1 | 1 | 1 | 20.2037 | 7.3355 | 12.8682
10 | 6 | 71.2917 | 1 | 1 | 1 | 20.2037 | 7.108 | 13.0957
10 | 7 | 68.8333 | 1 | 1 | 1 | 20.2037 | 7.4435 | 12.7602
10 | 8 | 69.0417 | 1 | 1 | 1 | 20.2037 | 7.4151 | 12.7886
10 | 9 | 67.25 | 1 | 1 | 1 | 20.2037 | 7.6596 | 12.5441
10 | 10 | 65.75 | 1 | 1 | 1 | 20.2037 | 7.8644 | 12.3393
10 | 11 | 63.5833 | 1 | 1 | 1 | 20.2037 | 8.1601 | 12.0436
10 | 12 | 63.5833 | 1 | 1 | 1 | 20.2037 | 8.1601 | 12.0436
10 | 13 | 65.9583 | 1 | 1 | 1 | 20.2037 | 7.8359 | 12.3678
10 | 14 | 73.75 | 1 | 1 | 1 | 20.2037 | 6.7724 | 13.4313
10 | 15 | 74.5 | 1 | 1 | 1 | 20.2037 | 6.6701 | 13.5336
10 | 16 | 73.125 | 1 | 1 | 1 | 20.2037 | 6.8577 | 13.346
10 | 17 | 75.9167 | 1 | 1 | 1 | 20.2037 | 6.4767 | 13.727
10 | 18 | 74.5417 | 1 | 1 | 1 | 20.2037 | 6.6644 | 13.5393
10 | 19 | 68.0833 | 1 | 1 | 1 | 20.2037 | 7.5459 | 12.6578
10 | 20 | 68.0833 | 1 | 1 | 1 | 20.2037 | 7.5459 | 12.6578
10 | 21 | 66.2917 | 1 | 1 | 1 | 20.2037 | 7.7904 | 12.4133
10 | 22 | 65.7083 | 1 | 1 | 1 | 20.2037 | 7.87 | 12.3337
10 | 23 | 64.125 | 1 | 1 | 1 | 20.2037 | 8.0862 | 12.1175
10 | 24 | 64.8333 | 1 | 1 | 1 | 20.2037 | 7.9895 | 12.2142
10 | 25 | 69.0417 | 1 | 1 | 1 | 20.2037 | 7.4151 | 12.7886
10 | 26 | 73.25 | 1 | 1 | 1 | 20.2037 | 6.8407 | 13.363
10 | 27 | 71.5 | 1 | 1 | 1 | 20.2037 | 7.0795 | 13.1242
10 | 28 | 68.2083 | 1 | 1 | 1 | 20.2037 | 7.5288 | 12.6749
10 | 29 | 63.1667 | 1 | 1 | 1 | 20.2037 | 8.217 | 11.9867
10 | 30 | 60.2917 | 1 | 1 | 1 | 20.2037 | 8.6094 | 11.5943
10 | 31 | 62.5 | 1 | 1 | 1 | 20.2037 | 8.308 | 11.8957
11 | 1 | 72.0833 | 1 | 1 | 1 | 20.2037 | 6.9999 | 13.2038
11 | 2 | 63.375 | 1 | 1 | 1 | 20.2037 | 8.1885 | 12.0152
11 | 3 | 61.25 | 1 | 1 | 1 | 20.2037 | 8.4786 | 11.7251
11 | 4 | 57.5833 | 1 | 1 | 1 | 20.2037 | 8.979 | 11.2247
11 | 5 | 60.4167 | 1 | 1 | 1 | 20.2037 | 8.5923 | 11.6114
11 | 6 | 61.875 | 1 | 1 | 1 | 20.2037 | 8.3933 | 11.8104
11 | 7 | 63.4583 | 1 | 1 | 1 | 20.2037 | 8.1771 | 12.0266
11 | 8 | 61.7083 | 1 | 1 | 1 | 20.2037 | 8.416 | 11.7877
11 | 9 | 62.2917 | 1 | 1 | 1 | 20.2037 | 8.3364 | 11.8673
11 | 10 | 62.1667 | 1 | 1 | 1 | 20.2037 | 8.3535 | 11.8502
11 | 11 | 59.625 | 1 | 1 | 1 | 20.2037 | 8.7004 | 11.5033
11 | 12 | 59.0833 | 1 | 1 | 1 | 20.2037 | 8.7743 | 11.4294
11 | 13 | 59.7917 | 1 | 1 | 1 | 20.2037 | 8.6776 | 11.5261
11 | 14 | 60.1667 | 1 | 1 | 1 | 20.2037 | 8.6264 | 11.5773
11 | 15 | 68.8333 | 1 | 1 | 1 | 20.2037 | 7.4435 | 12.7602
11 | 16 | 66.75 | 1 | 1 | 1 | 20.2037 | 7.7279 | 12.4758
11 | 17 | 63.75 | 1 | 1 | 1 | 20.2037 | 8.1373 | 12.0664
11 | 18 | 68.4583 | 1 | 1 | 1 | 20.2037 | 7.4947 | 12.709
11 | 19 | 65.3333 | 1 | 1 | 1 | 20.2037 | 7.9212 | 12.2825
11 | 20 | 68.875 | 1 | 1 | 1 | 20.2037 | 7.4378 | 12.7659
11 | 21 | 68.4583 | 1 | 1 | 1 | 20.2037 | 7.4947 | 12.709
11 | 22 | 66.625 | 1 | 1 | 1 | 20.2037 | 7.7449 | 12.4588
11 | 23 | 62.4583 | 1 | 1 | 1 | 20.2037 | 8.3136 | 11.8901
11 | 24 | 60.875 | 1 | 1 | 1 | 20.2037 | 8.5298 | 11.6739
11 | 25 | 62.0417 | 1 | 1 | 1 | 20.2037 | 8.3705 | 11.8332
11 | 26 | 61.5 | 1 | 1 | 1 | 20.2037 | 8.4444 | 11.7593
11 | 27 | 58.25 | 1 | 1 | 1 | 20.2037 | 8.888 | 11.3157
11 | 28 | 57.3333 | 1 | 1 | 1 | 20.2037 | 9.0132 | 11.1905
11 | 29 | 57.625 | 1 | 1 | 1 | 20.2037 | 8.9733 | 11.2304
11 | 30 | 60.6667 | 1 | 1 | 1 | 20.2037 | 8.5582 | 11.6455
12 | 1 | 50.25 | 1 | 1 | 1 | 20.2037 | 9.98 | 10.2237
12 | 2 | 50.2917 | 1 | 1 | 1 | 20.2037 | 9.9743 | 10.2294
12 | 3 | 51.9167 | 1 | 1 | 1 | 20.2037 | 9.7525 | 10.4512
12 | 4 | 50.375 | 1 | 1 | 1 | 20.2037 | 9.9629 | 10.2408
12 | 5 | 49.375 | 1 | 1 | 1 | 20.2037 | 10.0994 | 10.1043
12 | 6 | 49.7917 | 1 | 1 | 1 | 20.2037 | 10.0425 | 10.1612
12 | 7 | 51.4583 | 1 | 1 | 1 | 20.2037 | 9.815 | 10.3887
12 | 8 | 55.25 | 1 | 1 | 1 | 20.2037 | 9.2975 | 10.9062
12 | 9 | 55.9167 | 1 | 1 | 1 | 20.2037 | 9.2065 | 10.9972
12 | 10 | 62.5833 | 1 | 1 | 1 | 20.2037 | 8.2966 | 11.9071
12 | 11 | 65.875 | 1 | 1 | 1 | 20.2037 | 7.8473 | 12.3564
12 | 12 | 56.9167 | 1 | 1 | 1 | 20.2037 | 9.07 | 11.1337
12 | 13 | 57.0417 | 1 | 1 | 1 | 20.2037 | 9.053 | 11.1507
12 | 14 | 60.75 | 1 | 1 | 1 | 20.2037 | 8.5468 | 11.6569
12 | 15 | 59.5833 | 1 | 1 | 1 | 20.2037 | 8.7061 | 11.4976
12 | 16 | 62.75 | 1 | 1 | 1 | 20.2037 | 8.2738 | 11.9299
12 | 17 | 60.875 | 1 | 1 | 1 | 20.2037 | 8.5298 | 11.6739
12 | 18 | 60.7083 | 1 | 1 | 1 | 20.2037 | 8.5525 | 11.6512
12 | 19 | 64.375 | 1 | 1 | 1 | 20.2037 | 8.052 | 12.1517
12 | 20 | 57.875 | 1 | 1 | 1 | 20.2037 | 8.9392 | 11.2645
12 | 21 | 56.2917 | 1 | 1 | 1 | 20.2037 | 9.1553 | 11.0484
12 | 22 | 54.25 | 1 | 1 | 1 | 20.2037 | 9.434 | 10.7697
12 | 23 | 53.7917 | 1 | 1 | 1 | 20.2037 | 9.4966 | 10.7071
12 | 24 | 53.625 | 1 | 1 | 1 | 20.2037 | 9.5193 | 10.6844
12 | 25 | 52.9167 | 1 | 1 | 1 | 20.2037 | 9.616 | 10.5877
12 | 26 | 53.875 | 1 | 1 | 1 | 20.2037 | 9.4852 | 10.7185
12 | 27 | 57.875 | 1 | 1 | 1 | 20.2037 | 8.9392 | 11.2645
12 | 28 | 57.125 | 1 | 1 | 1 | 20.2037 | 9.0416 | 11.1621
12 | 29 | 55.7917 | 1 | 1 | 1 | 20.2037 | 9.2236 | 10.9801
12 | 30 | 53.2083 | 1 | 1 | 1 | 20.2037 | 9.5762 | 10.6275
12 | 31 | 53.2083 | 1 | 1 | 1 | 20.2037 | 9.5762 | 10.6275
1 | 1 | 51.7083 | 2 | 1 | 1 | 20.2037 | 12.1573 | 8.0464
1 | 2 | 55.1667 | 2 | 1 | 1 | 20.2037 | 11.6959 | 8.5078
1 | 3 | 51.4583 | 2 | 1 | 1 | 20.2037 | 12.1906 | 8.0131
1 | 4 | 50.0833 | 2 | 1 | 1 | 20.2037 | 12.374 | 7.8297
1 | 5 | 53.9583 | 2 | 1 | 1 | 20.2037 | 11.8571 | 8.3466
1 | 6 | 54.8333 | 2 | 1 | 1 | 20.2037 | 11.7404 | 8.4633
1 | 7 | 54.4583 | 2 | 1 | 1 | 20.2037 | 11.7904 | 8.4133
1 | 8 | 53.7083 | 2 | 1 | 1 | 20.2037 | 11.8905 | 8.3132
1 | 9 | 56.75 | 2 | 1 | 1 | 20.2037 | 11.4847 | 8.719
1 | 10 | 59 | 2 | 1 | 1 | 20.2037 | 11.1846 | 9.0191
1 | 11 | 57.875 | 2 | 1 | 1 | 20.2037 | 11.3347 | 8.869
1 | 12 | 55.875 | 2 | 1 | 1 | 20.2037 | 11.6015 | 8.6022
1 | 13 | 59.2917 | 2 | 1 | 1 | 20.2037 | 11.1457 | 9.058
1 | 14 | 64.7917 | 2 | 1 | 1 | 20.2037 | 10.412 | 9.7917
1 | 15 | 57.9167 | 2 | 1 | 1 | 20.2037 | 11.3291 | 8.8746
1 | 16 | 56.7083 | 2 | 1 | 1 | 20.2037 | 11.4903 | 8.7134
1 | 17 | 55.6667 | 2 | 1 | 1 | 20.2037 | 11.6293 | 8.5744
1 | 18 | 55.4583 | 2 | 1 | 1 | 20.2037 | 11.657 | 8.5467
1 | 19 | 55 | 2 | 1 | 1 | 20.2037 | 11.7182 | 8.4855
1 | 20 | 53.9167 | 2 | 1 | 1 | 20.2037 | 11.8627 | 8.341
1 | 21 | 56.5833 | 2 | 1 | 1 | 20.2037 | 11.507 | 8.6967
1 | 22 | 61.75 | 2 | 1 | 1 | 20.2037 | 10.8178 | 9.3859
1 | 23 | 56.0417 | 2 | 1 | 1 | 20.2037 | 11.5792 | 8.6245
1 | 24 | 52.7917 | 2 | 1 | 1 | 20.2037 | 12.0128 | 8.1909
1 | 25 | 54.5 | 2 | 1 | 1 | 20.2037 | 11.7849 | 8.4188
1 | 26 | 53.25 | 2 | 1 | 1 | 20.2037 | 11.9516 | 8.2521
1 | 27 | 54.25 | 2 | 1 | 1 | 20.2037 | 11.8182 | 8.3855
1 | 28 | 56.3333 | 2 | 1 | 1 | 20.2037 | 11.5403 | 8.6634
1 | 29 | 55.375 | 2 | 1 | 1 | 20.2037 | 11.6682 | 8.5355
1 | 30 | 53.1667 | 2 | 1 | 1 | 20.2037 | 11.9627 | 8.241
1 | 31 | 55.875 | 2 | 1 | 1 | 20.2037 | 11.6015 | 8.6022
2 | 1 | 51.4583 | 2 | 1 | 1 | 20.2037 | 12.1906 | 8.0131
2 | 2 | 51.2917 | 2 | 1 | 1 | 20.2037 | 12.2128 | 7.9909
2 | 3 | 52.0833 | 2 | 1 | 1 | 20.2037 | 12.1072 | 8.0965
2 | 4 | 53.625 | 2 | 1 | 1 | 20.2037 | 11.9016 | 8.3021
2 | 5 | 50.5833 | 2 | 1 | 1 | 20.2037 | 12.3073 | 7.8964
2 | 6 | 49.8333 | 2 | 1 | 1 | 20.2037 | 12.4074 | 7.7963
2 | 7 | 53.5417 | 2 | 1 | 1 | 20.2037 | 11.9127 | 8.291
2 | 8 | 55.9583 | 2 | 1 | 1 | 20.2037 | 11.5903 | 8.6134
2 | 9 | 62.0833 | 2 | 1 | 1 | 20.2037 | 10.7733 | 9.4304
2 | 10 | 59.4167 | 2 | 1 | 1 | 20.2037 | 11.129 | 9.0747
2 | 11 | 57.8333 | 2 | 1 | 1 | 20.2037 | 11.3402 | 8.8635
2 | 12 | 60 | 2 | 1 | 1 | 20.2037 | 11.0512 | 9.1525
2 | 13 | 52.9583 | 2 | 1 | 1 | 20.2037 | 11.9905 | 8.2132
2 | 14 | 52.375 | 2 | 1 | 1 | 20.2037 | 12.0683 | 8.1354
2 | 15 | 53.375 | 2 | 1 | 1 | 20.2037 | 11.9349 | 8.2688
2 | 16 | 53.375 | 2 | 1 | 1 | 20.2037 | 11.9349 | 8.2688
2 | 17 | 53.125 | 2 | 1 | 1 | 20.2037 | 11.9683 | 8.2354
2 | 18 | 53.625 | 2 | 1 | 1 | 20.2037 | 11.9016 | 8.3021
2 | 19 | 54.75 | 2 | 1 | 1 | 20.2037 | 11.7515 | 8.4522
2 | 20 | 54.75 | 2 | 1 | 1 | 20.2037 | 11.7515 | 8.4522
2 | 21 | 54.5417 | 2 | 1 | 1 | 20.2037 | 11.7793 | 8.4244
2 | 22 | 53.2917 | 2 | 1 | 1 | 20.2037 | 11.9461 | 8.2576
2 | 23 | 52 | 2 | 1 | 1 | 20.2037 | 12.1184 | 8.0853
2 | 24 | 54.3333 | 2 | 1 | 1 | 20.2037 | 11.8071 | 8.3966
2 | 25 | 54.5833 | 2 | 1 | 1 | 20.2037 | 11.7738 | 8.4299
2 | 26 | 61.625 | 2 | 1 | 1 | 20.2037 | 10.8344 | 9.3693
2 | 27 | 63.5417 | 2 | 1 | 1 | 20.2037 | 10.5788 | 9.6249
2 | 28 | 57.5833 | 2 | 1 | 1 | 20.2037 | 11.3736 | 8.8301
3 | 1 | 58.4167 | 2 | 1 | 1 | 20.2037 | 11.2624 | 8.9413
3 | 2 | 59.1667 | 2 | 1 | 1 | 20.2037 | 11.1624 | 9.0413
3 | 3 | 59.9167 | 2 | 1 | 1 | 20.2037 | 11.0623 | 9.1414
3 | 4 | 62.625 | 2 | 1 | 1 | 20.2037 | 10.7011 | 9.5026
3 | 5 | 63.0417 | 2 | 1 | 1 | 20.2037 | 10.6455 | 9.5582
3 | 6 | 66.0833 | 2 | 1 | 1 | 20.2037 | 10.2397 | 9.964
3 | 7 | 66.5417 | 2 | 1 | 1 | 20.2037 | 10.1786 | 10.0251
3 | 8 | 69.5417 | 2 | 1 | 1 | 20.2037 | 9.7784 | 10.4253
3 | 9 | 71.5417 | 2 | 1 | 1 | 20.2037 | 9.5116 | 10.6921
3 | 10 | 66.5 | 2 | 1 | 1 | 20.2037 | 10.1842 | 10.0195
3 | 11 | 63.9583 | 2 | 1 | 1 | 20.2037 | 10.5232 | 9.6805
3 | 12 | 66.875 | 2 | 1 | 1 | 20.2037 | 10.1341 | 10.0696
3 | 13 | 63.5 | 2 | 1 | 1 | 20.2037 | 10.5843 | 9.6194
3 | 14 | 62.7917 | 2 | 1 | 1 | 20.2037 | 10.6788 | 9.5249
3 | 15 | 66.2083 | 2 | 1 | 1 | 20.2037 | 10.2231 | 9.9806
3 | 16 | 72.4583 | 2 | 1 | 1 | 20.2037 | 9.3894 | 10.8143
3 | 17 | 66.625 | 2 | 1 | 1 | 20.2037 | 10.1675 | 10.0362
3 | 18 | 63.9167 | 2 | 1 | 1 | 20.2037 | 10.5288 | 9.6749
3 | 19 | 63.75 | 2 | 1 | 1 | 20.2037 | 10.551 | 9.6527
3 | 20 | 62.2917 | 2 | 1 | 1 | 20.2037 | 10.7455 | 9.4582
3 | 21 | 62.75 | 2 | 1 | 1 | 20.2037 | 10.6844 | 9.5193
3 | 22 | 61.0833 | 2 | 1 | 1 | 20.2037 | 10.9067 | 9.297
3 | 23 | 61.8333 | 2 | 1 | 1 | 20.2037 | 10.8067 | 9.397
3 | 24 | 62.375 | 2 | 1 | 1 | 20.2037 | 10.7344 | 9.4693
3 | 25 | 62.2083 | 2 | 1 | 1 | 20.2037 | 10.7566 | 9.4471
3 | 26 | 62.375 | 2 | 1 | 1 | 20.2037 | 10.7344 | 9.4693
3 | 27 | 61.2083 | 2 | 1 | 1 | 20.2037 | 10.89 | 9.3137
3 | 28 | 61.9167 | 2 | 1 | 1 | 20.2037 | 10.7955 | 9.4082
3 | 29 | 63.125 | 2 | 1 | 1 | 20.2037 | 10.6344 | 9.5693
3 | 30 | 62.5417 | 2 | 1 | 1 | 20.2037 | 10.7122 | 9.4915
3 | 31 | 60 | 2 | 1 | 1 | 20.2037 | 11.0512 | 9.1525
4 | 1 | 68.2917 | 2 | 1 | 1 | 20.2037 | 9.9452 | 10.2585
4 | 2 | 61.4583 | 2 | 1 | 1 | 20.2037 | 10.8567 | 9.347
4 | 3 | 60.25 | 2 | 1 | 1 | 20.2037 | 11.0179 | 9.1858
4 | 4 | 61.25 | 2 | 1 | 1 | 20.2037 | 10.8845 | 9.3192
4 | 5 | 61.2917 | 2 | 1 | 1 | 20.2037 | 10.8789 | 9.3248
4 | 6 | 61.875 | 2 | 1 | 1 | 20.2037 | 10.8011 | 9.4026
4 | 7 | 57.7917 | 2 | 1 | 1 | 20.2037 | 11.3458 | 8.8579
4 | 8 | 52.7083 | 2 | 1 | 1 | 20.2037 | 12.0239 | 8.1798
4 | 9 | 53.25 | 2 | 1 | 1 | 20.2037 | 11.9516 | 8.2521
4 | 10 | 56.7083 | 2 | 1 | 1 | 20.2037 | 11.4903 | 8.7134
4 | 11 | 60.1667 | 2 | 1 | 1 | 20.2037 | 11.029 | 9.1747
4 | 12 | 59.0833 | 2 | 1 | 1 | 20.2037 | 11.1735 | 9.0302
4 | 13 | 57.9583 | 2 | 1 | 1 | 20.2037 | 11.3236 | 8.8801
4 | 14 | 62.5833 | 2 | 1 | 1 | 20.2037 | 10.7066 | 9.4971
4 | 15 | 70.125 | 2 | 1 | 1 | 20.2037 | 9.7006 | 10.5031
4 | 16 | 72.9167 | 2 | 1 | 1 | 20.2037 | 9.3282 | 10.8755
4 | 17 | 65.7083 | 2 | 1 | 1 | 20.2037 | 10.2898 | 9.9139
4 | 18 | 63.1667 | 2 | 1 | 1 | 20.2037 | 10.6288 | 9.5749
4 | 19 | 63.4583 | 2 | 1 | 1 | 20.2037 | 10.5899 | 9.6138
4 | 20 | 60.875 | 2 | 1 | 1 | 20.2037 | 10.9345 | 9.2692
4 | 21 | 62.1667 | 2 | 1 | 1 | 20.2037 | 10.7622 | 9.4415
4 | 22 | 61 | 2 | 1 | 1 | 20.2037 | 10.9178 | 9.2859
4 | 23 | 61.8333 | 2 | 1 | 1 | 20.2037 | 10.8067 | 9.397
4 | 24 | 59.9167 | 2 | 1 | 1 | 20.2037 | 11.0623 | 9.1414
4 | 25 | 63.2917 | 2 | 1 | 1 | 20.2037 | 10.6121 | 9.5916
4 | 26 | 65.4167 | 2 | 1 | 1 | 20.2037 | 10.3287 | 9.875
4 | 27 | 66.875 | 2 | 1 | 1 | 20.2037 | 10.1341 | 10.0696
4 | 28 | 67.2083 | 2 | 1 | 1 | 20.2037 | 10.0897 | 10.114
4 | 29 | 63.5417 | 2 | 1 | 1 | 20.2037 | 10.5788 | 9.6249
4 | 30 | 67.9583 | 2 | 1 | 1 | 20.2037 | 9.9896 | 10.2141
5 | 1 | 67.0417 | 2 | 1 | 1 | 20.2037 | 10.1119 | 10.0918
5 | 2 | 67.1667 | 2 | 1 | 1 | 20.2037 | 10.0952 | 10.1085
5 | 3 | 65.625 | 2 | 1 | 1 | 20.2037 | 10.3009 | 9.9028
5 | 4 | 62.875 | 2 | 1 | 1 | 20.2037 | 10.6677 | 9.536
5 | 5 | 61.7917 | 2 | 1 | 1 | 20.2037 | 10.8122 | 9.3915
5 | 6 | 58.5417 | 2 | 1 | 1 | 20.2037 | 11.2457 | 8.958
5 | 7 | 54.9167 | 2 | 1 | 1 | 20.2037 | 11.7293 | 8.4744
5 | 8 | 60.3333 | 2 | 1 | 1 | 20.2037 | 11.0067 | 9.197
5 | 9 | 61.6667 | 2 | 1 | 1 | 20.2037 | 10.8289 | 9.3748
5 | 10 | 63.25 | 2 | 1 | 1 | 20.2037 | 10.6177 | 9.586
5 | 11 | 62.625 | 2 | 1 | 1 | 20.2037 | 10.7011 | 9.5026
5 | 12 | 61.7917 | 2 | 1 | 1 | 20.2037 | 10.8122 | 9.3915
5 | 13 | 62.5 | 2 | 1 | 1 | 20.2037 | 10.7177 | 9.486
5 | 14 | 61.0417 | 2 | 1 | 1 | 20.2037 | 10.9123 | 9.2914
5 | 15 | 58.875 | 2 | 1 | 1 | 20.2037 | 11.2013 | 9.0024
5 | 16 | 59.625 | 2 | 1 | 1 | 20.2037 | 11.1012 | 9.1025
5 | 17 | 60.7083 | 2 | 1 | 1 | 20.2037 | 10.9567 | 9.247
5 | 18 | 64.375 | 2 | 1 | 1 | 20.2037 | 10.4676 | 9.7361
5 | 19 | 69.0833 | 2 | 1 | 1 | 20.2037 | 9.8396 | 10.3641
5 | 20 | 72.1667 | 2 | 1 | 1 | 20.2037 | 9.4283 | 10.7754
5 | 21 | 65.7917 | 2 | 1 | 1 | 20.2037 | 10.2786 | 9.9251
5 | 22 | 56.625 | 2 | 1 | 1 | 20.2037 | 11.5014 | 8.7023
5 | 23 | 63.1667 | 2 | 1 | 1 | 20.2037 | 10.6288 | 9.5749
5 | 24 | 61.8333 | 2 | 1 | 1 | 20.2037 | 10.8067 | 9.397
5 | 25 | 62.6667 | 2 | 1 | 1 | 20.2037 | 10.6955 | 9.5082
5 | 26 | 63.9583 | 2 | 1 | 1 | 20.2037 | 10.5232 | 9.6805
5 | 27 | 62.6667 | 2 | 1 | 1 | 20.2037 | 10.6955 | 9.5082
5 | 28 | 64.1667 | 2 | 1 | 1 | 20.2037 | 10.4954 | 9.7083
5 | 29 | 63.2083 | 2 | 1 | 1 | 20.2037 | 10.6232 | 9.5805
5 | 30 | 62.5417 | 2 | 1 | 1 | 20.2037 | 10.7122 | 9.4915
5 | 31 | 62.125 | 2 | 1 | 1 | 20.2037 | 10.7678 | 9.4359
6 | 1 | 70 | 2 | 1 | 1 | 20.2037 | 9.7173 | 10.4864
6 | 2 | 68.0417 | 2 | 1 | 1 | 20.2037 | 9.9785 | 10.2252
6 | 3 | 69.0417 | 2 | 1 | 1 | 20.2037 | 9.8451 | 10.3586
6 | 4 | 68.0833 | 2 | 1 | 1 | 20.2037 | 9.973 | 10.2307
6 | 5 | 65.7917 | 2 | 1 | 1 | 20.2037 | 10.2786 | 9.9251
6 | 6 | 64.7083 | 2 | 1 | 1 | 20.2037 | 10.4232 | 9.7805
6 | 7 | 65.9583 | 2 | 1 | 1 | 20.2037 | 10.2564 | 9.9473
6 | 8 | 66.625 | 2 | 1 | 1 | 20.2037 | 10.1675 | 10.0362
6 | 9 | 66.9583 | 2 | 1 | 1 | 20.2037 | 10.123 | 10.0807
6 | 10 | 68.5 | 2 | 1 | 1 | 20.2037 | 9.9174 | 10.2863
6 | 11 | 69.2917 | 2 | 1 | 1 | 20.2037 | 9.8118 | 10.3919
6 | 12 | 66.625 | 2 | 1 | 1 | 20.2037 | 10.1675 | 10.0362
6 | 13 | 67.625 | 2 | 1 | 1 | 20.2037 | 10.0341 | 10.1696
6 | 14 | 68.125 | 2 | 1 | 1 | 20.2037 | 9.9674 | 10.2363
6 | 15 | 67.2917 | 2 | 1 | 1 | 20.2037 | 10.0786 | 10.1251
6 | 16 | 67.875 | 2 | 1 | 1 | 20.2037 | 10.0007 | 10.203
6 | 17 | 69.7083 | 2 | 1 | 1 | 20.2037 | 9.7562 | 10.4475
6 | 18 | 70.75 | 2 | 1 | 1 | 20.2037 | 9.6172 | 10.5865
6 | 19 | 71.7083 | 2 | 1 | 1 | 20.2037 | 9.4894 | 10.7143
6 | 20 | 73.125 | 2 | 1 | 1 | 20.2037 | 9.3004 | 10.9033
6 | 21 | 71.4167 | 2 | 1 | 1 | 20.2037 | 9.5283 | 10.6754
6 | 22 | 70.0833 | 2 | 1 | 1 | 20.2037 | 9.7062 | 10.4975
6 | 23 | 67.9583 | 2 | 1 | 1 | 20.2037 | 9.9896 | 10.2141
6 | 24 | 69.7917 | 2 | 1 | 1 | 20.2037 | 9.7451 | 10.4586
6 | 25 | 68.875 | 2 | 1 | 1 | 20.2037 | 9.8673 | 10.3364
6 | 26 | 71.6667 | 2 | 1 | 1 | 20.2037 | 9.495 | 10.7087
6 | 27 | 72.375 | 2 | 1 | 1 | 20.2037 | 9.4005 | 10.8032
6 | 28 | 72.0833 | 2 | 1 | 1 | 20.2037 | 9.4394 | 10.7643
6 | 29 | 72.375 | 2 | 1 | 1 | 20.2037 | 9.4005 | 10.8032
6 | 30 | 76.1667 | 2 | 1 | 1 | 20.2037 | 8.8947 | 11.309
7 | 1 | 74.2083 | 2 | 1 | 1 | 20.2037 | 9.1559 | 11.0478
7 | 2 | 70.0417 | 2 | 1 | 1 | 20.2037 | 9.7117 | 10.492
7 | 3 | 69.25 | 2 | 1 | 1 | 20.2037 | 9.8173 | 10.3864
7 | 4 | 70.5417 | 2 | 1 | 1 | 20.2037 | 9.645 | 10.5587
7 | 5 | 73.5 | 2 | 1 | 1 | 20.2037 | 9.2504 | 10.9533
7 | 6 | 75.7917 | 2 | 1 | 1 | 20.2037 | 8.9447 | 11.259
7 | 7 | 74.125 | 2 | 1 | 1 | 20.2037 | 9.167 | 11.0367
7 | 8 | 72.25 | 2 | 1 | 1 | 20.2037 | 9.4171 | 10.7866
7 | 9 | 69.6667 | 2 | 1 | 1 | 20.2037 | 9.7617 | 10.442
7 | 10 | 70.0833 | 2 | 1 | 1 | 20.2037 | 9.7062 | 10.4975
7 | 11 | 70.0417 | 2 | 1 | 1 | 20.2037 | 9.7117 | 10.492
7 | 12 | 69.25 | 2 | 1 | 1 | 20.2037 | 9.8173 | 10.3864
7 | 13 | 69.25 | 2 | 1 | 1 | 20.2037 | 9.8173 | 10.3864
7 | 14 | 66.875 | 2 | 1 | 1 | 20.2037 | 10.1341 | 10.0696
7 | 15 | 67.625 | 2 | 1 | 1 | 20.2037 | 10.0341 | 10.1696
7 | 16 | 68.25 | 2 | 1 | 1 | 20.2037 | 9.9507 | 10.253
7 | 17 | 69.2917 | 2 | 1 | 1 | 20.2037 | 9.8118 | 10.3919
7 | 18 | 71.9583 | 2 | 1 | 1 | 20.2037 | 9.4561 | 10.7476
7 | 19 | 71.5417 | 2 | 1 | 1 | 20.2037 | 9.5116 | 10.6921
7 | 20 | 68.5 | 2 | 1 | 1 | 20.2037 | 9.9174 | 10.2863
7 | 21 | 67.4167 | 2 | 1 | 1 | 20.2037 | 10.0619 | 10.1418
7 | 22 | 68.1667 | 2 | 1 | 1 | 20.2037 | 9.9618 | 10.2419
7 | 23 | 68.5417 | 2 | 1 | 1 | 20.2037 | 9.9118 | 10.2919
7 | 24 | 67.4167 | 2 | 1 | 1 | 20.2037 | 10.0619 | 10.1418
7 | 25 | 71.5417 | 2 | 1 | 1 | 20.2037 | 9.5116 | 10.6921
7 | 26 | 72.3333 | 2 | 1 | 1 | 20.2037 | 9.406 | 10.7977
7 | 27 | 71 | 2 | 1 | 1 | 20.2037 | 9.5839 | 10.6198
7 | 28 | 71.6667 | 2 | 1 | 1 | 20.2037 | 9.495 | 10.7087
7 | 29 | 68.9583 | 2 | 1 | 1 | 20.2037 | 9.8562 | 10.3475
7 | 30 | 67.5 | 2 | 1 | 1 | 20.2037 | 10.0508 | 10.1529
7 | 31 | 69.7917 | 2 | 1 | 1 | 20.2037 | 9.7451 | 10.4586
8 | 1 | 69.9167 | 2 | 1 | 1 | 20.2037 | 9.7284 | 10.4753
8 | 2 | 71.125 | 2 | 1 | 1 | 20.2037 | 9.5672 | 10.6365
8 | 3 | 71.3333 | 2 | 1 | 1 | 20.2037 | 9.5394 | 10.6643
8 | 4 | 71.125 | 2 | 1 | 1 | 20.2037 | 9.5672 | 10.6365
8 | 5 | 72.125 | 2 | 1 | 1 | 20.2037 | 9.4338 | 10.7699
8 | 6 | 72.8333 | 2 | 1 | 1 | 20.2037 | 9.3393 | 10.8644
8 | 7 | 73.3333 | 2 | 1 | 1 | 20.2037 | 9.2726 | 10.9311
8 | 8 | 72.3333 | 2 | 1 | 1 | 20.2037 | 9.406 | 10.7977
8 | 9 | 71.125 | 2 | 1 | 1 | 20.2037 | 9.5672 | 10.6365
8 | 10 | 70.4167 | 2 | 1 | 1 | 20.2037 | 9.6617 | 10.542
8 | 11 | 69.75 | 2 | 1 | 1 | 20.2037 | 9.7506 | 10.4531
8 | 12 | 69.4167 | 2 | 1 | 1 | 20.2037 | 9.7951 | 10.4086
8 | 13 | 70.75 | 2 | 1 | 1 | 20.2037 | 9.6172 | 10.5865
8 | 14 | 71.9583 | 2 | 1 | 1 | 20.2037 | 9.4561 | 10.7476
8 | 15 | 71.125 | 2 | 1 | 1 | 20.2037 | 9.5672 | 10.6365
8 | 16 | 71.4583 | 2 | 1 | 1 | 20.2037 | 9.5227 | 10.681
8 | 17 | 70.8333 | 2 | 1 | 1 | 20.2037 | 9.6061 | 10.5976
8 | 18 | 69.5 | 2 | 1 | 1 | 20.2037 | 9.784 | 10.4197
8 | 19 | 68.6667 | 2 | 1 | 1 | 20.2037 | 9.8951 | 10.3086
8 | 20 | 68.8333 | 2 | 1 | 1 | 20.2037 | 9.8729 | 10.3308
8 | 21 | 71.0833 | 2 | 1 | 1 | 20.2037 | 9.5728 | 10.6309
8 | 22 | 71.5833 | 2 | 1 | 1 | 20.2037 | 9.5061 | 10.6976
8 | 23 | 69.4583 | 2 | 1 | 1 | 20.2037 | 9.7895 | 10.4142
8 | 24 | 68.9583 | 2 | 1 | 1 | 20.2037 | 9.8562 | 10.3475
8 | 25 | 71.875 | 2 | 1 | 1 | 20.2037 | 9.4672 | 10.7365
8 | 26 | 71.9167 | 2 | 1 | 1 | 20.2037 | 9.4616 | 10.7421
8 | 27 | 70.9583 | 2 | 1 | 1 | 20.2037 | 9.5894 | 10.6143
8 | 28 | 68.25 | 2 | 1 | 1 | 20.2037 | 9.9507 | 10.253
8 | 29 | 70.4583 | 2 | 1 | 1 | 20.2037 | 9.6561 | 10.5476
8 | 30 | 71.2917 | 2 | 1 | 1 | 20.2037 | 9.545 | 10.6587
8 | 31 | 70.375 | 2 | 1 | 1 | 20.2037 | 9.6673 | 10.5364
9 | 1 | 71.7083 | 2 | 1 | 1 | 20.2037 | 9.4894 | 10.7143
9 | 2 | 75.75 | 2 | 1 | 1 | 20.2037 | 8.9503 | 11.2534
9 | 3 | 76.5 | 2 | 1 | 1 | 20.2037 | 8.8502 | 11.3535
9 | 4 | 76 | 2 | 1 | 1 | 20.2037 | 8.9169 | 11.2868
9 | 5 | 74.4167 | 2 | 1 | 1 | 20.2037 | 9.1281 | 11.0756
9 | 6 | 73.2083 | 2 | 1 | 1 | 20.2037 | 9.2893 | 10.9144
9 | 7 | 71.3333 | 2 | 1 | 1 | 20.2037 | 9.5394 | 10.6643
9 | 8 | 69.1667 | 2 | 1 | 1 | 20.2037 | 9.8284 | 10.3753
9 | 9 | 68.8333 | 2 | 1 | 1 | 20.2037 | 9.8729 | 10.3308
9 | 10 | 68.6667 | 2 | 1 | 1 | 20.2037 | 9.8951 | 10.3086
9 | 11 | 68.2083 | 2 | 1 | 1 | 20.2037 | 9.9563 | 10.2474
9 | 12 | 67.7917 | 2 | 1 | 1 | 20.2037 | 10.0119 | 10.1918
9 | 13 | 69.375 | 2 | 1 | 1 | 20.2037 | 9.8007 | 10.403
9 | 14 | 67.2083 | 2 | 1 | 1 | 20.2037 | 10.0897 | 10.114
9 | 15 | 66.75 | 2 | 1 | 1 | 20.2037 | 10.1508 | 10.0529
9 | 16 | 66.8333 | 2 | 1 | 1 | 20.2037 | 10.1397 | 10.064
9 | 17 | 71.625 | 2 | 1 | 1 | 20.2037 | 9.5005 | 10.7032
9 | 18 | 73.125 | 2 | 1 | 1 | 20.2037 | 9.3004 | 10.9033
9 | 19 | 69.0417 | 2 | 1 | 1 | 20.2037 | 9.8451 | 10.3586
9 | 20 | 67.0833 | 2 | 1 | 1 | 20.2037 | 10.1063 | 10.0974
9 | 21 | 66.0833 | 2 | 1 | 1 | 20.2037 | 10.2397 | 9.964
9 | 22 | 67.625 | 2 | 1 | 1 | 20.2037 | 10.0341 | 10.1696
9 | 23 | 69.5 | 2 | 1 | 1 | 20.2037 | 9.784 | 10.4197
9 | 24 | 67.6667 | 2 | 1 | 1 | 20.2037 | 10.0285 | 10.1752
9 | 25 | 68.25 | 2 | 1 | 1 | 20.2037 | 9.9507 | 10.253
9 | 26 | 66.5417 | 2 | 1 | 1 | 20.2037 | 10.1786 | 10.0251
9 | 27 | 65.9167 | 2 | 1 | 1 | 20.2037 | 10.262 | 9.9417
9 | 28 | 66.7917 | 2 | 1 | 1 | 20.2037 | 10.1453 | 10.0584
9 | 29 | 67 | 2 | 1 | 1 | 20.2037 | 10.1175 | 10.0862
9 | 30 | 66.7083 | 2 | 1 | 1 | 20.2037 | 10.1564 | 10.0473
10 | 1 | 77.5417 | 2 | 1 | 1 | 20.2037 | 8.7113 | 11.4924
10 | 2 | 78 | 2 | 1 | 1 | 20.2037 | 8.6501 | 11.5536
10 | 3 | 70.0417 | 2 | 1 | 1 | 20.2037 | 9.7117 | 10.492
10 | 4 | 67.9167 | 2 | 1 | 1 | 20.2037 | 9.9952 | 10.2085
10 | 5 | 69.625 | 2 | 1 | 1 | 20.2037 | 9.7673 | 10.4364
10 | 6 | 71.2917 | 2 | 1 | 1 | 20.2037 | 9.545 | 10.6587
10 | 7 | 68.8333 | 2 | 1 | 1 | 20.2037 | 9.8729 | 10.3308
10 | 8 | 69.0417 | 2 | 1 | 1 | 20.2037 | 9.8451 | 10.3586
10 | 9 | 67.25 | 2 | 1 | 1 | 20.2037 | 10.0841 | 10.1196
10 | 10 | 65.75 | 2 | 1 | 1 | 20.2037 | 10.2842 | 9.9195
10 | 11 | 63.5833 | 2 | 1 | 1 | 20.2037 | 10.5732 | 9.6305
10 | 12 | 63.5833 | 2 | 1 | 1 | 20.2037 | 10.5732 | 9.6305
10 | 13 | 65.9583 | 2 | 1 | 1 | 20.2037 | 10.2564 | 9.9473
10 | 14 | 73.75 | 2 | 1 | 1 | 20.2037 | 9.2171 | 10.9866
10 | 15 | 74.5 | 2 | 1 | 1 | 20.2037 | 9.117 | 11.0867
10 | 16 | 73.125 | 2 | 1 | 1 | 20.2037 | 9.3004 | 10.9033
10 | 17 | 75.9167 | 2 | 1 | 1 | 20.2037 | 8.928 | 11.2757
10 | 18 | 74.5417 | 2 | 1 | 1 | 20.2037 | 9.1115 | 11.0922
10 | 19 | 68.0833 | 2 | 1 | 1 | 20.2037 | 9.973 | 10.2307
10 | 20 | 68.0833 | 2 | 1 | 1 | 20.2037 | 9.973 | 10.2307
10 | 21 | 66.2917 | 2 | 1 | 1 | 20.2037 | 10.2119 | 9.9918
10 | 22 | 65.7083 | 2 | 1 | 1 | 20.2037 | 10.2898 | 9.9139
10 | 23 | 64.125 | 2 | 1 | 1 | 20.2037 | 10.501 | 9.7027
10 | 24 | 64.8333 | 2 | 1 | 1 | 20.2037 | 10.4065 | 9.7972
10 | 25 | 69.0417 | 2 | 1 | 1 | 20.2037 | 9.8451 | 10.3586
10 | 26 | 73.25 | 2 | 1 | 1 | 20.2037 | 9.2838 | 10.9199
10 | 27 | 71.5 | 2 | 1 | 1 | 20.2037 | 9.5172 | 10.6865
10 | 28 | 68.2083 | 2 | 1 | 1 | 20.2037 | 9.9563 | 10.2474
10 | 29 | 63.1667 | 2 | 1 | 1 | 20.2037 | 10.6288 | 9.5749
10 | 30 | 60.2917 | 2 | 1 | 1 | 20.2037 | 11.0123 | 9.1914
10 | 31 | 62.5 | 2 | 1 | 1 | 20.2037 | 10.7177 | 9.486
11 | 1 | 72.0833 | 2 | 1 | 1 | 20.2037 | 9.4394 | 10.7643
11 | 2 | 63.375 | 2 | 1 | 1 | 20.2037 | 10.601 | 9.6027
11 | 3 | 61.25 | 2 | 1 | 1 | 20.2037 | 10.8845 | 9.3192
11 | 4 | 57.5833 | 2 | 1 | 1 | 20.2037 | 11.3736 | 8.8301
11 | 5 | 60.4167 | 2 | 1 | 1 | 20.2037 | 10.9956 | 9.2081
11 | 6 | 61.875 | 2 | 1 | 1 | 20.2037 | 10.8011 | 9.4026
11 | 7 | 63.4583 | 2 | 1 | 1 | 20.2037 | 10.5899 | 9.6138
11 | 8 | 61.7083 | 2 | 1 | 1 | 20.2037 | 10.8233 | 9.3804
11 | 9 | 62.2917 | 2 | 1 | 1 | 20.2037 | 10.7455 | 9.4582
11 | 10 | 62.1667 | 2 | 1 | 1 | 20.2037 | 10.7622 | 9.4415
11 | 11 | 59.625 | 2 | 1 | 1 | 20.2037 | 11.1012 | 9.1025
11 | 12 | 59.0833 | 2 | 1 | 1 | 20.2037 | 11.1735 | 9.0302
11 | 13 | 59.7917 | 2 | 1 | 1 | 20.2037 | 11.079 | 9.1247
11 | 14 | 60.1667 | 2 | 1 | 1 | 20.2037 | 11.029 | 9.1747
11 | 15 | 68.8333 | 2 | 1 | 1 | 20.2037 | 9.8729 | 10.3308
11 | 16 | 66.75 | 2 | 1 | 1 | 20.2037 | 10.1508 | 10.0529
11 | 17 | 63.75 | 2 | 1 | 1 | 20.2037 | 10.551 | 9.6527
11 | 18 | 68.4583 | 2 | 1 | 1 | 20.2037 | 9.9229 | 10.2808
11 | 19 | 65.3333 | 2 | 1 | 1 | 20.2037 | 10.3398 | 9.8639
11 | 20 | 68.875 | 2 | 1 | 1 | 20.2037 | 9.8673 | 10.3364
11 | 21 | 68.4583 | 2 | 1 | 1 | 20.2037 | 9.9229 | 10.2808
11 | 22 | 66.625 | 2 | 1 | 1 | 20.2037 | 10.1675 | 10.0362
11 | 23 | 62.4583 | 2 | 1 | 1 | 20.2037 | 10.7233 | 9.4804
11 | 24 | 60.875 | 2 | 1 | 1 | 20.2037 | 10.9345 | 9.2692
11 | 25 | 62.0417 | 2 | 1 | 1 | 20.2037 | 10.7789 | 9.4248
11 | 26 | 61.5 | 2 | 1 | 1 | 20.2037 | 10.8511 | 9.3526
11 | 27 | 58.25 | 2 | 1 | 1 | 20.2037 | 11.2847 | 8.919
11 | 28 | 57.3333 | 2 | 1 | 1 | 20.2037 | 11.4069 | 8.7968
11 | 29 | 57.625 | 2 | 1 | 1 | 20.2037 | 11.368 | 8.8357
11 | 30 | 60.6667 | 2 | 1 | 1 | 20.2037 | 10.9623 | 9.2414
12 | 1 | 50.25 | 2 | 1 | 1 | 20.2037 | 12.3518 | 7.8519
12 | 2 | 50.2917 | 2 | 1 | 1 | 20.2037 | 12.3462 | 7.8575
12 | 3 | 51.9167 | 2 | 1 | 1 | 20.2037 | 12.1295 | 8.0742
12 | 4 | 50.375 | 2 | 1 | 1 | 20.2037 | 12.3351 | 7.8686
12 | 5 | 49.375 | 2 | 1 | 1 | 20.2037 | 12.4685 | 7.7352
12 | 6 | 49.7917 | 2 | 1 | 1 | 20.2037 | 12.4129 | 7.7908
12 | 7 | 51.4583 | 2 | 1 | 1 | 20.2037 | 12.1906 | 8.0131
12 | 8 | 55.25 | 2 | 1 | 1 | 20.2037 | 11.6848 | 8.5189
12 | 9 | 55.9167 | 2 | 1 | 1 | 20.2037 | 11.5959 | 8.6078
12 | 10 | 62.5833 | 2 | 1 | 1 | 20.2037 | 10.7066 | 9.4971
12 | 11 | 65.875 | 2 | 1 | 1 | 20.2037 | 10.2675 | 9.9362
12 | 12 | 56.9167 | 2 | 1 | 1 | 20.2037 | 11.4625 | 8.7412
12 | 13 | 57.0417 | 2 | 1 | 1 | 20.2037 | 11.4458 | 8.7579
12 | 14 | 60.75 | 2 | 1 | 1 | 20.2037 | 10.9512 | 9.2525
12 | 15 | 59.5833 | 2 | 1 | 1 | 20.2037 | 11.1068 | 9.0969
12 | 16 | 62.75 | 2 | 1 | 1 | 20.2037 | 10.6844 | 9.5193
12 | 17 | 60.875 | 2 | 1 | 1 | 20.2037 | 10.9345 | 9.2692
12 | 18 | 60.7083 | 2 | 1 | 1 | 20.2037 | 10.9567 | 9.247
12 | 19 | 64.375 | 2 | 1 | 1 | 20.2037 | 10.4676 | 9.7361
12 | 20 | 57.875 | 2 | 1 | 1 | 20.2037 | 11.3347 | 8.869
12 | 21 | 56.2917 | 2 | 1 | 1 | 20.2037 | 11.5459 | 8.6578
12 | 22 | 54.25 | 2 | 1 | 1 | 20.2037 | 11.8182 | 8.3855
12 | 23 | 53.7917 | 2 | 1 | 1 | 20.2037 | 11.8794 | 8.3243
12 | 24 | 53.625 | 2 | 1 | 1 | 20.2037 | 11.9016 | 8.3021
12 | 25 | 52.9167 | 2 | 1 | 1 | 20.2037 | 11.9961 | 8.2076
12 | 26 | 53.875 | 2 | 1 | 1 | 20.2037 | 11.8682 | 8.3355
12 | 27 | 57.875 | 2 | 1 | 1 | 20.2037 | 11.3347 | 8.869
12 | 28 | 57.125 | 2 | 1 | 1 | 20.2037 | 11.4347 | 8.769
12 | 29 | 55.7917 | 2 | 1 | 1 | 20.2037 | 11.6126 | 8.5911
12 | 30 | 53.2083 | 2 | 1 | 1 | 20.2037 | 11.9572 | 8.2465
12 | 31 | 53.2083 | 2 | 1 | 1 | 20.2037 | 11.9572 | 8.2465
1 | 1 | 51.7083 | 3 | 2 | 2 | 40.4074 | 25.0785 | 15.3289
1 | 2 | 55.1667 | 3 | 2 | 2 | 40.4074 | 23.8374 | 16.57
1 | 3 | 51.4583 | 3 | 2 | 2 | 40.4074 | 25.1682 | 15.2392
1 | 4 | 50.0833 | 3 | 2 | 2 | 40.4074 | 25.6616 | 14.7458
1 | 5 | 53.9583 | 3 | 2 | 2 | 40.4074 | 24.271 | 16.1364
1 | 6 | 54.8333 | 3 | 2 | 2 | 40.4074 | 23.957 | 16.4504
1 | 7 | 54.4583 | 3 | 2 | 2 | 40.4074 | 24.0916 | 16.3158
1 | 8 | 53.7083 | 3 | 2 | 2 | 40.4074 | 24.3607 | 16.0467
1 | 9 | 56.75 | 3 | 2 | 2 | 40.4074 | 23.2692 | 17.1382
1 | 10 | 59 | 3 | 2 | 2 | 40.4074 | 22.4618 | 17.9456
1 | 11 | 57.875 | 3 | 2 | 2 | 40.4074 | 22.8655 | 17.5419
1 | 12 | 55.875 | 3 | 2 | 2 | 40.4074 | 23.5832 | 16.8242
1 | 13 | 59.2917 | 3 | 2 | 2 | 40.4074 | 22.3571 | 18.0503
1 | 14 | 64.7917 | 3 | 2 | 2 | 40.4074 | 20.3834 | 20.024
1 | 15 | 57.9167 | 3 | 2 | 2 | 40.4074 | 22.8505 | 17.5569
1 | 16 | 56.7083 | 3 | 2 | 2 | 40.4074 | 23.2842 | 17.1232
1 | 17 | 55.6667 | 3 | 2 | 2 | 40.4074 | 23.658 | 16.7494
1 | 18 | 55.4583 | 3 | 2 | 2 | 40.4074 | 23.7327 | 16.6747
1 | 19 | 55 | 3 | 2 | 2 | 40.4074 | 23.8972 | 16.5102
1 | 20 | 53.9167 | 3 | 2 | 2 | 40.4074 | 24.286 | 16.1214
1 | 21 | 56.5833 | 3 | 2 | 2 | 40.4074 | 23.329 | 17.0784
1 | 22 | 61.75 | 3 | 2 | 2 | 40.4074 | 21.4749 | 18.9325
1 | 23 | 56.0417 | 3 | 2 | 2 | 40.4074 | 23.5234 | 16.884
1 | 24 | 52.7917 | 3 | 2 | 2 | 40.4074 | 24.6897 | 15.7177
1 | 25 | 54.5 | 3 | 2 | 2 | 40.4074 | 24.0766 | 16.3308
1 | 26 | 53.25 | 3 | 2 | 2 | 40.4074 | 24.5252 | 15.8822
1 | 27 | 54.25 | 3 | 2 | 2 | 40.4074 | 24.1664 | 16.241
1 | 28 | 56.3333 | 3 | 2 | 2 | 40.4074 | 23.4187 | 16.9887
1 | 29 | 55.375 | 3 | 2 | 2 | 40.4074 | 23.7626 | 16.6448
1 | 30 | 53.1667 | 3 | 2 | 2 | 40.4074 | 24.5551 | 15.8523
1 | 31 | 55.875 | 3 | 2 | 2 | 40.4074 | 23.5832 | 16.8242
2 | 1 | 51.4583 | 3 | 2 | 2 | 40.4074 | 25.1682 | 15.2392
2 | 2 | 51.2917 | 3 | 2 | 2 | 40.4074 | 25.228 | 15.1794
2 | 3 | 52.0833 | 3 | 2 | 2 | 40.4074 | 24.9439 | 15.4635
2 | 4 | 53.625 | 3 | 2 | 2 | 40.4074 | 24.3906 | 16.0168
2 | 5 | 50.5833 | 3 | 2 | 2 | 40.4074 | 25.4822 | 14.9252
2 | 6 | 49.8333 | 3 | 2 | 2 | 40.4074 | 25.7513 | 14.6561
2 | 7 | 53.5417 | 3 | 2 | 2 | 40.4074 | 24.4206 | 15.9868
2 | 8 | 55.9583 | 3 | 2 | 2 | 40.4074 | 23.5533 | 16.8541
2 | 9 | 62.0833 | 3 | 2 | 2 | 40.4074 | 21.3553 | 19.0521
2 | 10 | 59.4167 | 3 | 2 | 2 | 40.4074 | 22.3123 | 18.0951
2 | 11 | 57.8333 | 3 | 2 | 2 | 40.4074 | 22.8805 | 17.5269
2 | 12 | 60 | 3 | 2 | 2 | 40.4074 | 22.1029 | 18.3045
2 | 13 | 52.9583 | 3 | 2 | 2 | 40.4074 | 24.6299 | 15.7775
2 | 14 | 52.375 | 3 | 2 | 2 | 40.4074 | 24.8392 | 15.5682
2 | 15 | 53.375 | 3 | 2 | 2 | 40.4074 | 24.4804 | 15.927
2 | 16 | 53.375 | 3 | 2 | 2 | 40.4074 | 24.4804 | 15.927
2 | 17 | 53.125 | 3 | 2 | 2 | 40.4074 | 24.5701 | 15.8373
2 | 18 | 53.625 | 3 | 2 | 2 | 40.4074 | 24.3906 | 16.0168
2 | 19 | 54.75 | 3 | 2 | 2 | 40.4074 | 23.9869 | 16.4205
2 | 20 | 54.75 | 3 | 2 | 2 | 40.4074 | 23.9869 | 16.4205
2 | 21 | 54.5417 | 3 | 2 | 2 | 40.4074 | 24.0617 | 16.3457
2 | 22 | 53.2917 | 3 | 2 | 2 | 40.4074 | 24.5103 | 15.8971
2 | 23 | 52 | 3 | 2 | 2 | 40.4074 | 24.9738 | 15.4336
2 | 24 | 54.3333 | 3 | 2 | 2 | 40.4074 | 24.1365 | 16.2709
2 | 25 | 54.5833 | 3 | 2 | 2 | 40.4074 | 24.0467 | 16.3607
2 | 26 | 61.625 | 3 | 2 | 2 | 40.4074 | 21.5198 | 18.8876
2 | 27 | 63.5417 | 3 | 2 | 2 | 40.4074 | 20.832 | 19.5754
2 | 28 | 57.5833 | 3 | 2 | 2 | 40.4074 | 22.9702 | 17.4372
3 | 1 | 58.4167 | 3 | 2 | 2 | 40.4074 | 22.6711 | 17.7363
3 | 2 | 59.1667 | 3 | 2 | 2 | 40.4074 | 22.402 | 18.0054
3 | 3 | 59.9167 | 3 | 2 | 2 | 40.4074 | 22.1328 | 18.2746
3 | 4 | 62.625 | 3 | 2 | 2 | 40.4074 | 21.1609 | 19.2465
3 | 5 | 63.0417 | 3 | 2 | 2 | 40.4074 | 21.0114 | 19.396
3 | 6 | 66.0833 | 3 | 2 | 2 | 40.4074 | 19.9199 | 20.4875
3 | 7 | 66.5417 | 3 | 2 | 2 | 40.4074 | 19.7554 | 20.652
3 | 8 | 69.5417 | 3 | 2 | 2 | 40.4074 | 18.6788 | 21.7286
3 | 9 | 71.5417 | 3 | 2 | 2 | 40.4074 | 17.9611 | 22.4463
3 | 10 | 66.5 | 3 | 2 | 2 | 40.4074 | 19.7704 | 20.637
3 | 11 | 63.9583 | 3 | 2 | 2 | 40.4074 | 20.6824 | 19.725
3 | 12 | 66.875 | 3 | 2 | 2 | 40.4074 | 19.6358 | 20.7716
3 | 13 | 63.5 | 3 | 2 | 2 | 40.4074 | 20.8469 | 19.5605
3 | 14 | 62.7917 | 3 | 2 | 2 | 40.4074 | 21.1011 | 19.3063
3 | 15 | 66.2083 | 3 | 2 | 2 | 40.4074 | 19.875 | 20.5324
3 | 16 | 72.4583 | 3 | 2 | 2 | 40.4074 | 17.6322 | 22.7752
3 | 17 | 66.625 | 3 | 2 | 2 | 40.4074 | 19.7255 | 20.6819
3 | 18 | 63.9167 | 3 | 2 | 2 | 40.4074 | 20.6974 | 19.71
3 | 19 | 63.75 | 3 | 2 | 2 | 40.4074 | 20.7572 | 19.6502
3 | 20 | 62.2917 | 3 | 2 | 2 | 40.4074 | 21.2805 | 19.1269
3 | 21 | 62.75 | 3 | 2 | 2 | 40.4074 | 21.1161 | 19.2913
3 | 22 | 61.0833 | 3 | 2 | 2 | 40.4074 | 21.7142 | 18.6932
3 | 23 | 61.8333 | 3 | 2 | 2 | 40.4074 | 21.445 | 18.9624
3 | 24 | 62.375 | 3 | 2 | 2 | 40.4074 | 21.2506 | 19.1568
3 | 25 | 62.2083 | 3 | 2 | 2 | 40.4074 | 21.3105 | 19.0969
3 | 26 | 62.375 | 3 | 2 | 2 | 40.4074 | 21.2506 | 19.1568
3 | 27 | 61.2083 | 3 | 2 | 2 | 40.4074 | 21.6693 | 18.7381
3 | 28 | 61.9167 | 3 | 2 | 2 | 40.4074 | 21.4151 | 18.9923
3 | 29 | 63.125 | 3 | 2 | 2 | 40.4074 | 20.9815 | 19.4259
3 | 30 | 62.5417 | 3 | 2 | 2 | 40.4074 | 21.1908 | 19.2166
3 | 31 | 60 | 3 | 2 | 2 | 40.4074 | 22.1029 | 18.3045
4 | 1 | 68.2917 | 3 | 2 | 2 | 40.4074 | 19.1274 | 21.28
4 | 2 | 61.4583 | 3 | 2 | 2 | 40.4074 | 21.5796 | 18.8278
4 | 3 | 60.25 | 3 | 2 | 2 | 40.4074 | 22.0132 | 18.3942
4 | 4 | 61.25 | 3 | 2 | 2 | 40.4074 | 21.6544 | 18.753
4 | 5 | 61.2917 | 3 | 2 | 2 | 40.4074 | 21.6394 | 18.768
4 | 6 | 61.875 | 3 | 2 | 2 | 40.4074 | 21.4301 | 18.9773
4 | 7 | 57.7917 | 3 | 2 | 2 | 40.4074 | 22.8954 | 17.512
4 | 8 | 52.7083 | 3 | 2 | 2 | 40.4074 | 24.7196 | 15.6878
4 | 9 | 53.25 | 3 | 2 | 2 | 40.4074 | 24.5252 | 15.8822
4 | 10 | 56.7083 | 3 | 2 | 2 | 40.4074 | 23.2842 | 17.1232
4 | 11 | 60.1667 | 3 | 2 | 2 | 40.4074 | 22.0431 | 18.3643
4 | 12 | 59.0833 | 3 | 2 | 2 | 40.4074 | 22.4319 | 17.9755
4 | 13 | 57.9583 | 3 | 2 | 2 | 40.4074 | 22.8356 | 17.5718
4 | 14 | 62.5833 | 3 | 2 | 2 | 40.4074 | 21.1759 | 19.2315
4 | 15 | 70.125 | 3 | 2 | 2 | 40.4074 | 18.4695 | 21.9379
4 | 16 | 72.9167 | 3 | 2 | 2 | 40.4074 | 17.4677 | 22.9397
4 | 17 | 65.7083 | 3 | 2 | 2 | 40.4074 | 20.0544 | 20.353
4 | 18 | 63.1667 | 3 | 2 | 2 | 40.4074 | 20.9665 | 19.4409
4 | 19 | 63.4583 | 3 | 2 | 2 | 40.4074 | 20.8619 | 19.5455
4 | 20 | 60.875 | 3 | 2 | 2 | 40.4074 | 21.7889 | 18.6185
4 | 21 | 62.1667 | 3 | 2 | 2 | 40.4074 | 21.3254 | 19.082
4 | 22 | 61 | 3 | 2 | 2 | 40.4074 | 21.7441 | 18.6633
4 | 23 | 61.8333 | 3 | 2 | 2 | 40.4074 | 21.445 | 18.9624
4 | 24 | 59.9167 | 3 | 2 | 2 | 40.4074 | 22.1328 | 18.2746
4 | 25 | 63.2917 | 3 | 2 | 2 | 40.4074 | 20.9217 | 19.4857
4 | 26 | 65.4167 | 3 | 2 | 2 | 40.4074 | 20.1591 | 20.2483
4 | 27 | 66.875 | 3 | 2 | 2 | 40.4074 | 19.6358 | 20.7716
4 | 28 | 67.2083 | 3 | 2 | 2 | 40.4074 | 19.5162 | 20.8912
4 | 29 | 63.5417 | 3 | 2 | 2 | 40.4074 | 20.832 | 19.5754
4 | 30 | 67.9583 | 3 | 2 | 2 | 40.4074 | 19.247 | 21.1604
5 | 1 | 67.0417 | 3 | 2 | 2 | 40.4074 | 19.576 | 20.8314
5 | 2 | 67.1667 | 3 | 2 | 2 | 40.4074 | 19.5311 | 20.8763
5 | 3 | 65.625 | 3 | 2 | 2 | 40.4074 | 20.0844 | 20.323
5 | 4 | 62.875 | 3 | 2 | 2 | 40.4074 | 21.0712 | 19.3362
5 | 5 | 61.7917 | 3 | 2 | 2 | 40.4074 | 21.46 | 18.9474
5 | 6 | 58.5417 | 3 | 2 | 2 | 40.4074 | 22.6263 | 17.7811
5 | 7 | 54.9167 | 3 | 2 | 2 | 40.4074 | 23.9271 | 16.4803
5 | 8 | 60.3333 | 3 | 2 | 2 | 40.4074 | 21.9833 | 18.4241
5 | 9 | 61.6667 | 3 | 2 | 2 | 40.4074 | 21.5048 | 18.9026
5 | 10 | 63.25 | 3 | 2 | 2 | 40.4074 | 20.9366 | 19.4708
5 | 11 | 62.625 | 3 | 2 | 2 | 40.4074 | 21.1609 | 19.2465
5 | 12 | 61.7917 | 3 | 2 | 2 | 40.4074 | 21.46 | 18.9474
5 | 13 | 62.5 | 3 | 2 | 2 | 40.4074 | 21.2058 | 19.2016
5 | 14 | 61.0417 | 3 | 2 | 2 | 40.4074 | 21.7291 | 18.6783
5 | 15 | 58.875 | 3 | 2 | 2 | 40.4074 | 22.5066 | 17.9008
5 | 16 | 59.625 | 3 | 2 | 2 | 40.4074 | 22.2375 | 18.1699
5 | 17 | 60.7083 | 3 | 2 | 2 | 40.4074 | 21.8487 | 18.5587
5 | 18 | 64.375 | 3 | 2 | 2 | 40.4074 | 20.5329 | 19.8745
5 | 19 | 69.0833 | 3 | 2 | 2 | 40.4074 | 18.8433 | 21.5641
5 | 20 | 72.1667 | 3 | 2 | 2 | 40.4074 | 17.7368 | 22.6706
5 | 21 | 65.7917 | 3 | 2 | 2 | 40.4074 | 20.0245 | 20.3829
5 | 22 | 56.625 | 3 | 2 | 2 | 40.4074 | 23.3141 | 17.0933
5 | 23 | 63.1667 | 3 | 2 | 2 | 40.4074 | 20.9665 | 19.4409
5 | 24 | 61.8333 | 3 | 2 | 2 | 40.4074 | 21.445 | 18.9624
5 | 25 | 62.6667 | 3 | 2 | 2 | 40.4074 | 21.146 | 19.2614
5 | 26 | 63.9583 | 3 | 2 | 2 | 40.4074 | 20.6824 | 19.725
5 | 27 | 62.6667 | 3 | 2 | 2 | 40.4074 | 21.146 | 19.2614
5 | 28 | 64.1667 | 3 | 2 | 2 | 40.4074 | 20.6077 | 19.7997
5 | 29 | 63.2083 | 3 | 2 | 2 | 40.4074 | 20.9516 | 19.4558
5 | 30 | 62.5417 | 3 | 2 | 2 | 40.4074 | 21.1908 | 19.2166
5 | 31 | 62.125 | 3 | 2 | 2 | 40.4074 | 21.3404 | 19.067
6 | 1 | 70 | 3 | 2 | 2 | 40.4074 | 18.5143 | 21.8931
6 | 2 | 68.0417 | 3 | 2 | 2 | 40.4074 | 19.2171 | 21.1903
6 | 3 | 69.0417 | 3 | 2 | 2 | 40.4074 | 18.8583 | 21.5491
6 | 4 | 68.0833 | 3 | 2 | 2 | 40.4074 | 19.2022 | 21.2052
6 | 5 | 65.7917 | 3 | 2 | 2 | 40.4074 | 20.0245 | 20.3829
6 | 6 | 64.7083 | 3 | 2 | 2 | 40.4074 | 20.4133 | 19.9941
6 | 7 | 65.9583 | 3 | 2 | 2 | 40.4074 | 19.9647 | 20.4427
6 | 8 | 66.625 | 3 | 2 | 2 | 40.4074 | 19.7255 | 20.6819
6 | 9 | 66.9583 | 3 | 2 | 2 | 40.4074 | 19.6059 | 20.8015
6 | 10 | 68.5 | 3 | 2 | 2 | 40.4074 | 19.0526 | 21.3548
6 | 11 | 69.2917 | 3 | 2 | 2 | 40.4074 | 18.7685 | 21.6389
6 | 12 | 66.625 | 3 | 2 | 2 | 40.4074 | 19.7255 | 20.6819
6 | 13 | 67.625 | 3 | 2 | 2 | 40.4074 | 19.3666 | 21.0408
6 | 14 | 68.125 | 3 | 2 | 2 | 40.4074 | 19.1872 | 21.2202
6 | 15 | 67.2917 | 3 | 2 | 2 | 40.4074 | 19.4863 | 20.9211
6 | 16 | 67.875 | 3 | 2 | 2 | 40.4074 | 19.2769 | 21.1305
6 | 17 | 69.7083 | 3 | 2 | 2 | 40.4074 | 18.619 | 21.7884
6 | 18 | 70.75 | 3 | 2 | 2 | 40.4074 | 18.2452 | 22.1622
6 | 19 | 71.7083 | 3 | 2 | 2 | 40.4074 | 17.9013 | 22.5061
6 | 20 | 73.125 | 3 | 2 | 2 | 40.4074 | 17.3929 | 23.0145
6 | 21 | 71.4167 | 3 | 2 | 2 | 40.4074 | 18.006 | 22.4014
6 | 22 | 70.0833 | 3 | 2 | 2 | 40.4074 | 18.4844 | 21.923
6 | 23 | 67.9583 | 3 | 2 | 2 | 40.4074 | 19.247 | 21.1604
6 | 24 | 69.7917 | 3 | 2 | 2 | 40.4074 | 18.5891 | 21.8183
6 | 25 | 68.875 | 3 | 2 | 2 | 40.4074 | 18.9181 | 21.4893
6 | 26 | 71.6667 | 3 | 2 | 2 | 40.4074 | 17.9163 | 22.4911
6 | 27 | 72.375 | 3 | 2 | 2 | 40.4074 | 17.6621 | 22.7453
6 | 28 | 72.0833 | 3 | 2 | 2 | 40.4074 | 17.7667 | 22.6407
6 | 29 | 72.375 | 3 | 2 | 2 | 40.4074 | 17.6621 | 22.7453
6 | 30 | 76.1667 | 3 | 2 | 2 | 40.4074 | 16.3014 | 24.106
7 | 1 | 74.2083 | 3 | 2 | 2 | 40.4074 | 17.0042 | 23.4032
7 | 2 | 70.0417 | 3 | 2 | 2 | 40.4074 | 18.4994 | 21.908
7 | 3 | 69.25 | 3 | 2 | 2 | 40.4074 | 18.7835 | 21.6239
7 | 4 | 70.5417 | 3 | 2 | 2 | 40.4074 | 18.32 | 22.0874
7 | 5 | 73.5 | 3 | 2 | 2 | 40.4074 | 17.2583 | 23.1491
7 | 6 | 75.7917 | 3 | 2 | 2 | 40.4074 | 16.436 | 23.9714
7 | 7 | 74.125 | 3 | 2 | 2 | 40.4074 | 17.0341 | 23.3733
7 | 8 | 72.25 | 3 | 2 | 2 | 40.4074 | 17.7069 | 22.7005
7 | 9 | 69.6667 | 3 | 2 | 2 | 40.4074 | 18.634 | 21.7734
7 | 10 | 70.0833 | 3 | 2 | 2 | 40.4074 | 18.4844 | 21.923
7 | 11 | 70.0417 | 3 | 2 | 2 | 40.4074 | 18.4994 | 21.908
7 | 12 | 69.25 | 3 | 2 | 2 | 40.4074 | 18.7835 | 21.6239
7 | 13 | 69.25 | 3 | 2 | 2 | 40.4074 | 18.7835 | 21.6239
7 | 14 | 66.875 | 3 | 2 | 2 | 40.4074 | 19.6358 | 20.7716
7 | 15 | 67.625 | 3 | 2 | 2 | 40.4074 | 19.3666 | 21.0408
7 | 16 | 68.25 | 3 | 2 | 2 | 40.4074 | 19.1424 | 21.265
7 | 17 | 69.2917 | 3 | 2 | 2 | 40.4074 | 18.7685 | 21.6389
7 | 18 | 71.9583 | 3 | 2 | 2 | 40.4074 | 17.8116 | 22.5958
7 | 19 | 71.5417 | 3 | 2 | 2 | 40.4074 | 17.9611 | 22.4463
7 | 20 | 68.5 | 3 | 2 | 2 | 40.4074 | 19.0526 | 21.3548
7 | 21 | 67.4167 | 3 | 2 | 2 | 40.4074 | 19.4414 | 20.966
7 | 22 | 68.1667 | 3 | 2 | 2 | 40.4074 | 19.1723 | 21.2351
7 | 23 | 68.5417 | 3 | 2 | 2 | 40.4074 | 19.0377 | 21.3697
7 | 24 | 67.4167 | 3 | 2 | 2 | 40.4074 | 19.4414 | 20.966
7 | 25 | 71.5417 | 3 | 2 | 2 | 40.4074 | 17.9611 | 22.4463
7 | 26 | 72.3333 | 3 | 2 | 2 | 40.4074 | 17.677 | 22.7304
7 | 27 | 71 | 3 | 2 | 2 | 40.4074 | 18.1555 | 22.2519
7 | 28 | 71.6667 | 3 | 2 | 2 | 40.4074 | 17.9163 | 22.4911
7 | 29 | 68.9583 | 3 | 2 | 2 | 40.4074 | 18.8882 | 21.5192
7 | 30 | 67.5 | 3 | 2 | 2 | 40.4074 | 19.4115 | 20.9959
7 | 31 | 69.7917 | 3 | 2 | 2 | 40.4074 | 18.5891 | 21.8183
8 | 1 | 69.9167 | 3 | 2 | 2 | 40.4074 | 18.5443 | 21.8631
8 | 2 | 71.125 | 3 | 2 | 2 | 40.4074 | 18.1106 | 22.2968
8 | 3 | 71.3333 | 3 | 2 | 2 | 40.4074 | 18.0359 | 22.3715
8 | 4 | 71.125 | 3 | 2 | 2 | 40.4074 | 18.1106 | 22.2968
8 | 5 | 72.125 | 3 | 2 | 2 | 40.4074 | 17.7518 | 22.6556
8 | 6 | 72.8333 | 3 | 2 | 2 | 40.4074 | 17.4976 | 22.9098
8 | 7 | 73.3333 | 3 | 2 | 2 | 40.4074 | 17.3182 | 23.0892
8 | 8 | 72.3333 | 3 | 2 | 2 | 40.4074 | 17.677 | 22.7304
8 | 9 | 71.125 | 3 | 2 | 2 | 40.4074 | 18.1106 | 22.2968
8 | 10 | 70.4167 | 3 | 2 | 2 | 40.4074 | 18.3648 | 22.0426
8 | 11 | 69.75 | 3 | 2 | 2 | 40.4074 | 18.6041 | 21.8033
8 | 12 | 69.4167 | 3 | 2 | 2 | 40.4074 | 18.7237 | 21.6837
8 | 13 | 70.75 | 3 | 2 | 2 | 40.4074 | 18.2452 | 22.1622
8 | 14 | 71.9583 | 3 | 2 | 2 | 40.4074 | 17.8116 | 22.5958
8 | 15 | 71.125 | 3 | 2 | 2 | 40.4074 | 18.1106 | 22.2968
8 | 16 | 71.4583 | 3 | 2 | 2 | 40.4074 | 17.991 | 22.4164
8 | 17 | 70.8333 | 3 | 2 | 2 | 40.4074 | 18.2153 | 22.1921
8 | 18 | 69.5 | 3 | 2 | 2 | 40.4074 | 18.6938 | 21.7136
8 | 19 | 68.6667 | 3 | 2 | 2 | 40.4074 | 18.9928 | 21.4146
8 | 20 | 68.8333 | 3 | 2 | 2 | 40.4074 | 18.933 | 21.4744
8 | 21 | 71.0833 | 3 | 2 | 2 | 40.4074 | 18.1256 | 22.2818
8 | 22 | 71.5833 | 3 | 2 | 2 | 40.4074 | 17.9462 | 22.4612
8 | 23 | 69.4583 | 3 | 2 | 2 | 40.4074 | 18.7087 | 21.6987
8 | 24 | 68.9583 | 3 | 2 | 2 | 40.4074 | 18.8882 | 21.5192
8 | 25 | 71.875 | 3 | 2 | 2 | 40.4074 | 17.8415 | 22.5659
8 | 26 | 71.9167 | 3 | 2 | 2 | 40.4074 | 17.8265 | 22.5809
8 | 27 | 70.9583 | 3 | 2 | 2 | 40.4074 | 18.1704 | 22.237
8 | 28 | 68.25 | 3 | 2 | 2 | 40.4074 | 19.1424 | 21.265
8 | 29 | 70.4583 | 3 | 2 | 2 | 40.4074 | 18.3499 | 22.0575
8 | 30 | 71.2917 | 3 | 2 | 2 | 40.4074 | 18.0508 | 22.3566
8 | 31 | 70.375 | 3 | 2 | 2 | 40.4074 | 18.3798 | 22.0276
9 | 1 | 71.7083 | 3 | 2 | 2 | 40.4074 | 17.9013 | 22.5061
9 | 2 | 75.75 | 3 | 2 | 2 | 40.4074 | 16.4509 | 23.9565
9 | 3 | 76.5 | 3 | 2 | 2 | 40.4074 | 16.1818 | 24.2256
9 | 4 | 76 | 3 | 2 | 2 | 40.4074 | 16.3612 | 24.0462
9 | 5 | 74.4167 | 3 | 2 | 2 | 40.4074 | 16.9294 | 23.478
9 | 6 | 73.2083 | 3 | 2 | 2 | 40.4074 | 17.363 | 23.0444
9 | 7 | 71.3333 | 3 | 2 | 2 | 40.4074 | 18.0359 | 22.3715
9 | 8 | 69.1667 | 3 | 2 | 2 | 40.4074 | 18.8134 | 21.594
9 | 9 | 68.8333 | 3 | 2 | 2 | 40.4074 | 18.933 | 21.4744
9 | 10 | 68.6667 | 3 | 2 | 2 | 40.4074 | 18.9928 | 21.4146
9 | 11 | 68.2083 | 3 | 2 | 2 | 40.4074 | 19.1573 | 21.2501
9 | 12 | 67.7917 | 3 | 2 | 2 | 40.4074 | 19.3068 | 21.1006
9 | 13 | 69.375 | 3 | 2 | 2 | 40.4074 | 18.7386 | 21.6688
9 | 14 | 67.2083 | 3 | 2 | 2 | 40.4074 | 19.5162 | 20.8912
9 | 15 | 66.75 | 3 | 2 | 2 | 40.4074 | 19.6806 | 20.7268
9 | 16 | 66.8333 | 3 | 2 | 2 | 40.4074 | 19.6507 | 20.7567
9 | 17 | 71.625 | 3 | 2 | 2 | 40.4074 | 17.9312 | 22.4762
9 | 18 | 73.125 | 3 | 2 | 2 | 40.4074 | 17.3929 | 23.0145
9 | 19 | 69.0417 | 3 | 2 | 2 | 40.4074 | 18.8583 | 21.5491
9 | 20 | 67.0833 | 3 | 2 | 2 | 40.4074 | 19.561 | 20.8464
9 | 21 | 66.0833 | 3 | 2 | 2 | 40.4074 | 19.9199 | 20.4875
9 | 22 | 67.625 | 3 | 2 | 2 | 40.4074 | 19.3666 | 21.0408
9 | 23 | 69.5 | 3 | 2 | 2 | 40.4074 | 18.6938 | 21.7136
9 | 24 | 67.6667 | 3 | 2 | 2 | 40.4074 | 19.3517 | 21.0557
9 | 25 | 68.25 | 3 | 2 | 2 | 40.4074 | 19.1424 | 21.265
9 | 26 | 66.5417 | 3 | 2 | 2 | 40.4074 | 19.7554 | 20.652
9 | 27 | 65.9167 | 3 | 2 | 2 | 40.4074 | 19.9797 | 20.4277
9 | 28 | 66.7917 | 3 | 2 | 2 | 40.4074 | 19.6657 | 20.7417
9 | 29 | 67 | 3 | 2 | 2 | 40.4074 | 19.5909 | 20.8165
9 | 30 | 66.7083 | 3 | 2 | 2 | 40.4074 | 19.6956 | 20.7118
10 | 1 | 77.5417 | 3 | 2 | 2 | 40.4074 | 15.808 | 24.5994
10 | 2 | 78 | 3 | 2 | 2 | 40.4074 | 15.6435 | 24.7639
10 | 3 | 70.0417 | 3 | 2 | 2 | 40.4074 | 18.4994 | 21.908
10 | 4 | 67.9167 | 3 | 2 | 2 | 40.4074 | 19.262 | 21.1454
10 | 5 | 69.625 | 3 | 2 | 2 | 40.4074 | 18.6489 | 21.7585
10 | 6 | 71.2917 | 3 | 2 | 2 | 40.4074 | 18.0508 | 22.3566
10 | 7 | 68.8333 | 3 | 2 | 2 | 40.4074 | 18.933 | 21.4744
10 | 8 | 69.0417 | 3 | 2 | 2 | 40.4074 | 18.8583 | 21.5491
10 | 9 | 67.25 | 3 | 2 | 2 | 40.4074 | 19.5012 | 20.9062
10 | 10 | 65.75 | 3 | 2 | 2 | 40.4074 | 20.0395 | 20.3679
10 | 11 | 63.5833 | 3 | 2 | 2 | 40.4074 | 20.817 | 19.5904
10 | 12 | 63.5833 | 3 | 2 | 2 | 40.4074 | 20.817 | 19.5904
10 | 13 | 65.9583 | 3 | 2 | 2 | 40.4074 | 19.9647 | 20.4427
10 | 14 | 73.75 | 3 | 2 | 2 | 40.4074 | 17.1686 | 23.2388
10 | 15 | 74.5 | 3 | 2 | 2 | 40.4074 | 16.8995 | 23.5079
10 | 16 | 73.125 | 3 | 2 | 2 | 40.4074 | 17.3929 | 23.0145
10 | 17 | 75.9167 | 3 | 2 | 2 | 40.4074 | 16.3911 | 24.0163
10 | 18 | 74.5417 | 3 | 2 | 2 | 40.4074 | 16.8845 | 23.5229
10 | 19 | 68.0833 | 3 | 2 | 2 | 40.4074 | 19.2022 | 21.2052
10 | 20 | 68.0833 | 3 | 2 | 2 | 40.4074 | 19.2022 | 21.2052
10 | 21 | 66.2917 | 3 | 2 | 2 | 40.4074 | 19.8451 | 20.5623
10 | 22 | 65.7083 | 3 | 2 | 2 | 40.4074 | 20.0544 | 20.353
10 | 23 | 64.125 | 3 | 2 | 2 | 40.4074 | 20.6226 | 19.7848
10 | 24 | 64.8333 | 3 | 2 | 2 | 40.4074 | 20.3684 | 20.039
10 | 25 | 69.0417 | 3 | 2 | 2 | 40.4074 | 18.8583 | 21.5491
10 | 26 | 73.25 | 3 | 2 | 2 | 40.4074 | 17.3481 | 23.0593
10 | 27 | 71.5 | 3 | 2 | 2 | 40.4074 | 17.9761 | 22.4313
10 | 28 | 68.2083 | 3 | 2 | 2 | 40.4074 | 19.1573 | 21.2501
10 | 29 | 63.1667 | 3 | 2 | 2 | 40.4074 | 20.9665 | 19.4409
10 | 30 | 60.2917 | 3 | 2 | 2 | 40.4074 | 21.9983 | 18.4091
10 | 31 | 62.5 | 3 | 2 | 2 | 40.4074 | 21.2058 | 19.2016
11 | 1 | 72.0833 | 3 | 2 | 2 | 40.4074 | 17.7667 | 22.6407
11 | 2 | 63.375 | 3 | 2 | 2 | 40.4074 | 20.8918 | 19.5156
11 | 3 | 61.25 | 3 | 2 | 2 | 40.4074 | 21.6544 | 18.753
11 | 4 | 57.5833 | 3 | 2 | 2 | 40.4074 | 22.9702 | 17.4372
11 | 5 | 60.4167 | 3 | 2 | 2 | 40.4074 | 21.9534 | 18.454
11 | 6 | 61.875 | 3 | 2 | 2 | 40.4074 | 21.4301 | 18.9773
11 | 7 | 63.4583 | 3 | 2 | 2 | 40.4074 | 20.8619 | 19.5455
11 | 8 | 61.7083 | 3 | 2 | 2 | 40.4074 | 21.4899 | 18.9175
11 | 9 | 62.2917 | 3 | 2 | 2 | 40.4074 | 21.2805 | 19.1269
11 | 10 | 62.1667 | 3 | 2 | 2 | 40.4074 | 21.3254 | 19.082
11 | 11 | 59.625 | 3 | 2 | 2 | 40.4074 | 22.2375 | 18.1699
11 | 12 | 59.0833 | 3 | 2 | 2 | 40.4074 | 22.4319 | 17.9755
11 | 13 | 59.7917 | 3 | 2 | 2 | 40.4074 | 22.1777 | 18.2297
11 | 14 | 60.1667 | 3 | 2 | 2 | 40.4074 | 22.0431 | 18.3643
11 | 15 | 68.8333 | 3 | 2 | 2 | 40.4074 | 18.933 | 21.4744
11 | 16 | 66.75 | 3 | 2 | 2 | 40.4074 | 19.6806 | 20.7268
11 | 17 | 63.75 | 3 | 2 | 2 | 40.4074 | 20.7572 | 19.6502
11 | 18 | 68.4583 | 3 | 2 | 2 | 40.4074 | 19.0676 | 21.3398
11 | 19 | 65.3333 | 3 | 2 | 2 | 40.4074 | 20.189 | 20.2184
11 | 20 | 68.875 | 3 | 2 | 2 | 40.4074 | 18.9181 | 21.4893
11 | 21 | 68.4583 | 3 | 2 | 2 | 40.4074 | 19.0676 | 21.3398
11 | 22 | 66.625 | 3 | 2 | 2 | 40.4074 | 19.7255 | 20.6819
11 | 23 | 62.4583 | 3 | 2 | 2 | 40.4074 | 21.2207 | 19.1867
11 | 24 | 60.875 | 3 | 2 | 2 | 40.4074 | 21.7889 | 18.6185
11 | 25 | 62.0417 | 3 | 2 | 2 | 40.4074 | 21.3703 | 19.0371
11 | 26 | 61.5 | 3 | 2 | 2 | 40.4074 | 21.5646 | 18.8428
11 | 27 | 58.25 | 3 | 2 | 2 | 40.4074 | 22.7309 | 17.6765
11 | 28 | 57.3333 | 3 | 2 | 2 | 40.4074 | 23.0599 | 17.3475
11 | 29 | 57.625 | 3 | 2 | 2 | 40.4074 | 22.9552 | 17.4522
11 | 30 | 60.6667 | 3 | 2 | 2 | 40.4074 | 21.8637 | 18.5437
12 | 1 | 50.25 | 3 | 2 | 2 | 40.4074 | 25.6018 | 14.8056
12 | 2 | 50.2917 | 3 | 2 | 2 | 40.4074 | 25.5868 | 14.8206
12 | 3 | 51.9167 | 3 | 2 | 2 | 40.4074 | 25.0037 | 15.4037
12 | 4 | 50.375 | 3 | 2 | 2 | 40.4074 | 25.5569 | 14.8505
12 | 5 | 49.375 | 3 | 2 | 2 | 40.4074 | 25.9158 | 14.4916
12 | 6 | 49.7917 | 3 | 2 | 2 | 40.4074 | 25.7663 | 14.6411
12 | 7 | 51.4583 | 3 | 2 | 2 | 40.4074 | 25.1682 | 15.2392
12 | 8 | 55.25 | 3 | 2 | 2 | 40.4074 | 23.8075 | 16.5999
12 | 9 | 55.9167 | 3 | 2 | 2 | 40.4074 | 23.5683 | 16.8391
12 | 10 | 62.5833 | 3 | 2 | 2 | 40.4074 | 21.1759 | 19.2315
12 | 11 | 65.875 | 3 | 2 | 2 | 40.4074 | 19.9946 | 20.4128
12 | 12 | 56.9167 | 3 | 2 | 2 | 40.4074 | 23.2094 | 17.198
12 | 13 | 57.0417 | 3 | 2 | 2 | 40.4074 | 23.1645 | 17.2429
12 | 14 | 60.75 | 3 | 2 | 2 | 40.4074 | 21.8338 | 18.5736
12 | 15 | 59.5833 | 3 | 2 | 2 | 40.4074 | 22.2525 | 18.1549
12 | 16 | 62.75 | 3 | 2 | 2 | 40.4074 | 21.1161 | 19.2913
12 | 17 | 60.875 | 3 | 2 | 2 | 40.4074 | 21.7889 | 18.6185
12 | 18 | 60.7083 | 3 | 2 | 2 | 40.4074 | 21.8487 | 18.5587
12 | 19 | 64.375 | 3 | 2 | 2 | 40.4074 | 20.5329 | 19.8745
12 | 20 | 57.875 | 3 | 2 | 2 | 40.4074 | 22.8655 | 17.5419
12 | 21 | 56.2917 | 3 | 2 | 2 | 40.4074 | 23.4337 | 16.9737
12 | 22 | 54.25 | 3 | 2 | 2 | 40.4074 | 24.1664 | 16.241
12 | 23 | 53.7917 | 3 | 2 | 2 | 40.4074 | 24.3308 | 16.0766
12 | 24 | 53.625 | 3 | 2 | 2 | 40.4074 | 24.3906 | 16.0168
12 | 25 | 52.9167 | 3 | 2 | 2 | 40.4074 | 24.6448 | 15.7626
12 | 26 | 53.875 | 3 | 2 | 2 | 40.4074 | 24.3009 | 16.1065
12 | 27 | 57.875 | 3 | 2 | 2 | 40.4074 | 22.8655 | 17.5419
12 | 28 | 57.125 | 3 | 2 | 2 | 40.4074 | 23.1346 | 17.2728
12 | 29 | 55.7917 | 3 | 2 | 2 | 40.4074 | 23.6131 | 16.7943
12 | 30 | 53.2083 | 3 | 2 | 2 | 40.4074 | 24.5402 | 15.8672
12 | 31 | 53.2083 | 3 | 2 | 2 | 40.4074 | 24.5402 | 15.8672
1 | 1 | 51.7083 | 4 | 10 | 10 | 202.037 | 96.2712 | 105.7658
1 | 2 | 55.1667 | 4 | 10 | 10 | 202.037 | 87.3594 | 114.6776
1 | 3 | 51.4583 | 4 | 10 | 10 | 202.037 | 96.9155 | 105.1215
1 | 4 | 50.0833 | 4 | 10 | 10 | 202.037 | 100.4587 | 101.5783
1 | 5 | 53.9583 | 4 | 10 | 10 | 202.037 | 90.4732 | 111.5638
1 | 6 | 54.8333 | 4 | 10 | 10 | 202.037 | 88.2184 | 113.8186
1 | 7 | 54.4583 | 4 | 10 | 10 | 202.037 | 89.1847 | 112.8523
1 | 8 | 53.7083 | 4 | 10 | 10 | 202.037 | 91.1174 | 110.9196
1 | 9 | 56.75 | 4 | 10 | 10 | 202.037 | 83.2793 | 118.7577
1 | 10 | 59 | 4 | 10 | 10 | 202.037 | 77.4812 | 124.5558
1 | 11 | 57.875 | 4 | 10 | 10 | 202.037 | 80.3803 | 121.6567
1 | 12 | 55.875 | 4 | 10 | 10 | 202.037 | 85.5341 | 116.5029
1 | 13 | 59.2917 | 4 | 10 | 10 | 202.037 | 76.7296 | 125.3074
1 | 14 | 64.7917 | 4 | 10 | 10 | 202.037 | 62.5566 | 139.4804
1 | 15 | 57.9167 | 4 | 10 | 10 | 202.037 | 80.2729 | 121.7641
1 | 16 | 56.7083 | 4 | 10 | 10 | 202.037 | 83.3867 | 118.6503
1 | 17 | 55.6667 | 4 | 10 | 10 | 202.037 | 86.0709 | 115.9661
1 | 18 | 55.4583 | 4 | 10 | 10 | 202.037 | 86.6078 | 115.4292
1 | 19 | 55 | 4 | 10 | 10 | 202.037 | 87.7889 | 114.2481
1 | 20 | 53.9167 | 4 | 10 | 10 | 202.037 | 90.5806 | 111.4564
1 | 21 | 56.5833 | 4 | 10 | 10 | 202.037 | 83.7088 | 118.3282
1 | 22 | 61.75 | 4 | 10 | 10 | 202.037 | 70.3947 | 131.6423
1 | 23 | 56.0417 | 4 | 10 | 10 | 202.037 | 85.1046 | 116.9324
1 | 24 | 52.7917 | 4 | 10 | 10 | 202.037 | 93.4796 | 108.5574
1 | 25 | 54.5 | 4 | 10 | 10 | 202.037 | 89.0774 | 112.9596
1 | 26 | 53.25 | 4 | 10 | 10 | 202.037 | 92.2985 | 109.7385
1 | 27 | 54.25 | 4 | 10 | 10 | 202.037 | 89.7216 | 112.3154
1 | 28 | 56.3333 | 4 | 10 | 10 | 202.037 | 84.353 | 117.684
1 | 29 | 55.375 | 4 | 10 | 10 | 202.037 | 86.8225 | 115.2145
1 | 30 | 53.1667 | 4 | 10 | 10 | 202.037 | 92.5132 | 109.5238
1 | 31 | 55.875 | 4 | 10 | 10 | 202.037 | 85.5341 | 116.5029
2 | 1 | 51.4583 | 4 | 10 | 10 | 202.037 | 96.9155 | 105.1215
2 | 2 | 51.2917 | 4 | 10 | 10 | 202.037 | 97.345 | 104.692
2 | 3 | 52.0833 | 4 | 10 | 10 | 202.037 | 95.3049 | 106.7321
2 | 4 | 53.625 | 4 | 10 | 10 | 202.037 | 91.3322 | 110.7048
2 | 5 | 50.5833 | 4 | 10 | 10 | 202.037 | 99.1703 | 102.8667
2 | 6 | 49.8333 | 4 | 10 | 10 | 202.037 | 101.103 | 100.934
2 | 7 | 53.5417 | 4 | 10 | 10 | 202.037 | 91.5469 | 110.4901
2 | 8 | 55.9583 | 4 | 10 | 10 | 202.037 | 85.3193 | 116.7177
2 | 9 | 62.0833 | 4 | 10 | 10 | 202.037 | 69.5357 | 132.5013
2 | 10 | 59.4167 | 4 | 10 | 10 | 202.037 | 76.4075 | 125.6295
2 | 11 | 57.8333 | 4 | 10 | 10 | 202.037 | 80.4876 | 121.5494
2 | 12 | 60 | 4 | 10 | 10 | 202.037 | 74.9043 | 127.1327
2 | 13 | 52.9583 | 4 | 10 | 10 | 202.037 | 93.0501 | 108.9869
2 | 14 | 52.375 | 4 | 10 | 10 | 202.037 | 94.5533 | 107.4837
2 | 15 | 53.375 | 4 | 10 | 10 | 202.037 | 91.9764 | 110.0606
2 | 16 | 53.375 | 4 | 10 | 10 | 202.037 | 91.9764 | 110.0606
2 | 17 | 53.125 | 4 | 10 | 10 | 202.037 | 92.6206 | 109.4164
2 | 18 | 53.625 | 4 | 10 | 10 | 202.037 | 91.3322 | 110.7048
2 | 19 | 54.75 | 4 | 10 | 10 | 202.037 | 88.4331 | 113.6039
2 | 20 | 54.75 | 4 | 10 | 10 | 202.037 | 88.4331 | 113.6039
2 | 21 | 54.5417 | 4 | 10 | 10 | 202.037 | 88.97 | 113.067
2 | 22 | 53.2917 | 4 | 10 | 10 | 202.037 | 92.1911 | 109.8459
2 | 23 | 52 | 4 | 10 | 10 | 202.037 | 95.5196 | 106.5174
2 | 24 | 54.3333 | 4 | 10 | 10 | 202.037 | 89.5068 | 112.5302
2 | 25 | 54.5833 | 4 | 10 | 10 | 202.037 | 88.8626 | 113.1744
2 | 26 | 61.625 | 4 | 10 | 10 | 202.037 | 70.7168 | 131.3202
2 | 27 | 63.5417 | 4 | 10 | 10 | 202.037 | 65.7777 | 136.2593
2 | 28 | 57.5833 | 4 | 10 | 10 | 202.037 | 81.1319 | 120.9051
3 | 1 | 58.4167 | 4 | 10 | 10 | 202.037 | 78.9844 | 123.0526
3 | 2 | 59.1667 | 4 | 10 | 10 | 202.037 | 77.0517 | 124.9853
3 | 3 | 59.9167 | 4 | 10 | 10 | 202.037 | 75.119 | 126.918
3 | 4 | 62.625 | 4 | 10 | 10 | 202.037 | 68.1399 | 133.8971
3 | 5 | 63.0417 | 4 | 10 | 10 | 202.037 | 67.0662 | 134.9708
3 | 6 | 66.0833 | 4 | 10 | 10 | 202.037 | 59.2281 | 142.8089
3 | 7 | 66.5417 | 4 | 10 | 10 | 202.037 | 58.047 | 143.99
3 | 8 | 69.5417 | 4 | 10 | 10 | 202.037 | 50.3162 | 151.7208
3 | 9 | 71.5417 | 4 | 10 | 10 | 202.037 | 45.1624 | 156.8746
3 | 10 | 66.5 | 4 | 10 | 10 | 202.037 | 58.1543 | 143.8827
3 | 11 | 63.9583 | 4 | 10 | 10 | 202.037 | 64.704 | 137.333
3 | 12 | 66.875 | 4 | 10 | 10 | 202.037 | 57.188 | 144.849
3 | 13 | 63.5 | 4 | 10 | 10 | 202.037 | 65.8851 | 136.1519
3 | 14 | 62.7917 | 4 | 10 | 10 | 202.037 | 67.7104 | 134.3266
3 | 15 | 66.2083 | 4 | 10 | 10 | 202.037 | 58.9059 | 143.1311
3 | 16 | 72.4583 | 4 | 10 | 10 | 202.037 | 42.8002 | 159.2368
3 | 17 | 66.625 | 4 | 10 | 10 | 202.037 | 57.8322 | 144.2048
3 | 18 | 63.9167 | 4 | 10 | 10 | 202.037 | 64.8114 | 137.2256
3 | 19 | 63.75 | 4 | 10 | 10 | 202.037 | 65.2409 | 136.7961
3 | 20 | 62.2917 | 4 | 10 | 10 | 202.037 | 68.9989 | 133.0381
3 | 21 | 62.75 | 4 | 10 | 10 | 202.037 | 67.8178 | 134.2192
3 | 22 | 61.0833 | 4 | 10 | 10 | 202.037 | 72.1126 | 129.9244
3 | 23 | 61.8333 | 4 | 10 | 10 | 202.037 | 70.18 | 131.857
3 | 24 | 62.375 | 4 | 10 | 10 | 202.037 | 68.7841 | 133.2529
3 | 25 | 62.2083 | 4 | 10 | 10 | 202.037 | 69.2136 | 132.8234
3 | 26 | 62.375 | 4 | 10 | 10 | 202.037 | 68.7841 | 133.2529
3 | 27 | 61.2083 | 4 | 10 | 10 | 202.037 | 71.7905 | 130.2465
3 | 28 | 61.9167 | 4 | 10 | 10 | 202.037 | 69.9652 | 132.0718
3 | 29 | 63.125 | 4 | 10 | 10 | 202.037 | 66.8514 | 135.1856
3 | 30 | 62.5417 | 4 | 10 | 10 | 202.037 | 68.3546 | 133.6824
3 | 31 | 60 | 4 | 10 | 10 | 202.037 | 74.9043 | 127.1327
4 | 1 | 68.2917 | 4 | 10 | 10 | 202.037 | 53.5374 | 148.4996
4 | 2 | 61.4583 | 4 | 10 | 10 | 202.037 | 71.1463 | 130.8907
4 | 3 | 60.25 | 4 | 10 | 10 | 202.037 | 74.2601 | 127.7769
4 | 4 | 61.25 | 4 | 10 | 10 | 202.037 | 71.6832 | 130.3538
4 | 5 | 61.2917 | 4 | 10 | 10 | 202.037 | 71.5758 | 130.4612
4 | 6 | 61.875 | 4 | 10 | 10 | 202.037 | 70.0726 | 131.9644
4 | 7 | 57.7917 | 4 | 10 | 10 | 202.037 | 80.595 | 121.442
4 | 8 | 52.7083 | 4 | 10 | 10 | 202.037 | 93.6943 | 108.3427
4 | 9 | 53.25 | 4 | 10 | 10 | 202.037 | 92.2985 | 109.7385
4 | 10 | 56.7083 | 4 | 10 | 10 | 202.037 | 83.3867 | 118.6503
4 | 11 | 60.1667 | 4 | 10 | 10 | 202.037 | 74.4748 | 127.5622
4 | 12 | 59.0833 | 4 | 10 | 10 | 202.037 | 77.2665 | 124.7705
4 | 13 | 57.9583 | 4 | 10 | 10 | 202.037 | 80.1655 | 121.8715
4 | 14 | 62.5833 | 4 | 10 | 10 | 202.037 | 68.2473 | 133.7897
4 | 15 | 70.125 | 4 | 10 | 10 | 202.037 | 48.813 | 153.224
4 | 16 | 72.9167 | 4 | 10 | 10 | 202.037 | 41.6191 | 160.4179
4 | 17 | 65.7083 | 4 | 10 | 10 | 202.037 | 60.1944 | 141.8426
4 | 18 | 63.1667 | 4 | 10 | 10 | 202.037 | 66.7441 | 135.2929
4 | 19 | 63.4583 | 4 | 10 | 10 | 202.037 | 65.9925 | 136.0445
4 | 20 | 60.875 | 4 | 10 | 10 | 202.037 | 72.6495 | 129.3875
4 | 21 | 62.1667 | 4 | 10 | 10 | 202.037 | 69.321 | 132.716
4 | 22 | 61 | 4 | 10 | 10 | 202.037 | 72.3274 | 129.7096
4 | 23 | 61.8333 | 4 | 10 | 10 | 202.037 | 70.18 | 131.857
4 | 24 | 59.9167 | 4 | 10 | 10 | 202.037 | 75.119 | 126.918
4 | 25 | 63.2917 | 4 | 10 | 10 | 202.037 | 66.4219 | 135.615
4 | 26 | 65.4167 | 4 | 10 | 10 | 202.037 | 60.946 | 141.091
4 | 27 | 66.875 | 4 | 10 | 10 | 202.037 | 57.188 | 144.849
4 | 28 | 67.2083 | 4 | 10 | 10 | 202.037 | 56.329 | 145.708
4 | 29 | 63.5417 | 4 | 10 | 10 | 202.037 | 65.7777 | 136.2593
4 | 30 | 67.9583 | 4 | 10 | 10 | 202.037 | 54.3963 | 147.6407
5 | 1 | 67.0417 | 4 | 10 | 10 | 202.037 | 56.7585 | 145.2785
5 | 2 | 67.1667 | 4 | 10 | 10 | 202.037 | 56.4364 | 145.6006
5 | 3 | 65.625 | 4 | 10 | 10 | 202.037 | 60.4091 | 141.6279
5 | 4 | 62.875 | 4 | 10 | 10 | 202.037 | 67.4957 | 134.5413
5 | 5 | 61.7917 | 4 | 10 | 10 | 202.037 | 70.2873 | 131.7497
5 | 6 | 58.5417 | 4 | 10 | 10 | 202.037 | 78.6623 | 123.3747
5 | 7 | 54.9167 | 4 | 10 | 10 | 202.037 | 88.0036 | 114.0334
5 | 8 | 60.3333 | 4 | 10 | 10 | 202.037 | 74.0453 | 127.9917
5 | 9 | 61.6667 | 4 | 10 | 10 | 202.037 | 70.6094 | 131.4276
5 | 10 | 63.25 | 4 | 10 | 10 | 202.037 | 66.5293 | 135.5077
5 | 11 | 62.625 | 4 | 10 | 10 | 202.037 | 68.1399 | 133.8971
5 | 12 | 61.7917 | 4 | 10 | 10 | 202.037 | 70.2873 | 131.7497
5 | 13 | 62.5 | 4 | 10 | 10 | 202.037 | 68.462 | 133.575
5 | 14 | 61.0417 | 4 | 10 | 10 | 202.037 | 72.22 | 129.817
5 | 15 | 58.875 | 4 | 10 | 10 | 202.037 | 77.8033 | 124.2337
5 | 16 | 59.625 | 4 | 10 | 10 | 202.037 | 75.8706 | 126.1664
5 | 17 | 60.7083 | 4 | 10 | 10 | 202.037 | 73.079 | 128.958
5 | 18 | 64.375 | 4 | 10 | 10 | 202.037 | 63.6303 | 138.4067
5 | 19 | 69.0833 | 4 | 10 | 10 | 202.037 | 51.4973 | 150.5397
5 | 20 | 72.1667 | 4 | 10 | 10 | 202.037 | 43.5518 | 158.4852
5 | 21 | 65.7917 | 4 | 10 | 10 | 202.037 | 59.9797 | 142.0573
5 | 22 | 56.625 | 4 | 10 | 10 | 202.037 | 83.6014 | 118.4356
5 | 23 | 63.1667 | 4 | 10 | 10 | 202.037 | 66.7441 | 135.2929
5 | 24 | 61.8333 | 4 | 10 | 10 | 202.037 | 70.18 | 131.857
5 | 25 | 62.6667 | 4 | 10 | 10 | 202.037 | 68.0325 | 134.0045
5 | 26 | 63.9583 | 4 | 10 | 10 | 202.037 | 64.704 | 137.333
5 | 27 | 62.6667 | 4 | 10 | 10 | 202.037 | 68.0325 | 134.0045
5 | 28 | 64.1667 | 4 | 10 | 10 | 202.037 | 64.1671 | 137.8699
5 | 29 | 63.2083 | 4 | 10 | 10 | 202.037 | 66.6367 | 135.4003
5 | 30 | 62.5417 | 4 | 10 | 10 | 202.037 | 68.3546 | 133.6824
5 | 31 | 62.125 | 4 | 10 | 10 | 202.037 | 69.4284 | 132.6086
6 | 1 | 70 | 4 | 10 | 10 | 202.037 | 49.1351 | 152.9019
6 | 2 | 68.0417 | 4 | 10 | 10 | 202.037 | 54.1816 | 147.8554
6 | 3 | 69.0417 | 4 | 10 | 10 | 202.037 | 51.6047 | 150.4323
6 | 4 | 68.0833 | 4 | 10 | 10 | 202.037 | 54.0742 | 147.9628
6 | 5 | 65.7917 | 4 | 10 | 10 | 202.037 | 59.9797 | 142.0573
6 | 6 | 64.7083 | 4 | 10 | 10 | 202.037 | 62.7713 | 139.2657
6 | 7 | 65.9583 | 4 | 10 | 10 | 202.037 | 59.5502 | 142.4868
6 | 8 | 66.625 | 4 | 10 | 10 | 202.037 | 57.8322 | 144.2048
6 | 9 | 66.9583 | 4 | 10 | 10 | 202.037 | 56.9733 | 145.0637
6 | 10 | 68.5 | 4 | 10 | 10 | 202.037 | 53.0005 | 149.0365
6 | 11 | 69.2917 | 4 | 10 | 10 | 202.037 | 50.9604 | 151.0766
6 | 12 | 66.625 | 4 | 10 | 10 | 202.037 | 57.8322 | 144.2048
6 | 13 | 67.625 | 4 | 10 | 10 | 202.037 | 55.2553 | 146.7817
6 | 14 | 68.125 | 4 | 10 | 10 | 202.037 | 53.9668 | 148.0702
6 | 15 | 67.2917 | 4 | 10 | 10 | 202.037 | 56.1143 | 145.9227
6 | 16 | 67.875 | 4 | 10 | 10 | 202.037 | 54.6111 | 147.4259
6 | 17 | 69.7083 | 4 | 10 | 10 | 202.037 | 49.8867 | 152.1503
6 | 18 | 70.75 | 4 | 10 | 10 | 202.037 | 47.2024 | 154.8346
6 | 19 | 71.7083 | 4 | 10 | 10 | 202.037 | 44.7329 | 157.3041
6 | 20 | 73.125 | 4 | 10 | 10 | 202.037 | 41.0823 | 160.9547
6 | 21 | 71.4167 | 4 | 10 | 10 | 202.037 | 45.4845 | 156.5525
6 | 22 | 70.0833 | 4 | 10 | 10 | 202.037 | 48.9204 | 153.1166
6 | 23 | 67.9583 | 4 | 10 | 10 | 202.037 | 54.3963 | 147.6407
6 | 24 | 69.7917 | 4 | 10 | 10 | 202.037 | 49.672 | 152.365
6 | 25 | 68.875 | 4 | 10 | 10 | 202.037 | 52.0342 | 150.0028
6 | 26 | 71.6667 | 4 | 10 | 10 | 202.037 | 44.8403 | 157.1967
6 | 27 | 72.375 | 4 | 10 | 10 | 202.037 | 43.0149 | 159.0221
6 | 28 | 72.0833 | 4 | 10 | 10 | 202.037 | 43.7665 | 158.2705
6 | 29 | 72.375 | 4 | 10 | 10 | 202.037 | 43.0149 | 159.0221
6 | 30 | 76.1667 | 4 | 10 | 10 | 202.037 | 33.2441 | 168.7929
7 | 1 | 74.2083 | 4 | 10 | 10 | 202.037 | 38.2906 | 163.7464
7 | 2 | 70.0417 | 4 | 10 | 10 | 202.037 | 49.0278 | 153.0092
7 | 3 | 69.25 | 4 | 10 | 10 | 202.037 | 51.0678 | 150.9692
7 | 4 | 70.5417 | 4 | 10 | 10 | 202.037 | 47.7393 | 154.2977
7 | 5 | 73.5 | 4 | 10 | 10 | 202.037 | 40.1159 | 161.9211
7 | 6 | 75.7917 | 4 | 10 | 10 | 202.037 | 34.2105 | 167.8265
7 | 7 | 74.125 | 4 | 10 | 10 | 202.037 | 38.5053 | 163.5317
7 | 8 | 72.25 | 4 | 10 | 10 | 202.037 | 43.3371 | 158.6999
7 | 9 | 69.6667 | 4 | 10 | 10 | 202.037 | 49.9941 | 152.0429
7 | 10 | 70.0833 | 4 | 10 | 10 | 202.037 | 48.9204 | 153.1166
7 | 11 | 70.0417 | 4 | 10 | 10 | 202.037 | 49.0278 | 153.0092
7 | 12 | 69.25 | 4 | 10 | 10 | 202.037 | 51.0678 | 150.9692
7 | 13 | 69.25 | 4 | 10 | 10 | 202.037 | 51.0678 | 150.9692
7 | 14 | 66.875 | 4 | 10 | 10 | 202.037 | 57.188 | 144.849
7 | 15 | 67.625 | 4 | 10 | 10 | 202.037 | 55.2553 | 146.7817
7 | 16 | 68.25 | 4 | 10 | 10 | 202.037 | 53.6447 | 148.3923
7 | 17 | 69.2917 | 4 | 10 | 10 | 202.037 | 50.9604 | 151.0766
7 | 18 | 71.9583 | 4 | 10 | 10 | 202.037 | 44.0887 | 157.9483
7 | 19 | 71.5417 | 4 | 10 | 10 | 202.037 | 45.1624 | 156.8746
7 | 20 | 68.5 | 4 | 10 | 10 | 202.037 | 53.0005 | 149.0365
7 | 21 | 67.4167 | 4 | 10 | 10 | 202.037 | 55.7922 | 146.2448
7 | 22 | 68.1667 | 4 | 10 | 10 | 202.037 | 53.8595 | 148.1775
7 | 23 | 68.5417 | 4 | 10 | 10 | 202.037 | 52.8931 | 149.1439
7 | 24 | 67.4167 | 4 | 10 | 10 | 202.037 | 55.7922 | 146.2448
7 | 25 | 71.5417 | 4 | 10 | 10 | 202.037 | 45.1624 | 156.8746
7 | 26 | 72.3333 | 4 | 10 | 10 | 202.037 | 43.1223 | 158.9147
7 | 27 | 71 | 4 | 10 | 10 | 202.037 | 46.5582 | 155.4788
7 | 28 | 71.6667 | 4 | 10 | 10 | 202.037 | 44.8403 | 157.1967
7 | 29 | 68.9583 | 4 | 10 | 10 | 202.037 | 51.8194 | 150.2176
7 | 30 | 67.5 | 4 | 10 | 10 | 202.037 | 55.5774 | 146.4596
7 | 31 | 69.7917 | 4 | 10 | 10 | 202.037 | 49.672 | 152.365
8 | 1 | 69.9167 | 4 | 10 | 10 | 202.037 | 49.3499 | 152.6871
8 | 2 | 71.125 | 4 | 10 | 10 | 202.037 | 46.2361 | 155.8009
8 | 3 | 71.3333 | 4 | 10 | 10 | 202.037 | 45.6992 | 156.3378
8 | 4 | 71.125 | 4 | 10 | 10 | 202.037 | 46.2361 | 155.8009
8 | 5 | 72.125 | 4 | 10 | 10 | 202.037 | 43.6592 | 158.3778
8 | 6 | 72.8333 | 4 | 10 | 10 | 202.037 | 41.8339 | 160.2031
8 | 7 | 73.3333 | 4 | 10 | 10 | 202.037 | 40.5454 | 161.4916
8 | 8 | 72.3333 | 4 | 10 | 10 | 202.037 | 43.1223 | 158.9147
8 | 9 | 71.125 | 4 | 10 | 10 | 202.037 | 46.2361 | 155.8009
8 | 10 | 70.4167 | 4 | 10 | 10 | 202.037 | 48.0614 | 153.9756
8 | 11 | 69.75 | 4 | 10 | 10 | 202.037 | 49.7794 | 152.2576
8 | 12 | 69.4167 | 4 | 10 | 10 | 202.037 | 50.6383 | 151.3987
8 | 13 | 70.75 | 4 | 10 | 10 | 202.037 | 47.2024 | 154.8346
8 | 14 | 71.9583 | 4 | 10 | 10 | 202.037 | 44.0887 | 157.9483
8 | 15 | 71.125 | 4 | 10 | 10 | 202.037 | 46.2361 | 155.8009
8 | 16 | 71.4583 | 4 | 10 | 10 | 202.037 | 45.3771 | 156.6599
8 | 17 | 70.8333 | 4 | 10 | 10 | 202.037 | 46.9877 | 155.0493
8 | 18 | 69.5 | 4 | 10 | 10 | 202.037 | 50.4236 | 151.6134
8 | 19 | 68.6667 | 4 | 10 | 10 | 202.037 | 52.571 | 149.466
8 | 20 | 68.8333 | 4 | 10 | 10 | 202.037 | 52.1415 | 149.8955
8 | 21 | 71.0833 | 4 | 10 | 10 | 202.037 | 46.3435 | 155.6935
8 | 22 | 71.5833 | 4 | 10 | 10 | 202.037 | 45.055 | 156.982
8 | 23 | 69.4583 | 4 | 10 | 10 | 202.037 | 50.531 | 151.506
8 | 24 | 68.9583 | 4 | 10 | 10 | 202.037 | 51.8194 | 150.2176
8 | 25 | 71.875 | 4 | 10 | 10 | 202.037 | 44.3034 | 157.7336
8 | 26 | 71.9167 | 4 | 10 | 10 | 202.037 | 44.196 | 157.841
8 | 27 | 70.9583 | 4 | 10 | 10 | 202.037 | 46.6656 | 155.3714
8 | 28 | 68.25 | 4 | 10 | 10 | 202.037 | 53.6447 | 148.3923
8 | 29 | 70.4583 | 4 | 10 | 10 | 202.037 | 47.954 | 154.083
8 | 30 | 71.2917 | 4 | 10 | 10 | 202.037 | 45.8066 | 156.2304
8 | 31 | 70.375 | 4 | 10 | 10 | 202.037 | 48.1688 | 153.8682
9 | 1 | 71.7083 | 4 | 10 | 10 | 202.037 | 44.7329 | 157.3041
9 | 2 | 75.75 | 4 | 10 | 10 | 202.037 | 34.3178 | 167.7191
9 | 3 | 76.5 | 4 | 10 | 10 | 202.037 | 32.3852 | 169.6518
9 | 4 | 76 | 4 | 10 | 10 | 202.037 | 33.6736 | 168.3634
9 | 5 | 74.4167 | 4 | 10 | 10 | 202.037 | 37.7537 | 164.2833
9 | 6 | 73.2083 | 4 | 10 | 10 | 202.037 | 40.8675 | 161.1695
9 | 7 | 71.3333 | 4 | 10 | 10 | 202.037 | 45.6992 | 156.3378
9 | 8 | 69.1667 | 4 | 10 | 10 | 202.037 | 51.2826 | 150.7544
9 | 9 | 68.8333 | 4 | 10 | 10 | 202.037 | 52.1415 | 149.8955
9 | 10 | 68.6667 | 4 | 10 | 10 | 202.037 | 52.571 | 149.466
9 | 11 | 68.2083 | 4 | 10 | 10 | 202.037 | 53.7521 | 148.2849
9 | 12 | 67.7917 | 4 | 10 | 10 | 202.037 | 54.8258 | 147.2112
9 | 13 | 69.375 | 4 | 10 | 10 | 202.037 | 50.7457 | 151.2913
9 | 14 | 67.2083 | 4 | 10 | 10 | 202.037 | 56.329 | 145.708
9 | 15 | 66.75 | 4 | 10 | 10 | 202.037 | 57.5101 | 144.5269
9 | 16 | 66.8333 | 4 | 10 | 10 | 202.037 | 57.2954 | 144.7416
9 | 17 | 71.625 | 4 | 10 | 10 | 202.037 | 44.9476 | 157.0894
9 | 18 | 73.125 | 4 | 10 | 10 | 202.037 | 41.0823 | 160.9547
9 | 19 | 69.0417 | 4 | 10 | 10 | 202.037 | 51.6047 | 150.4323
9 | 20 | 67.0833 | 4 | 10 | 10 | 202.037 | 56.6511 | 145.3859
9 | 21 | 66.0833 | 4 | 10 | 10 | 202.037 | 59.2281 | 142.8089
9 | 22 | 67.625 | 4 | 10 | 10 | 202.037 | 55.2553 | 146.7817
9 | 23 | 69.5 | 4 | 10 | 10 | 202.037 | 50.4236 | 151.6134
9 | 24 | 67.6667 | 4 | 10 | 10 | 202.037 | 55.1479 | 146.8891
9 | 25 | 68.25 | 4 | 10 | 10 | 202.037 | 53.6447 | 148.3923
9 | 26 | 66.5417 | 4 | 10 | 10 | 202.037 | 58.047 | 143.99
9 | 27 | 65.9167 | 4 | 10 | 10 | 202.037 | 59.6575 | 142.3795
9 | 28 | 66.7917 | 4 | 10 | 10 | 202.037 | 57.4027 | 144.6343
9 | 29 | 67 | 4 | 10 | 10 | 202.037 | 56.8659 | 145.1711
9 | 30 | 66.7083 | 4 | 10 | 10 | 202.037 | 57.6175 | 144.4195
10 | 1 | 77.5417 | 4 | 10 | 10 | 202.037 | 29.7009 | 172.3361
10 | 2 | 78 | 4 | 10 | 10 | 202.037 | 28.5198 | 173.5172
10 | 3 | 70.0417 | 4 | 10 | 10 | 202.037 | 49.0278 | 153.0092
10 | 4 | 67.9167 | 4 | 10 | 10 | 202.037 | 54.5037 | 147.5333
10 | 5 | 69.625 | 4 | 10 | 10 | 202.037 | 50.1015 | 151.9355
10 | 6 | 71.2917 | 4 | 10 | 10 | 202.037 | 45.8066 | 156.2304
10 | 7 | 68.8333 | 4 | 10 | 10 | 202.037 | 52.1415 | 149.8955
10 | 8 | 69.0417 | 4 | 10 | 10 | 202.037 | 51.6047 | 150.4323
10 | 9 | 67.25 | 4 | 10 | 10 | 202.037 | 56.2217 | 145.8153
10 | 10 | 65.75 | 4 | 10 | 10 | 202.037 | 60.087 | 141.95
10 | 11 | 63.5833 | 4 | 10 | 10 | 202.037 | 65.6703 | 136.3667
10 | 12 | 63.5833 | 4 | 10 | 10 | 202.037 | 65.6703 | 136.3667
10 | 13 | 65.9583 | 4 | 10 | 10 | 202.037 | 59.5502 | 142.4868
10 | 14 | 73.75 | 4 | 10 | 10 | 202.037 | 39.4717 | 162.5653
10 | 15 | 74.5 | 4 | 10 | 10 | 202.037 | 37.539 | 164.498
10 | 16 | 73.125 | 4 | 10 | 10 | 202.037 | 41.0823 | 160.9547
10 | 17 | 75.9167 | 4 | 10 | 10 | 202.037 | 33.8884 | 168.1486
10 | 18 | 74.5417 | 4 | 10 | 10 | 202.037 | 37.4316 | 164.6054
10 | 19 | 68.0833 | 4 | 10 | 10 | 202.037 | 54.0742 | 147.9628
10 | 20 | 68.0833 | 4 | 10 | 10 | 202.037 | 54.0742 | 147.9628
10 | 21 | 66.2917 | 4 | 10 | 10 | 202.037 | 58.6912 | 143.3458
10 | 22 | 65.7083 | 4 | 10 | 10 | 202.037 | 60.1944 | 141.8426
10 | 23 | 64.125 | 4 | 10 | 10 | 202.037 | 64.2745 | 137.7625
10 | 24 | 64.8333 | 4 | 10 | 10 | 202.037 | 62.4492 | 139.5878
10 | 25 | 69.0417 | 4 | 10 | 10 | 202.037 | 51.6047 | 150.4323
10 | 26 | 73.25 | 4 | 10 | 10 | 202.037 | 40.7601 | 161.2769
10 | 27 | 71.5 | 4 | 10 | 10 | 202.037 | 45.2697 | 156.7672
10 | 28 | 68.2083 | 4 | 10 | 10 | 202.037 | 53.7521 | 148.2849
10 | 29 | 63.1667 | 4 | 10 | 10 | 202.037 | 66.7441 | 135.2929
10 | 30 | 60.2917 | 4 | 10 | 10 | 202.037 | 74.1527 | 127.8843
10 | 31 | 62.5 | 4 | 10 | 10 | 202.037 | 68.462 | 133.575
11 | 1 | 72.0833 | 4 | 10 | 10 | 202.037 | 43.7665 | 158.2705
11 | 2 | 63.375 | 4 | 10 | 10 | 202.037 | 66.2072 | 135.8298
11 | 3 | 61.25 | 4 | 10 | 10 | 202.037 | 71.6832 | 130.3538
11 | 4 | 57.5833 | 4 | 10 | 10 | 202.037 | 81.1319 | 120.9051
11 | 5 | 60.4167 | 4 | 10 | 10 | 202.037 | 73.8306 | 128.2064
11 | 6 | 61.875 | 4 | 10 | 10 | 202.037 | 70.0726 | 131.9644
11 | 7 | 63.4583 | 4 | 10 | 10 | 202.037 | 65.9925 | 136.0445
11 | 8 | 61.7083 | 4 | 10 | 10 | 202.037 | 70.5021 | 131.5349
11 | 9 | 62.2917 | 4 | 10 | 10 | 202.037 | 68.9989 | 133.0381
11 | 10 | 62.1667 | 4 | 10 | 10 | 202.037 | 69.321 | 132.716
11 | 11 | 59.625 | 4 | 10 | 10 | 202.037 | 75.8706 | 126.1664
11 | 12 | 59.0833 | 4 | 10 | 10 | 202.037 | 77.2665 | 124.7705
11 | 13 | 59.7917 | 4 | 10 | 10 | 202.037 | 75.4412 | 126.5958
11 | 14 | 60.1667 | 4 | 10 | 10 | 202.037 | 74.4748 | 127.5622
11 | 15 | 68.8333 | 4 | 10 | 10 | 202.037 | 52.1415 | 149.8955
11 | 16 | 66.75 | 4 | 10 | 10 | 202.037 | 57.5101 | 144.5269
11 | 17 | 63.75 | 4 | 10 | 10 | 202.037 | 65.2409 | 136.7961
11 | 18 | 68.4583 | 4 | 10 | 10 | 202.037 | 53.1079 | 148.9291
11 | 19 | 65.3333 | 4 | 10 | 10 | 202.037 | 61.1607 | 140.8763
11 | 20 | 68.875 | 4 | 10 | 10 | 202.037 | 52.0342 | 150.0028
11 | 21 | 68.4583 | 4 | 10 | 10 | 202.037 | 53.1079 | 148.9291
11 | 22 | 66.625 | 4 | 10 | 10 | 202.037 | 57.8322 | 144.2048
11 | 23 | 62.4583 | 4 | 10 | 10 | 202.037 | 68.5694 | 133.4676
11 | 24 | 60.875 | 4 | 10 | 10 | 202.037 | 72.6495 | 129.3875
11 | 25 | 62.0417 | 4 | 10 | 10 | 202.037 | 69.6431 | 132.3939
11 | 26 | 61.5 | 4 | 10 | 10 | 202.037 | 71.0389 | 130.9981
11 | 27 | 58.25 | 4 | 10 | 10 | 202.037 | 79.4139 | 122.6231
11 | 28 | 57.3333 | 4 | 10 | 10 | 202.037 | 81.7761 | 120.2609
11 | 29 | 57.625 | 4 | 10 | 10 | 202.037 | 81.0245 | 121.0125
11 | 30 | 60.6667 | 4 | 10 | 10 | 202.037 | 73.1864 | 128.8506
12 | 1 | 50.25 | 4 | 10 | 10 | 202.037 | 100.0293 | 102.0077
12 | 2 | 50.2917 | 4 | 10 | 10 | 202.037 | 99.9219 | 102.1151
12 | 3 | 51.9167 | 4 | 10 | 10 | 202.037 | 95.7344 | 106.3026
12 | 4 | 50.375 | 4 | 10 | 10 | 202.037 | 99.7071 | 102.3299
12 | 5 | 49.375 | 4 | 10 | 10 | 202.037 | 102.2841 | 99.7529
12 | 6 | 49.7917 | 4 | 10 | 10 | 202.037 | 101.2103 | 100.8267
12 | 7 | 51.4583 | 4 | 10 | 10 | 202.037 | 96.9155 | 105.1215
12 | 8 | 55.25 | 4 | 10 | 10 | 202.037 | 87.1447 | 114.8923
12 | 9 | 55.9167 | 4 | 10 | 10 | 202.037 | 85.4267 | 116.6103
12 | 10 | 62.5833 | 4 | 10 | 10 | 202.037 | 68.2473 | 133.7897
12 | 11 | 65.875 | 4 | 10 | 10 | 202.037 | 59.7649 | 142.2721
12 | 12 | 56.9167 | 4 | 10 | 10 | 202.037 | 82.8498 | 119.1872
12 | 13 | 57.0417 | 4 | 10 | 10 | 202.037 | 82.5277 | 119.5093
12 | 14 | 60.75 | 4 | 10 | 10 | 202.037 | 72.9716 | 129.0654
12 | 15 | 59.5833 | 4 | 10 | 10 | 202.037 | 75.978 | 126.059
12 | 16 | 62.75 | 4 | 10 | 10 | 202.037 | 67.8178 | 134.2192
12 | 17 | 60.875 | 4 | 10 | 10 | 202.037 | 72.6495 | 129.3875
12 | 18 | 60.7083 | 4 | 10 | 10 | 202.037 | 73.079 | 128.958
12 | 19 | 64.375 | 4 | 10 | 10 | 202.037 | 63.6303 | 138.4067
12 | 20 | 57.875 | 4 | 10 | 10 | 202.037 | 80.3803 | 121.6567
12 | 21 | 56.2917 | 4 | 10 | 10 | 202.037 | 84.4604 | 117.5766
12 | 22 | 54.25 | 4 | 10 | 10 | 202.037 | 89.7216 | 112.3154
12 | 23 | 53.7917 | 4 | 10 | 10 | 202.037 | 90.9027 | 111.1343
12 | 24 | 53.625 | 4 | 10 | 10 | 202.037 | 91.3322 | 110.7048
12 | 25 | 52.9167 | 4 | 10 | 10 | 202.037 | 93.1575 | 108.8795
12 | 26 | 53.875 | 4 | 10 | 10 | 202.037 | 90.6879 | 111.3491
12 | 27 | 57.875 | 4 | 10 | 10 | 202.037 | 80.3803 | 121.6567
12 | 28 | 57.125 | 4 | 10 | 10 | 202.037 | 82.3129 | 119.7241
12 | 29 | 55.7917 | 4 | 10 | 10 | 202.037 | 85.7488 | 116.2882
12 | 30 | 53.2083 | 4 | 10 | 10 | 202.037 | 92.4059 | 109.6311
12 | 31 | 53.2083 | 4 | 10 | 10 | 202.037 | 92.4059 | 109.6311
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083
51.7083
55.1667
51.4583
50.0833
53.9583
54.8333
54.4583
53.7083
56.75
59
57.875
55.875
59.2917
64.7917
57.9167
56.7083
55.6667
55.4583
55
53.9167
56.5833
61.75
56.0417
52.7917
54.5
53.25
54.25
56.3333
55.375
53.1667
55.875
51.4583
51.2917
52.0833
53.625
50.5833
49.8333
53.5417
55.9583
62.0833
59.4167
57.8333
60
52.9583
52.375
53.375
53.375
53.125
53.625
54.75
54.75
54.5417
53.2917
52
54.3333
54.5833
61.625
63.5417
57.5833
58.4167
59.1667
59.9167
62.625
63.0417
66.0833
66.5417
69.5417
71.5417
66.5
63.9583
66.875
63.5
62.7917
66.2083
72.4583
66.625
63.9167
63.75
62.2917
62.75
61.0833
61.8333
62.375
62.2083
62.375
61.2083
61.9167
63.125
62.5417
60
68.2917
61.4583
60.25
61.25
61.2917
61.875
57.7917
52.7083
53.25
56.7083
60.1667
59.0833
57.9583
62.5833
70.125
72.9167
65.7083
63.1667
63.4583
60.875
62.1667
61
61.8333
59.9167
63.2917
65.4167
66.875
67.2083
63.5417
67.9583
67.0417
67.1667
65.625
62.875
61.7917
58.5417
54.9167
60.3333
61.6667
63.25
62.625
61.7917
62.5
61.0417
58.875
59.625
60.7083
64.375
69.0833
72.1667
65.7917
56.625
63.1667
61.8333
62.6667
63.9583
62.6667
64.1667
63.2083
62.5417
62.125
70
68.0417
69.0417
68.0833
65.7917
64.7083
65.9583
66.625
66.9583
68.5
69.2917
66.625
67.625
68.125
67.2917
67.875
69.7083
70.75
71.7083
73.125
71.4167
70.0833
67.9583
69.7917
68.875
71.6667
72.375
72.0833
72.375
76.1667
74.2083
70.0417
69.25
70.5417
73.5
75.7917
74.125
72.25
69.6667
70.0833
70.0417
69.25
69.25
66.875
67.625
68.25
69.2917
71.9583
71.5417
68.5
67.4167
68.1667
68.5417
67.4167
71.5417
72.3333
71
71.6667
68.9583
67.5
69.7917
69.9167
71.125
71.3333
71.125
72.125
72.8333
73.3333
72.3333
71.125
70.4167
69.75
69.4167
70.75
71.9583
71.125
71.4583
70.8333
69.5
68.6667
68.8333
71.0833
71.5833
69.4583
68.9583
71.875
71.9167
70.9583
68.25
70.4583
71.2917
70.375
71.7083
75.75
76.5
76
74.4167
73.2083
71.3333
69.1667
68.8333
68.6667
68.2083
67.7917
69.375
67.2083
66.75
66.8333
71.625
73.125
69.0417
67.0833
66.0833
67.625
69.5
67.6667
68.25
66.5417
65.9167
66.7917
67
66.7083
77.5417
78
70.0417
67.9167
69.625
71.2917
68.8333
69.0417
67.25
65.75
63.5833
63.5833
65.9583
73.75
74.5
73.125
75.9167
74.5417
68.0833
68.0833
66.2917
65.7083
64.125
64.8333
69.0417
73.25
71.5
68.2083
63.1667
60.2917
62.5
72.0833
63.375
61.25
57.5833
60.4167
61.875
63.4583
61.7083
62.2917
62.1667
59.625
59.0833
59.7917
60.1667
68.8333
66.75
63.75
68.4583
65.3333
68.875
68.4583
66.625
62.4583
60.875
62.0417
61.5
58.25
57.3333
57.625
60.6667
50.25
50.2917
51.9167
50.375
49.375
49.7917
51.4583
55.25
55.9167
62.5833
65.875
56.9167
57.0417
60.75
59.5833
62.75
60.875
60.7083
64.375
57.875
56.2917
54.25
53.7917
53.625
52.9167
53.875
57.875
57.125
55.7917
53.2083
53.2083

## Sensitivity Analysis_CZ15
Month | Day | Average Daily Temperature (deg F) | Size Category | Baseline Heater Size (kW) | New Heater Size (kW) | Baseline Daily kWh | Treatment Daily kWh | Daily kWh Savings | Size Category | Average Energy Savings (kWh/day) | # of Operating Days | Annual Energy Savings (kWh/year) | Original Savings Methodology Savings (kWh/year) | % Difference
1 | 1 | 48.5 | 1 | 1 | 1 | 20.2037 | 10.2188 | 9.9849 | 1 | 13.7761 | 334 | 4601.211 | 4602.2934 | 0.02352%
1 | 2 | 50.5833 | 1 | 1 | 1 | 20.2037 | 9.9345 | 10.2692 | 2 | 11.3236 | 334 | 3782.0918 | 3783.1497 | 0.02796%
1 | 3 | 54.8333 | 1 | 1 | 1 | 20.2037 | 9.3544 | 10.8493 | 3 | 24.1453 | 334 | 8064.5416 | 8067.3876 | 0.03528%
1 | 4 | 50 | 1 | 1 | 1 | 20.2037 | 10.0141 | 10.1896 | 4 | 169.0753 | 334 | 56471.1394 | 56491.5758 | 0.03618%
1 | 5 | 52.0417 | 1 | 1 | 1 | 20.2037 | 9.7354 | 10.4683
1 | 6 | 52.0417 | 1 | 1 | 1 | 20.2037 | 9.7354 | 10.4683
1 | 7 | 56 | 1 | 1 | 1 | 20.2037 | 9.1951 | 11.0086
1 | 8 | 56.4167 | 1 | 1 | 1 | 20.2037 | 9.1383 | 11.0654
1 | 9 | 62 | 1 | 1 | 1 | 20.2037 | 8.3762 | 11.8275
1 | 10 | 64.5417 | 1 | 1 | 1 | 20.2037 | 8.0293 | 12.1744
1 | 11 | 63.25 | 1 | 1 | 1 | 20.2037 | 8.2056 | 11.9981
1 | 12 | 61.5833 | 1 | 1 | 1 | 20.2037 | 8.4331 | 11.7706
1 | 13 | 65.0833 | 1 | 1 | 1 | 20.2037 | 7.9554 | 12.2483
1 | 14 | 68.5833 | 1 | 1 | 1 | 20.2037 | 7.4776 | 12.7261
1 | 15 | 60.4583 | 1 | 1 | 1 | 20.2037 | 8.5866 | 11.6171
1 | 16 | 62.7083 | 1 | 1 | 1 | 20.2037 | 8.2795 | 11.9242
1 | 17 | 62.125 | 1 | 1 | 1 | 20.2037 | 8.3591 | 11.8446
1 | 18 | 59.3333 | 1 | 1 | 1 | 20.2037 | 8.7402 | 11.4635
1 | 19 | 61.0833 | 1 | 1 | 1 | 20.2037 | 8.5013 | 11.7024
1 | 20 | 57.3333 | 1 | 1 | 1 | 20.2037 | 9.0132 | 11.1905
1 | 21 | 59.1667 | 1 | 1 | 1 | 20.2037 | 8.7629 | 11.4408
1 | 22 | 62.75 | 1 | 1 | 1 | 20.2037 | 8.2738 | 11.9299
1 | 23 | 61.0417 | 1 | 1 | 1 | 20.2037 | 8.507 | 11.6967
1 | 24 | 53.9583 | 1 | 1 | 1 | 20.2037 | 9.4738 | 10.7299
1 | 25 | 56.7917 | 1 | 1 | 1 | 20.2037 | 9.0871 | 11.1166
1 | 26 | 54.2917 | 1 | 1 | 1 | 20.2037 | 9.4283 | 10.7754
1 | 27 | 55.5833 | 1 | 1 | 1 | 20.2037 | 9.252 | 10.9517
1 | 28 | 58.625 | 1 | 1 | 1 | 20.2037 | 8.8369 | 11.3668
1 | 29 | 59.5 | 1 | 1 | 1 | 20.2037 | 8.7174 | 11.4863
1 | 30 | 59.25 | 1 | 1 | 1 | 20.2037 | 8.7515 | 11.4522
1 | 31 | 59.25 | 1 | 1 | 1 | 20.2037 | 8.7515 | 11.4522
2 | 1 | 51.25 | 1 | 1 | 1 | 20.2037 | 9.8435 | 10.3602
2 | 2 | 53.7917 | 1 | 1 | 1 | 20.2037 | 9.4966 | 10.7071
2 | 3 | 57.3333 | 1 | 1 | 1 | 20.2037 | 9.0132 | 11.1905
2 | 4 | 54.2083 | 1 | 1 | 1 | 20.2037 | 9.4397 | 10.764
2 | 5 | 52.4583 | 1 | 1 | 1 | 20.2037 | 9.6785 | 10.5252
2 | 6 | 50.625 | 1 | 1 | 1 | 20.2037 | 9.9288 | 10.2749
2 | 7 | 55.4583 | 1 | 1 | 1 | 20.2037 | 9.2691 | 10.9346
2 | 8 | 58.625 | 1 | 1 | 1 | 20.2037 | 8.8369 | 11.3668
2 | 9 | 64.5833 | 1 | 1 | 1 | 20.2037 | 8.0236 | 12.1801
2 | 10 | 66.8333 | 1 | 1 | 1 | 20.2037 | 7.7165 | 12.4872
2 | 11 | 70.2083 | 1 | 1 | 1 | 20.2037 | 7.2558 | 12.9479
2 | 12 | 71.0417 | 1 | 1 | 1 | 20.2037 | 7.1421 | 13.0616
2 | 13 | 63.9583 | 1 | 1 | 1 | 20.2037 | 8.1089 | 12.0948
2 | 14 | 50.7083 | 1 | 1 | 1 | 20.2037 | 9.9174 | 10.2863
2 | 15 | 58.6667 | 1 | 1 | 1 | 20.2037 | 8.8312 | 11.3725
2 | 16 | 59.7917 | 1 | 1 | 1 | 20.2037 | 8.6776 | 11.5261
2 | 17 | 60.125 | 1 | 1 | 1 | 20.2037 | 8.6321 | 11.5716
2 | 18 | 62.6667 | 1 | 1 | 1 | 20.2037 | 8.2852 | 11.9185
2 | 19 | 60.9167 | 1 | 1 | 1 | 20.2037 | 8.5241 | 11.6796
2 | 20 | 59.125 | 1 | 1 | 1 | 20.2037 | 8.7686 | 11.4351
2 | 21 | 58.0417 | 1 | 1 | 1 | 20.2037 | 8.9165 | 11.2872
2 | 22 | 56.9167 | 1 | 1 | 1 | 20.2037 | 9.07 | 11.1337
2 | 23 | 56.5 | 1 | 1 | 1 | 20.2037 | 9.1269 | 11.0768
2 | 24 | 60.9583 | 1 | 1 | 1 | 20.2037 | 8.5184 | 11.6853
2 | 25 | 63.75 | 1 | 1 | 1 | 20.2037 | 8.1373 | 12.0664
2 | 26 | 68.4583 | 1 | 1 | 1 | 20.2037 | 7.4947 | 12.709
2 | 27 | 69.8333 | 1 | 1 | 1 | 20.2037 | 7.307 | 12.8967
2 | 28 | 69.9167 | 1 | 1 | 1 | 20.2037 | 7.2956 | 12.9081
3 | 1 | 58.625 | 1 | 1 | 1 | 20.2037 | 8.8369 | 11.3668
3 | 2 | 60.375 | 1 | 1 | 1 | 20.2037 | 8.598 | 11.6057
3 | 3 | 66.625 | 1 | 1 | 1 | 20.2037 | 7.7449 | 12.4588
3 | 4 | 68.25 | 1 | 1 | 1 | 20.2037 | 7.5231 | 12.6806
3 | 5 | 73.75 | 1 | 1 | 1 | 20.2037 | 6.7724 | 13.4313
3 | 6 | 76.0417 | 1 | 1 | 1 | 20.2037 | 6.4596 | 13.7441
3 | 7 | 74.2917 | 1 | 1 | 1 | 20.2037 | 6.6985 | 13.5052
3 | 8 | 75.7083 | 1 | 1 | 1 | 20.2037 | 6.5051 | 13.6986
3 | 9 | 73.5833 | 1 | 1 | 1 | 20.2037 | 6.7952 | 13.4085
3 | 10 | 73.3333 | 1 | 1 | 1 | 20.2037 | 6.8293 | 13.3744
3 | 11 | 72.3333 | 1 | 1 | 1 | 20.2037 | 6.9658 | 13.2379
3 | 12 | 70.0417 | 1 | 1 | 1 | 20.2037 | 7.2786 | 12.9251
3 | 13 | 69.7083 | 1 | 1 | 1 | 20.2037 | 7.3241 | 12.8796
3 | 14 | 73.0417 | 1 | 1 | 1 | 20.2037 | 6.8691 | 13.3346
3 | 15 | 76.3333 | 1 | 1 | 1 | 20.2037 | 6.4198 | 13.7839
3 | 16 | 76.6667 | 1 | 1 | 1 | 20.2037 | 6.3743 | 13.8294
3 | 17 | 75.4167 | 1 | 1 | 1 | 20.2037 | 6.5449 | 13.6588
3 | 18 | 72.8333 | 1 | 1 | 1 | 20.2037 | 6.8975 | 13.3062
3 | 19 | 70.4583 | 1 | 1 | 1 | 20.2037 | 7.2217 | 12.982
3 | 20 | 71.3333 | 1 | 1 | 1 | 20.2037 | 7.1023 | 13.1014
3 | 21 | 71.0833 | 1 | 1 | 1 | 20.2037 | 7.1364 | 13.0673
3 | 22 | 69.625 | 1 | 1 | 1 | 20.2037 | 7.3355 | 12.8682
3 | 23 | 73.8333 | 1 | 1 | 1 | 20.2037 | 6.7611 | 13.4426
3 | 24 | 75.6667 | 1 | 1 | 1 | 20.2037 | 6.5108 | 13.6929
3 | 25 | 72.8333 | 1 | 1 | 1 | 20.2037 | 6.8975 | 13.3062
3 | 26 | 68.375 | 1 | 1 | 1 | 20.2037 | 7.5061 | 12.6976
3 | 27 | 65.7083 | 1 | 1 | 1 | 20.2037 | 7.87 | 12.3337
3 | 28 | 69.2917 | 1 | 1 | 1 | 20.2037 | 7.381 | 12.8227
3 | 29 | 74.2917 | 1 | 1 | 1 | 20.2037 | 6.6985 | 13.5052
3 | 30 | 72.75 | 1 | 1 | 1 | 20.2037 | 6.9089 | 13.2948
3 | 31 | 69 | 1 | 1 | 1 | 20.2037 | 7.4208 | 12.7829
4 | 1 | 87.4167 | 1 | 1 | 1 | 20.2037 | 4.9071 | 15.2966
4 | 2 | 78.4167 | 1 | 1 | 1 | 20.2037 | 6.1355 | 14.0682
4 | 3 | 70.6667 | 1 | 1 | 1 | 20.2037 | 7.1933 | 13.0104
4 | 4 | 74.2917 | 1 | 1 | 1 | 20.2037 | 6.6985 | 13.5052
4 | 5 | 75.5417 | 1 | 1 | 1 | 20.2037 | 6.5279 | 13.6758
4 | 6 | 69.3333 | 1 | 1 | 1 | 20.2037 | 7.3753 | 12.8284
4 | 7 | 65.5 | 1 | 1 | 1 | 20.2037 | 7.8985 | 12.3052
4 | 8 | 55.0833 | 1 | 1 | 1 | 20.2037 | 9.3203 | 10.8834
4 | 9 | 57.3333 | 1 | 1 | 1 | 20.2037 | 9.0132 | 11.1905
4 | 10 | 63.7917 | 1 | 1 | 1 | 20.2037 | 8.1317 | 12.072
4 | 11 | 69.375 | 1 | 1 | 1 | 20.2037 | 7.3696 | 12.8341
4 | 12 | 72.5833 | 1 | 1 | 1 | 20.2037 | 6.9317 | 13.272
4 | 13 | 67.625 | 1 | 1 | 1 | 20.2037 | 7.6084 | 12.5953
4 | 14 | 70.6667 | 1 | 1 | 1 | 20.2037 | 7.1933 | 13.0104
4 | 15 | 76.5833 | 1 | 1 | 1 | 20.2037 | 6.3857 | 13.818
4 | 16 | 84.0417 | 1 | 1 | 1 | 20.2037 | 5.3677 | 14.836
4 | 17 | 83.5417 | 1 | 1 | 1 | 20.2037 | 5.436 | 14.7677
4 | 18 | 74.8333 | 1 | 1 | 1 | 20.2037 | 6.6246 | 13.5791
4 | 19 | 73.5 | 1 | 1 | 1 | 20.2037 | 6.8066 | 13.3971
4 | 20 | 72.875 | 1 | 1 | 1 | 20.2037 | 6.8919 | 13.3118
4 | 21 | 73.1667 | 1 | 1 | 1 | 20.2037 | 6.852 | 13.3517
4 | 22 | 72.4167 | 1 | 1 | 1 | 20.2037 | 6.9544 | 13.2493
4 | 23 | 74.1667 | 1 | 1 | 1 | 20.2037 | 6.7156 | 13.4881
4 | 24 | 71.5417 | 1 | 1 | 1 | 20.2037 | 7.0738 | 13.1299
4 | 25 | 75.6667 | 1 | 1 | 1 | 20.2037 | 6.5108 | 13.6929
4 | 26 | 76.5833 | 1 | 1 | 1 | 20.2037 | 6.3857 | 13.818
4 | 27 | 77.875 | 1 | 1 | 1 | 20.2037 | 6.2094 | 13.9943
4 | 28 | 80.75 | 1 | 1 | 1 | 20.2037 | 5.817 | 14.3867
4 | 29 | 75.7917 | 1 | 1 | 1 | 20.2037 | 6.4938 | 13.7099
4 | 30 | 71.4583 | 1 | 1 | 1 | 20.2037 | 7.0852 | 13.1185
5 | 1 | 85.875 | 1 | 1 | 1 | 20.2037 | 5.1175 | 15.0862
5 | 2 | 90.9167 | 1 | 1 | 1 | 20.2037 | 4.4293 | 15.7744
5 | 3 | 93.4167 | 1 | 1 | 1 | 20.2037 | 4.0881 | 16.1156
5 | 4 | 92.875 | 1 | 1 | 1 | 20.2037 | 4.162 | 16.0417
5 | 5 | 88.8333 | 1 | 1 | 1 | 20.2037 | 4.7137 | 15.49
5 | 6 | 70.875 | 1 | 1 | 1 | 20.2037 | 7.1648 | 13.0389
5 | 7 | 60.1667 | 1 | 1 | 1 | 20.2037 | 8.6264 | 11.5773
5 | 8 | 73.4583 | 1 | 1 | 1 | 20.2037 | 6.8122 | 13.3915
5 | 9 | 68.5833 | 1 | 1 | 1 | 20.2037 | 7.4776 | 12.7261
5 | 10 | 73.4583 | 1 | 1 | 1 | 20.2037 | 6.8122 | 13.3915
5 | 11 | 79.5 | 1 | 1 | 1 | 20.2037 | 5.9876 | 14.2161
5 | 12 | 83.5 | 1 | 1 | 1 | 20.2037 | 5.4416 | 14.7621
5 | 13 | 77.7917 | 1 | 1 | 1 | 20.2037 | 6.2208 | 13.9829
5 | 14 | 75.25 | 1 | 1 | 1 | 20.2037 | 6.5677 | 13.636
5 | 15 | 69.5 | 1 | 1 | 1 | 20.2037 | 7.3525 | 12.8512
5 | 16 | 70.25 | 1 | 1 | 1 | 20.2037 | 7.2501 | 12.9536
5 | 17 | 71.125 | 1 | 1 | 1 | 20.2037 | 7.1307 | 13.073
5 | 18 | 79.375 | 1 | 1 | 1 | 20.2037 | 6.0047 | 14.199
5 | 19 | 82.25 | 1 | 1 | 1 | 20.2037 | 5.6123 | 14.5914
5 | 20 | 87.75 | 1 | 1 | 1 | 20.2037 | 4.8616 | 15.3421
5 | 21 | 93.625 | 1 | 1 | 1 | 20.2037 | 4.0597 | 16.144
5 | 22 | 95.2917 | 1 | 1 | 1 | 20.2037 | 3.8322 | 16.3715
5 | 23 | 97.375 | 1 | 1 | 1 | 20.2037 | 3.5478 | 16.6559
5 | 24 | 91.875 | 1 | 1 | 1 | 20.2037 | 4.2985 | 15.9052
5 | 25 | 81.0417 | 1 | 1 | 1 | 20.2037 | 5.7772 | 14.4265
5 | 26 | 77.5833 | 1 | 1 | 1 | 20.2037 | 6.2492 | 13.9545
5 | 27 | 81.7917 | 1 | 1 | 1 | 20.2037 | 5.6748 | 14.5289
5 | 28 | 89.0417 | 1 | 1 | 1 | 20.2037 | 4.6853 | 15.5184
5 | 29 | 91.4583 | 1 | 1 | 1 | 20.2037 | 4.3554 | 15.8483
5 | 30 | 86.8333 | 1 | 1 | 1 | 20.2037 | 4.9867 | 15.217
5 | 31 | 81.7083 | 1 | 1 | 1 | 20.2037 | 5.6862 | 14.5175
6 | 1 | 94.2917 | 1 | 1 | 1 | 20.2037 | 3.9687 | 16.235
6 | 2 | 91.7083 | 1 | 1 | 1 | 20.2037 | 4.3213 | 15.8824
6 | 3 | 88.0417 | 1 | 1 | 1 | 20.2037 | 4.8217 | 15.382
6 | 4 | 86 | 1 | 1 | 1 | 20.2037 | 5.1004 | 15.1033
6 | 5 | 89.4167 | 1 | 1 | 1 | 20.2037 | 4.6341 | 15.5696
6 | 6 | 92 | 1 | 1 | 1 | 20.2037 | 4.2815 | 15.9222
6 | 7 | 95.125 | 1 | 1 | 1 | 20.2037 | 3.8549 | 16.3488
6 | 8 | 91.0833 | 1 | 1 | 1 | 20.2037 | 4.4066 | 15.7971
6 | 9 | 89.3333 | 1 | 1 | 1 | 20.2037 | 4.6454 | 15.5583
6 | 10 | 87.2083 | 1 | 1 | 1 | 20.2037 | 4.9355 | 15.2682
6 | 11 | 92.25 | 1 | 1 | 1 | 20.2037 | 4.2473 | 15.9564
6 | 12 | 90.7917 | 1 | 1 | 1 | 20.2037 | 4.4464 | 15.7573
6 | 13 | 91.5833 | 1 | 1 | 1 | 20.2037 | 4.3383 | 15.8654
6 | 14 | 89.6667 | 1 | 1 | 1 | 20.2037 | 4.5999 | 15.6038
6 | 15 | 88.5833 | 1 | 1 | 1 | 20.2037 | 4.7478 | 15.4559
6 | 16 | 88.875 | 1 | 1 | 1 | 20.2037 | 4.708 | 15.4957
6 | 17 | 91.75 | 1 | 1 | 1 | 20.2037 | 4.3156 | 15.8881
6 | 18 | 91.375 | 1 | 1 | 1 | 20.2037 | 4.3668 | 15.8369
6 | 19 | 89.0417 | 1 | 1 | 1 | 20.2037 | 4.6853 | 15.5184
6 | 20 | 88.875 | 1 | 1 | 1 | 20.2037 | 4.708 | 15.4957
6 | 21 | 88.875 | 1 | 1 | 1 | 20.2037 | 4.708 | 15.4957
6 | 22 | 89.5417 | 1 | 1 | 1 | 20.2037 | 4.617 | 15.5867
6 | 23 | 87.5417 | 1 | 1 | 1 | 20.2037 | 4.89 | 15.3137
6 | 24 | 83.2917 | 1 | 1 | 1 | 20.2037 | 5.4701 | 14.7336
6 | 25 | 88.6667 | 1 | 1 | 1 | 20.2037 | 4.7364 | 15.4673
6 | 26 | 93.3333 | 1 | 1 | 1 | 20.2037 | 4.0995 | 16.1042
6 | 27 | 97.1667 | 1 | 1 | 1 | 20.2037 | 3.5763 | 16.6274
6 | 28 | 102.375 | 1 | 1 | 1 | 20.2037 | 2.8654 | 17.3383
6 | 29 | 104.3333 | 1 | 1 | 1 | 20.2037 | 2.5981 | 17.6056
6 | 30 | 99.6667 | 1 | 1 | 1 | 20.2037 | 3.235 | 16.9687
7 | 1 | 98.625 | 1 | 1 | 1 | 20.2037 | 3.3772 | 16.8265
7 | 2 | 101.25 | 1 | 1 | 1 | 20.2037 | 3.0189 | 17.1848
7 | 3 | 93.8333 | 1 | 1 | 1 | 20.2037 | 4.0312 | 16.1725
7 | 4 | 94.7083 | 1 | 1 | 1 | 20.2037 | 3.9118 | 16.2919
7 | 5 | 95.75 | 1 | 1 | 1 | 20.2037 | 3.7696 | 16.4341
7 | 6 | 91.2083 | 1 | 1 | 1 | 20.2037 | 4.3895 | 15.8142
7 | 7 | 97.125 | 1 | 1 | 1 | 20.2037 | 3.582 | 16.6217
7 | 8 | 98.3333 | 1 | 1 | 1 | 20.2037 | 3.417 | 16.7867
7 | 9 | 98.7083 | 1 | 1 | 1 | 20.2037 | 3.3658 | 16.8379
7 | 10 | 95.0417 | 1 | 1 | 1 | 20.2037 | 3.8663 | 16.3374
7 | 11 | 90.4583 | 1 | 1 | 1 | 20.2037 | 4.4919 | 15.7118
7 | 12 | 87.8333 | 1 | 1 | 1 | 20.2037 | 4.8502 | 15.3535
7 | 13 | 84.75 | 1 | 1 | 1 | 20.2037 | 5.271 | 14.9327
7 | 14 | 83.9167 | 1 | 1 | 1 | 20.2037 | 5.3848 | 14.8189
7 | 15 | 84.375 | 1 | 1 | 1 | 20.2037 | 5.3222 | 14.8815
7 | 16 | 86 | 1 | 1 | 1 | 20.2037 | 5.1004 | 15.1033
7 | 17 | 91.5417 | 1 | 1 | 1 | 20.2037 | 4.344 | 15.8597
7 | 18 | 94.75 | 1 | 1 | 1 | 20.2037 | 3.9061 | 16.2976
7 | 19 | 97.1667 | 1 | 1 | 1 | 20.2037 | 3.5763 | 16.6274
7 | 20 | 96.875 | 1 | 1 | 1 | 20.2037 | 3.6161 | 16.5876
7 | 21 | 93.7917 | 1 | 1 | 1 | 20.2037 | 4.0369 | 16.1668
7 | 22 | 91 | 1 | 1 | 1 | 20.2037 | 4.418 | 15.7857
7 | 23 | 90.625 | 1 | 1 | 1 | 20.2037 | 4.4691 | 15.7346
7 | 24 | 91.0417 | 1 | 1 | 1 | 20.2037 | 4.4123 | 15.7914
7 | 25 | 95.9167 | 1 | 1 | 1 | 20.2037 | 3.7469 | 16.4568
7 | 26 | 95.9583 | 1 | 1 | 1 | 20.2037 | 3.7412 | 16.4625
7 | 27 | 90.9167 | 1 | 1 | 1 | 20.2037 | 4.4293 | 15.7744
7 | 28 | 93.4167 | 1 | 1 | 1 | 20.2037 | 4.0881 | 16.1156
7 | 29 | 94.9583 | 1 | 1 | 1 | 20.2037 | 3.8777 | 16.326
7 | 30 | 96.2083 | 1 | 1 | 1 | 20.2037 | 3.7071 | 16.4966
7 | 31 | 89.375 | 1 | 1 | 1 | 20.2037 | 4.6398 | 15.5639
8 | 1 | 99 | 1 | 1 | 1 | 20.2037 | 3.326 | 16.8777
8 | 2 | 95.2917 | 1 | 1 | 1 | 20.2037 | 3.8322 | 16.3715
8 | 3 | 92.25 | 1 | 1 | 1 | 20.2037 | 4.2473 | 15.9564
8 | 4 | 92.3333 | 1 | 1 | 1 | 20.2037 | 4.236 | 15.9677
8 | 5 | 96.2917 | 1 | 1 | 1 | 20.2037 | 3.6957 | 16.508
8 | 6 | 97.7917 | 1 | 1 | 1 | 20.2037 | 3.491 | 16.7127
8 | 7 | 93.4583 | 1 | 1 | 1 | 20.2037 | 4.0824 | 16.1213
8 | 8 | 92.5417 | 1 | 1 | 1 | 20.2037 | 4.2075 | 15.9962
8 | 9 | 94.8333 | 1 | 1 | 1 | 20.2037 | 3.8947 | 16.309
8 | 10 | 94.7083 | 1 | 1 | 1 | 20.2037 | 3.9118 | 16.2919
8 | 11 | 94.875 | 1 | 1 | 1 | 20.2037 | 3.8891 | 16.3146
8 | 12 | 94.5 | 1 | 1 | 1 | 20.2037 | 3.9402 | 16.2635
8 | 13 | 93.125 | 1 | 1 | 1 | 20.2037 | 4.1279 | 16.0758
8 | 14 | 93.25 | 1 | 1 | 1 | 20.2037 | 4.1109 | 16.0928
8 | 15 | 95.4583 | 1 | 1 | 1 | 20.2037 | 3.8094 | 16.3943
8 | 16 | 95 | 1 | 1 | 1 | 20.2037 | 3.872 | 16.3317
8 | 17 | 93.625 | 1 | 1 | 1 | 20.2037 | 4.0597 | 16.144
8 | 18 | 93.1667 | 1 | 1 | 1 | 20.2037 | 4.1222 | 16.0815
8 | 19 | 92 | 1 | 1 | 1 | 20.2037 | 4.2815 | 15.9222
8 | 20 | 90.4167 | 1 | 1 | 1 | 20.2037 | 4.4976 | 15.7061
8 | 21 | 91.9167 | 1 | 1 | 1 | 20.2037 | 4.2928 | 15.9109
8 | 22 | 91.4583 | 1 | 1 | 1 | 20.2037 | 4.3554 | 15.8483
8 | 23 | 93.4583 | 1 | 1 | 1 | 20.2037 | 4.0824 | 16.1213
8 | 24 | 94.625 | 1 | 1 | 1 | 20.2037 | 3.9232 | 16.2805
8 | 25 | 92.6667 | 1 | 1 | 1 | 20.2037 | 4.1905 | 16.0132
8 | 26 | 90.0833 | 1 | 1 | 1 | 20.2037 | 4.5431 | 15.6606
8 | 27 | 95 | 1 | 1 | 1 | 20.2037 | 3.872 | 16.3317
8 | 28 | 94.2917 | 1 | 1 | 1 | 20.2037 | 3.9687 | 16.235
8 | 29 | 93.2083 | 1 | 1 | 1 | 20.2037 | 4.1165 | 16.0872
8 | 30 | 86.2083 | 1 | 1 | 1 | 20.2037 | 5.072 | 15.1317
8 | 31 | 88.5 | 1 | 1 | 1 | 20.2037 | 4.7592 | 15.4445
9 | 1 | 98.4583 | 1 | 1 | 1 | 20.2037 | 3.4 | 16.8037
9 | 2 | 92.4167 | 1 | 1 | 1 | 20.2037 | 4.2246 | 15.9791
9 | 3 | 91.5417 | 1 | 1 | 1 | 20.2037 | 4.344 | 15.8597
9 | 4 | 92.875 | 1 | 1 | 1 | 20.2037 | 4.162 | 16.0417
9 | 5 | 95.25 | 1 | 1 | 1 | 20.2037 | 3.8379 | 16.3658
9 | 6 | 93.1667 | 1 | 1 | 1 | 20.2037 | 4.1222 | 16.0815
9 | 7 | 90.0417 | 1 | 1 | 1 | 20.2037 | 4.5488 | 15.6549
9 | 8 | 88.3333 | 1 | 1 | 1 | 20.2037 | 4.7819 | 15.4218
9 | 9 | 86.4167 | 1 | 1 | 1 | 20.2037 | 5.0435 | 15.1602
9 | 10 | 86.75 | 1 | 1 | 1 | 20.2037 | 4.998 | 15.2057
9 | 11 | 93.5 | 1 | 1 | 1 | 20.2037 | 4.0767 | 16.127
9 | 12 | 93.5833 | 1 | 1 | 1 | 20.2037 | 4.0654 | 16.1383
9 | 13 | 91.5833 | 1 | 1 | 1 | 20.2037 | 4.3383 | 15.8654
9 | 14 | 84.875 | 1 | 1 | 1 | 20.2037 | 5.254 | 14.9497
9 | 15 | 78.125 | 1 | 1 | 1 | 20.2037 | 6.1753 | 14.0284
9 | 16 | 79.75 | 1 | 1 | 1 | 20.2037 | 5.9535 | 14.2502
9 | 17 | 85.4583 | 1 | 1 | 1 | 20.2037 | 5.1743 | 15.0294
9 | 18 | 86.9167 | 1 | 1 | 1 | 20.2037 | 4.9753 | 15.2284
9 | 19 | 85.0833 | 1 | 1 | 1 | 20.2037 | 5.2255 | 14.9782
9 | 20 | 83.8333 | 1 | 1 | 1 | 20.2037 | 5.3961 | 14.8076
9 | 21 | 82.2083 | 1 | 1 | 1 | 20.2037 | 5.6179 | 14.5858
9 | 22 | 79.625 | 1 | 1 | 1 | 20.2037 | 5.9705 | 14.2332
9 | 23 | 81.25 | 1 | 1 | 1 | 20.2037 | 5.7487 | 14.455
9 | 24 | 82.75 | 1 | 1 | 1 | 20.2037 | 5.544 | 14.6597
9 | 25 | 88.0833 | 1 | 1 | 1 | 20.2037 | 4.8161 | 15.3876
9 | 26 | 89.5417 | 1 | 1 | 1 | 20.2037 | 4.617 | 15.5867
9 | 27 | 89.5833 | 1 | 1 | 1 | 20.2037 | 4.6113 | 15.5924
9 | 28 | 91.2083 | 1 | 1 | 1 | 20.2037 | 4.3895 | 15.8142
9 | 29 | 90.5833 | 1 | 1 | 1 | 20.2037 | 4.4748 | 15.7289
9 | 30 | 88.7917 | 1 | 1 | 1 | 20.2037 | 4.7194 | 15.4843
10 | 1 | 96.0833 | 1 | 1 | 1 | 20.2037 | 3.7241 | 16.4796
10 | 2 | 94.875 | 1 | 1 | 1 | 20.2037 | 3.8891 | 16.3146
10 | 3 | 90.375 | 1 | 1 | 1 | 20.2037 | 4.5033 | 15.7004
10 | 4 | 85.625 | 1 | 1 | 1 | 20.2037 | 5.1516 | 15.0521
10 | 5 | 83.4583 | 1 | 1 | 1 | 20.2037 | 5.4473 | 14.7564
10 | 6 | 83.2917 | 1 | 1 | 1 | 20.2037 | 5.4701 | 14.7336
10 | 7 | 83.625 | 1 | 1 | 1 | 20.2037 | 5.4246 | 14.7791
10 | 8 | 82.375 | 1 | 1 | 1 | 20.2037 | 5.5952 | 14.6085
10 | 9 | 79 | 1 | 1 | 1 | 20.2037 | 6.0559 | 14.1478
10 | 10 | 74.625 | 1 | 1 | 1 | 20.2037 | 6.653 | 13.5507
10 | 11 | 69.6667 | 1 | 1 | 1 | 20.2037 | 7.3298 | 12.8739
10 | 12 | 68.375 | 1 | 1 | 1 | 20.2037 | 7.5061 | 12.6976
10 | 13 | 73.1667 | 1 | 1 | 1 | 20.2037 | 6.852 | 13.3517
10 | 14 | 82.5417 | 1 | 1 | 1 | 20.2037 | 5.5724 | 14.6313
10 | 15 | 85.3333 | 1 | 1 | 1 | 20.2037 | 5.1914 | 15.0123
10 | 16 | 84.5833 | 1 | 1 | 1 | 20.2037 | 5.2938 | 14.9099
10 | 17 | 81.2083 | 1 | 1 | 1 | 20.2037 | 5.7544 | 14.4493
10 | 18 | 81.3333 | 1 | 1 | 1 | 20.2037 | 5.7374 | 14.4663
10 | 19 | 83.1667 | 1 | 1 | 1 | 20.2037 | 5.4871 | 14.7166
10 | 20 | 78.5833 | 1 | 1 | 1 | 20.2037 | 6.1127 | 14.091
10 | 21 | 74.2083 | 1 | 1 | 1 | 20.2037 | 6.7099 | 13.4938
10 | 22 | 72.7083 | 1 | 1 | 1 | 20.2037 | 6.9146 | 13.2891
10 | 23 | 70.3333 | 1 | 1 | 1 | 20.2037 | 7.2388 | 12.9649
10 | 24 | 68.9583 | 1 | 1 | 1 | 20.2037 | 7.4264 | 12.7773
10 | 25 | 71.4583 | 1 | 1 | 1 | 20.2037 | 7.0852 | 13.1185
10 | 26 | 73.9167 | 1 | 1 | 1 | 20.2037 | 6.7497 | 13.454
10 | 27 | 75 | 1 | 1 | 1 | 20.2037 | 6.6018 | 13.6019
10 | 28 | 75.625 | 1 | 1 | 1 | 20.2037 | 6.5165 | 13.6872
10 | 29 | 75.125 | 1 | 1 | 1 | 20.2037 | 6.5848 | 13.6189
10 | 30 | 75.875 | 1 | 1 | 1 | 20.2037 | 6.4824 | 13.7213
10 | 31 | 75.875 | 1 | 1 | 1 | 20.2037 | 6.4824 | 13.7213
11 | 1 | 75.0833 | 1 | 1 | 1 | 20.2037 | 6.5904 | 13.6133
11 | 2 | 70 | 1 | 1 | 1 | 20.2037 | 7.2843 | 12.9194
11 | 3 | 71.0417 | 1 | 1 | 1 | 20.2037 | 7.1421 | 13.0616
11 | 4 | 67.5417 | 1 | 1 | 1 | 20.2037 | 7.6198 | 12.5839
11 | 5 | 68.25 | 1 | 1 | 1 | 20.2037 | 7.5231 | 12.6806
11 | 6 | 68.5417 | 1 | 1 | 1 | 20.2037 | 7.4833 | 12.7204
11 | 7 | 69.5417 | 1 | 1 | 1 | 20.2037 | 7.3468 | 12.8569
11 | 8 | 68.3333 | 1 | 1 | 1 | 20.2037 | 7.5118 | 12.6919
11 | 9 | 67.5417 | 1 | 1 | 1 | 20.2037 | 7.6198 | 12.5839
11 | 10 | 67.0833 | 1 | 1 | 1 | 20.2037 | 7.6824 | 12.5213
11 | 11 | 63.5417 | 1 | 1 | 1 | 20.2037 | 8.1658 | 12.0379
11 | 12 | 65.75 | 1 | 1 | 1 | 20.2037 | 7.8644 | 12.3393
11 | 13 | 68.9167 | 1 | 1 | 1 | 20.2037 | 7.4321 | 12.7716
11 | 14 | 73.4167 | 1 | 1 | 1 | 20.2037 | 6.8179 | 13.3858
11 | 15 | 74.0417 | 1 | 1 | 1 | 20.2037 | 6.7326 | 13.4711
11 | 16 | 68.1667 | 1 | 1 | 1 | 20.2037 | 7.5345 | 12.6692
11 | 17 | 70.4167 | 1 | 1 | 1 | 20.2037 | 7.2274 | 12.9763
11 | 18 | 70.75 | 1 | 1 | 1 | 20.2037 | 7.1819 | 13.0218
11 | 19 | 66.6667 | 1 | 1 | 1 | 20.2037 | 7.7392 | 12.4645
11 | 20 | 70.5833 | 1 | 1 | 1 | 20.2037 | 7.2047 | 12.999
11 | 21 | 67.7083 | 1 | 1 | 1 | 20.2037 | 7.5971 | 12.6066
11 | 22 | 67.25 | 1 | 1 | 1 | 20.2037 | 7.6596 | 12.5441
11 | 23 | 65.2083 | 1 | 1 | 1 | 20.2037 | 7.9383 | 12.2654
11 | 24 | 70.875 | 1 | 1 | 1 | 20.2037 | 7.1648 | 13.0389
11 | 25 | 67.6667 | 1 | 1 | 1 | 20.2037 | 7.6028 | 12.6009
11 | 26 | 65.7083 | 1 | 1 | 1 | 20.2037 | 7.87 | 12.3337
11 | 27 | 57.5833 | 1 | 1 | 1 | 20.2037 | 8.979 | 11.2247
11 | 28 | 53.25 | 1 | 1 | 1 | 20.2037 | 9.5705 | 10.6332
11 | 29 | 54.9583 | 1 | 1 | 1 | 20.2037 | 9.3373 | 10.8664
11 | 30 | 58.4583 | 1 | 1 | 1 | 20.2037 | 8.8596 | 11.3441
12 | 1 | 49.875 | 1 | 1 | 1 | 20.2037 | 10.0312 | 10.1725
12 | 2 | 53.3333 | 1 | 1 | 1 | 20.2037 | 9.5591 | 10.6446
12 | 3 | 55 | 1 | 1 | 1 | 20.2037 | 9.3316 | 10.8721
12 | 4 | 51.0833 | 1 | 1 | 1 | 20.2037 | 9.8662 | 10.3375
12 | 5 | 47.2083 | 1 | 1 | 1 | 20.2037 | 10.3951 | 9.8086
12 | 6 | 52.9583 | 1 | 1 | 1 | 20.2037 | 9.6103 | 10.5934
12 | 7 | 51.125 | 1 | 1 | 1 | 20.2037 | 9.8605 | 10.3432
12 | 8 | 54.0833 | 1 | 1 | 1 | 20.2037 | 9.4568 | 10.7469
12 | 9 | 58.5 | 1 | 1 | 1 | 20.2037 | 8.8539 | 11.3498
12 | 10 | 62.125 | 1 | 1 | 1 | 20.2037 | 8.3591 | 11.8446
12 | 11 | 64.25 | 1 | 1 | 1 | 20.2037 | 8.0691 | 12.1346
12 | 12 | 62.7917 | 1 | 1 | 1 | 20.2037 | 8.2681 | 11.9356
12 | 13 | 62.0417 | 1 | 1 | 1 | 20.2037 | 8.3705 | 11.8332
12 | 14 | 64.2917 | 1 | 1 | 1 | 20.2037 | 8.0634 | 12.1403
12 | 15 | 64.625 | 1 | 1 | 1 | 20.2037 | 8.0179 | 12.1858
12 | 16 | 66.5417 | 1 | 1 | 1 | 20.2037 | 7.7563 | 12.4474
12 | 17 | 62.5833 | 1 | 1 | 1 | 20.2037 | 8.2966 | 11.9071
12 | 18 | 64.8333 | 1 | 1 | 1 | 20.2037 | 7.9895 | 12.2142
12 | 19 | 62.2917 | 1 | 1 | 1 | 20.2037 | 8.3364 | 11.8673
12 | 20 | 59.7083 | 1 | 1 | 1 | 20.2037 | 8.689 | 11.5147
12 | 21 | 61.4167 | 1 | 1 | 1 | 20.2037 | 8.4558 | 11.7479
12 | 22 | 57.875 | 1 | 1 | 1 | 20.2037 | 8.9392 | 11.2645
12 | 23 | 57.3333 | 1 | 1 | 1 | 20.2037 | 9.0132 | 11.1905
12 | 24 | 54.9583 | 1 | 1 | 1 | 20.2037 | 9.3373 | 10.8664
12 | 25 | 50.7083 | 1 | 1 | 1 | 20.2037 | 9.9174 | 10.2863
12 | 26 | 52.75 | 1 | 1 | 1 | 20.2037 | 9.6387 | 10.565
12 | 27 | 54.5833 | 1 | 1 | 1 | 20.2037 | 9.3885 | 10.8152
12 | 28 | 53.5 | 1 | 1 | 1 | 20.2037 | 9.5364 | 10.6673
12 | 29 | 54.75 | 1 | 1 | 1 | 20.2037 | 9.3658 | 10.8379
12 | 30 | 53.625 | 1 | 1 | 1 | 20.2037 | 9.5193 | 10.6844
12 | 31 | 50.2083 | 1 | 1 | 1 | 20.2037 | 9.9857 | 10.218
1 | 1 | 48.5 | 2 | 1 | 1 | 20.2037 | 12.5852 | 7.6185
1 | 2 | 50.5833 | 2 | 1 | 1 | 20.2037 | 12.3073 | 7.8964
1 | 3 | 54.8333 | 2 | 1 | 1 | 20.2037 | 11.7404 | 8.4633
1 | 4 | 50 | 2 | 1 | 1 | 20.2037 | 12.3851 | 7.8186
1 | 5 | 52.0417 | 2 | 1 | 1 | 20.2037 | 12.1128 | 8.0909
1 | 6 | 52.0417 | 2 | 1 | 1 | 20.2037 | 12.1128 | 8.0909
1 | 7 | 56 | 2 | 1 | 1 | 20.2037 | 11.5848 | 8.6189
1 | 8 | 56.4167 | 2 | 1 | 1 | 20.2037 | 11.5292 | 8.6745
1 | 9 | 62 | 2 | 1 | 1 | 20.2037 | 10.7844 | 9.4193
1 | 10 | 64.5417 | 2 | 1 | 1 | 20.2037 | 10.4454 | 9.7583
1 | 11 | 63.25 | 2 | 1 | 1 | 20.2037 | 10.6177 | 9.586
1 | 12 | 61.5833 | 2 | 1 | 1 | 20.2037 | 10.84 | 9.3637
1 | 13 | 65.0833 | 2 | 1 | 1 | 20.2037 | 10.3731 | 9.8306
1 | 14 | 68.5833 | 2 | 1 | 1 | 20.2037 | 9.9063 | 10.2974
1 | 15 | 60.4583 | 2 | 1 | 1 | 20.2037 | 10.9901 | 9.2136
1 | 16 | 62.7083 | 2 | 1 | 1 | 20.2037 | 10.6899 | 9.5138
1 | 17 | 62.125 | 2 | 1 | 1 | 20.2037 | 10.7678 | 9.4359
1 | 18 | 59.3333 | 2 | 1 | 1 | 20.2037 | 11.1401 | 9.0636
1 | 19 | 61.0833 | 2 | 1 | 1 | 20.2037 | 10.9067 | 9.297
1 | 20 | 57.3333 | 2 | 1 | 1 | 20.2037 | 11.4069 | 8.7968
1 | 21 | 59.1667 | 2 | 1 | 1 | 20.2037 | 11.1624 | 9.0413
1 | 22 | 62.75 | 2 | 1 | 1 | 20.2037 | 10.6844 | 9.5193
1 | 23 | 61.0417 | 2 | 1 | 1 | 20.2037 | 10.9123 | 9.2914
1 | 24 | 53.9583 | 2 | 1 | 1 | 20.2037 | 11.8571 | 8.3466
1 | 25 | 56.7917 | 2 | 1 | 1 | 20.2037 | 11.4792 | 8.7245
1 | 26 | 54.2917 | 2 | 1 | 1 | 20.2037 | 11.8127 | 8.391
1 | 27 | 55.5833 | 2 | 1 | 1 | 20.2037 | 11.6404 | 8.5633
1 | 28 | 58.625 | 2 | 1 | 1 | 20.2037 | 11.2346 | 8.9691
1 | 29 | 59.5 | 2 | 1 | 1 | 20.2037 | 11.1179 | 9.0858
1 | 30 | 59.25 | 2 | 1 | 1 | 20.2037 | 11.1513 | 9.0524
1 | 31 | 59.25 | 2 | 1 | 1 | 20.2037 | 11.1513 | 9.0524
2 | 1 | 51.25 | 2 | 1 | 1 | 20.2037 | 12.2184 | 7.9853
2 | 2 | 53.7917 | 2 | 1 | 1 | 20.2037 | 11.8794 | 8.3243
2 | 3 | 57.3333 | 2 | 1 | 1 | 20.2037 | 11.4069 | 8.7968
2 | 4 | 54.2083 | 2 | 1 | 1 | 20.2037 | 11.8238 | 8.3799
2 | 5 | 52.4583 | 2 | 1 | 1 | 20.2037 | 12.0572 | 8.1465
2 | 6 | 50.625 | 2 | 1 | 1 | 20.2037 | 12.3018 | 7.9019
2 | 7 | 55.4583 | 2 | 1 | 1 | 20.2037 | 11.657 | 8.5467
2 | 8 | 58.625 | 2 | 1 | 1 | 20.2037 | 11.2346 | 8.9691
2 | 9 | 64.5833 | 2 | 1 | 1 | 20.2037 | 10.4398 | 9.7639
2 | 10 | 66.8333 | 2 | 1 | 1 | 20.2037 | 10.1397 | 10.064
2 | 11 | 70.2083 | 2 | 1 | 1 | 20.2037 | 9.6895 | 10.5142
2 | 12 | 71.0417 | 2 | 1 | 1 | 20.2037 | 9.5783 | 10.6254
2 | 13 | 63.9583 | 2 | 1 | 1 | 20.2037 | 10.5232 | 9.6805
2 | 14 | 50.7083 | 2 | 1 | 1 | 20.2037 | 12.2907 | 7.913
2 | 15 | 58.6667 | 2 | 1 | 1 | 20.2037 | 11.2291 | 8.9746
2 | 16 | 59.7917 | 2 | 1 | 1 | 20.2037 | 11.079 | 9.1247
2 | 17 | 60.125 | 2 | 1 | 1 | 20.2037 | 11.0345 | 9.1692
2 | 18 | 62.6667 | 2 | 1 | 1 | 20.2037 | 10.6955 | 9.5082
2 | 19 | 60.9167 | 2 | 1 | 1 | 20.2037 | 10.9289 | 9.2748
2 | 20 | 59.125 | 2 | 1 | 1 | 20.2037 | 11.1679 | 9.0358
2 | 21 | 58.0417 | 2 | 1 | 1 | 20.2037 | 11.3124 | 8.8913
2 | 22 | 56.9167 | 2 | 1 | 1 | 20.2037 | 11.4625 | 8.7412
2 | 23 | 56.5 | 2 | 1 | 1 | 20.2037 | 11.5181 | 8.6856
2 | 24 | 60.9583 | 2 | 1 | 1 | 20.2037 | 10.9234 | 9.2803
2 | 25 | 63.75 | 2 | 1 | 1 | 20.2037 | 10.551 | 9.6527
2 | 26 | 68.4583 | 2 | 1 | 1 | 20.2037 | 9.9229 | 10.2808
2 | 27 | 69.8333 | 2 | 1 | 1 | 20.2037 | 9.7395 | 10.4642
2 | 28 | 69.9167 | 2 | 1 | 1 | 20.2037 | 9.7284 | 10.4753
3 | 1 | 58.625 | 2 | 1 | 1 | 20.2037 | 11.2346 | 8.9691
3 | 2 | 60.375 | 2 | 1 | 1 | 20.2037 | 11.0012 | 9.2025
3 | 3 | 66.625 | 2 | 1 | 1 | 20.2037 | 10.1675 | 10.0362
3 | 4 | 68.25 | 2 | 1 | 1 | 20.2037 | 9.9507 | 10.253
3 | 5 | 73.75 | 2 | 1 | 1 | 20.2037 | 9.2171 | 10.9866
3 | 6 | 76.0417 | 2 | 1 | 1 | 20.2037 | 8.9114 | 11.2923
3 | 7 | 74.2917 | 2 | 1 | 1 | 20.2037 | 9.1448 | 11.0589
3 | 8 | 75.7083 | 2 | 1 | 1 | 20.2037 | 8.9558 | 11.2479
3 | 9 | 73.5833 | 2 | 1 | 1 | 20.2037 | 9.2393 | 10.9644
3 | 10 | 73.3333 | 2 | 1 | 1 | 20.2037 | 9.2726 | 10.9311
3 | 11 | 72.3333 | 2 | 1 | 1 | 20.2037 | 9.406 | 10.7977
3 | 12 | 70.0417 | 2 | 1 | 1 | 20.2037 | 9.7117 | 10.492
3 | 13 | 69.7083 | 2 | 1 | 1 | 20.2037 | 9.7562 | 10.4475
3 | 14 | 73.0417 | 2 | 1 | 1 | 20.2037 | 9.3115 | 10.8922
3 | 15 | 76.3333 | 2 | 1 | 1 | 20.2037 | 8.8725 | 11.3312
3 | 16 | 76.6667 | 2 | 1 | 1 | 20.2037 | 8.828 | 11.3757
3 | 17 | 75.4167 | 2 | 1 | 1 | 20.2037 | 8.9947 | 11.209
3 | 18 | 72.8333 | 2 | 1 | 1 | 20.2037 | 9.3393 | 10.8644
3 | 19 | 70.4583 | 2 | 1 | 1 | 20.2037 | 9.6561 | 10.5476
3 | 20 | 71.3333 | 2 | 1 | 1 | 20.2037 | 9.5394 | 10.6643
3 | 21 | 71.0833 | 2 | 1 | 1 | 20.2037 | 9.5728 | 10.6309
3 | 22 | 69.625 | 2 | 1 | 1 | 20.2037 | 9.7673 | 10.4364
3 | 23 | 73.8333 | 2 | 1 | 1 | 20.2037 | 9.2059 | 10.9978
3 | 24 | 75.6667 | 2 | 1 | 1 | 20.2037 | 8.9614 | 11.2423
3 | 25 | 72.8333 | 2 | 1 | 1 | 20.2037 | 9.3393 | 10.8644
3 | 26 | 68.375 | 2 | 1 | 1 | 20.2037 | 9.934 | 10.2697
3 | 27 | 65.7083 | 2 | 1 | 1 | 20.2037 | 10.2898 | 9.9139
3 | 28 | 69.2917 | 2 | 1 | 1 | 20.2037 | 9.8118 | 10.3919
3 | 29 | 74.2917 | 2 | 1 | 1 | 20.2037 | 9.1448 | 11.0589
3 | 30 | 72.75 | 2 | 1 | 1 | 20.2037 | 9.3505 | 10.8532
3 | 31 | 69 | 2 | 1 | 1 | 20.2037 | 9.8507 | 10.353
4 | 1 | 87.4167 | 2 | 1 | 1 | 20.2037 | 7.394 | 12.8097
4 | 2 | 78.4167 | 2 | 1 | 1 | 20.2037 | 8.5946 | 11.6091
4 | 3 | 70.6667 | 2 | 1 | 1 | 20.2037 | 9.6284 | 10.5753
4 | 4 | 74.2917 | 2 | 1 | 1 | 20.2037 | 9.1448 | 11.0589
4 | 5 | 75.5417 | 2 | 1 | 1 | 20.2037 | 8.9781 | 11.2256
4 | 6 | 69.3333 | 2 | 1 | 1 | 20.2037 | 9.8062 | 10.3975
4 | 7 | 65.5 | 2 | 1 | 1 | 20.2037 | 10.3176 | 9.8861
4 | 8 | 55.0833 | 2 | 1 | 1 | 20.2037 | 11.7071 | 8.4966
4 | 9 | 57.3333 | 2 | 1 | 1 | 20.2037 | 11.4069 | 8.7968
4 | 10 | 63.7917 | 2 | 1 | 1 | 20.2037 | 10.5454 | 9.6583
4 | 11 | 69.375 | 2 | 1 | 1 | 20.2037 | 9.8007 | 10.403
4 | 12 | 72.5833 | 2 | 1 | 1 | 20.2037 | 9.3727 | 10.831
4 | 13 | 67.625 | 2 | 1 | 1 | 20.2037 | 10.0341 | 10.1696
4 | 14 | 70.6667 | 2 | 1 | 1 | 20.2037 | 9.6284 | 10.5753
4 | 15 | 76.5833 | 2 | 1 | 1 | 20.2037 | 8.8391 | 11.3646
4 | 16 | 84.0417 | 2 | 1 | 1 | 20.2037 | 7.8442 | 12.3595
4 | 17 | 83.5417 | 2 | 1 | 1 | 20.2037 | 7.9109 | 12.2928
4 | 18 | 74.8333 | 2 | 1 | 1 | 20.2037 | 9.0725 | 11.1312
4 | 19 | 73.5 | 2 | 1 | 1 | 20.2037 | 9.2504 | 10.9533
4 | 20 | 72.875 | 2 | 1 | 1 | 20.2037 | 9.3338 | 10.8699
4 | 21 | 73.1667 | 2 | 1 | 1 | 20.2037 | 9.2949 | 10.9088
4 | 22 | 72.4167 | 2 | 1 | 1 | 20.2037 | 9.3949 | 10.8088
4 | 23 | 74.1667 | 2 | 1 | 1 | 20.2037 | 9.1615 | 11.0422
4 | 24 | 71.5417 | 2 | 1 | 1 | 20.2037 | 9.5116 | 10.6921
4 | 25 | 75.6667 | 2 | 1 | 1 | 20.2037 | 8.9614 | 11.2423
4 | 26 | 76.5833 | 2 | 1 | 1 | 20.2037 | 8.8391 | 11.3646
4 | 27 | 77.875 | 2 | 1 | 1 | 20.2037 | 8.6668 | 11.5369
4 | 28 | 80.75 | 2 | 1 | 1 | 20.2037 | 8.2833 | 11.9204
4 | 29 | 75.7917 | 2 | 1 | 1 | 20.2037 | 8.9447 | 11.259
4 | 30 | 71.4583 | 2 | 1 | 1 | 20.2037 | 9.5227 | 10.681
5 | 1 | 85.875 | 2 | 1 | 1 | 20.2037 | 7.5997 | 12.604
5 | 2 | 90.9167 | 2 | 1 | 1 | 20.2037 | 6.9271 | 13.2766
5 | 3 | 93.4167 | 2 | 1 | 1 | 20.2037 | 6.5937 | 13.61
5 | 4 | 92.875 | 2 | 1 | 1 | 20.2037 | 6.6659 | 13.5378
5 | 5 | 88.8333 | 2 | 1 | 1 | 20.2037 | 7.205 | 12.9987
5 | 6 | 70.875 | 2 | 1 | 1 | 20.2037 | 9.6006 | 10.6031
5 | 7 | 60.1667 | 2 | 1 | 1 | 20.2037 | 11.029 | 9.1747
5 | 8 | 73.4583 | 2 | 1 | 1 | 20.2037 | 9.256 | 10.9477
5 | 9 | 68.5833 | 2 | 1 | 1 | 20.2037 | 9.9063 | 10.2974
5 | 10 | 73.4583 | 2 | 1 | 1 | 20.2037 | 9.256 | 10.9477
5 | 11 | 79.5 | 2 | 1 | 1 | 20.2037 | 8.45 | 11.7537
5 | 12 | 83.5 | 2 | 1 | 1 | 20.2037 | 7.9165 | 12.2872
5 | 13 | 77.7917 | 2 | 1 | 1 | 20.2037 | 8.6779 | 11.5258
5 | 14 | 75.25 | 2 | 1 | 1 | 20.2037 | 9.017 | 11.1867
5 | 15 | 69.5 | 2 | 1 | 1 | 20.2037 | 9.784 | 10.4197
5 | 16 | 70.25 | 2 | 1 | 1 | 20.2037 | 9.6839 | 10.5198
5 | 17 | 71.125 | 2 | 1 | 1 | 20.2037 | 9.5672 | 10.6365
5 | 18 | 79.375 | 2 | 1 | 1 | 20.2037 | 8.4667 | 11.737
5 | 19 | 82.25 | 2 | 1 | 1 | 20.2037 | 8.0832 | 12.1205
5 | 20 | 87.75 | 2 | 1 | 1 | 20.2037 | 7.3496 | 12.8541
5 | 21 | 93.625 | 2 | 1 | 1 | 20.2037 | 6.5659 | 13.6378
5 | 22 | 95.2917 | 2 | 1 | 1 | 20.2037 | 6.3435 | 13.8602
5 | 23 | 97.375 | 2 | 1 | 1 | 20.2037 | 6.0656 | 14.1381
5 | 24 | 91.875 | 2 | 1 | 1 | 20.2037 | 6.7993 | 13.4044
5 | 25 | 81.0417 | 2 | 1 | 1 | 20.2037 | 8.2444 | 11.9593
5 | 26 | 77.5833 | 2 | 1 | 1 | 20.2037 | 8.7057 | 11.498
5 | 27 | 81.7917 | 2 | 1 | 1 | 20.2037 | 8.1444 | 12.0593
5 | 28 | 89.0417 | 2 | 1 | 1 | 20.2037 | 7.1773 | 13.0264
5 | 29 | 91.4583 | 2 | 1 | 1 | 20.2037 | 6.8549 | 13.3488
5 | 30 | 86.8333 | 2 | 1 | 1 | 20.2037 | 7.4718 | 12.7319
5 | 31 | 81.7083 | 2 | 1 | 1 | 20.2037 | 8.1555 | 12.0482
6 | 1 | 94.2917 | 2 | 1 | 1 | 20.2037 | 6.4769 | 13.7268
6 | 2 | 91.7083 | 2 | 1 | 1 | 20.2037 | 6.8215 | 13.3822
6 | 3 | 88.0417 | 2 | 1 | 1 | 20.2037 | 7.3106 | 12.8931
6 | 4 | 86 | 2 | 1 | 1 | 20.2037 | 7.583 | 12.6207
6 | 5 | 89.4167 | 2 | 1 | 1 | 20.2037 | 7.1272 | 13.0765
6 | 6 | 92 | 2 | 1 | 1 | 20.2037 | 6.7826 | 13.4211
6 | 7 | 95.125 | 2 | 1 | 1 | 20.2037 | 6.3658 | 13.8379
6 | 8 | 91.0833 | 2 | 1 | 1 | 20.2037 | 6.9049 | 13.2988
6 | 9 | 89.3333 | 2 | 1 | 1 | 20.2037 | 7.1383 | 13.0654
6 | 10 | 87.2083 | 2 | 1 | 1 | 20.2037 | 7.4218 | 12.7819
6 | 11 | 92.25 | 2 | 1 | 1 | 20.2037 | 6.7493 | 13.4544
6 | 12 | 90.7917 | 2 | 1 | 1 | 20.2037 | 6.9438 | 13.2599
6 | 13 | 91.5833 | 2 | 1 | 1 | 20.2037 | 6.8382 | 13.3655
6 | 14 | 89.6667 | 2 | 1 | 1 | 20.2037 | 7.0939 | 13.1098
6 | 15 | 88.5833 | 2 | 1 | 1 | 20.2037 | 7.2384 | 12.9653
6 | 16 | 88.875 | 2 | 1 | 1 | 20.2037 | 7.1995 | 13.0042
6 | 17 | 91.75 | 2 | 1 | 1 | 20.2037 | 6.816 | 13.3877
6 | 18 | 91.375 | 2 | 1 | 1 | 20.2037 | 6.866 | 13.3377
6 | 19 | 89.0417 | 2 | 1 | 1 | 20.2037 | 7.1773 | 13.0264
6 | 20 | 88.875 | 2 | 1 | 1 | 20.2037 | 7.1995 | 13.0042
6 | 21 | 88.875 | 2 | 1 | 1 | 20.2037 | 7.1995 | 13.0042
6 | 22 | 89.5417 | 2 | 1 | 1 | 20.2037 | 7.1106 | 13.0931
6 | 23 | 87.5417 | 2 | 1 | 1 | 20.2037 | 7.3773 | 12.8264
6 | 24 | 83.2917 | 2 | 1 | 1 | 20.2037 | 7.9443 | 12.2594
6 | 25 | 88.6667 | 2 | 1 | 1 | 20.2037 | 7.2273 | 12.9764
6 | 26 | 93.3333 | 2 | 1 | 1 | 20.2037 | 6.6048 | 13.5989
6 | 27 | 97.1667 | 2 | 1 | 1 | 20.2037 | 6.0934 | 14.1103
6 | 28 | 102.375 | 2 | 1 | 1 | 20.2037 | 5.3987 | 14.805
6 | 29 | 104.3333 | 2 | 1 | 1 | 20.2037 | 5.1374 | 15.0663
6 | 30 | 99.6667 | 2 | 1 | 1 | 20.2037 | 5.7599 | 14.4438
7 | 1 | 98.625 | 2 | 1 | 1 | 20.2037 | 5.8989 | 14.3048
7 | 2 | 101.25 | 2 | 1 | 1 | 20.2037 | 5.5487 | 14.655
7 | 3 | 93.8333 | 2 | 1 | 1 | 20.2037 | 6.5381 | 13.6656
7 | 4 | 94.7083 | 2 | 1 | 1 | 20.2037 | 6.4214 | 13.7823
7 | 5 | 95.75 | 2 | 1 | 1 | 20.2037 | 6.2824 | 13.9213
7 | 6 | 91.2083 | 2 | 1 | 1 | 20.2037 | 6.8882 | 13.3155
7 | 7 | 97.125 | 2 | 1 | 1 | 20.2037 | 6.099 | 14.1047
7 | 8 | 98.3333 | 2 | 1 | 1 | 20.2037 | 5.9378 | 14.2659
7 | 9 | 98.7083 | 2 | 1 | 1 | 20.2037 | 5.8878 | 14.3159
7 | 10 | 95.0417 | 2 | 1 | 1 | 20.2037 | 6.3769 | 13.8268
7 | 11 | 90.4583 | 2 | 1 | 1 | 20.2037 | 6.9883 | 13.2154
7 | 12 | 87.8333 | 2 | 1 | 1 | 20.2037 | 7.3384 | 12.8653
7 | 13 | 84.75 | 2 | 1 | 1 | 20.2037 | 7.7497 | 12.454
7 | 14 | 83.9167 | 2 | 1 | 1 | 20.2037 | 7.8609 | 12.3428
7 | 15 | 84.375 | 2 | 1 | 1 | 20.2037 | 7.7998 | 12.4039
7 | 16 | 86 | 2 | 1 | 1 | 20.2037 | 7.583 | 12.6207
7 | 17 | 91.5417 | 2 | 1 | 1 | 20.2037 | 6.8438 | 13.3599
7 | 18 | 94.75 | 2 | 1 | 1 | 20.2037 | 6.4158 | 13.7879
7 | 19 | 97.1667 | 2 | 1 | 1 | 20.2037 | 6.0934 | 14.1103
7 | 20 | 96.875 | 2 | 1 | 1 | 20.2037 | 6.1323 | 14.0714
7 | 21 | 93.7917 | 2 | 1 | 1 | 20.2037 | 6.5436 | 13.6601
7 | 22 | 91 | 2 | 1 | 1 | 20.2037 | 6.916 | 13.2877
7 | 23 | 90.625 | 2 | 1 | 1 | 20.2037 | 6.966 | 13.2377
7 | 24 | 91.0417 | 2 | 1 | 1 | 20.2037 | 6.9105 | 13.2932
7 | 25 | 95.9167 | 2 | 1 | 1 | 20.2037 | 6.2602 | 13.9435
7 | 26 | 95.9583 | 2 | 1 | 1 | 20.2037 | 6.2546 | 13.9491
7 | 27 | 90.9167 | 2 | 1 | 1 | 20.2037 | 6.9271 | 13.2766
7 | 28 | 93.4167 | 2 | 1 | 1 | 20.2037 | 6.5937 | 13.61
7 | 29 | 94.9583 | 2 | 1 | 1 | 20.2037 | 6.388 | 13.8157
7 | 30 | 96.2083 | 2 | 1 | 1 | 20.2037 | 6.2213 | 13.9824
7 | 31 | 89.375 | 2 | 1 | 1 | 20.2037 | 7.1328 | 13.0709
8 | 1 | 99 | 2 | 1 | 1 | 20.2037 | 5.8489 | 14.3548
8 | 2 | 95.2917 | 2 | 1 | 1 | 20.2037 | 6.3435 | 13.8602
8 | 3 | 92.25 | 2 | 1 | 1 | 20.2037 | 6.7493 | 13.4544
8 | 4 | 92.3333 | 2 | 1 | 1 | 20.2037 | 6.7382 | 13.4655
8 | 5 | 96.2917 | 2 | 1 | 1 | 20.2037 | 6.2102 | 13.9935
8 | 6 | 97.7917 | 2 | 1 | 1 | 20.2037 | 6.0101 | 14.1936
8 | 7 | 93.4583 | 2 | 1 | 1 | 20.2037 | 6.5881 | 13.6156
8 | 8 | 92.5417 | 2 | 1 | 1 | 20.2037 | 6.7104 | 13.4933
8 | 9 | 94.8333 | 2 | 1 | 1 | 20.2037 | 6.4047 | 13.799
8 | 10 | 94.7083 | 2 | 1 | 1 | 20.2037 | 6.4214 | 13.7823
8 | 11 | 94.875 | 2 | 1 | 1 | 20.2037 | 6.3991 | 13.8046
8 | 12 | 94.5 | 2 | 1 | 1 | 20.2037 | 6.4491 | 13.7546
8 | 13 | 93.125 | 2 | 1 | 1 | 20.2037 | 6.6326 | 13.5711
8 | 14 | 93.25 | 2 | 1 | 1 | 20.2037 | 6.6159 | 13.5878
8 | 15 | 95.4583 | 2 | 1 | 1 | 20.2037 | 6.3213 | 13.8824
8 | 16 | 95 | 2 | 1 | 1 | 20.2037 | 6.3825 | 13.8212
8 | 17 | 93.625 | 2 | 1 | 1 | 20.2037 | 6.5659 | 13.6378
8 | 18 | 93.1667 | 2 | 1 | 1 | 20.2037 | 6.627 | 13.5767
8 | 19 | 92 | 2 | 1 | 1 | 20.2037 | 6.7826 | 13.4211
8 | 20 | 90.4167 | 2 | 1 | 1 | 20.2037 | 6.9938 | 13.2099
8 | 21 | 91.9167 | 2 | 1 | 1 | 20.2037 | 6.7937 | 13.41
8 | 22 | 91.4583 | 2 | 1 | 1 | 20.2037 | 6.8549 | 13.3488
8 | 23 | 93.4583 | 2 | 1 | 1 | 20.2037 | 6.5881 | 13.6156
8 | 24 | 94.625 | 2 | 1 | 1 | 20.2037 | 6.4325 | 13.7712
8 | 25 | 92.6667 | 2 | 1 | 1 | 20.2037 | 6.6937 | 13.51
8 | 26 | 90.0833 | 2 | 1 | 1 | 20.2037 | 7.0383 | 13.1654
8 | 27 | 95 | 2 | 1 | 1 | 20.2037 | 6.3825 | 13.8212
8 | 28 | 94.2917 | 2 | 1 | 1 | 20.2037 | 6.4769 | 13.7268
8 | 29 | 93.2083 | 2 | 1 | 1 | 20.2037 | 6.6214 | 13.5823
8 | 30 | 86.2083 | 2 | 1 | 1 | 20.2037 | 7.5552 | 12.6485
8 | 31 | 88.5 | 2 | 1 | 1 | 20.2037 | 7.2495 | 12.9542
9 | 1 | 98.4583 | 2 | 1 | 1 | 20.2037 | 5.9211 | 14.2826
9 | 2 | 92.4167 | 2 | 1 | 1 | 20.2037 | 6.7271 | 13.4766
9 | 3 | 91.5417 | 2 | 1 | 1 | 20.2037 | 6.8438 | 13.3599
9 | 4 | 92.875 | 2 | 1 | 1 | 20.2037 | 6.6659 | 13.5378
9 | 5 | 95.25 | 2 | 1 | 1 | 20.2037 | 6.3491 | 13.8546
9 | 6 | 93.1667 | 2 | 1 | 1 | 20.2037 | 6.627 | 13.5767
9 | 7 | 90.0417 | 2 | 1 | 1 | 20.2037 | 7.0439 | 13.1598
9 | 8 | 88.3333 | 2 | 1 | 1 | 20.2037 | 7.2717 | 12.932
9 | 9 | 86.4167 | 2 | 1 | 1 | 20.2037 | 7.5274 | 12.6763
9 | 10 | 86.75 | 2 | 1 | 1 | 20.2037 | 7.4829 | 12.7208
9 | 11 | 93.5 | 2 | 1 | 1 | 20.2037 | 6.5825 | 13.6212
9 | 12 | 93.5833 | 2 | 1 | 1 | 20.2037 | 6.5714 | 13.6323
9 | 13 | 91.5833 | 2 | 1 | 1 | 20.2037 | 6.8382 | 13.3655
9 | 14 | 84.875 | 2 | 1 | 1 | 20.2037 | 7.7331 | 12.4706
9 | 15 | 78.125 | 2 | 1 | 1 | 20.2037 | 8.6335 | 11.5702
9 | 16 | 79.75 | 2 | 1 | 1 | 20.2037 | 8.4167 | 11.787
9 | 17 | 85.4583 | 2 | 1 | 1 | 20.2037 | 7.6552 | 12.5485
9 | 18 | 86.9167 | 2 | 1 | 1 | 20.2037 | 7.4607 | 12.743
9 | 19 | 85.0833 | 2 | 1 | 1 | 20.2037 | 7.7053 | 12.4984
9 | 20 | 83.8333 | 2 | 1 | 1 | 20.2037 | 7.872 | 12.3317
9 | 21 | 82.2083 | 2 | 1 | 1 | 20.2037 | 8.0888 | 12.1149
9 | 22 | 79.625 | 2 | 1 | 1 | 20.2037 | 8.4334 | 11.7703
9 | 23 | 81.25 | 2 | 1 | 1 | 20.2037 | 8.2166 | 11.9871
9 | 24 | 82.75 | 2 | 1 | 1 | 20.2037 | 8.0165 | 12.1872
9 | 25 | 88.0833 | 2 | 1 | 1 | 20.2037 | 7.3051 | 12.8986
9 | 26 | 89.5417 | 2 | 1 | 1 | 20.2037 | 7.1106 | 13.0931
9 | 27 | 89.5833 | 2 | 1 | 1 | 20.2037 | 7.105 | 13.0987
9 | 28 | 91.2083 | 2 | 1 | 1 | 20.2037 | 6.8882 | 13.3155
9 | 29 | 90.5833 | 2 | 1 | 1 | 20.2037 | 6.9716 | 13.2321
9 | 30 | 88.7917 | 2 | 1 | 1 | 20.2037 | 7.2106 | 12.9931
10 | 1 | 96.0833 | 2 | 1 | 1 | 20.2037 | 6.2379 | 13.9658
10 | 2 | 94.875 | 2 | 1 | 1 | 20.2037 | 6.3991 | 13.8046
10 | 3 | 90.375 | 2 | 1 | 1 | 20.2037 | 6.9994 | 13.2043
10 | 4 | 85.625 | 2 | 1 | 1 | 20.2037 | 7.633 | 12.5707
10 | 5 | 83.4583 | 2 | 1 | 1 | 20.2037 | 7.922 | 12.2817
10 | 6 | 83.2917 | 2 | 1 | 1 | 20.2037 | 7.9443 | 12.2594
10 | 7 | 83.625 | 2 | 1 | 1 | 20.2037 | 7.8998 | 12.3039
10 | 8 | 82.375 | 2 | 1 | 1 | 20.2037 | 8.0665 | 12.1372
10 | 9 | 79 | 2 | 1 | 1 | 20.2037 | 8.5167 | 11.687
10 | 10 | 74.625 | 2 | 1 | 1 | 20.2037 | 9.1003 | 11.1034
10 | 11 | 69.6667 | 2 | 1 | 1 | 20.2037 | 9.7617 | 10.442
10 | 12 | 68.375 | 2 | 1 | 1 | 20.2037 | 9.934 | 10.2697
10 | 13 | 73.1667 | 2 | 1 | 1 | 20.2037 | 9.2949 | 10.9088
10 | 14 | 82.5417 | 2 | 1 | 1 | 20.2037 | 8.0443 | 12.1594
10 | 15 | 85.3333 | 2 | 1 | 1 | 20.2037 | 7.6719 | 12.5318
10 | 16 | 84.5833 | 2 | 1 | 1 | 20.2037 | 7.772 | 12.4317
10 | 17 | 81.2083 | 2 | 1 | 1 | 20.2037 | 8.2222 | 11.9815
10 | 18 | 81.3333 | 2 | 1 | 1 | 20.2037 | 8.2055 | 11.9982
10 | 19 | 83.1667 | 2 | 1 | 1 | 20.2037 | 7.9609 | 12.2428
10 | 20 | 78.5833 | 2 | 1 | 1 | 20.2037 | 8.5723 | 11.6314
10 | 21 | 74.2083 | 2 | 1 | 1 | 20.2037 | 9.1559 | 11.0478
10 | 22 | 72.7083 | 2 | 1 | 1 | 20.2037 | 9.356 | 10.8477
10 | 23 | 70.3333 | 2 | 1 | 1 | 20.2037 | 9.6728 | 10.5309
10 | 24 | 68.9583 | 2 | 1 | 1 | 20.2037 | 9.8562 | 10.3475
10 | 25 | 71.4583 | 2 | 1 | 1 | 20.2037 | 9.5227 | 10.681
10 | 26 | 73.9167 | 2 | 1 | 1 | 20.2037 | 9.1948 | 11.0089
10 | 27 | 75 | 2 | 1 | 1 | 20.2037 | 9.0503 | 11.1534
10 | 28 | 75.625 | 2 | 1 | 1 | 20.2037 | 8.9669 | 11.2368
10 | 29 | 75.125 | 2 | 1 | 1 | 20.2037 | 9.0336 | 11.1701
10 | 30 | 75.875 | 2 | 1 | 1 | 20.2037 | 8.9336 | 11.2701
10 | 31 | 75.875 | 2 | 1 | 1 | 20.2037 | 8.9336 | 11.2701
11 | 1 | 75.0833 | 2 | 1 | 1 | 20.2037 | 9.0392 | 11.1645
11 | 2 | 70 | 2 | 1 | 1 | 20.2037 | 9.7173 | 10.4864
11 | 3 | 71.0417 | 2 | 1 | 1 | 20.2037 | 9.5783 | 10.6254
11 | 4 | 67.5417 | 2 | 1 | 1 | 20.2037 | 10.0452 | 10.1585
11 | 5 | 68.25 | 2 | 1 | 1 | 20.2037 | 9.9507 | 10.253
11 | 6 | 68.5417 | 2 | 1 | 1 | 20.2037 | 9.9118 | 10.2919
11 | 7 | 69.5417 | 2 | 1 | 1 | 20.2037 | 9.7784 | 10.4253
11 | 8 | 68.3333 | 2 | 1 | 1 | 20.2037 | 9.9396 | 10.2641
11 | 9 | 67.5417 | 2 | 1 | 1 | 20.2037 | 10.0452 | 10.1585
11 | 10 | 67.0833 | 2 | 1 | 1 | 20.2037 | 10.1063 | 10.0974
11 | 11 | 63.5417 | 2 | 1 | 1 | 20.2037 | 10.5788 | 9.6249
11 | 12 | 65.75 | 2 | 1 | 1 | 20.2037 | 10.2842 | 9.9195
11 | 13 | 68.9167 | 2 | 1 | 1 | 20.2037 | 9.8618 | 10.3419
11 | 14 | 73.4167 | 2 | 1 | 1 | 20.2037 | 9.2615 | 10.9422
11 | 15 | 74.0417 | 2 | 1 | 1 | 20.2037 | 9.1782 | 11.0255
11 | 16 | 68.1667 | 2 | 1 | 1 | 20.2037 | 9.9618 | 10.2419
11 | 17 | 70.4167 | 2 | 1 | 1 | 20.2037 | 9.6617 | 10.542
11 | 18 | 70.75 | 2 | 1 | 1 | 20.2037 | 9.6172 | 10.5865
11 | 19 | 66.6667 | 2 | 1 | 1 | 20.2037 | 10.1619 | 10.0418
11 | 20 | 70.5833 | 2 | 1 | 1 | 20.2037 | 9.6395 | 10.5642
11 | 21 | 67.7083 | 2 | 1 | 1 | 20.2037 | 10.023 | 10.1807
11 | 22 | 67.25 | 2 | 1 | 1 | 20.2037 | 10.0841 | 10.1196
11 | 23 | 65.2083 | 2 | 1 | 1 | 20.2037 | 10.3565 | 9.8472
11 | 24 | 70.875 | 2 | 1 | 1 | 20.2037 | 9.6006 | 10.6031
11 | 25 | 67.6667 | 2 | 1 | 1 | 20.2037 | 10.0285 | 10.1752
11 | 26 | 65.7083 | 2 | 1 | 1 | 20.2037 | 10.2898 | 9.9139
11 | 27 | 57.5833 | 2 | 1 | 1 | 20.2037 | 11.3736 | 8.8301
11 | 28 | 53.25 | 2 | 1 | 1 | 20.2037 | 11.9516 | 8.2521
11 | 29 | 54.9583 | 2 | 1 | 1 | 20.2037 | 11.7237 | 8.48
11 | 30 | 58.4583 | 2 | 1 | 1 | 20.2037 | 11.2569 | 8.9468
12 | 1 | 49.875 | 2 | 1 | 1 | 20.2037 | 12.4018 | 7.8019
12 | 2 | 53.3333 | 2 | 1 | 1 | 20.2037 | 11.9405 | 8.2632
12 | 3 | 55 | 2 | 1 | 1 | 20.2037 | 11.7182 | 8.4855
12 | 4 | 51.0833 | 2 | 1 | 1 | 20.2037 | 12.2406 | 7.9631
12 | 5 | 47.2083 | 2 | 1 | 1 | 20.2037 | 12.7575 | 7.4462
12 | 6 | 52.9583 | 2 | 1 | 1 | 20.2037 | 11.9905 | 8.2132
12 | 7 | 51.125 | 2 | 1 | 1 | 20.2037 | 12.2351 | 7.9686
12 | 8 | 54.0833 | 2 | 1 | 1 | 20.2037 | 11.8405 | 8.3632
12 | 9 | 58.5 | 2 | 1 | 1 | 20.2037 | 11.2513 | 8.9524
12 | 10 | 62.125 | 2 | 1 | 1 | 20.2037 | 10.7678 | 9.4359
12 | 11 | 64.25 | 2 | 1 | 1 | 20.2037 | 10.4843 | 9.7194
12 | 12 | 62.7917 | 2 | 1 | 1 | 20.2037 | 10.6788 | 9.5249
12 | 13 | 62.0417 | 2 | 1 | 1 | 20.2037 | 10.7789 | 9.4248
12 | 14 | 64.2917 | 2 | 1 | 1 | 20.2037 | 10.4787 | 9.725
12 | 15 | 64.625 | 2 | 1 | 1 | 20.2037 | 10.4343 | 9.7694
12 | 16 | 66.5417 | 2 | 1 | 1 | 20.2037 | 10.1786 | 10.0251
12 | 17 | 62.5833 | 2 | 1 | 1 | 20.2037 | 10.7066 | 9.4971
12 | 18 | 64.8333 | 2 | 1 | 1 | 20.2037 | 10.4065 | 9.7972
12 | 19 | 62.2917 | 2 | 1 | 1 | 20.2037 | 10.7455 | 9.4582
12 | 20 | 59.7083 | 2 | 1 | 1 | 20.2037 | 11.0901 | 9.1136
12 | 21 | 61.4167 | 2 | 1 | 1 | 20.2037 | 10.8622 | 9.3415
12 | 22 | 57.875 | 2 | 1 | 1 | 20.2037 | 11.3347 | 8.869
12 | 23 | 57.3333 | 2 | 1 | 1 | 20.2037 | 11.4069 | 8.7968
12 | 24 | 54.9583 | 2 | 1 | 1 | 20.2037 | 11.7237 | 8.48
12 | 25 | 50.7083 | 2 | 1 | 1 | 20.2037 | 12.2907 | 7.913
12 | 26 | 52.75 | 2 | 1 | 1 | 20.2037 | 12.0183 | 8.1854
12 | 27 | 54.5833 | 2 | 1 | 1 | 20.2037 | 11.7738 | 8.4299
12 | 28 | 53.5 | 2 | 1 | 1 | 20.2037 | 11.9183 | 8.2854
12 | 29 | 54.75 | 2 | 1 | 1 | 20.2037 | 11.7515 | 8.4522
12 | 30 | 53.625 | 2 | 1 | 1 | 20.2037 | 11.9016 | 8.3021
12 | 31 | 50.2083 | 2 | 1 | 1 | 20.2037 | 12.3574 | 7.8463
1 | 1 | 48.5 | 3 | 2 | 2 | 40.4074 | 26.2298 | 14.1776
1 | 2 | 50.5833 | 3 | 2 | 2 | 40.4074 | 25.4822 | 14.9252
1 | 3 | 54.8333 | 3 | 2 | 2 | 40.4074 | 23.957 | 16.4504
1 | 4 | 50 | 3 | 2 | 2 | 40.4074 | 25.6915 | 14.7159
1 | 5 | 52.0417 | 3 | 2 | 2 | 40.4074 | 24.9588 | 15.4486
1 | 6 | 52.0417 | 3 | 2 | 2 | 40.4074 | 24.9588 | 15.4486
1 | 7 | 56 | 3 | 2 | 2 | 40.4074 | 23.5384 | 16.869
1 | 8 | 56.4167 | 3 | 2 | 2 | 40.4074 | 23.3888 | 17.0186
1 | 9 | 62 | 3 | 2 | 2 | 40.4074 | 21.3852 | 19.0222
1 | 10 | 64.5417 | 3 | 2 | 2 | 40.4074 | 20.4731 | 19.9343
1 | 11 | 63.25 | 3 | 2 | 2 | 40.4074 | 20.9366 | 19.4708
1 | 12 | 61.5833 | 3 | 2 | 2 | 40.4074 | 21.5347 | 18.8727
1 | 13 | 65.0833 | 3 | 2 | 2 | 40.4074 | 20.2787 | 20.1287
1 | 14 | 68.5833 | 3 | 2 | 2 | 40.4074 | 19.0227 | 21.3847
1 | 15 | 60.4583 | 3 | 2 | 2 | 40.4074 | 21.9385 | 18.4689
1 | 16 | 62.7083 | 3 | 2 | 2 | 40.4074 | 21.131 | 19.2764
1 | 17 | 62.125 | 3 | 2 | 2 | 40.4074 | 21.3404 | 19.067
1 | 18 | 59.3333 | 3 | 2 | 2 | 40.4074 | 22.3422 | 18.0652
1 | 19 | 61.0833 | 3 | 2 | 2 | 40.4074 | 21.7142 | 18.6932
1 | 20 | 57.3333 | 3 | 2 | 2 | 40.4074 | 23.0599 | 17.3475
1 | 21 | 59.1667 | 3 | 2 | 2 | 40.4074 | 22.402 | 18.0054
1 | 22 | 62.75 | 3 | 2 | 2 | 40.4074 | 21.1161 | 19.2913
1 | 23 | 61.0417 | 3 | 2 | 2 | 40.4074 | 21.7291 | 18.6783
1 | 24 | 53.9583 | 3 | 2 | 2 | 40.4074 | 24.271 | 16.1364
1 | 25 | 56.7917 | 3 | 2 | 2 | 40.4074 | 23.2543 | 17.1531
1 | 26 | 54.2917 | 3 | 2 | 2 | 40.4074 | 24.1514 | 16.256
1 | 27 | 55.5833 | 3 | 2 | 2 | 40.4074 | 23.6879 | 16.7195
1 | 28 | 58.625 | 3 | 2 | 2 | 40.4074 | 22.5964 | 17.811
1 | 29 | 59.5 | 3 | 2 | 2 | 40.4074 | 22.2824 | 18.125
1 | 30 | 59.25 | 3 | 2 | 2 | 40.4074 | 22.3721 | 18.0353
1 | 31 | 59.25 | 3 | 2 | 2 | 40.4074 | 22.3721 | 18.0353
2 | 1 | 51.25 | 3 | 2 | 2 | 40.4074 | 25.2429 | 15.1645
2 | 2 | 53.7917 | 3 | 2 | 2 | 40.4074 | 24.3308 | 16.0766
2 | 3 | 57.3333 | 3 | 2 | 2 | 40.4074 | 23.0599 | 17.3475
2 | 4 | 54.2083 | 3 | 2 | 2 | 40.4074 | 24.1813 | 16.2261
2 | 5 | 52.4583 | 3 | 2 | 2 | 40.4074 | 24.8093 | 15.5981
2 | 6 | 50.625 | 3 | 2 | 2 | 40.4074 | 25.4672 | 14.9402
2 | 7 | 55.4583 | 3 | 2 | 2 | 40.4074 | 23.7327 | 16.6747
2 | 8 | 58.625 | 3 | 2 | 2 | 40.4074 | 22.5964 | 17.811
2 | 9 | 64.5833 | 3 | 2 | 2 | 40.4074 | 20.4582 | 19.9492
2 | 10 | 66.8333 | 3 | 2 | 2 | 40.4074 | 19.6507 | 20.7567
2 | 11 | 70.2083 | 3 | 2 | 2 | 40.4074 | 18.4396 | 21.9678
2 | 12 | 71.0417 | 3 | 2 | 2 | 40.4074 | 18.1405 | 22.2669
2 | 13 | 63.9583 | 3 | 2 | 2 | 40.4074 | 20.6824 | 19.725
2 | 14 | 50.7083 | 3 | 2 | 2 | 40.4074 | 25.4373 | 14.9701
2 | 15 | 58.6667 | 3 | 2 | 2 | 40.4074 | 22.5814 | 17.826
2 | 16 | 59.7917 | 3 | 2 | 2 | 40.4074 | 22.1777 | 18.2297
2 | 17 | 60.125 | 3 | 2 | 2 | 40.4074 | 22.0581 | 18.3493
2 | 18 | 62.6667 | 3 | 2 | 2 | 40.4074 | 21.146 | 19.2614
2 | 19 | 60.9167 | 3 | 2 | 2 | 40.4074 | 21.774 | 18.6334
2 | 20 | 59.125 | 3 | 2 | 2 | 40.4074 | 22.4169 | 17.9905
2 | 21 | 58.0417 | 3 | 2 | 2 | 40.4074 | 22.8057 | 17.6017
2 | 22 | 56.9167 | 3 | 2 | 2 | 40.4074 | 23.2094 | 17.198
2 | 23 | 56.5 | 3 | 2 | 2 | 40.4074 | 23.3589 | 17.0485
2 | 24 | 60.9583 | 3 | 2 | 2 | 40.4074 | 21.759 | 18.6484
2 | 25 | 63.75 | 3 | 2 | 2 | 40.4074 | 20.7572 | 19.6502
2 | 26 | 68.4583 | 3 | 2 | 2 | 40.4074 | 19.0676 | 21.3398
2 | 27 | 69.8333 | 3 | 2 | 2 | 40.4074 | 18.5742 | 21.8332
2 | 28 | 69.9167 | 3 | 2 | 2 | 40.4074 | 18.5443 | 21.8631
3 | 1 | 58.625 | 3 | 2 | 2 | 40.4074 | 22.5964 | 17.811
3 | 2 | 60.375 | 3 | 2 | 2 | 40.4074 | 21.9684 | 18.439
3 | 3 | 66.625 | 3 | 2 | 2 | 40.4074 | 19.7255 | 20.6819
3 | 4 | 68.25 | 3 | 2 | 2 | 40.4074 | 19.1424 | 21.265
3 | 5 | 73.75 | 3 | 2 | 2 | 40.4074 | 17.1686 | 23.2388
3 | 6 | 76.0417 | 3 | 2 | 2 | 40.4074 | 16.3462 | 24.0612
3 | 7 | 74.2917 | 3 | 2 | 2 | 40.4074 | 16.9743 | 23.4331
3 | 8 | 75.7083 | 3 | 2 | 2 | 40.4074 | 16.4659 | 23.9415
3 | 9 | 73.5833 | 3 | 2 | 2 | 40.4074 | 17.2284 | 23.179
3 | 10 | 73.3333 | 3 | 2 | 2 | 40.4074 | 17.3182 | 23.0892
3 | 11 | 72.3333 | 3 | 2 | 2 | 40.4074 | 17.677 | 22.7304
3 | 12 | 70.0417 | 3 | 2 | 2 | 40.4074 | 18.4994 | 21.908
3 | 13 | 69.7083 | 3 | 2 | 2 | 40.4074 | 18.619 | 21.7884
3 | 14 | 73.0417 | 3 | 2 | 2 | 40.4074 | 17.4228 | 22.9846
3 | 15 | 76.3333 | 3 | 2 | 2 | 40.4074 | 16.2416 | 24.1658
3 | 16 | 76.6667 | 3 | 2 | 2 | 40.4074 | 16.122 | 24.2854
3 | 17 | 75.4167 | 3 | 2 | 2 | 40.4074 | 16.5705 | 23.8369
3 | 18 | 72.8333 | 3 | 2 | 2 | 40.4074 | 17.4976 | 22.9098
3 | 19 | 70.4583 | 3 | 2 | 2 | 40.4074 | 18.3499 | 22.0575
3 | 20 | 71.3333 | 3 | 2 | 2 | 40.4074 | 18.0359 | 22.3715
3 | 21 | 71.0833 | 3 | 2 | 2 | 40.4074 | 18.1256 | 22.2818
3 | 22 | 69.625 | 3 | 2 | 2 | 40.4074 | 18.6489 | 21.7585
3 | 23 | 73.8333 | 3 | 2 | 2 | 40.4074 | 17.1387 | 23.2687
3 | 24 | 75.6667 | 3 | 2 | 2 | 40.4074 | 16.4808 | 23.9266
3 | 25 | 72.8333 | 3 | 2 | 2 | 40.4074 | 17.4976 | 22.9098
3 | 26 | 68.375 | 3 | 2 | 2 | 40.4074 | 19.0975 | 21.3099
3 | 27 | 65.7083 | 3 | 2 | 2 | 40.4074 | 20.0544 | 20.353
3 | 28 | 69.2917 | 3 | 2 | 2 | 40.4074 | 18.7685 | 21.6389
3 | 29 | 74.2917 | 3 | 2 | 2 | 40.4074 | 16.9743 | 23.4331
3 | 30 | 72.75 | 3 | 2 | 2 | 40.4074 | 17.5275 | 22.8799
3 | 31 | 69 | 3 | 2 | 2 | 40.4074 | 18.8732 | 21.5342
4 | 1 | 87.4167 | 3 | 2 | 2 | 40.4074 | 12.2642 | 28.1432
4 | 2 | 78.4167 | 3 | 2 | 2 | 40.4074 | 15.494 | 24.9134
4 | 3 | 70.6667 | 3 | 2 | 2 | 40.4074 | 18.2751 | 22.1323
4 | 4 | 74.2917 | 3 | 2 | 2 | 40.4074 | 16.9743 | 23.4331
4 | 5 | 75.5417 | 3 | 2 | 2 | 40.4074 | 16.5257 | 23.8817
4 | 6 | 69.3333 | 3 | 2 | 2 | 40.4074 | 18.7536 | 21.6538
4 | 7 | 65.5 | 3 | 2 | 2 | 40.4074 | 20.1292 | 20.2782
4 | 8 | 55.0833 | 3 | 2 | 2 | 40.4074 | 23.8673 | 16.5401
4 | 9 | 57.3333 | 3 | 2 | 2 | 40.4074 | 23.0599 | 17.3475
4 | 10 | 63.7917 | 3 | 2 | 2 | 40.4074 | 20.7423 | 19.6651
4 | 11 | 69.375 | 3 | 2 | 2 | 40.4074 | 18.7386 | 21.6688
4 | 12 | 72.5833 | 3 | 2 | 2 | 40.4074 | 17.5873 | 22.8201
4 | 13 | 67.625 | 3 | 2 | 2 | 40.4074 | 19.3666 | 21.0408
4 | 14 | 70.6667 | 3 | 2 | 2 | 40.4074 | 18.2751 | 22.1323
4 | 15 | 76.5833 | 3 | 2 | 2 | 40.4074 | 16.1519 | 24.2555
4 | 16 | 84.0417 | 3 | 2 | 2 | 40.4074 | 13.4754 | 26.932
4 | 17 | 83.5417 | 3 | 2 | 2 | 40.4074 | 13.6548 | 26.7526
4 | 18 | 74.8333 | 3 | 2 | 2 | 40.4074 | 16.7799 | 23.6275
4 | 19 | 73.5 | 3 | 2 | 2 | 40.4074 | 17.2583 | 23.1491
4 | 20 | 72.875 | 3 | 2 | 2 | 40.4074 | 17.4826 | 22.9248
4 | 21 | 73.1667 | 3 | 2 | 2 | 40.4074 | 17.378 | 23.0294
4 | 22 | 72.4167 | 3 | 2 | 2 | 40.4074 | 17.6471 | 22.7603
4 | 23 | 74.1667 | 3 | 2 | 2 | 40.4074 | 17.0191 | 23.3883
4 | 24 | 71.5417 | 3 | 2 | 2 | 40.4074 | 17.9611 | 22.4463
4 | 25 | 75.6667 | 3 | 2 | 2 | 40.4074 | 16.4808 | 23.9266
4 | 26 | 76.5833 | 3 | 2 | 2 | 40.4074 | 16.1519 | 24.2555
4 | 27 | 77.875 | 3 | 2 | 2 | 40.4074 | 15.6883 | 24.7191
4 | 28 | 80.75 | 3 | 2 | 2 | 40.4074 | 14.6566 | 25.7508
4 | 29 | 75.7917 | 3 | 2 | 2 | 40.4074 | 16.436 | 23.9714
4 | 30 | 71.4583 | 3 | 2 | 2 | 40.4074 | 17.991 | 22.4164
5 | 1 | 85.875 | 3 | 2 | 2 | 40.4074 | 12.8175 | 27.5899
5 | 2 | 90.9167 | 3 | 2 | 2 | 40.4074 | 11.0082 | 29.3992
5 | 3 | 93.4167 | 3 | 2 | 2 | 40.4074 | 10.1111 | 30.2963
5 | 4 | 92.875 | 3 | 2 | 2 | 40.4074 | 10.3055 | 30.1019
5 | 5 | 88.8333 | 3 | 2 | 2 | 40.4074 | 11.7559 | 28.6515
5 | 6 | 70.875 | 3 | 2 | 2 | 40.4074 | 18.2003 | 22.2071
5 | 7 | 60.1667 | 3 | 2 | 2 | 40.4074 | 22.0431 | 18.3643
5 | 8 | 73.4583 | 3 | 2 | 2 | 40.4074 | 17.2733 | 23.1341
5 | 9 | 68.5833 | 3 | 2 | 2 | 40.4074 | 19.0227 | 21.3847
5 | 10 | 73.4583 | 3 | 2 | 2 | 40.4074 | 17.2733 | 23.1341
5 | 11 | 79.5 | 3 | 2 | 2 | 40.4074 | 15.1052 | 25.3022
5 | 12 | 83.5 | 3 | 2 | 2 | 40.4074 | 13.6698 | 26.7376
5 | 13 | 77.7917 | 3 | 2 | 2 | 40.4074 | 15.7182 | 24.6892
5 | 14 | 75.25 | 3 | 2 | 2 | 40.4074 | 16.6303 | 23.7771
5 | 15 | 69.5 | 3 | 2 | 2 | 40.4074 | 18.6938 | 21.7136
5 | 16 | 70.25 | 3 | 2 | 2 | 40.4074 | 18.4246 | 21.9828
5 | 17 | 71.125 | 3 | 2 | 2 | 40.4074 | 18.1106 | 22.2968
5 | 18 | 79.375 | 3 | 2 | 2 | 40.4074 | 15.1501 | 25.2573
5 | 19 | 82.25 | 3 | 2 | 2 | 40.4074 | 14.1183 | 26.2891
5 | 20 | 87.75 | 3 | 2 | 2 | 40.4074 | 12.1446 | 28.2628
5 | 21 | 93.625 | 3 | 2 | 2 | 40.4074 | 10.0363 | 30.3711
5 | 22 | 95.2917 | 3 | 2 | 2 | 40.4074 | 9.4382 | 30.9692
5 | 23 | 97.375 | 3 | 2 | 2 | 40.4074 | 8.6906 | 31.7168
5 | 24 | 91.875 | 3 | 2 | 2 | 40.4074 | 10.6643 | 29.7431
5 | 25 | 81.0417 | 3 | 2 | 2 | 40.4074 | 14.552 | 25.8554
5 | 26 | 77.5833 | 3 | 2 | 2 | 40.4074 | 15.793 | 24.6144
5 | 27 | 81.7917 | 3 | 2 | 2 | 40.4074 | 14.2828 | 26.1246
5 | 28 | 89.0417 | 3 | 2 | 2 | 40.4074 | 11.6811 | 28.7263
5 | 29 | 91.4583 | 3 | 2 | 2 | 40.4074 | 10.8139 | 29.5935
5 | 30 | 86.8333 | 3 | 2 | 2 | 40.4074 | 12.4736 | 27.9338
5 | 31 | 81.7083 | 3 | 2 | 2 | 40.4074 | 14.3127 | 26.0947
6 | 1 | 94.2917 | 3 | 2 | 2 | 40.4074 | 9.7971 | 30.6103
6 | 2 | 91.7083 | 3 | 2 | 2 | 40.4074 | 10.7241 | 29.6833
6 | 3 | 88.0417 | 3 | 2 | 2 | 40.4074 | 12.04 | 28.3674
6 | 4 | 86 | 3 | 2 | 2 | 40.4074 | 12.7726 | 27.6348
6 | 5 | 89.4167 | 3 | 2 | 2 | 40.4074 | 11.5465 | 28.8609
6 | 6 | 92 | 3 | 2 | 2 | 40.4074 | 10.6195 | 29.7879
6 | 7 | 95.125 | 3 | 2 | 2 | 40.4074 | 9.498 | 30.9094
6 | 8 | 91.0833 | 3 | 2 | 2 | 40.4074 | 10.9484 | 29.459
6 | 9 | 89.3333 | 3 | 2 | 2 | 40.4074 | 11.5764 | 28.831
6 | 10 | 87.2083 | 3 | 2 | 2 | 40.4074 | 12.339 | 28.0684
6 | 11 | 92.25 | 3 | 2 | 2 | 40.4074 | 10.5298 | 29.8776
6 | 12 | 90.7917 | 3 | 2 | 2 | 40.4074 | 11.0531 | 29.3543
6 | 13 | 91.5833 | 3 | 2 | 2 | 40.4074 | 10.769 | 29.6384
6 | 14 | 89.6667 | 3 | 2 | 2 | 40.4074 | 11.4568 | 28.9506
6 | 15 | 88.5833 | 3 | 2 | 2 | 40.4074 | 11.8456 | 28.5618
6 | 16 | 88.875 | 3 | 2 | 2 | 40.4074 | 11.7409 | 28.6665
6 | 17 | 91.75 | 3 | 2 | 2 | 40.4074 | 10.7092 | 29.6982
6 | 18 | 91.375 | 3 | 2 | 2 | 40.4074 | 10.8438 | 29.5636
6 | 19 | 89.0417 | 3 | 2 | 2 | 40.4074 | 11.6811 | 28.7263
6 | 20 | 88.875 | 3 | 2 | 2 | 40.4074 | 11.7409 | 28.6665
6 | 21 | 88.875 | 3 | 2 | 2 | 40.4074 | 11.7409 | 28.6665
6 | 22 | 89.5417 | 3 | 2 | 2 | 40.4074 | 11.5017 | 28.9057
6 | 23 | 87.5417 | 3 | 2 | 2 | 40.4074 | 12.2194 | 28.188
6 | 24 | 83.2917 | 3 | 2 | 2 | 40.4074 | 13.7445 | 26.6629
6 | 25 | 88.6667 | 3 | 2 | 2 | 40.4074 | 11.8157 | 28.5917
6 | 26 | 93.3333 | 3 | 2 | 2 | 40.4074 | 10.141 | 30.2664
6 | 27 | 97.1667 | 3 | 2 | 2 | 40.4074 | 8.7654 | 31.642
6 | 28 | 102.375 | 3 | 2 | 2 | 40.4074 | 6.8963 | 33.5111
6 | 29 | 104.3333 | 3 | 2 | 2 | 40.4074 | 6.1936 | 34.2138
6 | 30 | 99.6667 | 3 | 2 | 2 | 40.4074 | 7.8682 | 32.5392
7 | 1 | 98.625 | 3 | 2 | 2 | 40.4074 | 8.242 | 32.1654
7 | 2 | 101.25 | 3 | 2 | 2 | 40.4074 | 7.3 | 33.1074
7 | 3 | 93.8333 | 3 | 2 | 2 | 40.4074 | 9.9616 | 30.4458
7 | 4 | 94.7083 | 3 | 2 | 2 | 40.4074 | 9.6476 | 30.7598
7 | 5 | 95.75 | 3 | 2 | 2 | 40.4074 | 9.2738 | 31.1336
7 | 6 | 91.2083 | 3 | 2 | 2 | 40.4074 | 10.9036 | 29.5038
7 | 7 | 97.125 | 3 | 2 | 2 | 40.4074 | 8.7803 | 31.6271
7 | 8 | 98.3333 | 3 | 2 | 2 | 40.4074 | 8.3467 | 32.0607
7 | 9 | 98.7083 | 3 | 2 | 2 | 40.4074 | 8.2121 | 32.1953
7 | 10 | 95.0417 | 3 | 2 | 2 | 40.4074 | 9.5279 | 30.8794
7 | 11 | 90.4583 | 3 | 2 | 2 | 40.4074 | 11.1727 | 29.2347
7 | 12 | 87.8333 | 3 | 2 | 2 | 40.4074 | 12.1147 | 28.2927
7 | 13 | 84.75 | 3 | 2 | 2 | 40.4074 | 13.2212 | 27.1862
7 | 14 | 83.9167 | 3 | 2 | 2 | 40.4074 | 13.5202 | 26.8872
7 | 15 | 84.375 | 3 | 2 | 2 | 40.4074 | 13.3558 | 27.0516
7 | 16 | 86 | 3 | 2 | 2 | 40.4074 | 12.7726 | 27.6348
7 | 17 | 91.5417 | 3 | 2 | 2 | 40.4074 | 10.784 | 29.6234
7 | 18 | 94.75 | 3 | 2 | 2 | 40.4074 | 9.6326 | 30.7748
7 | 19 | 97.1667 | 3 | 2 | 2 | 40.4074 | 8.7654 | 31.642
7 | 20 | 96.875 | 3 | 2 | 2 | 40.4074 | 8.87 | 31.5374
7 | 21 | 93.7917 | 3 | 2 | 2 | 40.4074 | 9.9765 | 30.4309
7 | 22 | 91 | 3 | 2 | 2 | 40.4074 | 10.9783 | 29.4291
7 | 23 | 90.625 | 3 | 2 | 2 | 40.4074 | 11.1129 | 29.2945
7 | 24 | 91.0417 | 3 | 2 | 2 | 40.4074 | 10.9634 | 29.444
7 | 25 | 95.9167 | 3 | 2 | 2 | 40.4074 | 9.2139 | 31.1935
7 | 26 | 95.9583 | 3 | 2 | 2 | 40.4074 | 9.199 | 31.2084
7 | 27 | 90.9167 | 3 | 2 | 2 | 40.4074 | 11.0082 | 29.3992
7 | 28 | 93.4167 | 3 | 2 | 2 | 40.4074 | 10.1111 | 30.2963
7 | 29 | 94.9583 | 3 | 2 | 2 | 40.4074 | 9.5579 | 30.8495
7 | 30 | 96.2083 | 3 | 2 | 2 | 40.4074 | 9.1093 | 31.2981
7 | 31 | 89.375 | 3 | 2 | 2 | 40.4074 | 11.5615 | 28.8459
8 | 1 | 99 | 3 | 2 | 2 | 40.4074 | 8.1075 | 32.2999
8 | 2 | 95.2917 | 3 | 2 | 2 | 40.4074 | 9.4382 | 30.9692
8 | 3 | 92.25 | 3 | 2 | 2 | 40.4074 | 10.5298 | 29.8776
8 | 4 | 92.3333 | 3 | 2 | 2 | 40.4074 | 10.4999 | 29.9075
8 | 5 | 96.2917 | 3 | 2 | 2 | 40.4074 | 9.0794 | 31.328
8 | 6 | 97.7917 | 3 | 2 | 2 | 40.4074 | 8.5411 | 31.8663
8 | 7 | 93.4583 | 3 | 2 | 2 | 40.4074 | 10.0961 | 30.3113
8 | 8 | 92.5417 | 3 | 2 | 2 | 40.4074 | 10.4251 | 29.9823
8 | 9 | 94.8333 | 3 | 2 | 2 | 40.4074 | 9.6027 | 30.8047
8 | 10 | 94.7083 | 3 | 2 | 2 | 40.4074 | 9.6476 | 30.7598
8 | 11 | 94.875 | 3 | 2 | 2 | 40.4074 | 9.5878 | 30.8196
8 | 12 | 94.5 | 3 | 2 | 2 | 40.4074 | 9.7223 | 30.6851
8 | 13 | 93.125 | 3 | 2 | 2 | 40.4074 | 10.2158 | 30.1916
8 | 14 | 93.25 | 3 | 2 | 2 | 40.4074 | 10.1709 | 30.2365
8 | 15 | 95.4583 | 3 | 2 | 2 | 40.4074 | 9.3784 | 31.029
8 | 16 | 95 | 3 | 2 | 2 | 40.4074 | 9.5429 | 30.8645
8 | 17 | 93.625 | 3 | 2 | 2 | 40.4074 | 10.0363 | 30.3711
8 | 18 | 93.1667 | 3 | 2 | 2 | 40.4074 | 10.2008 | 30.2066
8 | 19 | 92 | 3 | 2 | 2 | 40.4074 | 10.6195 | 29.7879
8 | 20 | 90.4167 | 3 | 2 | 2 | 40.4074 | 11.1877 | 29.2197
8 | 21 | 91.9167 | 3 | 2 | 2 | 40.4074 | 10.6494 | 29.758
8 | 22 | 91.4583 | 3 | 2 | 2 | 40.4074 | 10.8139 | 29.5935
8 | 23 | 93.4583 | 3 | 2 | 2 | 40.4074 | 10.0961 | 30.3113
8 | 24 | 94.625 | 3 | 2 | 2 | 40.4074 | 9.6775 | 30.7299
8 | 25 | 92.6667 | 3 | 2 | 2 | 40.4074 | 10.3802 | 30.0272
8 | 26 | 90.0833 | 3 | 2 | 2 | 40.4074 | 11.3073 | 29.1001
8 | 27 | 95 | 3 | 2 | 2 | 40.4074 | 9.5429 | 30.8645
8 | 28 | 94.2917 | 3 | 2 | 2 | 40.4074 | 9.7971 | 30.6103
8 | 29 | 93.2083 | 3 | 2 | 2 | 40.4074 | 10.1859 | 30.2215
8 | 30 | 86.2083 | 3 | 2 | 2 | 40.4074 | 12.6979 | 27.7095
8 | 31 | 88.5 | 3 | 2 | 2 | 40.4074 | 11.8755 | 28.5319
9 | 1 | 98.4583 | 3 | 2 | 2 | 40.4074 | 8.3019 | 32.1055
9 | 2 | 92.4167 | 3 | 2 | 2 | 40.4074 | 10.47 | 29.9374
9 | 3 | 91.5417 | 3 | 2 | 2 | 40.4074 | 10.784 | 29.6234
9 | 4 | 92.875 | 3 | 2 | 2 | 40.4074 | 10.3055 | 30.1019
9 | 5 | 95.25 | 3 | 2 | 2 | 40.4074 | 9.4532 | 30.9542
9 | 6 | 93.1667 | 3 | 2 | 2 | 40.4074 | 10.2008 | 30.2066
9 | 7 | 90.0417 | 3 | 2 | 2 | 40.4074 | 11.3222 | 29.0852
9 | 8 | 88.3333 | 3 | 2 | 2 | 40.4074 | 11.9353 | 28.4721
9 | 9 | 86.4167 | 3 | 2 | 2 | 40.4074 | 12.6231 | 27.7843
9 | 10 | 86.75 | 3 | 2 | 2 | 40.4074 | 12.5035 | 27.9039
9 | 11 | 93.5 | 3 | 2 | 2 | 40.4074 | 10.0812 | 30.3262
9 | 12 | 93.5833 | 3 | 2 | 2 | 40.4074 | 10.0513 | 30.3561
9 | 13 | 91.5833 | 3 | 2 | 2 | 40.4074 | 10.769 | 29.6384
9 | 14 | 84.875 | 3 | 2 | 2 | 40.4074 | 13.1763 | 27.2311
9 | 15 | 78.125 | 3 | 2 | 2 | 40.4074 | 15.5986 | 24.8088
9 | 16 | 79.75 | 3 | 2 | 2 | 40.4074 | 15.0155 | 25.3919
9 | 17 | 85.4583 | 3 | 2 | 2 | 40.4074 | 12.967 | 27.4404
9 | 18 | 86.9167 | 3 | 2 | 2 | 40.4074 | 12.4437 | 27.9637
9 | 19 | 85.0833 | 3 | 2 | 2 | 40.4074 | 13.1016 | 27.3058
9 | 20 | 83.8333 | 3 | 2 | 2 | 40.4074 | 13.5501 | 26.8573
9 | 21 | 82.2083 | 3 | 2 | 2 | 40.4074 | 14.1333 | 26.2741
9 | 22 | 79.625 | 3 | 2 | 2 | 40.4074 | 15.0603 | 25.3471
9 | 23 | 81.25 | 3 | 2 | 2 | 40.4074 | 14.4772 | 25.9302
9 | 24 | 82.75 | 3 | 2 | 2 | 40.4074 | 13.9389 | 26.4685
9 | 25 | 88.0833 | 3 | 2 | 2 | 40.4074 | 12.025 | 28.3824
9 | 26 | 89.5417 | 3 | 2 | 2 | 40.4074 | 11.5017 | 28.9057
9 | 27 | 89.5833 | 3 | 2 | 2 | 40.4074 | 11.4867 | 28.9207
9 | 28 | 91.2083 | 3 | 2 | 2 | 40.4074 | 10.9036 | 29.5038
9 | 29 | 90.5833 | 3 | 2 | 2 | 40.4074 | 11.1279 | 29.2795
9 | 30 | 88.7917 | 3 | 2 | 2 | 40.4074 | 11.7708 | 28.6366
10 | 1 | 96.0833 | 3 | 2 | 2 | 40.4074 | 9.1541 | 31.2533
10 | 2 | 94.875 | 3 | 2 | 2 | 40.4074 | 9.5878 | 30.8196
10 | 3 | 90.375 | 3 | 2 | 2 | 40.4074 | 11.2026 | 29.2048
10 | 4 | 85.625 | 3 | 2 | 2 | 40.4074 | 12.9072 | 27.5002
10 | 5 | 83.4583 | 3 | 2 | 2 | 40.4074 | 13.6847 | 26.7227
10 | 6 | 83.2917 | 3 | 2 | 2 | 40.4074 | 13.7445 | 26.6629
10 | 7 | 83.625 | 3 | 2 | 2 | 40.4074 | 13.6249 | 26.7825
10 | 8 | 82.375 | 3 | 2 | 2 | 40.4074 | 14.0735 | 26.3339
10 | 9 | 79 | 3 | 2 | 2 | 40.4074 | 15.2846 | 25.1228
10 | 10 | 74.625 | 3 | 2 | 2 | 40.4074 | 16.8546 | 23.5528
10 | 11 | 69.6667 | 3 | 2 | 2 | 40.4074 | 18.634 | 21.7734
10 | 12 | 68.375 | 3 | 2 | 2 | 40.4074 | 19.0975 | 21.3099
10 | 13 | 73.1667 | 3 | 2 | 2 | 40.4074 | 17.378 | 23.0294
10 | 14 | 82.5417 | 3 | 2 | 2 | 40.4074 | 14.0137 | 26.3937
10 | 15 | 85.3333 | 3 | 2 | 2 | 40.4074 | 13.0119 | 27.3955
10 | 16 | 84.5833 | 3 | 2 | 2 | 40.4074 | 13.281 | 27.1264
10 | 17 | 81.2083 | 3 | 2 | 2 | 40.4074 | 14.4922 | 25.9152
10 | 18 | 81.3333 | 3 | 2 | 2 | 40.4074 | 14.4473 | 25.9601
10 | 19 | 83.1667 | 3 | 2 | 2 | 40.4074 | 13.7894 | 26.618
10 | 20 | 78.5833 | 3 | 2 | 2 | 40.4074 | 15.4342 | 24.9732
10 | 21 | 74.2083 | 3 | 2 | 2 | 40.4074 | 17.0042 | 23.4032
10 | 22 | 72.7083 | 3 | 2 | 2 | 40.4074 | 17.5424 | 22.865
10 | 23 | 70.3333 | 3 | 2 | 2 | 40.4074 | 18.3947 | 22.0127
10 | 24 | 68.9583 | 3 | 2 | 2 | 40.4074 | 18.8882 | 21.5192
10 | 25 | 71.4583 | 3 | 2 | 2 | 40.4074 | 17.991 | 22.4164
10 | 26 | 73.9167 | 3 | 2 | 2 | 40.4074 | 17.1088 | 23.2986
10 | 27 | 75 | 3 | 2 | 2 | 40.4074 | 16.7201 | 23.6873
10 | 28 | 75.625 | 3 | 2 | 2 | 40.4074 | 16.4958 | 23.9116
10 | 29 | 75.125 | 3 | 2 | 2 | 40.4074 | 16.6752 | 23.7322
10 | 30 | 75.875 | 3 | 2 | 2 | 40.4074 | 16.4061 | 24.0013
10 | 31 | 75.875 | 3 | 2 | 2 | 40.4074 | 16.4061 | 24.0013
11 | 1 | 75.0833 | 3 | 2 | 2 | 40.4074 | 16.6902 | 23.7172
11 | 2 | 70 | 3 | 2 | 2 | 40.4074 | 18.5143 | 21.8931
11 | 3 | 71.0417 | 3 | 2 | 2 | 40.4074 | 18.1405 | 22.2669
11 | 4 | 67.5417 | 3 | 2 | 2 | 40.4074 | 19.3965 | 21.0109
11 | 5 | 68.25 | 3 | 2 | 2 | 40.4074 | 19.1424 | 21.265
11 | 6 | 68.5417 | 3 | 2 | 2 | 40.4074 | 19.0377 | 21.3697
11 | 7 | 69.5417 | 3 | 2 | 2 | 40.4074 | 18.6788 | 21.7286
11 | 8 | 68.3333 | 3 | 2 | 2 | 40.4074 | 19.1124 | 21.295
11 | 9 | 67.5417 | 3 | 2 | 2 | 40.4074 | 19.3965 | 21.0109
11 | 10 | 67.0833 | 3 | 2 | 2 | 40.4074 | 19.561 | 20.8464
11 | 11 | 63.5417 | 3 | 2 | 2 | 40.4074 | 20.832 | 19.5754
11 | 12 | 65.75 | 3 | 2 | 2 | 40.4074 | 20.0395 | 20.3679
11 | 13 | 68.9167 | 3 | 2 | 2 | 40.4074 | 18.9031 | 21.5043
11 | 14 | 73.4167 | 3 | 2 | 2 | 40.4074 | 17.2883 | 23.1191
11 | 15 | 74.0417 | 3 | 2 | 2 | 40.4074 | 17.064 | 23.3434
11 | 16 | 68.1667 | 3 | 2 | 2 | 40.4074 | 19.1723 | 21.2351
11 | 17 | 70.4167 | 3 | 2 | 2 | 40.4074 | 18.3648 | 22.0426
11 | 18 | 70.75 | 3 | 2 | 2 | 40.4074 | 18.2452 | 22.1622
11 | 19 | 66.6667 | 3 | 2 | 2 | 40.4074 | 19.7105 | 20.6969
11 | 20 | 70.5833 | 3 | 2 | 2 | 40.4074 | 18.305 | 22.1024
11 | 21 | 67.7083 | 3 | 2 | 2 | 40.4074 | 19.3367 | 21.0707
11 | 22 | 67.25 | 3 | 2 | 2 | 40.4074 | 19.5012 | 20.9062
11 | 23 | 65.2083 | 3 | 2 | 2 | 40.4074 | 20.2339 | 20.1735
11 | 24 | 70.875 | 3 | 2 | 2 | 40.4074 | 18.2003 | 22.2071
11 | 25 | 67.6667 | 3 | 2 | 2 | 40.4074 | 19.3517 | 21.0557
11 | 26 | 65.7083 | 3 | 2 | 2 | 40.4074 | 20.0544 | 20.353
11 | 27 | 57.5833 | 3 | 2 | 2 | 40.4074 | 22.9702 | 17.4372
11 | 28 | 53.25 | 3 | 2 | 2 | 40.4074 | 24.5252 | 15.8822
11 | 29 | 54.9583 | 3 | 2 | 2 | 40.4074 | 23.9122 | 16.4952
11 | 30 | 58.4583 | 3 | 2 | 2 | 40.4074 | 22.6562 | 17.7512
12 | 1 | 49.875 | 3 | 2 | 2 | 40.4074 | 25.7364 | 14.671
12 | 2 | 53.3333 | 3 | 2 | 2 | 40.4074 | 24.4953 | 15.9121
12 | 3 | 55 | 3 | 2 | 2 | 40.4074 | 23.8972 | 16.5102
12 | 4 | 51.0833 | 3 | 2 | 2 | 40.4074 | 25.3027 | 15.1047
12 | 5 | 47.2083 | 3 | 2 | 2 | 40.4074 | 26.6933 | 13.7141
12 | 6 | 52.9583 | 3 | 2 | 2 | 40.4074 | 24.6299 | 15.7775
12 | 7 | 51.125 | 3 | 2 | 2 | 40.4074 | 25.2878 | 15.1196
12 | 8 | 54.0833 | 3 | 2 | 2 | 40.4074 | 24.2262 | 16.1812
12 | 9 | 58.5 | 3 | 2 | 2 | 40.4074 | 22.6412 | 17.7662
12 | 10 | 62.125 | 3 | 2 | 2 | 40.4074 | 21.3404 | 19.067
12 | 11 | 64.25 | 3 | 2 | 2 | 40.4074 | 20.5778 | 19.8296
12 | 12 | 62.7917 | 3 | 2 | 2 | 40.4074 | 21.1011 | 19.3063
12 | 13 | 62.0417 | 3 | 2 | 2 | 40.4074 | 21.3703 | 19.0371
12 | 14 | 64.2917 | 3 | 2 | 2 | 40.4074 | 20.5628 | 19.8446
12 | 15 | 64.625 | 3 | 2 | 2 | 40.4074 | 20.4432 | 19.9642
12 | 16 | 66.5417 | 3 | 2 | 2 | 40.4074 | 19.7554 | 20.652
12 | 17 | 62.5833 | 3 | 2 | 2 | 40.4074 | 21.1759 | 19.2315
12 | 18 | 64.8333 | 3 | 2 | 2 | 40.4074 | 20.3684 | 20.039
12 | 19 | 62.2917 | 3 | 2 | 2 | 40.4074 | 21.2805 | 19.1269
12 | 20 | 59.7083 | 3 | 2 | 2 | 40.4074 | 22.2076 | 18.1998
12 | 21 | 61.4167 | 3 | 2 | 2 | 40.4074 | 21.5945 | 18.8129
12 | 22 | 57.875 | 3 | 2 | 2 | 40.4074 | 22.8655 | 17.5419
12 | 23 | 57.3333 | 3 | 2 | 2 | 40.4074 | 23.0599 | 17.3475
12 | 24 | 54.9583 | 3 | 2 | 2 | 40.4074 | 23.9122 | 16.4952
12 | 25 | 50.7083 | 3 | 2 | 2 | 40.4074 | 25.4373 | 14.9701
12 | 26 | 52.75 | 3 | 2 | 2 | 40.4074 | 24.7046 | 15.7028
12 | 27 | 54.5833 | 3 | 2 | 2 | 40.4074 | 24.0467 | 16.3607
12 | 28 | 53.5 | 3 | 2 | 2 | 40.4074 | 24.4355 | 15.9719
12 | 29 | 54.75 | 3 | 2 | 2 | 40.4074 | 23.9869 | 16.4205
12 | 30 | 53.625 | 3 | 2 | 2 | 40.4074 | 24.3906 | 16.0168
12 | 31 | 50.2083 | 3 | 2 | 2 | 40.4074 | 25.6167 | 14.7907
1 | 1 | 48.5 | 4 | 10 | 10 | 202.037 | 104.5389 | 97.4981
1 | 2 | 50.5833 | 4 | 10 | 10 | 202.037 | 99.1703 | 102.8667
1 | 3 | 54.8333 | 4 | 10 | 10 | 202.037 | 88.2184 | 113.8186
1 | 4 | 50 | 4 | 10 | 10 | 202.037 | 100.6735 | 101.3635
1 | 5 | 52.0417 | 4 | 10 | 10 | 202.037 | 95.4123 | 106.6247
1 | 6 | 52.0417 | 4 | 10 | 10 | 202.037 | 95.4123 | 106.6247
1 | 7 | 56 | 4 | 10 | 10 | 202.037 | 85.212 | 116.825
1 | 8 | 56.4167 | 4 | 10 | 10 | 202.037 | 84.1383 | 117.8987
1 | 9 | 62 | 4 | 10 | 10 | 202.037 | 69.7505 | 132.2865
1 | 10 | 64.5417 | 4 | 10 | 10 | 202.037 | 63.2008 | 138.8362
1 | 11 | 63.25 | 4 | 10 | 10 | 202.037 | 66.5293 | 135.5077
1 | 12 | 61.5833 | 4 | 10 | 10 | 202.037 | 70.8242 | 131.2128
1 | 13 | 65.0833 | 4 | 10 | 10 | 202.037 | 61.805 | 140.232
1 | 14 | 68.5833 | 4 | 10 | 10 | 202.037 | 52.7858 | 149.2512
1 | 15 | 60.4583 | 4 | 10 | 10 | 202.037 | 73.7232 | 128.3138
1 | 16 | 62.7083 | 4 | 10 | 10 | 202.037 | 67.9252 | 134.1118
1 | 17 | 62.125 | 4 | 10 | 10 | 202.037 | 69.4284 | 132.6086
1 | 18 | 59.3333 | 4 | 10 | 10 | 202.037 | 76.6222 | 125.4148
1 | 19 | 61.0833 | 4 | 10 | 10 | 202.037 | 72.1126 | 129.9244
1 | 20 | 57.3333 | 4 | 10 | 10 | 202.037 | 81.7761 | 120.2609
1 | 21 | 59.1667 | 4 | 10 | 10 | 202.037 | 77.0517 | 124.9853
1 | 22 | 62.75 | 4 | 10 | 10 | 202.037 | 67.8178 | 134.2192
1 | 23 | 61.0417 | 4 | 10 | 10 | 202.037 | 72.22 | 129.817
1 | 24 | 53.9583 | 4 | 10 | 10 | 202.037 | 90.4732 | 111.5638
1 | 25 | 56.7917 | 4 | 10 | 10 | 202.037 | 83.1719 | 118.8651
1 | 26 | 54.2917 | 4 | 10 | 10 | 202.037 | 89.6142 | 112.4228
1 | 27 | 55.5833 | 4 | 10 | 10 | 202.037 | 86.2857 | 115.7513
1 | 28 | 58.625 | 4 | 10 | 10 | 202.037 | 78.4476 | 123.5894
1 | 29 | 59.5 | 4 | 10 | 10 | 202.037 | 76.1928 | 125.8442
1 | 30 | 59.25 | 4 | 10 | 10 | 202.037 | 76.837 | 125.2
1 | 31 | 59.25 | 4 | 10 | 10 | 202.037 | 76.837 | 125.2
2 | 1 | 51.25 | 4 | 10 | 10 | 202.037 | 97.4523 | 104.5847
2 | 2 | 53.7917 | 4 | 10 | 10 | 202.037 | 90.9027 | 111.1343
2 | 3 | 57.3333 | 4 | 10 | 10 | 202.037 | 81.7761 | 120.2609
2 | 4 | 54.2083 | 4 | 10 | 10 | 202.037 | 89.829 | 112.208
2 | 5 | 52.4583 | 4 | 10 | 10 | 202.037 | 94.3386 | 107.6984
2 | 6 | 50.625 | 4 | 10 | 10 | 202.037 | 99.0629 | 102.9741
2 | 7 | 55.4583 | 4 | 10 | 10 | 202.037 | 86.6078 | 115.4292
2 | 8 | 58.625 | 4 | 10 | 10 | 202.037 | 78.4476 | 123.5894
2 | 9 | 64.5833 | 4 | 10 | 10 | 202.037 | 63.0934 | 138.9436
2 | 10 | 66.8333 | 4 | 10 | 10 | 202.037 | 57.2954 | 144.7416
2 | 11 | 70.2083 | 4 | 10 | 10 | 202.037 | 48.5983 | 153.4387
2 | 12 | 71.0417 | 4 | 10 | 10 | 202.037 | 46.4508 | 155.5862
2 | 13 | 63.9583 | 4 | 10 | 10 | 202.037 | 64.704 | 137.333
2 | 14 | 50.7083 | 4 | 10 | 10 | 202.037 | 98.8482 | 103.1888
2 | 15 | 58.6667 | 4 | 10 | 10 | 202.037 | 78.3402 | 123.6968
2 | 16 | 59.7917 | 4 | 10 | 10 | 202.037 | 75.4412 | 126.5958
2 | 17 | 60.125 | 4 | 10 | 10 | 202.037 | 74.5822 | 127.4548
2 | 18 | 62.6667 | 4 | 10 | 10 | 202.037 | 68.0325 | 134.0045
2 | 19 | 60.9167 | 4 | 10 | 10 | 202.037 | 72.5421 | 129.4949
2 | 20 | 59.125 | 4 | 10 | 10 | 202.037 | 77.1591 | 124.8779
2 | 21 | 58.0417 | 4 | 10 | 10 | 202.037 | 79.9508 | 122.0862
2 | 22 | 56.9167 | 4 | 10 | 10 | 202.037 | 82.8498 | 119.1872
2 | 23 | 56.5 | 4 | 10 | 10 | 202.037 | 83.9235 | 118.1135
2 | 24 | 60.9583 | 4 | 10 | 10 | 202.037 | 72.4348 | 129.6022
2 | 25 | 63.75 | 4 | 10 | 10 | 202.037 | 65.2409 | 136.7961
2 | 26 | 68.4583 | 4 | 10 | 10 | 202.037 | 53.1079 | 148.9291
2 | 27 | 69.8333 | 4 | 10 | 10 | 202.037 | 49.5646 | 152.4724
2 | 28 | 69.9167 | 4 | 10 | 10 | 202.037 | 49.3499 | 152.6871
3 | 1 | 58.625 | 4 | 10 | 10 | 202.037 | 78.4476 | 123.5894
3 | 2 | 60.375 | 4 | 10 | 10 | 202.037 | 73.938 | 128.099
3 | 3 | 66.625 | 4 | 10 | 10 | 202.037 | 57.8322 | 144.2048
3 | 4 | 68.25 | 4 | 10 | 10 | 202.037 | 53.6447 | 148.3923
3 | 5 | 73.75 | 4 | 10 | 10 | 202.037 | 39.4717 | 162.5653
3 | 6 | 76.0417 | 4 | 10 | 10 | 202.037 | 33.5662 | 168.4708
3 | 7 | 74.2917 | 4 | 10 | 10 | 202.037 | 38.0759 | 163.9611
3 | 8 | 75.7083 | 4 | 10 | 10 | 202.037 | 34.4252 | 167.6118
3 | 9 | 73.5833 | 4 | 10 | 10 | 202.037 | 39.9012 | 162.1358
3 | 10 | 73.3333 | 4 | 10 | 10 | 202.037 | 40.5454 | 161.4916
3 | 11 | 72.3333 | 4 | 10 | 10 | 202.037 | 43.1223 | 158.9147
3 | 12 | 70.0417 | 4 | 10 | 10 | 202.037 | 49.0278 | 153.0092
3 | 13 | 69.7083 | 4 | 10 | 10 | 202.037 | 49.8867 | 152.1503
3 | 14 | 73.0417 | 4 | 10 | 10 | 202.037 | 41.297 | 160.74
3 | 15 | 76.3333 | 4 | 10 | 10 | 202.037 | 32.8146 | 169.2224
3 | 16 | 76.6667 | 4 | 10 | 10 | 202.037 | 31.9557 | 170.0813
3 | 17 | 75.4167 | 4 | 10 | 10 | 202.037 | 35.1768 | 166.8602
3 | 18 | 72.8333 | 4 | 10 | 10 | 202.037 | 41.8339 | 160.2031
3 | 19 | 70.4583 | 4 | 10 | 10 | 202.037 | 47.954 | 154.083
3 | 20 | 71.3333 | 4 | 10 | 10 | 202.037 | 45.6992 | 156.3378
3 | 21 | 71.0833 | 4 | 10 | 10 | 202.037 | 46.3435 | 155.6935
3 | 22 | 69.625 | 4 | 10 | 10 | 202.037 | 50.1015 | 151.9355
3 | 23 | 73.8333 | 4 | 10 | 10 | 202.037 | 39.2569 | 162.7801
3 | 24 | 75.6667 | 4 | 10 | 10 | 202.037 | 34.5326 | 167.5044
3 | 25 | 72.8333 | 4 | 10 | 10 | 202.037 | 41.8339 | 160.2031
3 | 26 | 68.375 | 4 | 10 | 10 | 202.037 | 53.3226 | 148.7144
3 | 27 | 65.7083 | 4 | 10 | 10 | 202.037 | 60.1944 | 141.8426
3 | 28 | 69.2917 | 4 | 10 | 10 | 202.037 | 50.9604 | 151.0766
3 | 29 | 74.2917 | 4 | 10 | 10 | 202.037 | 38.0759 | 163.9611
3 | 30 | 72.75 | 4 | 10 | 10 | 202.037 | 42.0486 | 159.9884
3 | 31 | 69 | 4 | 10 | 10 | 202.037 | 51.712 | 150.325
4 | 1 | 87.4167 | 4 | 10 | 10 | 202.037 | 4.2538 | 197.7832
4 | 2 | 78.4167 | 4 | 10 | 10 | 202.037 | 27.4461 | 174.5909
4 | 3 | 70.6667 | 4 | 10 | 10 | 202.037 | 47.4172 | 154.6198
4 | 4 | 74.2917 | 4 | 10 | 10 | 202.037 | 38.0759 | 163.9611
4 | 5 | 75.5417 | 4 | 10 | 10 | 202.037 | 34.8547 | 167.1823
4 | 6 | 69.3333 | 4 | 10 | 10 | 202.037 | 50.8531 | 151.1839
4 | 7 | 65.5 | 4 | 10 | 10 | 202.037 | 60.7313 | 141.3057
4 | 8 | 55.0833 | 4 | 10 | 10 | 202.037 | 87.5741 | 114.4628
4 | 9 | 57.3333 | 4 | 10 | 10 | 202.037 | 81.7761 | 120.2609
4 | 10 | 63.7917 | 4 | 10 | 10 | 202.037 | 65.1335 | 136.9035
4 | 11 | 69.375 | 4 | 10 | 10 | 202.037 | 50.7457 | 151.2913
4 | 12 | 72.5833 | 4 | 10 | 10 | 202.037 | 42.4781 | 159.5589
4 | 13 | 67.625 | 4 | 10 | 10 | 202.037 | 55.2553 | 146.7817
4 | 14 | 70.6667 | 4 | 10 | 10 | 202.037 | 47.4172 | 154.6198
4 | 15 | 76.5833 | 4 | 10 | 10 | 202.037 | 32.1704 | 169.8666
4 | 16 | 84.0417 | 4 | 10 | 10 | 202.037 | 12.9509 | 189.0861
4 | 17 | 83.5417 | 4 | 10 | 10 | 202.037 | 14.2394 | 187.7976
4 | 18 | 74.8333 | 4 | 10 | 10 | 202.037 | 36.68 | 165.357
4 | 19 | 73.5 | 4 | 10 | 10 | 202.037 | 40.1159 | 161.9211
4 | 20 | 72.875 | 4 | 10 | 10 | 202.037 | 41.7265 | 160.3105
4 | 21 | 73.1667 | 4 | 10 | 10 | 202.037 | 40.9749 | 161.0621
4 | 22 | 72.4167 | 4 | 10 | 10 | 202.037 | 42.9076 | 159.1294
4 | 23 | 74.1667 | 4 | 10 | 10 | 202.037 | 38.398 | 163.639
4 | 24 | 71.5417 | 4 | 10 | 10 | 202.037 | 45.1624 | 156.8746
4 | 25 | 75.6667 | 4 | 10 | 10 | 202.037 | 34.5326 | 167.5044
4 | 26 | 76.5833 | 4 | 10 | 10 | 202.037 | 32.1704 | 169.8666
4 | 27 | 77.875 | 4 | 10 | 10 | 202.037 | 28.8419 | 173.1951
4 | 28 | 80.75 | 4 | 10 | 10 | 202.037 | 21.4333 | 180.6037
4 | 29 | 75.7917 | 4 | 10 | 10 | 202.037 | 34.2105 | 167.8265
4 | 30 | 71.4583 | 4 | 10 | 10 | 202.037 | 45.3771 | 156.6599
5 | 1 | 85.875 | 4 | 10 | 10 | 202.037 | 8.2266 | 193.8104
5 | 2 | 90.9167 | 4 | 10 | 10 | 202.037 | -4.7654 | 206.8024
5 | 3 | 93.4167 | 4 | 10 | 10 | 202.037 | -11.2077 | 213.2447
5 | 4 | 92.875 | 4 | 10 | 10 | 202.037 | -9.8119 | 211.8489
5 | 5 | 88.8333 | 4 | 10 | 10 | 202.037 | 0.60318 | 201.4338
5 | 6 | 70.875 | 4 | 10 | 10 | 202.037 | 46.8803 | 155.1567
5 | 7 | 60.1667 | 4 | 10 | 10 | 202.037 | 74.4748 | 127.5622
5 | 8 | 73.4583 | 4 | 10 | 10 | 202.037 | 40.2233 | 161.8137
5 | 9 | 68.5833 | 4 | 10 | 10 | 202.037 | 52.7858 | 149.2512
5 | 10 | 73.4583 | 4 | 10 | 10 | 202.037 | 40.2233 | 161.8137
5 | 11 | 79.5 | 4 | 10 | 10 | 202.037 | 24.6544 | 177.3826
5 | 12 | 83.5 | 4 | 10 | 10 | 202.037 | 14.3467 | 187.6903
5 | 13 | 77.7917 | 4 | 10 | 10 | 202.037 | 29.0566 | 172.9804
5 | 14 | 75.25 | 4 | 10 | 10 | 202.037 | 35.6063 | 166.4307
5 | 15 | 69.5 | 4 | 10 | 10 | 202.037 | 50.4236 | 151.6134
5 | 16 | 70.25 | 4 | 10 | 10 | 202.037 | 48.4909 | 153.5461
5 | 17 | 71.125 | 4 | 10 | 10 | 202.037 | 46.2361 | 155.8009
5 | 18 | 79.375 | 4 | 10 | 10 | 202.037 | 24.9765 | 177.0605
5 | 19 | 82.25 | 4 | 10 | 10 | 202.037 | 17.5679 | 184.4691
5 | 20 | 87.75 | 4 | 10 | 10 | 202.037 | 3.3948 | 198.6422
5 | 21 | 93.625 | 4 | 10 | 10 | 202.037 | -11.7446 | 213.7816
5 | 22 | 95.2917 | 4 | 10 | 10 | 202.037 | -16.0394 | 218.0764
5 | 23 | 97.375 | 4 | 10 | 10 | 202.037 | -21.408 | 223.445
5 | 24 | 91.875 | 4 | 10 | 10 | 202.037 | -7.2349 | 209.2719
5 | 25 | 81.0417 | 4 | 10 | 10 | 202.037 | 20.6817 | 181.3553
5 | 26 | 77.5833 | 4 | 10 | 10 | 202.037 | 29.5935 | 172.4435
5 | 27 | 81.7917 | 4 | 10 | 10 | 202.037 | 18.749 | 183.288
5 | 28 | 89.0417 | 4 | 10 | 10 | 202.037 | 0.066318 | 201.9707
5 | 29 | 91.4583 | 4 | 10 | 10 | 202.037 | -6.1612 | 208.1982
5 | 30 | 86.8333 | 4 | 10 | 10 | 202.037 | 5.757 | 196.28
5 | 31 | 81.7083 | 4 | 10 | 10 | 202.037 | 18.9637 | 183.0733
6 | 1 | 94.2917 | 4 | 10 | 10 | 202.037 | -13.4625 | 215.4995
6 | 2 | 91.7083 | 4 | 10 | 10 | 202.037 | -6.8055 | 208.8425
6 | 3 | 88.0417 | 4 | 10 | 10 | 202.037 | 2.6432 | 199.3938
6 | 4 | 86 | 4 | 10 | 10 | 202.037 | 7.9044 | 194.1326
6 | 5 | 89.4167 | 4 | 10 | 10 | 202.037 | -0.90003 | 202.937
6 | 6 | 92 | 4 | 10 | 10 | 202.037 | -7.5571 | 209.5941
6 | 7 | 95.125 | 4 | 10 | 10 | 202.037 | -15.6099 | 217.6469
6 | 8 | 91.0833 | 4 | 10 | 10 | 202.037 | -5.1949 | 207.2319
6 | 9 | 89.3333 | 4 | 10 | 10 | 202.037 | -0.68528 | 202.7223
6 | 10 | 87.2083 | 4 | 10 | 10 | 202.037 | 4.7907 | 197.2463
6 | 11 | 92.25 | 4 | 10 | 10 | 202.037 | -8.2013 | 210.2383
6 | 12 | 90.7917 | 4 | 10 | 10 | 202.037 | -4.4433 | 206.4803
6 | 13 | 91.5833 | 4 | 10 | 10 | 202.037 | -6.4833 | 208.5203
6 | 14 | 89.6667 | 4 | 10 | 10 | 202.037 | -1.5443 | 203.5813
6 | 15 | 88.5833 | 4 | 10 | 10 | 202.037 | 1.2474 | 200.7896
6 | 16 | 88.875 | 4 | 10 | 10 | 202.037 | 0.4958 | 201.5412
6 | 17 | 91.75 | 4 | 10 | 10 | 202.037 | -6.9128 | 208.9498
6 | 18 | 91.375 | 4 | 10 | 10 | 202.037 | -5.9465 | 207.9835
6 | 19 | 89.0417 | 4 | 10 | 10 | 202.037 | 0.066318 | 201.9707
6 | 20 | 88.875 | 4 | 10 | 10 | 202.037 | 0.4958 | 201.5412
6 | 21 | 88.875 | 4 | 10 | 10 | 202.037 | 0.4958 | 201.5412
6 | 22 | 89.5417 | 4 | 10 | 10 | 202.037 | -1.2221 | 203.2591
6 | 23 | 87.5417 | 4 | 10 | 10 | 202.037 | 3.9317 | 198.1053
6 | 24 | 83.2917 | 4 | 10 | 10 | 202.037 | 14.8836 | 187.1534
6 | 25 | 88.6667 | 4 | 10 | 10 | 202.037 | 1.0327 | 201.0043
6 | 26 | 93.3333 | 4 | 10 | 10 | 202.037 | -10.993 | 213.03
6 | 27 | 97.1667 | 4 | 10 | 10 | 202.037 | -20.8711 | 222.9081
6 | 28 | 102.375 | 4 | 10 | 10 | 202.037 | -34.2926 | 236.3296
6 | 29 | 104.3333 | 4 | 10 | 10 | 202.037 | -39.339 | 241.376
6 | 30 | 99.6667 | 4 | 10 | 10 | 202.037 | -27.3134 | 229.3504
7 | 1 | 98.625 | 4 | 10 | 10 | 202.037 | -24.6291 | 226.6661
7 | 2 | 101.25 | 4 | 10 | 10 | 202.037 | -31.3936 | 233.4306
7 | 3 | 93.8333 | 4 | 10 | 10 | 202.037 | -12.2814 | 214.3184
7 | 4 | 94.7083 | 4 | 10 | 10 | 202.037 | -14.5362 | 216.5732
7 | 5 | 95.75 | 4 | 10 | 10 | 202.037 | -17.2205 | 219.2575
7 | 6 | 91.2083 | 4 | 10 | 10 | 202.037 | -5.517 | 207.554
7 | 7 | 97.125 | 4 | 10 | 10 | 202.037 | -20.7638 | 222.8008
7 | 8 | 98.3333 | 4 | 10 | 10 | 202.037 | -23.8775 | 225.9145
7 | 9 | 98.7083 | 4 | 10 | 10 | 202.037 | -24.8439 | 226.8809
7 | 10 | 95.0417 | 4 | 10 | 10 | 202.037 | -15.3952 | 217.4322
7 | 11 | 90.4583 | 4 | 10 | 10 | 202.037 | -3.5843 | 205.6213
7 | 12 | 87.8333 | 4 | 10 | 10 | 202.037 | 3.1801 | 198.8569
7 | 13 | 84.75 | 4 | 10 | 10 | 202.037 | 11.1256 | 190.9114
7 | 14 | 83.9167 | 4 | 10 | 10 | 202.037 | 13.273 | 188.764
7 | 15 | 84.375 | 4 | 10 | 10 | 202.037 | 12.0919 | 189.9451
7 | 16 | 86 | 4 | 10 | 10 | 202.037 | 7.9044 | 194.1326
7 | 17 | 91.5417 | 4 | 10 | 10 | 202.037 | -6.376 | 208.413
7 | 18 | 94.75 | 4 | 10 | 10 | 202.037 | -14.6436 | 216.6806
7 | 19 | 97.1667 | 4 | 10 | 10 | 202.037 | -20.8711 | 222.9081
7 | 20 | 96.875 | 4 | 10 | 10 | 202.037 | -20.1195 | 222.1565
7 | 21 | 93.7917 | 4 | 10 | 10 | 202.037 | -12.174 | 214.211
7 | 22 | 91 | 4 | 10 | 10 | 202.037 | -4.9801 | 207.0171
7 | 23 | 90.625 | 4 | 10 | 10 | 202.037 | -4.0138 | 206.0508
7 | 24 | 91.0417 | 4 | 10 | 10 | 202.037 | -5.0875 | 207.1245
7 | 25 | 95.9167 | 4 | 10 | 10 | 202.037 | -17.65 | 219.687
7 | 26 | 95.9583 | 4 | 10 | 10 | 202.037 | -17.7574 | 219.7944
7 | 27 | 90.9167 | 4 | 10 | 10 | 202.037 | -4.7654 | 206.8024
7 | 28 | 93.4167 | 4 | 10 | 10 | 202.037 | -11.2077 | 213.2447
7 | 29 | 94.9583 | 4 | 10 | 10 | 202.037 | -15.1804 | 217.2174
7 | 30 | 96.2083 | 4 | 10 | 10 | 202.037 | -18.4016 | 220.4386
7 | 31 | 89.375 | 4 | 10 | 10 | 202.037 | -0.79265 | 202.8297
8 | 1 | 99 | 4 | 10 | 10 | 202.037 | -25.5955 | 227.6325
8 | 2 | 95.2917 | 4 | 10 | 10 | 202.037 | -16.0394 | 218.0764
8 | 3 | 92.25 | 4 | 10 | 10 | 202.037 | -8.2013 | 210.2383
8 | 4 | 92.3333 | 4 | 10 | 10 | 202.037 | -8.416 | 210.453
8 | 5 | 96.2917 | 4 | 10 | 10 | 202.037 | -18.6163 | 220.6533
8 | 6 | 97.7917 | 4 | 10 | 10 | 202.037 | -22.4817 | 224.5187
8 | 7 | 93.4583 | 4 | 10 | 10 | 202.037 | -11.3151 | 213.3521
8 | 8 | 92.5417 | 4 | 10 | 10 | 202.037 | -8.9529 | 210.9899
8 | 9 | 94.8333 | 4 | 10 | 10 | 202.037 | -14.8583 | 216.8953
8 | 10 | 94.7083 | 4 | 10 | 10 | 202.037 | -14.5362 | 216.5732
8 | 11 | 94.875 | 4 | 10 | 10 | 202.037 | -14.9657 | 217.0027
8 | 12 | 94.5 | 4 | 10 | 10 | 202.037 | -13.9994 | 216.0364
8 | 13 | 93.125 | 4 | 10 | 10 | 202.037 | -10.4561 | 212.4931
8 | 14 | 93.25 | 4 | 10 | 10 | 202.037 | -10.7782 | 212.8152
8 | 15 | 95.4583 | 4 | 10 | 10 | 202.037 | -16.4689 | 218.5059
8 | 16 | 95 | 4 | 10 | 10 | 202.037 | -15.2878 | 217.3248
8 | 17 | 93.625 | 4 | 10 | 10 | 202.037 | -11.7446 | 213.7816
8 | 18 | 93.1667 | 4 | 10 | 10 | 202.037 | -10.5635 | 212.6005
8 | 19 | 92 | 4 | 10 | 10 | 202.037 | -7.5571 | 209.5941
8 | 20 | 90.4167 | 4 | 10 | 10 | 202.037 | -3.4769 | 205.5139
8 | 21 | 91.9167 | 4 | 10 | 10 | 202.037 | -7.3423 | 209.3793
8 | 22 | 91.4583 | 4 | 10 | 10 | 202.037 | -6.1612 | 208.1982
8 | 23 | 93.4583 | 4 | 10 | 10 | 202.037 | -11.3151 | 213.3521
8 | 24 | 94.625 | 4 | 10 | 10 | 202.037 | -14.3215 | 216.3585
8 | 25 | 92.6667 | 4 | 10 | 10 | 202.037 | -9.275 | 211.312
8 | 26 | 90.0833 | 4 | 10 | 10 | 202.037 | -2.618 | 204.655
8 | 27 | 95 | 4 | 10 | 10 | 202.037 | -15.2878 | 217.3248
8 | 28 | 94.2917 | 4 | 10 | 10 | 202.037 | -13.4625 | 215.4995
8 | 29 | 93.2083 | 4 | 10 | 10 | 202.037 | -10.6708 | 212.7078
8 | 30 | 86.2083 | 4 | 10 | 10 | 202.037 | 7.3676 | 194.6694
8 | 31 | 88.5 | 4 | 10 | 10 | 202.037 | 1.4621 | 200.5749
9 | 1 | 98.4583 | 4 | 10 | 10 | 202.037 | -24.1997 | 226.2367
9 | 2 | 92.4167 | 4 | 10 | 10 | 202.037 | -8.6308 | 210.6678
9 | 3 | 91.5417 | 4 | 10 | 10 | 202.037 | -6.376 | 208.413
9 | 4 | 92.875 | 4 | 10 | 10 | 202.037 | -9.8119 | 211.8489
9 | 5 | 95.25 | 4 | 10 | 10 | 202.037 | -15.932 | 217.969
9 | 6 | 93.1667 | 4 | 10 | 10 | 202.037 | -10.5635 | 212.6005
9 | 7 | 90.0417 | 4 | 10 | 10 | 202.037 | -2.5106 | 204.5476
9 | 8 | 88.3333 | 4 | 10 | 10 | 202.037 | 1.8916 | 200.1454
9 | 9 | 86.4167 | 4 | 10 | 10 | 202.037 | 6.8307 | 195.2063
9 | 10 | 86.75 | 4 | 10 | 10 | 202.037 | 5.9718 | 196.0652
9 | 11 | 93.5 | 4 | 10 | 10 | 202.037 | -11.4224 | 213.4594
9 | 12 | 93.5833 | 4 | 10 | 10 | 202.037 | -11.6372 | 213.6742
9 | 13 | 91.5833 | 4 | 10 | 10 | 202.037 | -6.4833 | 208.5203
9 | 14 | 84.875 | 4 | 10 | 10 | 202.037 | 10.8035 | 191.2335
9 | 15 | 78.125 | 4 | 10 | 10 | 202.037 | 28.1977 | 173.8393
9 | 16 | 79.75 | 4 | 10 | 10 | 202.037 | 24.0102 | 178.0268
9 | 17 | 85.4583 | 4 | 10 | 10 | 202.037 | 9.3003 | 192.7367
9 | 18 | 86.9167 | 4 | 10 | 10 | 202.037 | 5.5423 | 196.4947
9 | 19 | 85.0833 | 4 | 10 | 10 | 202.037 | 10.2666 | 191.7704
9 | 20 | 83.8333 | 4 | 10 | 10 | 202.037 | 13.4878 | 188.5492
9 | 21 | 82.2083 | 4 | 10 | 10 | 202.037 | 17.6753 | 184.3617
9 | 22 | 79.625 | 4 | 10 | 10 | 202.037 | 24.3323 | 177.7047
9 | 23 | 81.25 | 4 | 10 | 10 | 202.037 | 20.1448 | 181.8922
9 | 24 | 82.75 | 4 | 10 | 10 | 202.037 | 16.2794 | 185.7576
9 | 25 | 88.0833 | 4 | 10 | 10 | 202.037 | 2.5359 | 199.5011
9 | 26 | 89.5417 | 4 | 10 | 10 | 202.037 | -1.2221 | 203.2591
9 | 27 | 89.5833 | 4 | 10 | 10 | 202.037 | -1.3295 | 203.3665
9 | 28 | 91.2083 | 4 | 10 | 10 | 202.037 | -5.517 | 207.554
9 | 29 | 90.5833 | 4 | 10 | 10 | 202.037 | -3.9064 | 205.9434
9 | 30 | 88.7917 | 4 | 10 | 10 | 202.037 | 0.71055 | 201.3265
10 | 1 | 96.0833 | 4 | 10 | 10 | 202.037 | -18.0795 | 220.1165
10 | 2 | 94.875 | 4 | 10 | 10 | 202.037 | -14.9657 | 217.0027
10 | 3 | 90.375 | 4 | 10 | 10 | 202.037 | -3.3696 | 205.4066
10 | 4 | 85.625 | 4 | 10 | 10 | 202.037 | 8.8708 | 193.1662
10 | 5 | 83.4583 | 4 | 10 | 10 | 202.037 | 14.4541 | 187.5829
10 | 6 | 83.2917 | 4 | 10 | 10 | 202.037 | 14.8836 | 187.1534
10 | 7 | 83.625 | 4 | 10 | 10 | 202.037 | 14.0246 | 188.0124
10 | 8 | 82.375 | 4 | 10 | 10 | 202.037 | 17.2458 | 184.7912
10 | 9 | 79 | 4 | 10 | 10 | 202.037 | 25.9429 | 176.0941
10 | 10 | 74.625 | 4 | 10 | 10 | 202.037 | 37.2169 | 164.8201
10 | 11 | 69.6667 | 4 | 10 | 10 | 202.037 | 49.9941 | 152.0429
10 | 12 | 68.375 | 4 | 10 | 10 | 202.037 | 53.3226 | 148.7144
10 | 13 | 73.1667 | 4 | 10 | 10 | 202.037 | 40.9749 | 161.0621
10 | 14 | 82.5417 | 4 | 10 | 10 | 202.037 | 16.8163 | 185.2207
10 | 15 | 85.3333 | 4 | 10 | 10 | 202.037 | 9.6224 | 192.4146
10 | 16 | 84.5833 | 4 | 10 | 10 | 202.037 | 11.5551 | 190.4819
10 | 17 | 81.2083 | 4 | 10 | 10 | 202.037 | 20.2522 | 181.7848
10 | 18 | 81.3333 | 4 | 10 | 10 | 202.037 | 19.9301 | 182.1069
10 | 19 | 83.1667 | 4 | 10 | 10 | 202.037 | 15.2057 | 186.8313
10 | 20 | 78.5833 | 4 | 10 | 10 | 202.037 | 27.0166 | 175.0204
10 | 21 | 74.2083 | 4 | 10 | 10 | 202.037 | 38.2906 | 163.7464
10 | 22 | 72.7083 | 4 | 10 | 10 | 202.037 | 42.156 | 159.881
10 | 23 | 70.3333 | 4 | 10 | 10 | 202.037 | 48.2762 | 153.7608
10 | 24 | 68.9583 | 4 | 10 | 10 | 202.037 | 51.8194 | 150.2176
10 | 25 | 71.4583 | 4 | 10 | 10 | 202.037 | 45.3771 | 156.6599
10 | 26 | 73.9167 | 4 | 10 | 10 | 202.037 | 39.0422 | 162.9948
10 | 27 | 75 | 4 | 10 | 10 | 202.037 | 36.2505 | 165.7865
10 | 28 | 75.625 | 4 | 10 | 10 | 202.037 | 34.64 | 167.397
10 | 29 | 75.125 | 4 | 10 | 10 | 202.037 | 35.9284 | 166.1086
10 | 30 | 75.875 | 4 | 10 | 10 | 202.037 | 33.9957 | 168.0413
10 | 31 | 75.875 | 4 | 10 | 10 | 202.037 | 33.9957 | 168.0413
11 | 1 | 75.0833 | 4 | 10 | 10 | 202.037 | 36.0358 | 166.0012
11 | 2 | 70 | 4 | 10 | 10 | 202.037 | 49.1351 | 152.9019
11 | 3 | 71.0417 | 4 | 10 | 10 | 202.037 | 46.4508 | 155.5862
11 | 4 | 67.5417 | 4 | 10 | 10 | 202.037 | 55.47 | 146.567
11 | 5 | 68.25 | 4 | 10 | 10 | 202.037 | 53.6447 | 148.3923
11 | 6 | 68.5417 | 4 | 10 | 10 | 202.037 | 52.8931 | 149.1439
11 | 7 | 69.5417 | 4 | 10 | 10 | 202.037 | 50.3162 | 151.7208
11 | 8 | 68.3333 | 4 | 10 | 10 | 202.037 | 53.43 | 148.607
11 | 9 | 67.5417 | 4 | 10 | 10 | 202.037 | 55.47 | 146.567
11 | 10 | 67.0833 | 4 | 10 | 10 | 202.037 | 56.6511 | 145.3859
11 | 11 | 63.5417 | 4 | 10 | 10 | 202.037 | 65.7777 | 136.2593
11 | 12 | 65.75 | 4 | 10 | 10 | 202.037 | 60.087 | 141.95
11 | 13 | 68.9167 | 4 | 10 | 10 | 202.037 | 51.9268 | 150.1102
11 | 14 | 73.4167 | 4 | 10 | 10 | 202.037 | 40.3307 | 161.7063
11 | 15 | 74.0417 | 4 | 10 | 10 | 202.037 | 38.7201 | 163.3169
11 | 16 | 68.1667 | 4 | 10 | 10 | 202.037 | 53.8595 | 148.1775
11 | 17 | 70.4167 | 4 | 10 | 10 | 202.037 | 48.0614 | 153.9756
11 | 18 | 70.75 | 4 | 10 | 10 | 202.037 | 47.2024 | 154.8346
11 | 19 | 66.6667 | 4 | 10 | 10 | 202.037 | 57.7249 | 144.3121
11 | 20 | 70.5833 | 4 | 10 | 10 | 202.037 | 47.6319 | 154.4051
11 | 21 | 67.7083 | 4 | 10 | 10 | 202.037 | 55.0406 | 146.9964
11 | 22 | 67.25 | 4 | 10 | 10 | 202.037 | 56.2217 | 145.8153
11 | 23 | 65.2083 | 4 | 10 | 10 | 202.037 | 61.4829 | 140.5541
11 | 24 | 70.875 | 4 | 10 | 10 | 202.037 | 46.8803 | 155.1567
11 | 25 | 67.6667 | 4 | 10 | 10 | 202.037 | 55.1479 | 146.8891
11 | 26 | 65.7083 | 4 | 10 | 10 | 202.037 | 60.1944 | 141.8426
11 | 27 | 57.5833 | 4 | 10 | 10 | 202.037 | 81.1319 | 120.9051
11 | 28 | 53.25 | 4 | 10 | 10 | 202.037 | 92.2985 | 109.7385
11 | 29 | 54.9583 | 4 | 10 | 10 | 202.037 | 87.8963 | 114.1407
11 | 30 | 58.4583 | 4 | 10 | 10 | 202.037 | 78.8771 | 123.1599
12 | 1 | 49.875 | 4 | 10 | 10 | 202.037 | 100.9956 | 101.0414
12 | 2 | 53.3333 | 4 | 10 | 10 | 202.037 | 92.0838 | 109.9532
12 | 3 | 55 | 4 | 10 | 10 | 202.037 | 87.7889 | 114.2481
12 | 4 | 51.0833 | 4 | 10 | 10 | 202.037 | 97.8818 | 104.1552
12 | 5 | 47.2083 | 4 | 10 | 10 | 202.037 | 107.8674 | 94.1696
12 | 6 | 52.9583 | 4 | 10 | 10 | 202.037 | 93.0501 | 108.9869
12 | 7 | 51.125 | 4 | 10 | 10 | 202.037 | 97.7744 | 104.2626
12 | 8 | 54.0833 | 4 | 10 | 10 | 202.037 | 90.1511 | 111.8859
12 | 9 | 58.5 | 4 | 10 | 10 | 202.037 | 78.7697 | 123.2673
12 | 10 | 62.125 | 4 | 10 | 10 | 202.037 | 69.4284 | 132.6086
12 | 11 | 64.25 | 4 | 10 | 10 | 202.037 | 63.9524 | 138.0846
12 | 12 | 62.7917 | 4 | 10 | 10 | 202.037 | 67.7104 | 134.3266
12 | 13 | 62.0417 | 4 | 10 | 10 | 202.037 | 69.6431 | 132.3939
12 | 14 | 64.2917 | 4 | 10 | 10 | 202.037 | 63.845 | 138.192
12 | 15 | 64.625 | 4 | 10 | 10 | 202.037 | 62.9861 | 139.0509
12 | 16 | 66.5417 | 4 | 10 | 10 | 202.037 | 58.047 | 143.99
12 | 17 | 62.5833 | 4 | 10 | 10 | 202.037 | 68.2473 | 133.7897
12 | 18 | 64.8333 | 4 | 10 | 10 | 202.037 | 62.4492 | 139.5878
12 | 19 | 62.2917 | 4 | 10 | 10 | 202.037 | 68.9989 | 133.0381
12 | 20 | 59.7083 | 4 | 10 | 10 | 202.037 | 75.6559 | 126.3811
12 | 21 | 61.4167 | 4 | 10 | 10 | 202.037 | 71.2537 | 130.7833
12 | 22 | 57.875 | 4 | 10 | 10 | 202.037 | 80.3803 | 121.6567
12 | 23 | 57.3333 | 4 | 10 | 10 | 202.037 | 81.7761 | 120.2609
12 | 24 | 54.9583 | 4 | 10 | 10 | 202.037 | 87.8963 | 114.1407
12 | 25 | 50.7083 | 4 | 10 | 10 | 202.037 | 98.8482 | 103.1888
12 | 26 | 52.75 | 4 | 10 | 10 | 202.037 | 93.587 | 108.45
12 | 27 | 54.5833 | 4 | 10 | 10 | 202.037 | 88.8626 | 113.1744
12 | 28 | 53.5 | 4 | 10 | 10 | 202.037 | 91.6543 | 110.3827
12 | 29 | 54.75 | 4 | 10 | 10 | 202.037 | 88.4331 | 113.6039
12 | 30 | 53.625 | 4 | 10 | 10 | 202.037 | 91.3322 | 110.7048
12 | 31 | 50.2083 | 4 | 10 | 10 | 202.037 | 100.1366 | 101.9004

## SAVINGS CALCULATOR (hidden)
Savings Estimate Calculator
Select these Parameter |  |  |  | Auto-Calculated Savings Estimates
Climate Zone | Site Size Category | Baseline Heater Size (kW) | New Heater Size (kW) | Baseline Heater Designation | Avg. Temp (F) | Baseline Daily kWh | Treatment Daily kWh | Annual kWh Savings
15 | 4 | 10 | 10 | Undersized | 76.28 | 202.037 | 32.9521 | 56474.362

## Regression Results
Baseline For Undersized
All |  | 20.2037 |  | Climate Zone | Yearly Avg Temp. (°F)
Baseline For Properly-Sized |  |  |  | 6 | 63.95
Site Size Category | Regression Coefficients |  |  | 8 | 65.95
| Intercept | Temp. |  | 9 | 65.38
1 | 105.9085 | -1.1784 |  | 10 | 65.63
2 | 88.9213 | -0.7006 |  | 13 | 66.03
3 | 139.8546 | -0.9318 |  | 14 | 63.79
|  |  |  | 15 | 76.28
|  |  |  | 16 | 52.74
Treatment
Site Size Category | Regression Coefficients
| Intercept | Heater Size | Heater Size * Temp. | Annual Oper. Days: | 334
1 | 3.7032 | 13.1354 | -0.13649
2 | 5.8599 | 13.1949 | -0.13339 | Size Category | Proper-Sized Threshold
3 | 10.2591 | 16.6877 | -0.17943 | 1 | 2
4 | 229.5194 | 0 | -2.5769 | 2 | 2
|  |  |  | 3 | 6

## Sample Savings Estimate (hidden)
Table 6: Sample Savings - Climate Zone 8
| Baseline Heater Size | New Heater Size | Baseline Heater Designation | Baseline Daily kWh | Treatment Daily kWh | Annual kWh Savings
1 | 1 | 1 | Undersized | 20.2037 | 7.8371 | 4130.4579
| 3 | 3 | Proper-Sized | 28.1959 | 16.1048 | 4038.4299
2 | 1 | 1 | Undersized | 20.2037 | 10.2575 | 3322.0227
| 6 | 6 | Proper-Sized | 42.7168 | 32.2456 | 3497.3652
3 | 2 | 2 | Undersized | 40.4074 | 19.9677 | 6826.8517
| 6 | 6 | Proper-Sized | 78.4023 | 39.3851 | 13031.7494
4 | 10 | 10 | Undersized | 202.037 | 59.5716 | 47583.4289

## CBH Baseline Data w Heater Size
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | Baseline Heater Size kW | Heater Size X Temp
COCFD | 2 | 1 | 52 | 21.12 | 1 | 52
COCFD | 2 | 1 | 46 | 21.12 | 1 | 46
COCFD | 2 | 1 | 31 | 21.12 | 1 | 31
COCFD | 2 | 1 | 31 | 21.12 | 1 | 31
COCFD | 2 | 1 | 32 | 21.12 | 1 | 32
COCFD | 2 | 1 | 31 | 21.12 | 1 | 31
COCFD | 2 | 1 | 30 | 21.12 | 1 | 30
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 39 | 21.12 | 1 | 39
COCFD | 2 | 1 | 38 | 21.12 | 1 | 38
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 45 | 21.12 | 1 | 45
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 33 | 21.12 | 1 | 33
COCFD | 2 | 1 | 38 | 20.67 | 1 | 38
COCFD | 2 | 1 | 35 | 19.87 | 1 | 35
COCFD | 2 | 1 | 32 | 21.12 | 1 | 32
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 32 | 21.12 | 1 | 32
COCFD | 2 | 1 | 44 | 19.66 | 1 | 44
COCFD | 2 | 1 | 34 | 21.12 | 1 | 34
COCFD | 2 | 1 | 37 | 21.12 | 1 | 37
COCFD | 2 | 1 | 33 | 21.12 | 1 | 33
COCFD | 2 | 1 | 28 | 21.12 | 1 | 28
COCFD | 2 | 1 | 31 | 21.12 | 1 | 31
COCFD | 2 | 1 | 34 | 21.12 | 1 | 34
COCFD | 2 | 1 | 32 | 21.12 | 1 | 32
COCFD | 2 | 1 | 36 | 21.12 | 1 | 36
COCFD | 2 | 1 | 34 | 21.12 | 1 | 34
COCFD | 2 | 1 | 30 | 21.12 | 1 | 30
COCFD | 2 | 1 | 27 | 21.12 | 1 | 27
COCFD | 2 | 1 | 28 | 21.12 | 1 | 28
COCFD | 2 | 1 | 36 | 21.12 | 1 | 36
COCFD | 2 | 1 | 30 | 21.12 | 1 | 30
COCFD | 2 | 1 | 32 | 21.12 | 1 | 32
COCFD | 2 | 1 | 38 | 21.12 | 1 | 38
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 36 | 21.12 | 1 | 36
COCFD | 2 | 1 | 35 | 19.85 | 1 | 35
COCFD | 2 | 1 | 33 | 19.94 | 1 | 33
COCFD | 2 | 1 | 30 | 19.84 | 1 | 30
COCFD | 2 | 1 | 35 | 20.07 | 1 | 35
COCFD | 2 | 1 | 48 | 21.12 | 1 | 48
KE ECAM | 2 | 1 | 36 | 22.32 | 1 | 36
KE ECAM | 2 | 1 | 46 | 21.82 | 1 | 46
KE ECAM | 2 | 1 | 41 | 22.32 | 1 | 41
KE ECAM | 2 | 1 | 38 | 22.32 | 1 | 38
KE ECAM | 2 | 1 | 30 | 22.32 | 1 | 30
KE ECAM | 2 | 1 | 30 | 22.32 | 1 | 30
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 42 | 21.69 | 1 | 42
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 39 | 22.32 | 1 | 39
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 28 | 22.32 | 1 | 28
KE ECAM | 2 | 1 | 24 | 22.32 | 1 | 24
KE ECAM | 2 | 1 | 25 | 22.32 | 1 | 25
KE ECAM | 2 | 1 | 26 | 22.06 | 1 | 26
KE ECAM | 2 | 1 | 29 | 22.32 | 1 | 29
KE ECAM | 2 | 1 | 29 | 22.32 | 1 | 29
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 41 | 22.32 | 1 | 41
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 24 | 22.32 | 1 | 24
KE ECAM | 2 | 1 | 29 | 22.32 | 1 | 29
KE ECAM | 2 | 1 | 34 | 22.32 | 1 | 34
KE ECAM | 2 | 1 | 25 | 22.32 | 1 | 25
KE ECAM | 2 | 1 | 31 | 22.32 | 1 | 31
KE ECAM | 2 | 1 | 34 | 22.32 | 1 | 34
KE ECAM | 2 | 1 | 29 | 21.92 | 1 | 29
KE ECAM | 2 | 1 | 18 | 22.32 | 1 | 18
KE ECAM | 2 | 1 | 22 | 22.12 | 1 | 22
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 34 | 22.32 | 1 | 34
KE ECAM | 2 | 1 | 34 | 22.32 | 1 | 34
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 26 | 22.32 | 1 | 26
KRMC | 3 | 0 | 33 | 83 | 6 | 198
KRMC | 3 | 0 | 14 | 98.93 | 6 | 84
KRMC | 3 | 0 | 20 | 85.7 | 6 | 120
KRMC | 3 | 0 | 21 | 86.8 | 6 | 126
KRMC | 3 | 0 | 18 | 89.06 | 6 | 108
KRMC | 3 | 0 | 16 | 93.15 | 6 | 96
KRMC | 3 | 0 | 14 | 106.25 | 6 | 84
KRMC | 3 | 0 | 20 | 101.37 | 6 | 120
KRMC | 3 | 0 | 30 | 80.93 | 6 | 180
KRMC | 3 | 0 | 35 | 83.64 | 6 | 210
KRMC | 3 | 0 | 30 | 92.52 | 6 | 180
KRMC | 3 | 0 | 25 | 89.17 | 6 | 150
KRMC | 3 | 0 | 19 | 82.92 | 6 | 114
KRMC | 3 | 0 | 20 | 96.73 | 6 | 120
KRMC | 3 | 0 | 38 | 63.45 | 6 | 228
KRMC | 3 | 0 | 32 | 80.41 | 6 | 192
KRMC | 3 | 0 | 24 | 84.01 | 6 | 144
KRMC | 3 | 0 | 19 | 90.2 | 6 | 114
KRMC | 3 | 0 | 29 | 98.03 | 6 | 174
KRMC | 3 | 0 | 39 | 70.46 | 6 | 234
KRMC | 3 | 0 | 38 | 72.97 | 6 | 228
KRMC | 3 | 0 | 31 | 99.6 | 6 | 186
KRMC | 3 | 0 | 23 | 103.96 | 6 | 138
KRMC | 3 | 0 | 30 | 86.62 | 6 | 180
KRMC | 3 | 0 | 35 | 69.46 | 6 | 210
KRMC | 3 | 0 | 32 | 78.05 | 6 | 192
KRMC | 3 | 0 | 33 | 69.65 | 6 | 198
KRMC | 3 | 0 | 27 | 92.92 | 6 | 162
KRMC | 3 | 0 | 16 | 101.64 | 6 | 96
KRMC | 3 | 0 | 20 | 99.81 | 6 | 120
COCTV | 2 | 1 | 22 | 21.12 | 1 | 22
COCTV | 2 | 1 | 24 | 21.12 | 1 | 24
COCTV | 2 | 1 | 25 | 21.12 | 1 | 25
COCTV | 2 | 1 | 27 | 21.12 | 1 | 27
COCTV | 2 | 1 | 32 | 21.12 | 1 | 32
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 20 | 21.12 | 1 | 20
COCTV | 2 | 1 | 16 | 21.12 | 1 | 16
COCTV | 2 | 1 | 13 | 21.12 | 1 | 13
COCTV | 2 | 1 | 21 | 21.12 | 1 | 21
COCTV | 2 | 1 | 22 | 21.12 | 1 | 22
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 24 | 21.12 | 1 | 24
COCTV | 2 | 1 | 25 | 21.12 | 1 | 25
COCTV | 2 | 1 | 18 | 21.12 | 1 | 18
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
COCTV | 2 | 1 | 17 | 21.12 | 1 | 17
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 36 | 21.12 | 1 | 36
COCTV | 2 | 1 | 21 | 21.12 | 1 | 21
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 25 | 21.12 | 1 | 25
COCTV | 2 | 1 | 23 | 21.12 | 1 | 23
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 22 | 21.12 | 1 | 22
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
COCTV | 2 | 1 | 29 | 21.12 | 1 | 29
COCTV | 2 | 1 | 29 | 21.12 | 1 | 29
COCTV | 2 | 1 | 27 | 21.12 | 1 | 27
COCTV | 2 | 1 | 22 | 21.12 | 1 | 22
COCTV | 2 | 1 | 52 | 20.26 | 1 | 52
COCTV | 2 | 1 | 36 | 21.12 | 1 | 36
COCTV | 2 | 1 | 26 | 20.04 | 1 | 26
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
COCTV | 2 | 1 | 38 | 21.12 | 1 | 38
COCTV | 2 | 1 | 46 | 21.12 | 1 | 46
COCTV | 2 | 1 | 45 | 21.12 | 1 | 45
COCTV | 2 | 1 | 23 | 21.12 | 1 | 23
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 39 | 21.12 | 1 | 39
COCTV | 2 | 1 | 36 | 21.12 | 1 | 36
COCTV | 2 | 1 | 32 | 21.12 | 1 | 32
COCTV | 2 | 1 | 38 | 21.12 | 1 | 38
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
COCTV | 2 | 1 | 33 | 19.87 | 1 | 33
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 30 | 19.97 | 1 | 30
COCTV | 2 | 1 | 23 | 20.05 | 1 | 23
COCTV | 2 | 1 | 38 | 19.88 | 1 | 38
COCTV | 2 | 1 | 20 | 20.23 | 1 | 20
COCTV | 2 | 1 | 27 | 20.08 | 1 | 27
COCTV | 2 | 1 | 34 | 20.12 | 1 | 34
COCTV | 2 | 1 | 35 | 20.12 | 1 | 35
COCTV | 2 | 1 | 36 | 20.06 | 1 | 36
COCTV | 2 | 1 | 31 | 20.04 | 1 | 31
COCTV | 2 | 1 | 35 | 20.01 | 1 | 35
COCTV | 2 | 1 | 38 | 19.8 | 1 | 38
COCTV | 2 | 1 | 48 | 19.07 | 1 | 48
COCTV | 2 | 1 | 44 | 21.12 | 1 | 44
COCTV | 2 | 1 | 37 | 21.12 | 1 | 37
COCTV | 2 | 1 | 17 | 21.12 | 1 | 17
COCTV | 2 | 1 | 14 | 21.12 | 1 | 14
COCTV | 2 | 1 | 15 | 21.12 | 1 | 15
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 36 | 21.12 | 1 | 36
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 29 | 21.12 | 1 | 29
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 34 | 21.12 | 1 | 34
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 32 | 21.12 | 1 | 32
COCTV | 2 | 1 | 36 | 21.12 | 1 | 36
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 32 | 21.12 | 1 | 32
COCTV | 2 | 1 | 34 | 21.12 | 1 | 34
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 32 | 20.7 | 1 | 32
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 27 | 21.12 | 1 | 27
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
COCTV | 2 | 1 | 32 | 21.12 | 1 | 32
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
TCWWTP | 1 | 1 | 54 | 11.11 | 1 | 54
TCWWTP | 1 | 1 | 52 | 11.03 | 1 | 52
TCWWTP | 1 | 1 | 63 | 9.84 | 1 | 63
TCWWTP | 1 | 1 | 57 | 11.28 | 1 | 57
TCWWTP | 1 | 1 | 44 | 12.37 | 1 | 44
TCWWTP | 1 | 1 | 63 | 9.86 | 1 | 63
TCWWTP | 1 | 1 | 48 | 12.02 | 1 | 48
TCWWTP | 1 | 1 | 51 | 11.9 | 1 | 51
TCWWTP | 1 | 1 | 53 | 11.15 | 1 | 53
TCWWTP | 1 | 1 | 44 | 12.53 | 1 | 44
TCWWTP | 1 | 1 | 72 | 7.65 | 1 | 72
TCWWTP | 1 | 1 | 55 | 7.24 | 1 | 55
TCWWTP | 1 | 1 | 58 | 10.42 | 1 | 58
TCWWTP | 1 | 1 | 58 | 10 | 1 | 58
TCWWTP | 1 | 1 | 54 | 11.33 | 1 | 54
TCWWTP | 1 | 1 | 59 | 10.04 | 1 | 59
TCWWTP | 1 | 1 | 61 | 10.18 | 1 | 61
TCWWTP | 1 | 1 | 58 | 10.17 | 1 | 58
TCWWTP | 1 | 1 | 47 | 12.2 | 1 | 47
TCWWTP | 1 | 1 | 56 | 10.55 | 1 | 56
TCWWTP | 1 | 1 | 64 | 10 | 1 | 64
TCWWTP | 1 | 1 | 48 | 11.89 | 1 | 48
TCWWTP | 1 | 1 | 49 | 11.95 | 1 | 49
TCWWTP | 1 | 1 | 40 | 12.82 | 1 | 40
TCWWTP | 1 | 1 | 45 | 12.33 | 1 | 45
TCWWTP | 1 | 1 | 47 | 10.3 | 1 | 47
TCWWTP | 1 | 1 | 39 | 11.37 | 1 | 39
TCWWTP | 1 | 1 | 53 | 9.62 | 1 | 53
TCWWTP | 1 | 1 | 47 | 10.53 | 1 | 47
TCWWTP | 1 | 1 | 48 | 10.63 | 1 | 48
TCWWTP | 1 | 1 | 36 | 11.76 | 1 | 36
TCWWTP | 1 | 1 | 65 | 9.4 | 1 | 65
TCWWTP | 1 | 1 | 58 | 10.03 | 1 | 58
TCWWTP | 1 | 1 | 53 | 9.83 | 1 | 53
TCWWTP | 1 | 1 | 48 | 11.69 | 1 | 48
TCWWTP | 1 | 1 | 58 | 10.47 | 1 | 58
TCWWTP | 1 | 1 | 41 | 12.61 | 1 | 41
TCWWTP | 1 | 1 | 58 | 10.18 | 1 | 58
TCWWTP | 1 | 1 | 47 | 12 | 1 | 47
TCWWTP | 1 | 1 | 56 | 11.3 | 1 | 56
TCWWTP | 1 | 1 | 41 | 12.85 | 1 | 41
TCWWTP | 1 | 1 | 60 | 8.86 | 1 | 60
TCWWTP | 1 | 1 | 56 | 9.16 | 1 | 56
TCWWTP | 1 | 1 | 57 | 10.28 | 1 | 57
TCWWTP | 1 | 1 | 43 | 12.52 | 1 | 43
TCWWTP | 1 | 1 | 38 | 13.29 | 1 | 38
TCWWTP | 1 | 1 | 48 | 11.75 | 1 | 48
TCWWTP | 1 | 1 | 55 | 9.43 | 1 | 55
TCWWTP | 1 | 1 | 54 | 9.44 | 1 | 54
TCWWTP | 1 | 1 | 59 | 8.62 | 1 | 59
TCWWTP | 1 | 1 | 64 | 8 | 1 | 64
TCWWTP | 1 | 1 | 50 | 12.5 | 1 | 50
TCWWTP | 1 | 1 | 35 | 13.05 | 1 | 35
TCWWTP | 1 | 1 | 42 | 12.68 | 1 | 42
TCWWTP | 1 | 1 | 58 | 11.45 | 1 | 58
TCWWTP | 1 | 1 | 57 | 10.58 | 1 | 57
TCWWTP | 1 | 1 | 46 | 12.31 | 1 | 46
TCWWTP | 1 | 1 | 45 | 12.22 | 1 | 45
TCWWTP | 1 | 1 | 52 | 11.02 | 1 | 52
TCWWTP | 1 | 1 | 45 | 12.06 | 1 | 45
TCWWTP | 1 | 1 | 62 | 9.8 | 1 | 62
TCWWTP | 1 | 1 | 54 | 10.73 | 1 | 54
TCWWTP | 1 | 1 | 64 | 9.66 | 1 | 64
TCWWTP | 1 | 1 | 67 | 8.87 | 1 | 67
TCWWTP | 1 | 1 | 50 | 10.3 | 1 | 50
TCWWTP | 1 | 1 | 43 | 12.04 | 1 | 43
TCWWTP | 1 | 1 | 56 | 10.69 | 1 | 56
TCWWTP | 1 | 1 | 39 | 12.99 | 1 | 39
TCWWTP | 1 | 1 | 70 | 7.96 | 1 | 70
TCWWTP | 1 | 1 | 68 | 8.17 | 1 | 68
TCWWTP | 1 | 1 | 68 | 9.35 | 1 | 68
TCWWTP | 1 | 1 | 62 | 9.59 | 1 | 62
TCWWTP | 1 | 1 | 49 | 12.4 | 1 | 49
TCWWTP | 1 | 1 | 48 | 11.4 | 1 | 48
TCWWTP | 1 | 1 | 54 | 10.62 | 1 | 54
TCWWTP | 1 | 1 | 56 | 10.53 | 1 | 56
TCWWTP | 1 | 1 | 45 | 12.14 | 1 | 45
TCWWTP | 1 | 1 | 44 | 12.12 | 1 | 44
TCWWTP | 1 | 1 | 44 | 12.34 | 1 | 44
TCWWTP | 1 | 1 | 51 | 8.93 | 1 | 51
TCWWTP | 1 | 1 | 58 | 10.91 | 1 | 58
TCWWTP | 1 | 1 | 51 | 11.47 | 1 | 51
TCWWTP | 1 | 1 | 45 | 12.59 | 1 | 45
TCWWTP | 1 | 1 | 43 | 12.77 | 1 | 43
TCWWTP | 1 | 1 | 48 | 11.86 | 1 | 48
TCWWTP | 1 | 1 | 44 | 12.07 | 1 | 44
TCWWTP | 1 | 1 | 59 | 10.56 | 1 | 59
TCWWTP | 1 | 1 | 46 | 12.18 | 1 | 46
TCWWTP | 1 | 1 | 44 | 12.14 | 1 | 44
TCWP | 2 | 1 | 47 | 21.14 | 1 | 47
TCWP | 2 | 1 | 32 | 23.28 | 1 | 32
TCWP | 2 | 1 | 28 | 23.28 | 1 | 28
TCWP | 2 | 1 | 26 | 22.99 | 1 | 26
TCWP | 2 | 1 | 30 | 22.93 | 1 | 30
TCWP | 2 | 1 | 32 | 23.28 | 1 | 32
TCWP | 2 | 1 | 36 | 23.06 | 1 | 36
TCWP | 2 | 1 | 47 | 21.3 | 1 | 47
TCWP | 2 | 1 | 33 | 23.28 | 1 | 33
TCWP | 2 | 1 | 30 | 23.12 | 1 | 30
TCWP | 2 | 1 | 42 | 22.64 | 1 | 42
TCWP | 2 | 1 | 37 | 23.16 | 1 | 37
TCWP | 2 | 1 | 34 | 21.51 | 1 | 34
TCWP | 2 | 1 | 41 | 23.16 | 1 | 41
TCWP | 2 | 1 | 35 | 22.98 | 1 | 35
TCWP | 2 | 1 | 33 | 23.28 | 1 | 33
TCWP | 2 | 1 | 34 | 23.28 | 1 | 34
TCWP | 2 | 1 | 34 | 22.43 | 1 | 34
TCWP | 2 | 1 | 28 | 22.42 | 1 | 28
TCWP | 2 | 1 | 31 | 23.28 | 1 | 31
TCWP | 2 | 1 | 33 | 23.17 | 1 | 33
TCWP | 2 | 1 | 32 | 22.93 | 1 | 32
TCWP | 2 | 1 | 41 | 21.12 | 1 | 41
TCWP | 2 | 1 | 33 | 22.38 | 1 | 33
TCWP | 2 | 1 | 38 | 21 | 1 | 38
TCWP | 2 | 1 | 30 | 23.28 | 1 | 30
TCWP | 2 | 1 | 30 | 23.28 | 1 | 30
TCWP | 2 | 1 | 45 | 20.95 | 1 | 45
TCWP | 2 | 1 | 31 | 23.28 | 1 | 31
TCWP | 2 | 1 | 35 | 22.71 | 1 | 35
TCWP | 2 | 1 | 44 | 19.64 | 1 | 44
TCWP | 2 | 1 | 39 | 20.98 | 1 | 39
TCWP | 2 | 1 | 38 | 21.84 | 1 | 38
TCWP | 2 | 1 | 38 | 21.54 | 1 | 38
TCWP | 2 | 1 | 45 | 21.21 | 1 | 45
TCWP | 2 | 1 | 40 | 22.95 | 1 | 40
TCWP | 2 | 1 | 40 | 22.11 | 1 | 40
TCWP | 2 | 1 | 40 | 20.57 | 1 | 40
TCWP | 2 | 1 | 43 | 22.08 | 1 | 43
TCWP | 2 | 1 | 47 | 20.01 | 1 | 47
TCWP | 2 | 1 | 42 | 20.15 | 1 | 42
TCWP | 2 | 1 | 35 | 22.01 | 1 | 35
TCWP | 2 | 1 | 35 | 22.61 | 1 | 35
TCWP | 2 | 1 | 34 | 23.2 | 1 | 34
TCWP | 2 | 1 | 36 | 23.28 | 1 | 36
HCNW | 1 | 0 | 47 | 51.5 | 6 | 282
HCNW | 1 | 0 | 36 | 60.6 | 6 | 216
HCNW | 1 | 0 | 48 | 50.7 | 6 | 288
HCNW | 1 | 0 | 33 | 67.1 | 6 | 198
HCNW | 1 | 0 | 34 | 66.5 | 6 | 204
HCNW | 1 | 0 | 38 | 62.2 | 6 | 228
HCNW | 1 | 0 | 45 | 52.3 | 6 | 270
HCNW | 1 | 0 | 55 | 38.9 | 6 | 330
HCNW | 1 | 0 | 44 | 55.2 | 6 | 264
HCNW | 1 | 0 | 43 | 56.7 | 6 | 258
HCNW | 1 | 0 | 38 | 59.9 | 6 | 228
HCNW | 1 | 0 | 31 | 70.4 | 6 | 186
HCNW | 1 | 0 | 55 | 45.6 | 6 | 330
HCNW | 1 | 0 | 43 | 52.9 | 6 | 258
HCNW | 1 | 0 | 45 | 54.5 | 6 | 270
HCNW | 1 | 0 | 31 | 69.6 | 6 | 186
HCNW | 1 | 0 | 25 | 82.5 | 6 | 150
HCNW | 1 | 0 | 22 | 80 | 6 | 132
HCNW | 1 | 0 | 26 | 76.4 | 6 | 156
HCNW | 1 | 0 | 44 | 55.6 | 6 | 264
HCNW | 1 | 0 | 56 | 44.3 | 6 | 336
HCNW | 1 | 0 | 36 | 60.7 | 6 | 216
HCNW | 1 | 0 | 38 | 55.7 | 6 | 228
HCNW | 1 | 0 | 44 | 55.9 | 6 | 264
HCNW | 1 | 0 | 47 | 50.2 | 6 | 282
HCNW | 1 | 0 | 44 | 52.6 | 6 | 264
HCNW | 1 | 0 | 46 | 51.8 | 6 | 276
HCNW | 1 | 0 | 46 | 51.9 | 6 | 276
HCNW | 1 | 0 | 31 | 70.4 | 6 | 186
HCNW | 1 | 0 | 57 | 43.4 | 6 | 342
HCNW | 1 | 0 | 31 | 67.8 | 6 | 186
HCNW | 1 | 0 | 48 | 53.2 | 6 | 288
HCNW | 1 | 0 | 43 | 56.1 | 6 | 258
HCNW | 1 | 0 | 39 | 58.4 | 6 | 234
HCNW | 1 | 0 | 44 | 54.5 | 6 | 264
HCNW | 1 | 0 | 44 | 56.4 | 6 | 264
HCNW | 1 | 0 | 34 | 63.6 | 6 | 204
HCNW | 1 | 0 | 36 | 60.6 | 6 | 216
HCNW | 1 | 0 | 55 | 45.5 | 6 | 330
HCNW | 1 | 0 | 59 | 34.5 | 6 | 354
HCNW | 1 | 0 | 59 | 35.1 | 6 | 354
HCNW | 1 | 0 | 57 | 37.8 | 6 | 342
HCNW | 1 | 0 | 29 | 70.9 | 6 | 174
HCNW | 1 | 0 | 56 | 38.6 | 6 | 336
HCNW | 1 | 0 | 58 | 35.9 | 6 | 348
HCNW | 1 | 0 | 52 | 42.1 | 6 | 312
HCNW | 1 | 0 | 60 | 34 | 6 | 360
HCNW | 1 | 0 | 58 | 37.3 | 6 | 348
HCNW | 1 | 0 | 54 | 38.6 | 6 | 324
HCNW | 1 | 0 | 59 | 41.6 | 6 | 354
HCNW | 1 | 0 | 55 | 40.9 | 6 | 330
HCNW | 1 | 0 | 56 | 40.7 | 6 | 336
HCNW | 1 | 0 | 53 | 42.3 | 6 | 318
HCNW | 1 | 0 | 54 | 40.7 | 6 | 324
HCNW | 1 | 0 | 58 | 36.9 | 6 | 348
HCNW | 1 | 0 | 58 | 36.6 | 6 | 348
HCNW | 1 | 0 | 56 | 39.3 | 6 | 336
HCNW | 1 | 0 | 55 | 39.7 | 6 | 330
HCNW | 1 | 0 | 40 | 58.8 | 6 | 240
HCNW | 1 | 0 | 56 | 36.7 | 6 | 336
PCDC | 2 | 0 | 71 | 32 | 6 | 426
PCDC | 2 | 0 | 52 | 52.3 | 6 | 312
PCDC | 2 | 0 | 56 | 56.5 | 6 | 336
PCDC | 2 | 0 | 72 | 35.5 | 6 | 432
PCDC | 2 | 0 | 79 | 17 | 6 | 474
PCDC | 2 | 0 | 66 | 43.5 | 6 | 396
PCDC | 2 | 0 | 77 | 26.9 | 6 | 462
PCDC | 2 | 0 | 52 | 60.2 | 6 | 312
PCDC | 2 | 0 | 68 | 35.2 | 6 | 408
PCDC | 2 | 0 | 64 | 46.2 | 6 | 384
PCDC | 2 | 0 | 74 | 24.8 | 6 | 444
PCDC | 2 | 0 | 54 | 58.7 | 6 | 324
PCDC | 2 | 0 | 64 | 39.3 | 6 | 384
PCDC | 2 | 0 | 49 | 50.9 | 6 | 294
PCDC | 2 | 0 | 46 | 60.6 | 6 | 276
PCDC | 2 | 0 | 64 | 48.8 | 6 | 384
PCDC | 2 | 0 | 63 | 47.7 | 6 | 378
PCDC | 2 | 0 | 57 | 46.8 | 6 | 342
PCDC | 2 | 0 | 60 | 46.7 | 6 | 360
PCDC | 2 | 0 | 58 | 52.3 | 6 | 348
PCDC | 2 | 0 | 56 | 57.1 | 6 | 336
PCDC | 2 | 0 | 53 | 58.3 | 6 | 318
PCDC | 2 | 0 | 50 | 64.8 | 6 | 300
PCDC | 2 | 0 | 53 | 61.9 | 6 | 318
PCDC | 2 | 0 | 66 | 46.5 | 6 | 396
PCDC | 2 | 0 | 67 | 31.4 | 6 | 402
PCDC | 2 | 0 | 44 | 74.7 | 6 | 264
PCDC | 2 | 0 | 61 | 46 | 6 | 366
PCDC | 2 | 0 | 49 | 73.1 | 6 | 294
PCDC | 2 | 0 | 57 | 55.5 | 6 | 342
PCDC | 2 | 0 | 58 | 41.8 | 6 | 348
PCDC | 2 | 0 | 72 | 38.1 | 6 | 432
PCDC | 2 | 0 | 74 | 25.2 | 6 | 444
PCDC | 2 | 0 | 74 | 30.8 | 6 | 444
PCDC | 2 | 0 | 57 | 57.2 | 6 | 342
PCDC | 2 | 0 | 54 | 55.3 | 6 | 324
PCDC | 2 | 0 | 67 | 42.6 | 6 | 402
PCDC | 2 | 0 | 71 | 38.6 | 6 | 426
PCDC | 2 | 0 | 71 | 38.9 | 6 | 426
PCDC | 2 | 0 | 59 | 51.8 | 6 | 354
PCDC | 2 | 0 | 59 | 46.9 | 6 | 354
PCDC | 2 | 0 | 46 | 71.8 | 6 | 276
PCDC | 2 | 0 | 61 | 50.6 | 6 | 366
PCDC | 2 | 0 | 52 | 60.7 | 6 | 312
PCDC | 2 | 0 | 76 | 31.4 | 6 | 456
PCDC | 2 | 0 | 45 | 72.6 | 6 | 270
PCDC | 2 | 0 | 52 | 67.6 | 6 | 312
PCDC | 2 | 0 | 55 | 57.4 | 6 | 330
PCDC | 2 | 0 | 50 | 62.5 | 6 | 300
PCDC | 2 | 0 | 65 | 51.8 | 6 | 390
PCDC | 2 | 0 | 58 | 51.1 | 6 | 348
PCDC | 2 | 0 | 45 | 68.5 | 6 | 270
PCDC | 2 | 0 | 74 | 39.1 | 6 | 444
PCDC | 2 | 0 | 75 | 31.4 | 6 | 450
PCDC | 2 | 0 | 66 | 41.8 | 6 | 396
PCDC | 2 | 0 | 56 | 52.5 | 6 | 336
PCDC | 2 | 0 | 75 | 33.2 | 6 | 450
PCDC | 2 | 0 | 74 | 33.6 | 6 | 444
PCDC | 2 | 0 | 75 | 32.2 | 6 | 450
PCDC | 2 | 0 | 64 | 44.1 | 6 | 384
PCDC | 2 | 0 | 72 | 31.9 | 6 | 432
PCDC | 2 | 0 | 73 | 31.2 | 6 | 438
PCDC | 2 | 0 | 69 | 37.3 | 6 | 414
PCDC | 2 | 0 | 71 | 31.9 | 6 | 426
PCDC | 2 | 0 | 72 | 33.4 | 6 | 432
PCDC | 2 | 0 | 68 | 39.7 | 6 | 408
PCDC | 2 | 0 | 66 | 37.2 | 6 | 396
PCDC | 2 | 0 | 70 | 32.2 | 6 | 420
PCDC | 2 | 0 | 60 | 51.9 | 6 | 360
PCDC | 2 | 0 | 71 | 35.8 | 6 | 426
PCDC | 2 | 0 |  | 45.5 | 6
PCDC | 2 | 0 | 58 | 61.8 | 6 | 348
PCDC | 2 | 0 | 43 | 75.2 | 6 | 258
PCDC | 2 | 0 | 47 | 66.6 | 6 | 282
PCDC | 2 | 0 | 58 | 54 | 6 | 348
PCDC | 2 | 0 | 60 | 50.1 | 6 | 360
PCDC | 2 | 0 | 62 | 46.4 | 6 | 372
PCDC | 2 | 0 | 53 | 63 | 6 | 318
PCDC | 2 | 0 | 71 | 35.4 | 6 | 426
PCDC | 2 | 0 | 51 | 66.2 | 6 | 306
PCDC | 2 | 0 | 76 | 34.3 | 6 | 456
PCDC | 2 | 0 | 73 | 29.1 | 6 | 438
PCDC | 2 | 0 | 77 | 24.2 | 6 | 462
PCDC | 2 | 0 | 65 | 44.9 | 6 | 390
PCDC | 2 | 0 | 63 | 45.4 | 6 | 378
PCDC | 2 | 0 | 72 | 43.7 | 6 | 432
PCDC | 2 | 0 | 64 | 46 | 6 | 384
PCDC | 2 | 0 | 83 | 23.2 | 6 | 498
PCDC | 2 | 0 | 57 | 54.5 | 6 | 342
PCDC | 2 | 0 | 66 | 45.4 | 6 | 396
PCDC | 2 | 0 | 57 | 53.6 | 6 | 342
PCDC | 2 | 0 | 67 | 39.7 | 6 | 402
PCDC | 2 | 0 | 72 | 33.7 | 6 | 432
PCDC | 2 | 0 |  | 48.8 | 6
PCDC | 2 | 0 | 46 | 70.1 | 6 | 276
PCDC | 2 | 0 | 73 | 30.7 | 6 | 438
PCDC | 2 | 0 | 49 | 65.3 | 6 | 294
PCDC | 2 | 0 | 68 | 41.5 | 6 | 408
PCDC | 2 | 0 | 64 | 41.7 | 6 | 384
PCDC | 2 | 0 | 69 | 37.7 | 6 | 414
PCDC | 2 | 0 | 68 | 47.5 | 6 | 408
PCDC | 2 | 0 | 51 | 63.6 | 6 | 306
PCDC | 2 | 0 | 55 | 56.8 | 6 | 330
PCDC | 2 | 0 | 73 | 34.2 | 6 | 438
PCDC | 2 | 0 | 60 | 51.5 | 6 | 360
PCDC | 2 | 0 | 42 | 76.7 | 6 | 252
PCDC | 2 | 0 | 53 | 56.8 | 6 | 318
PCDC | 2 | 0 | 48 | 69.3 | 6 | 288
PCDC | 2 | 0 | 64 | 44 | 6 | 384
PCDC | 2 | 0 | 56 | 55.4 | 6 | 336
PCDC | 2 | 0 | 42 | 75.7 | 6 | 252
PCDC | 2 | 0 | 53 | 50.8 | 6 | 318
PCDC | 2 | 0 | 41 | 75.4 | 6 | 246
PCDC | 2 | 0 | 58 | 55.3 | 6 | 348
PCDC | 2 | 0 | 69 | 39.2 | 6 | 414
PCDC | 2 | 0 | 65 | 46.4 | 6 | 390
PCDC | 2 | 0 | 72 | 37 | 6 | 432
PCDC | 2 | 0 | 73 | 24.1 | 6 | 438
PCDC | 2 | 0 |  | 36.7 | 6
PCDC | 2 | 0 | 60 | 49.5 | 6 | 360
PCDC | 2 | 0 | 59 | 47.5 | 6 | 354
PCDC | 2 | 0 | 70 | 40.5 | 6 | 420
PCDC | 2 | 0 | 48 | 67.7 | 6 | 288
PCDC | 2 | 0 | 51 | 65.7 | 6 | 306
PCDC | 2 | 0 | 58 | 50.3 | 6 | 348
PCDC | 2 | 0 | 48 | 71.6 | 6 | 288
PCDC | 2 | 0 | 52 | 59.9 | 6 | 312
PCDC | 2 | 0 | 50 | 72.8 | 6 | 300
PCDC | 2 | 0 | 59 | 48.4 | 6 | 354
PCDC | 2 | 0 | 64 | 43 | 6 | 384
PCDC | 2 | 0 | 56 | 55.3 | 6 | 336
PCDC | 2 | 0 | 65 | 50 | 6 | 390
PCDC | 2 | 0 | 75 | 20.4 | 6 | 450
PCDC | 2 | 0 |  | 38.2 | 6
PCDC | 2 | 0 | 66 | 31 | 6 | 396
PCDC | 2 | 0 | 73 | 33.7 | 6 | 438
PCDC | 2 | 0 | 75 | 34.3 | 6 | 450
PCDC | 2 | 0 | 51 | 51.6 | 6 | 306
PCDC | 2 | 0 | 58 | 51.1 | 6 | 348
PCDC | 2 | 0 | 47 | 72.6 | 6 | 282
PCDC | 2 | 0 | 48 | 69.1 | 6 | 288
PCDC | 2 | 0 | 57 | 57.8 | 6 | 342
PCDC | 2 | 0 | 48 | 63.8 | 6 | 288
PCDC | 2 | 0 | 40 | 80.7 | 6 | 240
COMW | 2 | 1 | 45 | 22 | 1 | 45
COMW | 2 | 1 | 38 | 22.8 | 1 | 38
COMW | 2 | 1 | 33 | 22.8 | 1 | 33
COMW | 2 | 1 | 28 | 22.8 | 1 | 28
COMW | 2 | 1 | 27 | 22.8 | 1 | 27
COMW | 2 | 1 | 29 | 22.8 | 1 | 29
COMW | 2 | 1 | 35 | 22.8 | 1 | 35
COMW | 2 | 1 | 39 | 22.1 | 1 | 39
COMW | 2 | 1 | 33 | 22.8 | 1 | 33
COMW | 2 | 1 | 38 | 22.8 | 1 | 38
COMW | 2 | 1 | 35 | 22.8 | 1 | 35
COMW | 2 | 1 | 33 | 22.8 | 1 | 33
COMW | 2 | 1 | 47 | 22.8 | 1 | 47
COMW | 2 | 1 | 47 | 21.6 | 1 | 47
COMW | 2 | 1 | 38 | 22.8 | 1 | 38
COMW | 2 | 1 | 36 | 22.8 | 1 | 36
COMW | 2 | 1 | 35 | 22.8 | 1 | 35
COMW | 2 | 1 | 32 | 22.8 | 1 | 32
COMKR | 2 | 1 | 29 | 21.9 | 1 | 29
COMKR | 2 | 1 | 33 | 19.9 | 1 | 33
COMKR | 2 | 1 | 47 | 21.6 | 1 | 47
COMKR | 2 | 1 | 33 | 20.8 | 1 | 33
COMKR | 2 | 1 | 35 | 21.2 | 1 | 35
COMKR | 2 | 1 | 36 | 20.8 | 1 | 36
COMKR | 2 | 1 | 38 | 21.7 | 1 | 38
COMKR | 2 | 1 | 38 | 20.1 | 1 | 38
COMKR | 2 | 1 | 28 | 21 | 1 | 28
COMKR | 2 | 1 | 45 | 16.8 | 1 | 45
COMKR | 2 | 1 | 27 | 20.3 | 1 | 27
COMKR | 2 | 1 | 38 | 20.4 | 1 | 38
COMKR | 2 | 1 | 35 | 22.3 | 1 | 35
COMKR | 2 | 1 | 32 | 22.3 | 1 | 32
COMKR | 2 | 1 | 33 | 20.4 | 1 | 33
COMKR | 2 | 1 | 39 | 21 | 1 | 39
COMKR | 2 | 1 | 35 | 21.3 | 1 | 35
COMKR | 2 | 1 | 47 | 17.9 | 1 | 47
COCWWTP | 3 | 0 | 30 | 111.33 | 6 | 180
COCWWTP | 3 | 0 | 25 | 115.4 | 6 | 150
COCWWTP | 3 | 0 | 24 | 112.24 | 6 | 144
COCWWTP | 3 | 0 | 13 | 126.58 | 6 | 78
COCWWTP | 3 | 0 | 23 | 117.89 | 6 | 138
COCWWTP | 3 | 0 | 23 | 121.38 | 6 | 138
COCWWTP | 3 | 0 | 22 | 124.61 | 6 | 132
COCWWTP | 3 | 0 | 22 | 120.53 | 6 | 132
COCWWTP | 3 | 0 | 27 | 114.24 | 6 | 162
COCWWTP | 3 | 0 | 35 | 101.63 | 6 | 210
COCWWTP | 3 | 0 | 30 | 103.82 | 6 | 180
COCWWTP | 3 | 0 | 33 | 110.19 | 6 | 198
COCWWTP | 3 | 0 | 35 | 104.85 | 6 | 210
COCWWTP | 3 | 0 | 36 | 108.81 | 6 | 216
COCWWTP | 3 | 0 | 27 | 114.66 | 6 | 162
COCWWTP | 3 | 0 | 29 | 121.22 | 6 | 174
COCWWTP | 3 | 0 | 22 | 122.18 | 6 | 132
COCWWTP | 3 | 0 | 32 | 107.27 | 6 | 192
COCWWTP | 3 | 0 | 38 | 97.29 | 6 | 228
COCWWTP | 3 | 0 | 36 | 111.2 | 6 | 216
COCWWTP | 3 | 0 | 32 | 104.25 | 6 | 192
COCWWTP | 3 | 0 | 38 | 101.91 | 6 | 228
COCWWTP | 3 | 0 | 35 | 104.64 | 6 | 210
COCWWTP | 3 | 0 | 33 | 108.23 | 6 | 198
COCWWTP | 3 | 0 | 29 | 112.79 | 6 | 174
COCWWTP | 3 | 0 | 32 | 103.43 | 6 | 192
COCWWTP | 3 | 0 | 35 | 107.67 | 6 | 210
COCWWTP | 3 | 0 | 22 | 113.54 | 6 | 132
COCWWTP | 3 | 0 | 15 | 118.41 | 6 | 90
COCWWTP | 3 | 0 | 35 | 104.75 | 6 | 210
COCWWTP | 3 | 0 | 33 | 99.61 | 6 | 198
COCWWTP | 3 | 0 | 27 | 111.06 | 6 | 162
COCWWTP | 3 | 0 | 39 | 108.75 | 6 | 234
COCWWTP | 3 | 0 | 28 | 119.15 | 6 | 168
COCWWTP | 3 | 0 | 35 | 101.97 | 6 | 210
COCWWTP | 3 | 0 | 45 | 103.31 | 6 | 270
COCWWTP | 3 | 0 | 38 | 105.3 | 6 | 228
COCWWTP | 3 | 0 | 35 | 107.67 | 6 | 210
COCWWTP | 3 | 0 | 35 | 121.97 | 6 | 210
COCWWTP | 3 | 0 | 31 | 108.73 | 6 | 186
COCWWTP | 3 | 0 | 34 | 107.82 | 6 | 204
COCWWTP | 3 | 0 | 31 | 112.35 | 6 | 186
COCWWTP | 3 | 0 | 35 | 107.22 | 6 | 210
COCWWTP | 3 | 0 | 29 | 114.12 | 6 | 174
COCWWTP | 3 | 0 | 28 | 109.18 | 6 | 168
COCWWTP | 3 | 0 | 31 | 112.2 | 6 | 186
COCWWTP | 3 | 0 | 32 | 124.2 | 6 | 192
COCWWTP | 3 | 0 | 31 | 115.31 | 6 | 186
COCWWTP | 3 | 0 | 30 | 107.83 | 6 | 180
COCWWTP | 3 | 0 | 35 | 101.9 | 6 | 210
COCWWTP | 3 | 0 | 30 | 118.7 | 6 | 180
COCWWTP | 3 | 0 | 18 | 122.01 | 6 | 108
COCWWTP | 3 | 0 | 32 | 122.28 | 6 | 192
COCWWTP | 3 | 0 | 36 | 99.23 | 6 | 216
COCWWTP | 3 | 0 | 28 | 117.11 | 6 | 168
COCWWTP | 3 | 0 | 27 | 115.82 | 6 | 162
COCWWTP | 3 | 0 | 14 | 127.5 | 6 | 84
COCWWTP | 3 | 0 | 17 | 117.79 | 6 | 102
COCWWTP | 3 | 0 | 30 | 115.86 | 6 | 180
COCWWTP | 3 | 0 | 21 | 121.73 | 6 | 126
COCWWTP | 3 | 0 | 20 | 121.41 | 6 | 120
COCWWTP | 3 | 0 | 21 | 128.59 | 6 | 126
COCWWTP | 3 | 0 | 17 | 128.33 | 6 | 102
COCWWTP | 3 | 0 | 16 | 128.92 | 6 | 96
COCWWTP | 3 | 0 | 20 | 115.5 | 6 | 120
COCWWTP | 3 | 0 | 44 | 93.32 | 6 | 264
COCWWTP | 3 | 0 | 28 | 114.78 | 6 | 168
COCWWTP | 3 | 0 | 23 | 117.13 | 6 | 138
COCCH | 1 | 1 | 44 | 10.89 | 0.5 | 22
COCCH | 1 | 1 | 45 | 11.04 | 0.5 | 22.5
COCCH | 1 | 1 | 38 | 10.92 | 0.5 | 19
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 38 | 11.04 | 0.5 | 19
COCCH | 1 | 1 | 48 | 11.04 | 0.5 | 24
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 52 | 11.04 | 0.5 | 26
COCCH | 1 | 1 | 36 | 11.04 | 0.5 | 18
COCCH | 1 | 1 | 39 | 11.04 | 0.5 | 19.5
COCCH | 1 | 1 | 35 | 10.9 | 0.5 | 17.5
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 46 | 11.04 | 0.5 | 23
COCCH | 1 | 1 | 38 | 11.04 | 0.5 | 19
COCCH | 1 | 1 | 27 | 11.04 | 0.5 | 13.5
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 30 | 10.91 | 0.5 | 15
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 24 | 11.04 | 0.5 | 12
COCCH | 1 | 1 | 25 | 10.92 | 0.5 | 12.5
COCCH | 1 | 1 | 35 | 10.92 | 0.5 | 17.5
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 25 | 11.04 | 0.5 | 12.5
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 36 | 10.84 | 0.5 | 18
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 29 | 11.04 | 0.5 | 14.5
COCCH | 1 | 1 | 26 | 11.04 | 0.5 | 13
COCCH | 1 | 1 | 36 | 11.04 | 0.5 | 18
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 29 | 10.92 | 0.5 | 14.5
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 36 | 11.04 | 0.5 | 18
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 37 | 11.04 | 0.5 | 18.5
COCCH | 1 | 1 | 34 | 11.04 | 0.5 | 17
COCCH | 1 | 1 | 29 | 11.04 | 0.5 | 14.5
COCCH | 1 | 1 | 35 | 10.91 | 0.5 | 17.5
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 27 | 11.04 | 0.5 | 13.5
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 38 | 11.04 | 0.5 | 19
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 27 | 11.04 | 0.5 | 13.5
COCCH | 1 | 1 | 25 | 11.04 | 0.5 | 12.5
COCCH | 1 | 1 | 22 | 11.04 | 0.5 | 11
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 33 | 10.91 | 0.5 | 16.5
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 34 | 11.04 | 0.5 | 17
COCCH | 1 | 1 | 34 | 11.04 | 0.5 | 17
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 36 | 11.04 | 0.5 | 18
COCCH | 1 | 1 | 35 | 10.91 | 0.5 | 17.5
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 27 | 11.04 | 0.5 | 13.5
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 22 | 11.04 | 0.5 | 11
COCCH | 1 | 1 | 36 | 11.04 | 0.5 | 18
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
Kid Kare | 1 | 1 | 30 | 21.36 | 1 | 30
Kid Kare | 1 | 1 | 38 | 19.93 | 1 | 38
Kid Kare | 1 | 1 | 30 | 21.36 | 1 | 30
Kid Kare | 1 | 1 | 34 | 21.36 | 1 | 34
Kid Kare | 1 | 1 | 31 | 21.11 | 1 | 31
Kid Kare | 1 | 1 | 32 | 21.36 | 1 | 32
Kid Kare | 1 | 1 | 29 | 21.36 | 1 | 29
Kid Kare | 1 | 1 | 33 | 21.36 | 1 | 33
Kid Kare | 1 | 1 | 33 | 21.36 | 1 | 33
Kid Kare | 1 | 1 | 34 | 21.36 | 1 | 34
Kid Kare | 1 | 1 | 34 | 21.36 | 1 | 34
Kid Kare | 1 | 1 | 30 | 21.36 | 1 | 30
Kid Kare | 1 | 1 | 14 | 21.36 | 1 | 14
Kid Kare | 1 | 1 | 33 | 21.36 | 1 | 33
Kid Kare | 1 | 1 | 20 | 21.36 | 1 | 20
Kid Kare | 1 | 1 | 16 | 21.36 | 1 | 16
Kid Kare | 1 | 1 | 24 | 21.36 | 1 | 24
Kid Kare | 1 | 1 | 20 | 21.36 | 1 | 20
Kid Kare | 1 | 1 | 20 | 21.36 | 1 | 20
Kid Kare | 1 | 1 | 19 | 21.36 | 1 | 19
Kid Kare | 1 | 1 | 32 | 21.12 | 1 | 32
Kid Kare | 1 | 1 | 19 | 21.36 | 1 | 19
Kid Kare | 1 | 1 | 18 | 21.36 | 1 | 18
Kid Kare | 1 | 1 | 14 | 21.36 | 1 | 14
Kid Kare | 1 | 1 | 30 | 20.91 | 1 | 30
Kid Kare | 1 | 1 | 35 | 21.36 | 1 | 35
Kid Kare | 1 | 1 | 33 | 21.36 | 1 | 33
Kid Kare | 1 | 1 | 30 | 21.36 | 1 | 30
Kid Kare | 1 | 1 | 25 | 21.36 | 1 | 25
Kid Kare | 1 | 1 | 20 | 21.36 | 1 | 20
Kid Kare | 1 | 1 | 34 | 20.61 | 1 | 34
Kid Kare | 1 | 1 | 21 | 21.36 | 1 | 21
Kid Kare | 1 | 1 | 26 | 21.36 | 1 | 26
Kid Kare | 1 | 1 | 32 | 21.36 | 1 | 32
Kid Kare | 1 | 1 | 40 | 20.86 | 1 | 40
Kid Kare | 1 | 1 | 16 | 21.36 | 1 | 16
Kid Kare | 1 | 1 | 27 | 21.36 | 1 | 27
Kid Kare | 1 | 1 | 35 | 21.11 | 1 | 35
Kid Kare | 1 | 1 | 27 | 21.36 | 1 | 27
Kid Kare | 1 | 1 | 32 | 20.86 | 1 | 32
Kid Kare | 1 | 1 | 31 | 21.36 | 1 | 31
Kid Kare | 1 | 1 | 37 | 20.9 | 1 | 37
Kid Kare | 1 | 1 | 36 | 20.33 | 1 | 36
Kid Kare | 1 | 1 | 31 | 21.36 | 1 | 31
Kid Kare | 1 | 1 | 27 | 21.36 | 1 | 27
Kid Kare | 1 | 1 | 34 | 21.11 | 1 | 34
Kid Kare | 1 | 1 | 39 | 20.21 | 1 | 39
Kid Kare | 1 | 1 | 30 | 21.36 | 1 | 30
Kid Kare | 1 | 1 | 23 | 21.36 | 1 | 23
Kid Kare | 1 | 1 | 38 | 20.1 | 1 | 38
Kid Kare | 1 | 1 | 39 | 20.34 | 1 | 39
Kid Kare | 1 | 1 | 32 | 20.43 | 1 | 32
Kid Kare | 1 | 1 | 29 | 20.63 | 1 | 29
BayView | 3 | 1 | 48 | 33.36 | 1.5 | 72
BayView | 3 | 1 | 52 | 33.36 | 1.5 | 78
BayView | 3 | 1 | 44 | 33.36 | 1.5 | 66
BayView | 3 | 1 | 42 | 33.36 | 1.5 | 63
BayView | 3 | 1 | 47 | 33.36 | 1.5 | 70.5
BayView | 3 | 1 | 52 | 33.36 | 1.5 | 78
BayView | 3 | 1 | 59 | 33.36 | 1.5 | 88.5
BayView | 3 | 1 | 63 | 33.36 | 1.5 | 94.5
BayView | 3 | 1 | 61 | 33.36 | 1.5 | 91.5
BayView | 3 | 1 | 50 | 33.36 | 1.5 | 75
BayView | 3 | 1 | 41 | 33.36 | 1.5 | 61.5
BayView | 3 | 1 | 46 | 33.36 | 1.5 | 69
BayView | 3 | 1 | 54 | 33.36 | 1.5 | 81
BayView | 3 | 1 | 47 | 33.36 | 1.5 | 70.5
BayView | 3 | 1 | 39 | 33.36 | 1.5 | 58.5
BayView | 3 | 1 | 41 | 33.36 | 1.5 | 61.5
BayView | 3 | 1 | 45 | 33.36 | 1.5 | 67.5
BayView | 3 | 1 | 34 | 33.36 | 1.5 | 51
BayView | 3 | 1 | 38 | 33.36 | 1.5 | 57
BayView | 3 | 1 | 40 | 33.33 | 1.5 | 60
BayView | 3 | 1 | 52 | 33.36 | 1.5 | 78
BayView | 3 | 1 | 44 | 33.36 | 1.5 | 66
BayView | 3 | 1 | 60 | 33.36 | 1.5 | 90
BayView | 3 | 1 | 45 | 33.36 | 1.5 | 67.5
BayView | 3 | 1 | 41 | 33.36 | 1.5 | 61.5
BayView | 3 | 1 | 38 | 33.31 | 1.5 | 57
BayView | 3 | 1 | 35 | 33.36 | 1.5 | 52.5
BayView | 3 | 1 | 34 | 33.36 | 1.5 | 51
BayView | 3 | 1 | 33 | 33.36 | 1.5 | 49.5
BayView | 3 | 1 | 36 | 33.36 | 1.5 | 54
BayView | 3 | 1 | 33 | 33.36 | 1.5 | 49.5
BayView | 3 | 1 | 33 | 33.36 | 1.5 | 49.5
BayView | 3 | 1 | 36 | 33.36 | 1.5 | 54
BayView | 3 | 1 | 45 | 33.36 | 1.5 | 67.5
BayView | 3 | 1 | 37 | 33.36 | 1.5 | 55.5
BayView | 3 | 1 | 44 | 33.36 | 1.5 | 66
BayView | 3 | 1 | 40 | 33.35 | 1.5 | 60
BayView | 3 | 1 | 47 | 33.36 | 1.5 | 70.5
BayView | 3 | 1 | 40 | 33.36 | 1.5 | 60
BayView | 3 | 1 | 36 | 33.36 | 1.5 | 54
BayView | 3 | 1 | 38 | 33.36 | 1.5 | 57
BayView | 3 | 1 | 35 | 33.36 | 1.5 | 52.5
BayView | 3 | 1 | 35 | 32.99 | 1.5 | 52.5
BayView | 3 | 1 | 34 | 32.26 | 1.5 | 51
BayView | 3 | 1 | 38 | 32.39 | 1.5 | 57
BayView | 3 | 1 | 43 | 33.1 | 1.5 | 64.5
BayView | 3 | 1 | 49 | 33.35 | 1.5 | 73.5
BayView | 3 | 1 | 49 | 33.36 | 1.5 | 73.5
BayView | 3 | 1 | 41 | 33.36 | 1.5 | 61.5
BayView | 3 | 1 | 42 | 33.36 | 1.5 | 63
BLDG210 | 2 | 0 | 34 | 47.95 | 2.5 | 85
BLDG210 | 2 | 0 | 46 | 38.73 | 2.5 | 115
BLDG210 | 2 | 0 | 33 | 44.7 | 2.5 | 82.5
BLDG210 | 2 | 0 | 34 | 51.14 | 2.5 | 85
BLDG210 | 2 | 0 | 35 | 48.59 | 2.5 | 87.5
BLDG210 | 2 | 0 | 44 | 43.79 | 2.5 | 110
BLDG210 | 2 | 0 | 46 | 42.09 | 2.5 | 115
BLDG210 | 2 | 0 | 34 | 46.4 | 2.5 | 85
BLDG210 | 2 | 0 | 41 | 47.68 | 2.5 | 102.5
BLDG210 | 2 | 0 | 36 | 43.68 | 2.5 | 90
BLDG210 | 2 | 0 | 35 | 49.39 | 2.5 | 87.5
BLDG210 | 2 | 0 | 32 | 48.16 | 2.5 | 80
BLDG210 | 2 | 0 | 34 | 47.36 | 2.5 | 85
BLDG210 | 2 | 0 | 32 | 49.76 | 2.5 | 80
BLDG210 | 2 | 0 | 33 | 48.43 | 2.5 | 82.5
BLDG210 | 2 | 0 | 30 | 49.71 | 2.5 | 75
BLDG210 | 2 | 0 | 32 | 48.16 | 2.5 | 80
BLDG210 | 2 | 0 | 32 | 48.43 | 2.5 | 80
BLDG210 | 2 | 0 | 29 | 50.61 | 2.5 | 72.5
BLDG210 | 2 | 0 | 35 | 48.43 | 2.5 | 87.5
BLDG210 | 2 | 0 | 42 | 45.76 | 2.5 | 105
BNS GEN | 3 | 1 | 48 | 44.4 | 4.95 | 237.59
BNS GEN | 3 | 1 | 33 | 44.4 | 4.95 | 163.34
BNS GEN | 3 | 1 | 34 | 44.4 | 4.95 | 168.29
BNS GEN | 3 | 1 | 35 | 44.4 | 4.95 | 173.25
BNS GEN | 3 | 1 | 49 | 44.4 | 4.95 | 242.54
BNS GEN | 3 | 1 | 52 | 44.4 | 4.95 | 257.39
BNS GEN | 3 | 1 | 59 | 44.4 | 4.95 | 292.04
BNS GEN | 3 | 1 | 63 | 44.4 | 4.95 | 311.84
BNS GEN | 3 | 1 | 61 | 44.4 | 4.95 | 301.94
BNS GEN | 3 | 1 | 50 | 44.4 | 4.95 | 247.49
BNS GEN | 3 | 1 | 36 | 44.4 | 4.95 | 178.19
BNS GEN | 3 | 1 | 46 | 44.4 | 4.95 | 227.69
BNS GEN | 3 | 1 | 34 | 43.47 | 4.95 | 168.29
BNS GEN | 3 | 1 | 47 | 44.4 | 4.95 | 232.64
BNS GEN | 3 | 1 | 39 | 44.4 | 4.95 | 193.04
BNS GEN | 3 | 1 | 41 | 44.4 | 4.95 | 202.94
BNS GEN | 3 | 1 | 47 | 44.4 | 4.95 | 232.64
BNS GEN | 3 | 1 | 38 | 43.48 | 4.95 | 188.09
BNS GEN | 3 | 1 | 52 | 43.47 | 4.95 | 257.39
BNS GEN | 3 | 1 | 44 | 43.48 | 4.95 | 217.79
BNS GEN | 3 | 1 | 60 | 43.48 | 4.95 | 297
BNS GEN | 3 | 1 | 41 | 43.48 | 4.95 | 202.94
BNS GEN | 3 | 1 | 45 | 44.4 | 4.95 | 222.74
BNS GEN | 3 | 1 | 44 | 44.4 | 4.95 | 217.79
BNS GEN | 3 | 1 | 40 | 43.48 | 4.95 | 198
BNS GEN | 3 | 1 | 33 | 44.4 | 4.95 | 163.34
BNS GEN | 3 | 1 | 42 | 44.4 | 4.95 | 207.89
BNS GEN | 3 | 1 | 42 | 44.4 | 4.95 | 207.89
BNS GEN | 3 | 1 | 52 | 44.4 | 4.95 | 257.39
BNS GEN | 3 | 1 | 47 | 44.4 | 4.95 | 232.64
BNS GEN | 3 | 1 | 54 | 44.4 | 4.95 | 267.29
BNS GEN | 3 | 1 | 49 | 44.4 | 4.95 | 242.54
BNS GEN | 3 | 1 | 43 | 44.4 | 4.95 | 212.84
BNS GEN | 3 | 1 | 38 | 44.4 | 4.95 | 188.09
BNS GEN | 3 | 1 | 34 | 44.4 | 4.95 | 168.29
BNS GEN | 3 | 1 | 35 | 44.4 | 4.95 | 173.25
BNS GEN | 3 | 1 | 37 | 44.4 | 4.95 | 183.14
BNS GEN | 3 | 1 | 33 | 44.4 | 4.95 | 163.34
BNS GEN | 3 | 1 | 36 | 44.4 | 4.95 | 178.19
BNS GEN | 3 | 1 | 44 | 44.4 | 4.95 | 217.79
BNS GEN | 3 | 1 | 35 | 44.4 | 4.95 | 173.25
BNS GEN | 3 | 1 | 45 | 44.4 | 4.95 | 222.74
BNS GEN | 3 | 1 | 41 | 44.4 | 4.95 | 202.94
BNS GEN | 3 | 1 | 40 | 44.4 | 4.95 | 198
BNS GEN | 3 | 1 | 41 | 44.4 | 4.95 | 202.94
BNS GEN | 3 | 1 | 40 | 44.4 | 4.95 | 198
BNS GEN | 3 | 1 | 36 | 44.4 | 4.95 | 178.19
BNS GEN | 3 | 1 | 38 | 44.4 | 4.95 | 188.09
NQ | 4 | 1 | 37 | 228.96 | 10 | 370
NQ | 4 | 1 | 40 | 228.96 | 10 | 400
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 43 | 226.69 | 10 | 430
NQ | 4 | 1 | 38 | 228.49 | 10 | 380
NQ | 4 | 1 | 37 | 228.96 | 10 | 370
NQ | 4 | 1 | 36 | 228.96 | 10 | 360
NQ | 4 | 1 | 37 | 228.96 | 10 | 370
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 38 | 228.96 | 10 | 380
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 37 | 228.96 | 10 | 370
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 46 | 228.96 | 10 | 460
NQ | 4 | 1 | 52 | 228.96 | 10 | 520
NQ | 4 | 1 | 43 | 226.8 | 10 | 430
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 38 | 228.96 | 10 | 380
NQ | 4 | 1 | 33 | 228.96 | 10 | 330
NQ | 4 | 1 | 42 | 228.96 | 10 | 420
NQ | 4 | 1 | 37 | 228.96 | 10 | 370
NQ | 4 | 1 | 36 | 228.96 | 10 | 360
NQ | 4 | 1 | 40 | 224.97 | 10 | 400
NQ | 4 | 1 | 41 | 228.96 | 10 | 410
NQ | 4 | 1 | 40 | 228.96 | 10 | 400
NQ | 4 | 1 | 32 | 228.96 | 10 | 320
NQ | 4 | 1 | 43 | 228.96 | 10 | 430
NQ | 4 | 1 | 32 | 228.65 | 10 | 320
NQ | 4 | 1 | 32 | 228.96 | 10 | 320
NQ | 4 | 1 | 30 | 228.96 | 10 | 300
NQ | 4 | 1 | 30 | 228.96 | 10 | 300
NQ | 4 | 1 | 24 | 228.96 | 10 | 240
NQ | 4 | 1 | 10 | 228.96 | 10 | 100
NQ | 4 | 1 | 8 | 228.96 | 10 | 80
NQ | 4 | 1 | 9 | 228.96 | 10 | 90
NQ | 4 | 1 | 35 | 227.87 | 10 | 350
NQ | 4 | 1 | 35 | 228.96 | 10 | 350
NQ | 4 | 1 | 38 | 228.96 | 10 | 380
NQ | 4 | 1 | 35 | 228.82 | 10 | 350
NQ | 4 | 1 | 34 | 228.96 | 10 | 340
NQ | 4 | 1 | 35 | 228.69 | 10 | 350
NQ | 4 | 1 | 34 | 226.37 | 10 | 340
NQ | 4 | 1 | 33 | 227.72 | 10 | 330
NQ | 4 | 1 | 32 | 228.96 | 10 | 320
NQ | 4 | 1 | 39 | 228.23 | 10 | 390
NQ | 4 | 1 | 36 | 215.89 | 10 | 360
NQ | 4 | 1 | 36 | 228.96 | 10 | 360
NQ | 4 | 1 | 43 | 228.96 | 10 | 430
NQ | 4 | 1 | 41 | 228.96 | 10 | 410
NQ | 4 | 1 | 24 | 228.96 | 10 | 240

## BL Size1 Var
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | Baseline Heater Size kW | Heater Size X Temp
HCNW | 1 | 0 | 47 | 51.5 | 6 | 282 | SUMMARY OUTPUT
HCNW | 1 | 0 | 36 | 60.6 | 6 | 216
HCNW | 1 | 0 | 48 | 50.7 | 6 | 288 | Regression Statistics
HCNW | 1 | 0 | 33 | 67.1 | 6 | 198 | Multiple R | 0.98258
HCNW | 1 | 0 | 34 | 66.5 | 6 | 204 | R Square | 0.96547
HCNW | 1 | 0 | 38 | 62.2 | 6 | 228 | Adjusted R Square | 0.96487
HCNW | 1 | 0 | 45 | 52.3 | 6 | 270 | Standard Error | 2.3296
HCNW | 1 | 0 | 55 | 38.9 | 6 | 330 | Observations | 60
HCNW | 1 | 0 | 44 | 55.2 | 6 | 264
HCNW | 1 | 0 | 43 | 56.7 | 6 | 258 | ANOVA
HCNW | 1 | 0 | 38 | 59.9 | 6 | 228 |  | df | SS | MS | F | Significance F
HCNW | 1 | 0 | 31 | 70.4 | 6 | 186 | Regression | 1 | 8800.089 | 8800.089 | 1621.4618 | 4.3172e-44
HCNW | 1 | 0 | 55 | 45.6 | 6 | 330 | Residual | 58 | 314.7809 | 5.4273
HCNW | 1 | 0 | 43 | 52.9 | 6 | 258 | Total | 59 | 9114.8698
HCNW | 1 | 0 | 45 | 54.5 | 6 | 270
HCNW | 1 | 0 | 31 | 69.6 | 6 | 186 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
HCNW | 1 | 0 | 25 | 82.5 | 6 | 150 | Intercept | 105.9085 | 1.3717 | 77.2104 | 3.5698e-60 | 103.1628 | 108.6542 | 103.1628 | 108.6542
HCNW | 1 | 0 | 22 | 80 | 6 | 132 | X Variable 1 | -1.1784 | 0.029263 | -40.2674 | 4.3172e-44 | -1.2369 | -1.1198 | -1.2369 | -1.1198
HCNW | 1 | 0 | 26 | 76.4 | 6 | 156
HCNW | 1 | 0 | 44 | 55.6 | 6 | 264
HCNW | 1 | 0 | 56 | 44.3 | 6 | 336
HCNW | 1 | 0 | 36 | 60.7 | 6 | 216
HCNW | 1 | 0 | 38 | 55.7 | 6 | 228
HCNW | 1 | 0 | 44 | 55.9 | 6 | 264
HCNW | 1 | 0 | 47 | 50.2 | 6 | 282
HCNW | 1 | 0 | 44 | 52.6 | 6 | 264
HCNW | 1 | 0 | 46 | 51.8 | 6 | 276
HCNW | 1 | 0 | 46 | 51.9 | 6 | 276
HCNW | 1 | 0 | 31 | 70.4 | 6 | 186
HCNW | 1 | 0 | 57 | 43.4 | 6 | 342
HCNW | 1 | 0 | 31 | 67.8 | 6 | 186
HCNW | 1 | 0 | 48 | 53.2 | 6 | 288
HCNW | 1 | 0 | 43 | 56.1 | 6 | 258
HCNW | 1 | 0 | 39 | 58.4 | 6 | 234
HCNW | 1 | 0 | 44 | 54.5 | 6 | 264
HCNW | 1 | 0 | 44 | 56.4 | 6 | 264
HCNW | 1 | 0 | 34 | 63.6 | 6 | 204
HCNW | 1 | 0 | 36 | 60.6 | 6 | 216
HCNW | 1 | 0 | 55 | 45.5 | 6 | 330
HCNW | 1 | 0 | 59 | 34.5 | 6 | 354
HCNW | 1 | 0 | 59 | 35.1 | 6 | 354
HCNW | 1 | 0 | 57 | 37.8 | 6 | 342
HCNW | 1 | 0 | 29 | 70.9 | 6 | 174
HCNW | 1 | 0 | 56 | 38.6 | 6 | 336
HCNW | 1 | 0 | 58 | 35.9 | 6 | 348
HCNW | 1 | 0 | 52 | 42.1 | 6 | 312
HCNW | 1 | 0 | 60 | 34 | 6 | 360
HCNW | 1 | 0 | 58 | 37.3 | 6 | 348
HCNW | 1 | 0 | 54 | 38.6 | 6 | 324
HCNW | 1 | 0 | 59 | 41.6 | 6 | 354
HCNW | 1 | 0 | 55 | 40.9 | 6 | 330
HCNW | 1 | 0 | 56 | 40.7 | 6 | 336
HCNW | 1 | 0 | 53 | 42.3 | 6 | 318
HCNW | 1 | 0 | 54 | 40.7 | 6 | 324
HCNW | 1 | 0 | 58 | 36.9 | 6 | 348
HCNW | 1 | 0 | 58 | 36.6 | 6 | 348
HCNW | 1 | 0 | 56 | 39.3 | 6 | 336
HCNW | 1 | 0 | 55 | 39.7 | 6 | 330
HCNW | 1 | 0 | 40 | 58.8 | 6 | 240
HCNW | 1 | 0 | 56 | 36.7 | 6 | 336

## BL Size2 Var
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | Baseline Heater Size kW | Heater Size X Temp
PCDC | 2 | 0 | 71 | 32 | 6 | 426 | SUMMARY OUTPUT
PCDC | 2 | 0 | 52 | 52.3 | 6 | 312
PCDC | 2 | 0 | 56 | 56.5 | 6 | 336 | Regression Statistics
PCDC | 2 | 0 | 72 | 35.5 | 6 | 432 | Multiple R | 0.67329
PCDC | 2 | 0 | 79 | 17 | 6 | 474 | R Square | 0.45332
PCDC | 2 | 0 | 66 | 43.5 | 6 | 396 | Adjusted R Square | 0.44988
PCDC | 2 | 0 | 77 | 26.9 | 6 | 462 | Standard Error | 9.8789
PCDC | 2 | 0 | 52 | 60.2 | 6 | 312 | Observations | 161
PCDC | 2 | 0 | 68 | 35.2 | 6 | 408
PCDC | 2 | 0 | 64 | 46.2 | 6 | 384 | ANOVA
PCDC | 2 | 0 | 74 | 24.8 | 6 | 444 |  | df | SS | MS | F | Significance F
PCDC | 2 | 0 | 54 | 58.7 | 6 | 324 | Regression | 1 | 12867.0371 | 12867.0371 | 131.8445 | 1.3158e-22
PCDC | 2 | 0 | 64 | 39.3 | 6 | 384 | Residual | 159 | 15517.205 | 97.5925
PCDC | 2 | 0 | 49 | 50.9 | 6 | 294 | Total | 160 | 28384.2421
PCDC | 2 | 0 | 46 | 60.6 | 6 | 276
PCDC | 2 | 0 | 64 | 48.8 | 6 | 384 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
PCDC | 2 | 0 | 63 | 47.7 | 6 | 378 | Intercept | 88.9213 | 3.6124 | 24.6155 | 4.1111e-56 | 81.7868 | 96.0557 | 81.7868 | 96.0557
PCDC | 2 | 0 | 57 | 46.8 | 6 | 342 | X Variable 1 | -0.7006 | 0.061015 | -11.4824 | 1.3158e-22 | -0.8211 | -0.58009 | -0.8211 | -0.58009
PCDC | 2 | 0 | 60 | 46.7 | 6 | 360
PCDC | 2 | 0 | 58 | 52.3 | 6 | 348
PCDC | 2 | 0 | 56 | 57.1 | 6 | 336
PCDC | 2 | 0 | 53 | 58.3 | 6 | 318
PCDC | 2 | 0 | 50 | 64.8 | 6 | 300
PCDC | 2 | 0 | 53 | 61.9 | 6 | 318
PCDC | 2 | 0 | 66 | 46.5 | 6 | 396
PCDC | 2 | 0 | 67 | 31.4 | 6 | 402
PCDC | 2 | 0 | 44 | 74.7 | 6 | 264
PCDC | 2 | 0 | 61 | 46 | 6 | 366
PCDC | 2 | 0 | 49 | 73.1 | 6 | 294
PCDC | 2 | 0 | 57 | 55.5 | 6 | 342
PCDC | 2 | 0 | 58 | 41.8 | 6 | 348
PCDC | 2 | 0 | 72 | 38.1 | 6 | 432
PCDC | 2 | 0 | 74 | 25.2 | 6 | 444
PCDC | 2 | 0 | 74 | 30.8 | 6 | 444
PCDC | 2 | 0 | 57 | 57.2 | 6 | 342
PCDC | 2 | 0 | 54 | 55.3 | 6 | 324
PCDC | 2 | 0 | 67 | 42.6 | 6 | 402
PCDC | 2 | 0 | 71 | 38.6 | 6 | 426
PCDC | 2 | 0 | 71 | 38.9 | 6 | 426
PCDC | 2 | 0 | 59 | 51.8 | 6 | 354
PCDC | 2 | 0 | 59 | 46.9 | 6 | 354
PCDC | 2 | 0 | 46 | 71.8 | 6 | 276
PCDC | 2 | 0 | 61 | 50.6 | 6 | 366
PCDC | 2 | 0 | 52 | 60.7 | 6 | 312
PCDC | 2 | 0 | 76 | 31.4 | 6 | 456
PCDC | 2 | 0 | 45 | 72.6 | 6 | 270
PCDC | 2 | 0 | 52 | 67.6 | 6 | 312
PCDC | 2 | 0 | 55 | 57.4 | 6 | 330
PCDC | 2 | 0 | 50 | 62.5 | 6 | 300
PCDC | 2 | 0 | 65 | 51.8 | 6 | 390
PCDC | 2 | 0 | 58 | 51.1 | 6 | 348
PCDC | 2 | 0 | 45 | 68.5 | 6 | 270
PCDC | 2 | 0 | 74 | 39.1 | 6 | 444
PCDC | 2 | 0 | 75 | 31.4 | 6 | 450
PCDC | 2 | 0 | 66 | 41.8 | 6 | 396
PCDC | 2 | 0 | 56 | 52.5 | 6 | 336
PCDC | 2 | 0 | 75 | 33.2 | 6 | 450
PCDC | 2 | 0 | 74 | 33.6 | 6 | 444
PCDC | 2 | 0 | 75 | 32.2 | 6 | 450
PCDC | 2 | 0 | 64 | 44.1 | 6 | 384
PCDC | 2 | 0 | 72 | 31.9 | 6 | 432
PCDC | 2 | 0 | 73 | 31.2 | 6 | 438
PCDC | 2 | 0 | 69 | 37.3 | 6 | 414
PCDC | 2 | 0 | 71 | 31.9 | 6 | 426
PCDC | 2 | 0 | 72 | 33.4 | 6 | 432
PCDC | 2 | 0 | 68 | 39.7 | 6 | 408
PCDC | 2 | 0 | 66 | 37.2 | 6 | 396
PCDC | 2 | 0 | 70 | 32.2 | 6 | 420
PCDC | 2 | 0 | 60 | 51.9 | 6 | 360
PCDC | 2 | 0 | 71 | 35.8 | 6 | 426
PCDC | 2 | 0 | 58 | 61.8 | 6 | 348
PCDC | 2 | 0 | 43 | 75.2 | 6 | 258
PCDC | 2 | 0 | 47 | 66.6 | 6 | 282
PCDC | 2 | 0 | 58 | 54 | 6 | 348
PCDC | 2 | 0 | 60 | 50.1 | 6 | 360
PCDC | 2 | 0 | 62 | 46.4 | 6 | 372
PCDC | 2 | 0 | 53 | 63 | 6 | 318
PCDC | 2 | 0 | 71 | 35.4 | 6 | 426
PCDC | 2 | 0 | 51 | 66.2 | 6 | 306
PCDC | 2 | 0 | 76 | 34.3 | 6 | 456
PCDC | 2 | 0 | 73 | 29.1 | 6 | 438
PCDC | 2 | 0 | 77 | 24.2 | 6 | 462
PCDC | 2 | 0 | 65 | 44.9 | 6 | 390
PCDC | 2 | 0 | 63 | 45.4 | 6 | 378
PCDC | 2 | 0 | 72 | 43.7 | 6 | 432
PCDC | 2 | 0 | 64 | 46 | 6 | 384
PCDC | 2 | 0 | 83 | 23.2 | 6 | 498
PCDC | 2 | 0 | 57 | 54.5 | 6 | 342
PCDC | 2 | 0 | 66 | 45.4 | 6 | 396
PCDC | 2 | 0 | 57 | 53.6 | 6 | 342
PCDC | 2 | 0 | 67 | 39.7 | 6 | 402
PCDC | 2 | 0 | 72 | 33.7 | 6 | 432
PCDC | 2 | 0 | 46 | 70.1 | 6 | 276
PCDC | 2 | 0 | 73 | 30.7 | 6 | 438
PCDC | 2 | 0 | 49 | 65.3 | 6 | 294
PCDC | 2 | 0 | 68 | 41.5 | 6 | 408
PCDC | 2 | 0 | 64 | 41.7 | 6 | 384
PCDC | 2 | 0 | 69 | 37.7 | 6 | 414
PCDC | 2 | 0 | 68 | 47.5 | 6 | 408
PCDC | 2 | 0 | 51 | 63.6 | 6 | 306
PCDC | 2 | 0 | 55 | 56.8 | 6 | 330
PCDC | 2 | 0 | 73 | 34.2 | 6 | 438
PCDC | 2 | 0 | 60 | 51.5 | 6 | 360
PCDC | 2 | 0 | 42 | 76.7 | 6 | 252
PCDC | 2 | 0 | 53 | 56.8 | 6 | 318
PCDC | 2 | 0 | 48 | 69.3 | 6 | 288
PCDC | 2 | 0 | 64 | 44 | 6 | 384
PCDC | 2 | 0 | 56 | 55.4 | 6 | 336
PCDC | 2 | 0 | 42 | 75.7 | 6 | 252
PCDC | 2 | 0 | 53 | 50.8 | 6 | 318
PCDC | 2 | 0 | 41 | 75.4 | 6 | 246
PCDC | 2 | 0 | 58 | 55.3 | 6 | 348
PCDC | 2 | 0 | 69 | 39.2 | 6 | 414
PCDC | 2 | 0 | 65 | 46.4 | 6 | 390
PCDC | 2 | 0 | 72 | 37 | 6 | 432
PCDC | 2 | 0 | 73 | 24.1 | 6 | 438
PCDC | 2 | 0 | 60 | 49.5 | 6 | 360
PCDC | 2 | 0 | 59 | 47.5 | 6 | 354
PCDC | 2 | 0 | 70 | 40.5 | 6 | 420
PCDC | 2 | 0 | 48 | 67.7 | 6 | 288
PCDC | 2 | 0 | 51 | 65.7 | 6 | 306
PCDC | 2 | 0 | 58 | 50.3 | 6 | 348
PCDC | 2 | 0 | 48 | 71.6 | 6 | 288
PCDC | 2 | 0 | 52 | 59.9 | 6 | 312
PCDC | 2 | 0 | 50 | 72.8 | 6 | 300
PCDC | 2 | 0 | 59 | 48.4 | 6 | 354
PCDC | 2 | 0 | 64 | 43 | 6 | 384
PCDC | 2 | 0 | 56 | 55.3 | 6 | 336
PCDC | 2 | 0 | 65 | 50 | 6 | 390
PCDC | 2 | 0 | 75 | 20.4 | 6 | 450
PCDC | 2 | 0 | 66 | 31 | 6 | 396
PCDC | 2 | 0 | 73 | 33.7 | 6 | 438
PCDC | 2 | 0 | 75 | 34.3 | 6 | 450
PCDC | 2 | 0 | 51 | 51.6 | 6 | 306
PCDC | 2 | 0 | 58 | 51.1 | 6 | 348
PCDC | 2 | 0 | 47 | 72.6 | 6 | 282
PCDC | 2 | 0 | 48 | 69.1 | 6 | 288
PCDC | 2 | 0 | 57 | 57.8 | 6 | 342
PCDC | 2 | 0 | 48 | 63.8 | 6 | 288
PCDC | 2 | 0 | 40 | 80.7 | 6 | 240
BLDG210 | 2 | 0 | 34 | 47.95 | 2.5 | 85
BLDG210 | 2 | 0 | 46 | 38.73 | 2.5 | 115
BLDG210 | 2 | 0 | 33 | 44.7 | 2.5 | 82.5
BLDG210 | 2 | 0 | 34 | 51.14 | 2.5 | 85
BLDG210 | 2 | 0 | 35 | 48.59 | 2.5 | 87.5
BLDG210 | 2 | 0 | 44 | 43.79 | 2.5 | 110
BLDG210 | 2 | 0 | 46 | 42.09 | 2.5 | 115
BLDG210 | 2 | 0 | 34 | 46.4 | 2.5 | 85
BLDG210 | 2 | 0 | 41 | 47.68 | 2.5 | 102.5
BLDG210 | 2 | 0 | 36 | 43.68 | 2.5 | 90
BLDG210 | 2 | 0 | 35 | 49.39 | 2.5 | 87.5
BLDG210 | 2 | 0 | 32 | 48.16 | 2.5 | 80
BLDG210 | 2 | 0 | 34 | 47.36 | 2.5 | 85
BLDG210 | 2 | 0 | 32 | 49.76 | 2.5 | 80
BLDG210 | 2 | 0 | 33 | 48.43 | 2.5 | 82.5
BLDG210 | 2 | 0 | 30 | 49.71 | 2.5 | 75
BLDG210 | 2 | 0 | 32 | 48.16 | 2.5 | 80
BLDG210 | 2 | 0 | 32 | 48.43 | 2.5 | 80
BLDG210 | 2 | 0 | 29 | 50.61 | 2.5 | 72.5
BLDG210 | 2 | 0 | 35 | 48.43 | 2.5 | 87.5
BLDG210 | 2 | 0 | 42 | 45.76 | 2.5 | 105

## BL Size3 Var (hidden)
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | Baseline Heater Size kW | Heater Size X Temp
COCWWTP | 3 | 0 | 30 | 111.33 | 6 | 180 | SUMMARY OUTPUT
COCWWTP | 3 | 0 | 25 | 115.4 | 6 | 150
COCWWTP | 3 | 0 | 24 | 112.24 | 6 | 144 | Regression Statistics
COCWWTP | 3 | 0 | 13 | 126.58 | 6 | 78 | Multiple R | 0.79204
COCWWTP | 3 | 0 | 23 | 117.89 | 6 | 138 | R Square | 0.62732
COCWWTP | 3 | 0 | 23 | 121.38 | 6 | 138 | Adjusted R Square | 0.62167
COCWWTP | 3 | 0 | 22 | 124.61 | 6 | 132 | Standard Error | 5.1396
COCWWTP | 3 | 0 | 22 | 120.53 | 6 | 132 | Observations | 68
COCWWTP | 3 | 0 | 27 | 114.24 | 6 | 162
COCWWTP | 3 | 0 | 35 | 101.63 | 6 | 210 | ANOVA
COCWWTP | 3 | 0 | 30 | 103.82 | 6 | 180 |  | df | SS | MS | F | Significance F
COCWWTP | 3 | 0 | 33 | 110.19 | 6 | 198 | Regression | 1 | 2934.7004 | 2934.7004 | 111.0962 | 8.752e-16
COCWWTP | 3 | 0 | 35 | 104.85 | 6 | 210 | Residual | 66 | 1743.4463 | 26.4159
COCWWTP | 3 | 0 | 36 | 108.81 | 6 | 216 | Total | 67 | 4678.1466
COCWWTP | 3 | 0 | 27 | 114.66 | 6 | 162
COCWWTP | 3 | 0 | 29 | 121.22 | 6 | 174 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
COCWWTP | 3 | 0 | 22 | 122.18 | 6 | 132 | Intercept | 139.8546 | 2.6384 | 53.0073 | 7.9701e-56 | 134.5869 | 145.1223 | 134.5869 | 145.1223
COCWWTP | 3 | 0 | 32 | 107.27 | 6 | 192 | X Variable 1 | -0.9318 | 0.088404 | -10.5402 | 8.752e-16 | -1.1083 | -0.7553 | -1.1083 | -0.7553
COCWWTP | 3 | 0 | 38 | 97.29 | 6 | 228
COCWWTP | 3 | 0 | 36 | 111.2 | 6 | 216
COCWWTP | 3 | 0 | 32 | 104.25 | 6 | 192
COCWWTP | 3 | 0 | 38 | 101.91 | 6 | 228
COCWWTP | 3 | 0 | 35 | 104.64 | 6 | 210
COCWWTP | 3 | 0 | 33 | 108.23 | 6 | 198
COCWWTP | 3 | 0 | 29 | 112.79 | 6 | 174
COCWWTP | 3 | 0 | 32 | 103.43 | 6 | 192
COCWWTP | 3 | 0 | 35 | 107.67 | 6 | 210
COCWWTP | 3 | 0 | 22 | 113.54 | 6 | 132
COCWWTP | 3 | 0 | 15 | 118.41 | 6 | 90
COCWWTP | 3 | 0 | 35 | 104.75 | 6 | 210
COCWWTP | 3 | 0 | 33 | 99.61 | 6 | 198
COCWWTP | 3 | 0 | 27 | 111.06 | 6 | 162
COCWWTP | 3 | 0 | 39 | 108.75 | 6 | 234
COCWWTP | 3 | 0 | 28 | 119.15 | 6 | 168
COCWWTP | 3 | 0 | 35 | 101.97 | 6 | 210
COCWWTP | 3 | 0 | 45 | 103.31 | 6 | 270
COCWWTP | 3 | 0 | 38 | 105.3 | 6 | 228
COCWWTP | 3 | 0 | 35 | 107.67 | 6 | 210
COCWWTP | 3 | 0 | 35 | 121.97 | 6 | 210
COCWWTP | 3 | 0 | 31 | 108.73 | 6 | 186
COCWWTP | 3 | 0 | 34 | 107.82 | 6 | 204
COCWWTP | 3 | 0 | 31 | 112.35 | 6 | 186
COCWWTP | 3 | 0 | 35 | 107.22 | 6 | 210
COCWWTP | 3 | 0 | 29 | 114.12 | 6 | 174
COCWWTP | 3 | 0 | 28 | 109.18 | 6 | 168
COCWWTP | 3 | 0 | 31 | 112.2 | 6 | 186
COCWWTP | 3 | 0 | 32 | 124.2 | 6 | 192
COCWWTP | 3 | 0 | 31 | 115.31 | 6 | 186
COCWWTP | 3 | 0 | 30 | 107.83 | 6 | 180
COCWWTP | 3 | 0 | 35 | 101.9 | 6 | 210
COCWWTP | 3 | 0 | 30 | 118.7 | 6 | 180
COCWWTP | 3 | 0 | 18 | 122.01 | 6 | 108
COCWWTP | 3 | 0 | 32 | 122.28 | 6 | 192
COCWWTP | 3 | 0 | 36 | 99.23 | 6 | 216
COCWWTP | 3 | 0 | 28 | 117.11 | 6 | 168
COCWWTP | 3 | 0 | 27 | 115.82 | 6 | 162
COCWWTP | 3 | 0 | 14 | 127.5 | 6 | 84
COCWWTP | 3 | 0 | 17 | 117.79 | 6 | 102
COCWWTP | 3 | 0 | 30 | 115.86 | 6 | 180
COCWWTP | 3 | 0 | 21 | 121.73 | 6 | 126
COCWWTP | 3 | 0 | 20 | 121.41 | 6 | 120
COCWWTP | 3 | 0 | 21 | 128.59 | 6 | 126
COCWWTP | 3 | 0 | 17 | 128.33 | 6 | 102
COCWWTP | 3 | 0 | 16 | 128.92 | 6 | 96
COCWWTP | 3 | 0 | 20 | 115.5 | 6 | 120
COCWWTP | 3 | 0 | 44 | 93.32 | 6 | 264
COCWWTP | 3 | 0 | 28 | 114.78 | 6 | 168
COCWWTP | 3 | 0 | 23 | 117.13 | 6 | 138

## BL Flat
Site | Size Category | Baseline Heater Size kW | Mode
COCCH | 1 | 0.5 | 11.04 | SUMMARY OUTPUT
Kid Kare | 1 | 1 | 21.36
TCWWTP | 1 | 1 | 10.93 | Regression Statistics
COCFD | 2 | 1 | 21.12 | Multiple R | 0.96612
COCTV | 2 | 1 | 21.12 | R Square | 0.9334
COMKR | 2 | 1 | 20.65 | Adjusted R Square | 0.84249
COMW | 2 | 1 | 22.8 | Standard Error | 18.907
KE ECAM | 2 | 1 | 22.32 | Observations | 12
TCWP | 2 | 1 | 22.31
BayView | 3 | 1.5 | 33.36 | ANOVA
BNS GEN | 3 | 4.95 | 44.4 |  | df | SS | MS | F | Significance F
NQ | 4 | 10 | 228.96 | Regression | 1 | 55106.6017 | 55106.6017 | 154.1555 | 2.1191e-07
|  |  |  | Residual | 11 | 3932.2154 | 357.4741
|  |  |  | Total | 12 | 59038.8171
[5 empty] | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
|  |  |  | Intercept | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | X Variable 1 | 20.2037 | 1.6272 | 12.4159 | 8.1893e-08 | 16.6222 | 23.7852 | 16.6222 | 23.7852

## Treatment Data w Heater Size
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | New Rated Heater Size kW | Heater Size X Temp
COCFD | 2 | 1 | 66 | 10.42 | 1 | 66
COCFD | 2 | 1 | 48 | 18.38 | 1 | 48
COCFD | 2 | 1 | 70 | 8.26 | 1 | 70
COCFD | 2 | 1 | 76 | 6.77 | 1 | 76
COCFD | 2 | 1 | 61 | 12.87 | 1 | 61
COCFD | 2 | 1 | 67 | 11.41 | 1 | 67
COCFD | 2 | 1 | 73 | 8.99 | 1 | 73
COCFD | 2 | 1 | 69 | 10.32 | 1 | 69
COCFD | 2 | 1 | 76 | 8.3 | 1 | 76
COCFD | 2 | 1 | 81 | 6.57 | 1 | 81
COCFD | 2 | 1 | 78 | 6.79 | 1 | 78
COCFD | 2 | 1 | 70 | 8.7 | 1 | 70
COCFD | 2 | 1 | 63 | 13.54 | 1 | 63
COCFD | 2 | 1 | 73 | 8.71 | 1 | 73
COCFD | 2 | 1 | 64 | 15.11 | 1 | 64
COCFD | 2 | 1 | 80 | 4.11 | 1 | 80
COCFD | 2 | 1 | 57 | 13.6 | 1 | 57
COCFD | 2 | 1 | 58 | 12.83 | 1 | 58
COCFD | 2 | 1 | 57 | 12.04 | 1 | 57
COCFD | 2 | 1 | 62 | 12.06 | 1 | 62
COCFD | 2 | 1 | 54 | 14.79 | 1 | 54
COCFD | 2 | 1 | 81 | 7.18 | 1 | 81
COCFD | 2 | 1 | 78 | 7.91 | 1 | 78
COCFD | 2 | 1 | 68 | 11.03 | 1 | 68
COCFD | 2 | 1 | 74 | 5.53 | 1 | 74
COCFD | 2 | 1 | 54 | 16.96 | 1 | 54
COCFD | 2 | 1 | 65 | 12.97 | 1 | 65
COCFD | 2 | 1 | 54 | 15.47 | 1 | 54
COCFD | 2 | 1 | 51 | 16.28 | 1 | 51
COCFD | 2 | 1 | 52 | 13.98 | 1 | 52
COCFD | 2 | 1 | 60 | 11.82 | 1 | 60
COCFD | 2 | 1 | 60 | 11.86 | 1 | 60
COCFD | 2 | 1 | 63 | 11.75 | 1 | 63
COCFD | 2 | 1 | 65 | 10.49 | 1 | 65
COCFD | 2 | 1 | 67 | 8.82 | 1 | 67
COCFD | 2 | 1 | 58 | 14.66 | 1 | 58
COCFD | 2 | 1 | 56 | 14.25 | 1 | 56
COCFD | 2 | 1 | 76 | 7.76 | 1 | 76
COCFD | 2 | 1 | 54 | 15.72 | 1 | 54
COCFD | 2 | 1 | 51 | 15.47 | 1 | 51
COCFD | 2 | 1 | 49 | 17.77 | 1 | 49
COCFD | 2 | 1 | 49 | 18.79 | 1 | 49
COCFD | 2 | 1 | 54 | 15.29 | 1 | 54
COCFD | 2 | 1 | 56 | 16.1 | 1 | 56
COCFD | 2 | 1 | 69 | 9.36 | 1 | 69
COCFD | 2 | 1 | 43 | 21.31 | 1 | 43
COCFD | 2 | 1 | 50 | 17.61 | 1 | 50
COCFD | 2 | 1 | 65 | 10.46 | 1 | 65
COCFD | 2 | 1 | 69 | 9.64 | 1 | 69
COCFD | 2 | 1 | 78 | 7.01 | 1 | 78
COCFD | 2 | 1 | 79 | 6.39 | 1 | 79
COCFD | 2 | 1 | 75 | 8.71 | 1 | 75
COCFD | 2 | 1 | 72 | 7.5 | 1 | 72
COCFD | 2 | 1 | 66 | 9.42 | 1 | 66
COCFD | 2 | 1 | 62 | 11.73 | 1 | 62
COCFD | 2 | 1 | 66 | 11.12 | 1 | 66
COCFD | 2 | 1 | 69 | 9.71 | 1 | 69
COCFD | 2 | 1 | 68 | 9.53 | 1 | 68
COCFD | 2 | 1 | 65 | 9.72 | 1 | 65
KE ECAM | 2 | 1 | 68 | 16.93 | 1 | 68
KE ECAM | 2 | 1 | 66 | 12.05 | 1 | 66
KE ECAM | 2 | 1 | 65 | 12.97 | 1 | 65
KE ECAM | 2 | 1 | 70 | 10.35 | 1 | 70
KE ECAM | 2 | 1 | 74 | 8.51 | 1 | 74
KE ECAM | 2 | 1 | 71 | 11.1 | 1 | 71
KE ECAM | 2 | 1 | 66 | 11.65 | 1 | 66
KE ECAM | 2 | 1 | 72 | 12.36 | 1 | 72
KE ECAM | 2 | 1 | 69 | 10.35 | 1 | 69
KE ECAM | 2 | 1 | 69 | 10.5 | 1 | 69
KE ECAM | 2 | 1 | 72 | 10.37 | 1 | 72
KE ECAM | 2 | 1 | 72 | 11.15 | 1 | 72
KE ECAM | 2 | 1 | 75 | 10.83 | 1 | 75
KE ECAM | 2 | 1 | 78 | 7.17 | 1 | 78
KE ECAM | 2 | 1 | 73 | 12.69 | 1 | 73
KE ECAM | 2 | 1 | 66 | 14.54 | 1 | 66
KE ECAM | 2 | 1 | 63 | 12.58 | 1 | 63
KE ECAM | 2 | 1 | 59 | 13.99 | 1 | 59
KE ECAM | 2 | 1 | 60 | 13.88 | 1 | 60
KE ECAM | 2 | 1 | 65 | 13.56 | 1 | 65
KE ECAM | 2 | 1 | 59 | 14.75 | 1 | 59
KE ECAM | 2 | 1 | 60 | 15.37 | 1 | 60
KE ECAM | 2 | 1 | 50 | 20.37 | 1 | 50
KE ECAM | 2 | 1 | 81 | 7.73 | 1 | 81
KE ECAM | 2 | 1 | 71 | 16.36 | 1 | 71
KE ECAM | 2 | 1 | 70 | 11.17 | 1 | 70
KE ECAM | 2 | 1 | 54 | 14.73 | 1 | 54
KE ECAM | 2 | 1 | 79 | 10.78 | 1 | 79
KRMC | 3 | 0 | 71 | 14.29 | 6 | 426
KRMC | 3 | 0 | 76 | 13.02 | 6 | 456
KRMC | 3 | 0 | 72 | 15.42 | 6 | 432
KRMC | 3 | 0 | 72 | 14.38 | 6 | 432
KRMC | 3 | 0 | 72 | 14.21 | 6 | 432
KRMC | 3 | 0 | 74 | 14.39 | 6 | 444
KRMC | 3 | 0 | 73 | 13.16 | 6 | 438
KRMC | 3 | 0 | 71 | 14.88 | 6 | 426
KRMC | 3 | 0 | 67 | 16.17 | 6 | 402
KRMC | 3 | 0 | 71 | 10.77 | 6 | 426
KRMC | 3 | 0 | 67 | 18.29 | 6 | 402
KRMC | 3 | 0 | 76 | 13.36 | 6 | 456
KRMC | 3 | 0 | 68 | 18.15 | 6 | 408
KRMC | 3 | 0 | 62 | 23.68 | 6 | 372
KRMC | 3 | 0 | 58 | 24.13 | 6 | 348
KRMC | 3 | 0 | 52 | 25.73 | 6 | 312
KRMC | 3 | 0 | 55 | 25.04 | 6 | 330
KRMC | 3 | 0 | 52 | 27.79 | 6 | 312
KRMC | 3 | 0 | 56 | 27.79 | 6 | 336
KRMC | 3 | 0 | 53 | 27.79 | 6 | 318
KRMC | 3 | 0 | 54 | 27.92 | 6 | 324
KRMC | 3 | 0 | 54 | 29.43 | 6 | 324
KRMC | 3 | 0 | 51 | 31.62 | 6 | 306
KRMC | 3 | 0 | 54 | 29.98 | 6 | 324
KRMC | 3 | 0 | 56 | 26.97 | 6 | 336
KRMC | 3 | 0 | 58 | 26.69 | 6 | 348
KRMC | 3 | 0 | 59 | 26.56 | 6 | 354
KRMC | 3 | 0 | 62 | 21.39 | 6 | 372
KRMC | 3 | 0 | 50 | 29.57 | 6 | 300
KRMC | 3 | 0 | 51 | 29.43 | 6 | 306
KRMC | 3 | 0 | 51 | 29.02 | 6 | 306
KRMC | 3 | 0 | 57 | 26.97 | 6 | 342
KRMC | 3 | 0 | 58 | 26.28 | 6 | 348
KRMC | 3 | 0 | 52 | 28.06 | 6 | 312
KRMC | 3 | 0 | 62 | 18.9 | 6 | 372
KRMC | 3 | 0 | 47 | 31.21 | 6 | 282
KRMC | 3 | 0 | 60 | 13.42 | 6 | 360
KRMC | 3 | 0 | 49 | 28.2 | 6 | 294
KRMC | 3 | 0 | 49 | 29.43 | 6 | 294
KRMC | 3 | 0 | 78 | 11.77 | 6 | 468
KRMC | 3 | 0 | 62 | 22.59 | 6 | 372
KRMC | 3 | 0 | 71 | 10.99 | 6 | 426
KRMC | 3 | 0 | 65 | 20.95 | 6 | 390
KRMC | 3 | 0 | 42 | 34.49 | 6 | 252
KRMC | 3 | 0 | 67 | 18.24 | 6 | 402
KRMC | 3 | 0 | 72 | 15.53 | 6 | 432
KRMC | 3 | 0 | 68 | 15.72 | 6 | 408
KRMC | 3 | 0 | 62 | 18.2 | 6 | 372
KRMC | 3 | 0 | 68 | 18.27 | 6 | 408
KRMC | 3 | 0 | 62 | 14.68 | 6 | 372
KRMC | 3 | 0 | 77 | 13.15 | 6 | 462
KRMC | 3 | 0 | 70 | 14.5 | 6 | 420
KRMC | 3 | 0 | 70 | 17.17 | 6 | 420
KRMC | 3 | 0 | 65 | 19.53 | 6 | 390
KRMC | 3 | 0 | 65 | 19.49 | 6 | 390
KRMC | 3 | 0 | 71 | 17.72 | 6 | 426
KRMC | 3 | 0 | 74 | 12.91 | 6 | 444
KRMC | 3 | 0 | 66 | 20 | 6 | 396
KRMC | 3 | 0 | 53 | 26.69 | 6 | 318
KRMC | 3 | 0 | 64 | 19.92 | 6 | 384
KRMC | 3 | 0 | 59 | 24.09 | 6 | 354
KRMC | 3 | 0 | 66 | 14.99 | 6 | 396
KRMC | 3 | 0 | 55 | 17.72 | 6 | 330
KRMC | 3 | 0 | 64 | 18.21 | 6 | 384
KRMC | 3 | 0 | 51 | 28.2 | 6 | 306
KRMC | 3 | 0 | 48 | 25.88 | 6 | 288
KRMC | 3 | 0 | 58 | 27.19 | 6 | 348
KRMC | 3 | 0 | 58 | 22.84 | 6 | 348
KRMC | 3 | 0 | 59 | 14 | 6 | 354
KRMC | 3 | 0 | 68 | 17.48 | 6 | 408
KRMC | 3 | 0 | 73 | 16.97 | 6 | 438
KRMC | 3 | 0 | 61 | 25.53 | 6 | 366
KRMC | 3 | 0 | 69 | 16.85 | 6 | 414
KRMC | 3 | 0 | 65 | 19.93 | 6 | 390
KRMC | 3 | 0 | 61 | 21.35 | 6 | 366
COCTV | 2 | 1 | 79 | 6.47 | 1 | 79
COCTV | 2 | 1 | 66 | 8.82 | 1 | 66
COCTV | 2 | 1 | 75 | 6.72 | 1 | 75
COCTV | 2 | 1 | 69 | 7.28 | 1 | 69
COCTV | 2 | 1 | 65 | 7.09 | 1 | 65
COCTV | 2 | 1 | 70 | 6.24 | 1 | 70
COCTV | 2 | 1 | 66 | 8.71 | 1 | 66
COCTV | 2 | 1 | 62 | 8.78 | 1 | 62
COCTV | 2 | 1 | 69 | 7.62 | 1 | 69
COCTV | 2 | 1 | 68 | 7.36 | 1 | 68
COCTV | 2 | 1 | 73 | 7.39 | 1 | 73
COCTV | 2 | 1 | 66 | 8.88 | 1 | 66
COCTV | 2 | 1 | 76 | 5.31 | 1 | 76
COCTV | 2 | 1 | 73 | 6.52 | 1 | 73
COCTV | 2 | 1 | 78 | 6.54 | 1 | 78
COCTV | 2 | 1 | 81 | 6.89 | 1 | 81
COCTV | 2 | 1 | 74 | 5.81 | 1 | 74
COCTV | 2 | 1 | 61 | 7.77 | 1 | 61
COCTV | 2 | 1 | 76 | 6.11 | 1 | 76
COCTV | 2 | 1 | 63 | 8.66 | 1 | 63
COCTV | 2 | 1 | 72 | 5.25 | 1 | 72
COCTV | 2 | 1 | 69 | 7.89 | 1 | 69
COCTV | 2 | 1 | 64 | 9.89 | 1 | 64
COCTV | 2 | 1 | 70 | 7.76 | 1 | 70
COCTV | 2 | 1 | 58 | 10.48 | 1 | 58
COCTV | 2 | 1 | 57 | 10.26 | 1 | 57
COCTV | 2 | 1 | 67 | 7.51 | 1 | 67
COCTV | 2 | 1 | 78 | 4.96 | 1 | 78
COCTV | 2 | 1 | 78 | 4.93 | 1 | 78
COCTV | 2 | 1 | 76 | 5.97 | 1 | 76
COCTV | 2 | 1 | 81 | 4.98 | 1 | 81
COCTV | 2 | 1 | 80 | 4.56 | 1 | 80
TCWWTP | 1 | 1 | 12 | 9.48 | 1 | 12
TCWWTP | 1 | 1 | 32 | 7.79 | 1 | 32
TCWWTP | 1 | 1 | 29 | 8.01 | 1 | 29
TCWWTP | 1 | 1 | 38 | 7.82 | 1 | 38
TCWWTP | 1 | 1 | 34 | 8.02 | 1 | 34
TCWWTP | 1 | 1 | 33 | 8.17 | 1 | 33
TCWWTP | 1 | 1 | 33 | 8.26 | 1 | 33
TCWWTP | 1 | 1 | 31 | 8.39 | 1 | 31
TCWWTP | 1 | 1 | 31 | 8.22 | 1 | 31
TCWWTP | 1 | 1 | 33 | 8.56 | 1 | 33
TCWWTP | 1 | 1 | 34 | 8.1 | 1 | 34
TCWWTP | 1 | 1 | 35 | 8.48 | 1 | 35
TCWWTP | 1 | 1 | 22 | 8.26 | 1 | 22
TCWWTP | 1 | 1 | 30 | 8.8 | 1 | 30
TCWWTP | 1 | 1 | 29 | 8.52 | 1 | 29
TCWWTP | 1 | 1 | 31 | 8.56 | 1 | 31
TCWWTP | 1 | 1 | 39 | 7.86 | 1 | 39
TCWWTP | 1 | 1 | 22 | 8.58 | 1 | 22
TCWWTP | 1 | 1 | 22 | 8.38 | 1 | 22
TCWWTP | 1 | 1 | 19 | 9.05 | 1 | 19
TCWWTP | 1 | 1 | 27 | 8.4 | 1 | 27
TCWWTP | 1 | 1 | 30 | 8.21 | 1 | 30
TCWWTP | 1 | 1 | 38 | 8.13 | 1 | 38
TCWWTP | 1 | 1 | 34 | 8.15 | 1 | 34
TCWWTP | 1 | 1 | 32 | 8.02 | 1 | 32
TCWWTP | 1 | 1 | 25 | 8.22 | 1 | 25
TCWWTP | 1 | 1 | 19 | 8.66 | 1 | 19
TCWWTP | 1 | 1 | 30 | 7.94 | 1 | 30
TCWWTP | 1 | 1 | 18 | 8.99 | 1 | 18
TCWWTP | 1 | 1 | 34 | 8.21 | 1 | 34
TCWWTP | 1 | 1 | 26 | 8.22 | 1 | 26
TCWWTP | 1 | 1 | 3 | 9.57 | 1 | 3
TCWWTP | 1 | 1 | 5 | 9.52 | 1 | 5
TCWWTP | 1 | 1 | 26 | 8.55 | 1 | 26
TCWWTP | 1 | 1 | 26 | 8.41 | 1 | 26
TCWWTP | 1 | 1 | 40 | 7.94 | 1 | 40
TCWWTP | 1 | 1 | 36 | 7.55 | 1 | 36
TCWWTP | 1 | 1 | 24 | 8.82 | 1 | 24
TCWWTP | 1 | 1 | 22 | 8.55 | 1 | 22
TCWWTP | 1 | 1 | 16 | 9.03 | 1 | 16
TCWWTP | 1 | 1 | 19 | 8.73 | 1 | 19
TCWWTP | 1 | 1 | 39 | 7.17 | 1 | 39
TCWWTP | 1 | 1 | 30 | 7.02 | 1 | 30
TCWWTP | 1 | 1 | 37 | 7.08 | 1 | 37
TCWWTP | 1 | 1 | 28 | 7.83 | 1 | 28
TCWWTP | 1 | 1 | 32 | 8.65 | 1 | 32
TCWWTP | 1 | 1 | 25 | 8.4 | 1 | 25
TCWWTP | 1 | 1 | 16 | 7.7 | 1 | 16
TCWWTP | 1 | 1 | 27 | 8.19 | 1 | 27
TCWWTP | 1 | 1 | 30 | 7.1 | 1 | 30
TCWWTP | 1 | 1 | 15 | 8.83 | 1 | 15
TCWWTP | 1 | 1 | 33 | 8.41 | 1 | 33
TCWWTP | 1 | 1 | 40 | 7.94 | 1 | 40
TCWWTP | 1 | 1 | 38 | 8.06 | 1 | 38
TCWWTP | 1 | 1 | 32 | 7.87 | 1 | 32
TCWWTP | 1 | 1 | 37 | 7.99 | 1 | 37
TCWWTP | 1 | 1 | 35 | 8.99 | 1 | 35
TCWWTP | 1 | 1 | 25 | 8.4 | 1 | 25
TCWWTP | 1 | 1 | 39 | 7.74 | 1 | 39
TCWWTP | 1 | 1 | 15 | 8.89 | 1 | 15
TCWWTP | 1 | 1 | 19 | 8.77 | 1 | 19
TCWWTP | 1 | 1 | 29 | 8.39 | 1 | 29
TCWWTP | 1 | 1 | 35 | 8.57 | 1 | 35
TCWWTP | 1 | 1 | 34 | 7.95 | 1 | 34
TCWWTP | 1 | 1 | 36 | 7.69 | 1 | 36
TCWWTP | 1 | 1 | 23 | 9.35 | 1 | 23
TCWWTP | 1 | 1 | 24 | 8.18 | 1 | 24
TCWWTP | 1 | 1 | 39 | 7.02 | 1 | 39
TCWWTP | 1 | 1 | 42 | 7.72 | 1 | 42
TCWWTP | 1 | 1 | 41 | 8.17 | 1 | 41
TCWWTP | 1 | 1 | 25 | 8.17 | 1 | 25
TCWWTP | 1 | 1 | 36 | 8.28 | 1 | 36
TCWWTP | 1 | 1 | 34 | 8.16 | 1 | 34
TCWWTP | 1 | 1 | 40 | 7.97 | 1 | 40
TCWWTP | 1 | 1 | 32 | 8.14 | 1 | 32
TCWWTP | 1 | 1 | 28 | 7.21 | 1 | 28
TCWWTP | 1 | 1 | 33 | 7.14 | 1 | 33
TCWWTP | 1 | 1 | 27 | 7.16 | 1 | 27
TCWWTP | 1 | 1 | 18 | 9.38 | 1 | 18
TCWP | 2 | 1 | 45 | 10.17 | 1 | 45
TCWP | 2 | 1 | 35 | 10.82 | 1 | 35
TCWP | 2 | 1 | 37 | 10.57 | 1 | 37
TCWP | 2 | 1 | 37 | 10.64 | 1 | 37
TCWP | 2 | 1 | 31 | 10.96 | 1 | 31
TCWP | 2 | 1 | 31 | 11.14 | 1 | 31
TCWP | 2 | 1 | 33 | 10.77 | 1 | 33
TCWP | 2 | 1 | 44 | 10.73 | 1 | 44
TCWP | 2 | 1 | 28 | 11.01 | 1 | 28
TCWP | 2 | 1 | 34 | 10.58 | 1 | 34
TCWP | 2 | 1 | 33 | 10.71 | 1 | 33
TCWP | 2 | 1 | 38 | 10.75 | 1 | 38
TCWP | 2 | 1 | 37 | 10.92 | 1 | 37
TCWP | 2 | 1 | 30 | 10.54 | 1 | 30
TCWP | 2 | 1 | 32 | 9.94 | 1 | 32
TCWP | 2 | 1 | 37 | 10.42 | 1 | 37
TCWP | 2 | 1 | 34 | 10.4 | 1 | 34
TCWP | 2 | 1 | 50 | 10.27 | 1 | 50
TCWP | 2 | 1 | 29 | 10.54 | 1 | 29
TCWP | 2 | 1 | 51 | 9.15 | 1 | 51
TCWP | 2 | 1 | 35 | 9.89 | 1 | 35
TCWP | 2 | 1 | 33 | 10.34 | 1 | 33
TCWP | 2 | 1 | 40 | 9.99 | 1 | 40
TCWP | 2 | 1 | 34 | 10.71 | 1 | 34
TCWP | 2 | 1 | 34 | 9.68 | 1 | 34
TCWP | 2 | 1 | 50 | 10.4 | 1 | 50
TCWP | 2 | 1 | 29 | 10.73 | 1 | 29
TCWP | 2 | 1 | 44 | 10.78 | 1 | 44
TCWP | 2 | 1 | 41 | 10.68 | 1 | 41
TCWP | 2 | 1 | 39 | 10.71 | 1 | 39
TCWP | 2 | 1 | 35 | 10.66 | 1 | 35
TCWP | 2 | 1 | 32 | 10.73 | 1 | 32
TCWP | 2 | 1 | 39 | 10.46 | 1 | 39
TCWP | 2 | 1 | 43 | 10.08 | 1 | 43
TCWP | 2 | 1 | 35 | 10.91 | 1 | 35
TCWP | 2 | 1 | 32 | 10.45 | 1 | 32
TCWP | 2 | 1 | 32 | 10.51 | 1 | 32
TCWP | 2 | 1 | 30 | 10.78 | 1 | 30
TCWP | 2 | 1 | 40 | 10.71 | 1 | 40
TCWP | 2 | 1 | 29 | 11.05 | 1 | 29
HCNW | 1 | 0 | 54 | 37.7 | 6 | 324
HCNW | 1 | 0 | 58 | 19.7 | 6 | 348
HCNW | 1 | 0 | 54 | 29.2 | 6 | 324
HCNW | 1 | 0 | 51 | 41 | 6 | 306
HCNW | 1 | 0 | 51 | 42.2 | 6 | 306
HCNW | 1 | 0 | 44 | 46.2 | 6 | 264
HCNW | 1 | 0 | 38 | 54.9 | 6 | 228
HCNW | 1 | 0 | 34 | 55.2 | 6 | 204
HCNW | 1 | 0 | 43 | 51.4 | 6 | 258
HCNW | 1 | 0 | 55 | 38.2 | 6 | 330
HCNW | 1 | 0 | 60 | 18.8 | 6 | 360
HCNW | 1 | 0 | 52 | 40.3 | 6 | 312
HCNW | 1 | 0 | 43 | 49.5 | 6 | 258
HCNW | 1 | 0 | 35 | 56.8 | 6 | 210
HCNW | 1 | 0 | 32 | 60.8 | 6 | 192
HCNW | 1 | 0 | 32 | 60.8 | 6 | 192
HCNW | 1 | 0 | 47 | 46.9 | 6 | 282
HCNW | 1 | 0 | 44 | 48.8 | 6 | 264
HCNW | 1 | 0 | 34 | 57 | 6 | 204
HCNW | 1 | 0 | 53 | 40.3 | 6 | 318
HCNW | 1 | 0 | 51 | 40 | 6 | 306
HCNW | 1 | 0 | 56 | 35.6 | 6 | 336
HCNW | 1 | 0 | 53 | 37 | 6 | 318
HCNW | 1 | 0 | 54 | 36.3 | 6 | 324
HCNW | 1 | 0 | 54 | 37.2 | 6 | 324
HCNW | 1 | 0 | 50 | 41.5 | 6 | 300
HCNW | 1 | 0 | 47 | 44.3 | 6 | 282
HCNW | 1 | 0 | 42 | 48.1 | 6 | 252
HCNW | 1 | 0 | 52 | 40.3 | 6 | 312
HCNW | 1 | 0 | 59 | 31.8 | 6 | 354
HCNW | 1 | 0 | 57 | 34.4 | 6 | 342
HCNW | 1 | 0 | 62 | 28 | 6 | 372
HCNW | 1 | 0 | 51 | 40.8 | 6 | 306
HCNW | 1 | 0 | 51 | 39.1 | 6 | 306
HCNW | 1 | 0 | 49 | 37.9 | 6 | 294
HCNW | 1 | 0 | 49 | 41.7 | 6 | 294
HCNW | 1 | 0 | 53 | 38.2 | 6 | 318
HCNW | 1 | 0 | 62 | 29.9 | 6 | 372
HCNW | 1 | 0 | 65 | 25.6 | 6 | 390
HCNW | 1 | 0 | 62 | 29.7 | 6 | 372
HCNW | 1 | 0 | 35 | 52.5 | 6 | 210
HCNW | 1 | 0 | 58 | 33.4 | 6 | 348
HCNW | 1 | 0 | 32 | 57.3 | 6 | 192
HCNW | 1 | 0 | 27 | 64.4 | 6 | 162
HCNW | 1 | 0 | 52 | 38.9 | 6 | 312
HCNW | 1 | 0 | 26 | 64.4 | 6 | 156
HCNW | 1 | 0 | 41 | 50.9 | 6 | 246
HCNW | 1 | 0 | 31 | 60.4 | 6 | 186
HCNW | 1 | 0 | 37 | 53.2 | 6 | 222
HCNW | 1 | 0 | 34 | 55.7 | 6 | 204
HCNW | 1 | 0 | 38 | 52.8 | 6 | 228
HCNW | 1 | 0 | 42 | 47.4 | 6 | 252
HCNW | 1 | 0 | 38 | 51 | 6 | 228
HCNW | 1 | 0 | 41 | 51.8 | 6 | 246
HCNW | 1 | 0 | 43 | 47.8 | 6 | 258
HCNW | 1 | 0 | 42 | 47.7 | 6 | 252
HCNW | 1 | 0 | 49 | 43 | 6 | 294
HCNW | 1 | 0 | 40 | 50.6 | 6 | 240
HCNW | 1 | 0 | 35 | 57.8 | 6 | 210
HCNW | 1 | 0 | 33 | 59 | 6 | 198
HCNW | 1 | 0 | 31 | 57.6 | 6 | 186
HCNW | 1 | 0 | 36 | 56.4 | 6 | 216
HCNW | 1 | 0 | 35 | 49.6 | 6 | 210
HCNW | 1 | 0 | 36 | 55.3 | 6 | 216
HCNW | 1 | 0 | 37 | 51.4 | 6 | 222
HCNW | 1 | 0 | 33 | 58.2 | 6 | 198
HCNW | 1 | 0 | 42 | 46.7 | 6 | 252
HCNW | 1 | 0 | 43 | 46.5 | 6 | 258
HCNW | 1 | 0 | 44 | 45.8 | 6 | 264
HCNW | 1 | 0 | 46 | 41.6 | 6 | 276
HCNW | 1 | 0 | 47 | 42.5 | 6 | 282
HCNW | 1 | 0 | 49 | 42.1 | 6 | 294
HCNW | 1 | 0 | 44 | 44.6 | 6 | 264
HCNW | 1 | 0 | 36 | 57.5 | 6 | 216
HCNW | 1 | 0 | 46 | 47.3 | 6 | 276
HCNW | 1 | 0 | 30 | 60.2 | 6 | 180
HCNW | 1 | 0 | 27 | 62.5 | 6 | 162
HCNW | 1 | 0 | 33 | 60.7 | 6 | 198
HCNW | 1 | 0 | 33 | 51.9 | 6 | 198
HCNW | 1 | 0 | 43 | 49.3 | 6 | 258
HCNW | 1 | 0 | 39 | 53 | 6 | 234
HCNW | 1 | 0 | 38 | 54.2 | 6 | 228
HCNW | 1 | 0 | 35 | 57.5 | 6 | 210
HCNW | 1 | 0 | 32 | 48.1 | 6 | 192
HCNW | 1 | 0 | 30 | 61.2 | 6 | 180
HCNW | 1 | 0 | 49 | 43.2 | 6 | 294
HCNW | 1 | 0 | 33 | 53.8 | 6 | 198
PCDC | 2 | 0 | 56 | 35.7 | 6 | 336
PCDC | 2 | 0 | 35 | 54.4 | 6 | 210
PCDC | 2 | 0 | 49 | 48 | 6 | 294
PCDC | 2 | 0 | 57 | 38.7 | 6 | 342
PCDC | 2 | 0 | 56 | 37.5 | 6 | 336
PCDC | 2 | 0 | 59 | 34.8 | 6 | 354
PCDC | 2 | 0 | 54 | 32.1 | 6 | 324
PCDC | 2 | 0 | 44 | 39.4 | 6 | 264
PCDC | 2 | 0 | 55 | 30.4 | 6 | 330
PCDC | 2 | 0 | 46 | 53.7 | 6 | 276
PCDC | 2 | 0 | 56 | 27.3 | 6 | 336
PCDC | 2 | 0 | 59 | 25.6 | 6 | 354
PCDC | 2 | 0 | 48 | 49 | 6 | 288
PCDC | 2 | 0 | 34 | 63 | 6 | 204
PCDC | 2 | 0 | 51 | 43.2 | 6 | 306
PCDC | 2 | 0 | 44 | 52.7 | 6 | 264
PCDC | 2 | 0 | 57 | 39.8 | 6 | 342
PCDC | 2 | 0 | 42 | 52.7 | 6 | 252
PCDC | 2 | 0 | 49 | 47.7 | 6 | 294
PCDC | 2 | 0 | 58 | 35.4 | 6 | 348
PCDC | 2 | 0 | 59 | 34.3 | 6 | 354
PCDC | 2 | 0 | 59 | 36.2 | 6 | 354
PCDC | 2 | 0 | 63 | 30.7 | 6 | 378
PCDC | 2 | 0 | 62 | 33.8 | 6 | 372
PCDC | 2 | 0 | 60 | 36.5 | 6 | 360
PCDC | 2 | 0 | 38 | 59.1 | 6 | 228
PCDC | 2 | 0 | 38 | 58.9 | 6 | 228
PCDC | 2 | 0 | 37 | 48.4 | 6 | 222
PCDC | 2 | 0 | 48 | 49.1 | 6 | 288
PCDC | 2 | 0 | 44 | 44.4 | 6 | 264
PCDC | 2 | 0 | 34 | 62.4 | 6 | 204
PCDC | 2 | 0 | 45 | 42.2 | 6 | 270
PCDC | 2 | 0 | 57 | 37.1 | 6 | 342
PCDC | 2 | 0 | 64 | 31.3 | 6 | 384
PCDC | 2 | 0 | 57 | 35.6 | 6 | 342
PCDC | 2 | 0 | 44 | 51.3 | 6 | 264
PCDC | 2 | 0 | 31 | 72 | 6 | 186
PCDC | 2 | 0 | 48 | 51.3 | 6 | 288
PCDC | 2 | 0 | 46 | 50.6 | 6 | 276
PCDC | 2 | 0 | 43 | 51 | 6 | 258
PCDC | 2 | 0 | 45 | 50.5 | 6 | 270
PCDC | 2 | 0 | 40 | 59.6 | 6 | 240
PCDC | 2 | 0 | 58 | 36.2 | 6 | 348
PCDC | 2 | 0 | 41 | 57.7 | 6 | 246
PCDC | 2 | 0 | 61 | 33.8 | 6 | 366
PCDC | 2 | 0 | 43 | 53.6 | 6 | 258
PCDC | 2 | 0 | 48 | 48.5 | 6 | 288
PCDC | 2 | 0 | 43 | 45.5 | 6 | 258
PCDC | 2 | 0 | 54 | 39.6 | 6 | 324
PCDC | 2 | 0 | 61 | 32.2 | 6 | 366
PCDC | 2 | 0 | 57 | 37 | 6 | 342
COMW | 2 | 1 | 36 | 18.4 | 1 | 36
COMW | 2 | 1 | 45 | 16.9 | 1 | 45
COMW | 2 | 1 | 52 | 15.3 | 1 | 52
COMW | 2 | 1 | 53 | 15.9 | 1 | 53
COMW | 2 | 1 | 53 | 14.2 | 1 | 53
COMW | 2 | 1 | 50 | 15.1 | 1 | 50
COMW | 2 | 1 | 43 | 15.3 | 1 | 43
COMW | 2 | 1 | 29 | 16.9 | 1 | 29
COMW | 2 | 1 | 40 | 14 | 1 | 40
COMW | 2 | 1 | 44 | 15.6 | 1 | 44
COMW | 2 | 1 | 35 | 16.9 | 1 | 35
COMW | 2 | 1 | 37 | 18.1 | 1 | 37
COMW | 2 | 1 | 32 | 15.8 | 1 | 32
COMW | 2 | 1 | 31 | 16.9 | 1 | 31
COMW | 2 | 1 | 32 | 17.1 | 1 | 32
COMW | 2 | 1 | 35 | 16.6 | 1 | 35
COMW | 2 | 1 | 40 | 16.6 | 1 | 40
COMW | 2 | 1 | 43 | 15.2 | 1 | 43
COMW | 2 | 1 | 43 | 16.2 | 1 | 43
COMW | 2 | 1 | 42 | 14.7 | 1 | 42
COMW | 2 | 1 | 46 | 16.3 | 1 | 46
COMW | 2 | 1 | 34 | 16.5 | 1 | 34
COMKR | 2 | 1 | 40 | 10.9 | 1 | 40
COMKR | 2 | 1 | 43 | 11.1 | 1 | 43
COMKR | 2 | 1 | 50 | 8.7 | 1 | 50
COMKR | 2 | 1 | 53 | 9.3 | 1 | 53
COMKR | 2 | 1 | 53 | 10.8 | 1 | 53
COMKR | 2 | 1 | 52 | 10.6 | 1 | 52
COMKR | 2 | 1 | 35 | 11.9 | 1 | 35
COMKR | 2 | 1 | 36 | 12.5 | 1 | 36
COMKR | 2 | 1 | 32 | 12.8 | 1 | 32
COMKR | 2 | 1 | 45 | 12.7 | 1 | 45
COMKR | 2 | 1 | 29 | 12.8 | 1 | 29
COMKR | 2 | 1 | 34 | 12.3 | 1 | 34
COMKR | 2 | 1 | 46 | 11.8 | 1 | 46
COMKR | 2 | 1 | 37 | 11.4 | 1 | 37
COMKR | 2 | 1 | 32 | 14.7 | 1 | 32
COMKR | 2 | 1 | 31 | 13.4 | 1 | 31
COMKR | 2 | 1 | 35 | 12.9 | 1 | 35
COMKR | 2 | 1 | 43 | 10.6 | 1 | 43
COMKR | 2 | 1 | 43 | 11.7 | 1 | 43
COMKR | 2 | 1 | 42 | 11.2 | 1 | 42
COMKR | 2 | 1 | 44 | 10.1 | 1 | 44
COMKR | 2 | 1 | 40 | 13.5 | 1 | 40
COCWWTP | 3 | 0 | 81 | 32.05 | 6 | 486
COCWWTP | 3 | 0 | 78 | 31.93 | 6 | 468
COCWWTP | 3 | 0 | 79 | 29.67 | 6 | 474
COCWWTP | 3 | 0 | 76 | 28.4 | 6 | 456
COCWWTP | 3 | 0 | 76 | 30.83 | 6 | 456
COCWWTP | 3 | 0 | 62 | 40.46 | 6 | 372
COCWWTP | 3 | 0 | 54 | 44.24 | 6 | 324
COCWWTP | 3 | 0 | 67 | 34.75 | 6 | 402
COCWWTP | 3 | 0 | 69 | 38.29 | 6 | 414
COCWWTP | 3 | 0 | 68 | 35.65 | 6 | 408
COCWWTP | 3 | 0 | 65 | 44.66 | 6 | 390
COCWWTP | 3 | 0 | 54 | 55.77 | 6 | 324
COCWWTP | 3 | 0 | 51 | 55.72 | 6 | 306
COCWWTP | 3 | 0 | 52 | 52.55 | 6 | 312
COCWWTP | 3 | 0 | 60 | 46.88 | 6 | 360
COCWWTP | 3 | 0 | 60 | 42.96 | 6 | 360
COCWWTP | 3 | 0 | 50 | 60.42 | 6 | 300
COCWWTP | 3 | 0 | 65 | 38.29 | 6 | 390
COCWWTP | 3 | 0 | 64 | 47.7 | 6 | 384
COCWWTP | 3 | 0 | 65 | 38.9 | 6 | 390
COCWWTP | 3 | 0 | 56 | 50.26 | 6 | 336
COCWWTP | 3 | 0 | 54 | 51.97 | 6 | 324
COCWWTP | 3 | 0 | 54 | 49.76 | 6 | 324
COCWWTP | 3 | 0 | 49 | 61.9 | 6 | 294
COCWWTP | 3 | 0 | 54 | 52.64 | 6 | 324
COCWWTP | 3 | 0 | 56 | 52.56 | 6 | 336
COCWWTP | 3 | 0 | 48 | 60.48 | 6 | 288
COCWWTP | 3 | 0 | 43 | 66.12 | 6 | 258
COCWWTP | 3 | 0 | 63 | 43.44 | 6 | 378
COCWWTP | 3 | 0 | 70 | 35.71 | 6 | 420
COCWWTP | 3 | 0 | 62 | 43.08 | 6 | 372
COCWWTP | 3 | 0 | 78 | 25.51 | 6 | 468
COCWWTP | 3 | 0 | 68 | 35.74 | 6 | 408
COCWWTP | 3 | 0 | 66 | 41.92 | 6 | 396
COCWWTP | 3 | 0 | 66 | 37.87 | 6 | 396
COCWWTP | 3 | 0 | 72 | 30.53 | 6 | 432
COCWWTP | 3 | 0 | 69 | 32.6 | 6 | 414
COCWWTP | 3 | 0 | 75 | 32.73 | 6 | 450
COCWWTP | 3 | 0 | 69 | 37.08 | 6 | 414
COCWWTP | 3 | 0 | 66 | 39.5 | 6 | 396
COCWWTP | 3 | 0 | 51 | 55.2 | 6 | 306
COCWWTP | 3 | 0 | 78 | 26.82 | 6 | 468
COCWWTP | 3 | 0 | 81 | 26.05 | 6 | 486
COCWWTP | 3 | 0 | 76 | 27.53 | 6 | 456
COCWWTP | 3 | 0 | 69 | 35.64 | 6 | 414
COCWWTP | 3 | 0 | 73 | 30.06 | 6 | 438
COCWWTP | 3 | 0 | 67 | 36.65 | 6 | 402
COCWWTP | 3 | 0 | 61 | 44.7 | 6 | 366
COCWWTP | 3 | 0 | 58 | 48.21 | 6 | 348
COCWWTP | 3 | 0 | 63 | 44.13 | 6 | 378
COCWWTP | 3 | 0 | 65 | 36.59 | 6 | 390
COCWWTP | 3 | 0 | 58 | 33.82 | 6 | 348
COCWWTP | 3 | 0 | 57 | 40.95 | 6 | 342
COCWWTP | 3 | 0 | 80 | 16.14 | 6 | 480
COCWWTP | 3 | 0 | 70 | 33.86 | 6 | 420
COCWWTP | 3 | 0 | 73 | 25.06 | 6 | 438
COCWWTP | 3 | 0 | 74 | 29.67 | 6 | 444
COCWWTP | 3 | 0 | 57 | 45.79 | 6 | 342
COCWWTP | 3 | 0 | 49 | 57.41 | 6 | 294
COCCH | 1 | 1 | 43 | 10.92 | 1 | 43
COCCH | 1 | 1 | 75 | 5.69 | 1 | 75
COCCH | 1 | 1 | 65 | 6.05 | 1 | 65
COCCH | 1 | 1 | 66 | 6.18 | 1 | 66
COCCH | 1 | 1 | 70 | 5.47 | 1 | 70
COCCH | 1 | 1 | 48 | 9.79 | 1 | 48
COCCH | 1 | 1 | 56 | 8.88 | 1 | 56
COCCH | 1 | 1 | 54 | 8.39 | 1 | 54
COCCH | 1 | 1 | 69 | 5.75 | 1 | 69
COCCH | 1 | 1 | 49 | 9.58 | 1 | 49
COCCH | 1 | 1 | 68 | 6.16 | 1 | 68
COCCH | 1 | 1 | 49 | 9.53 | 1 | 49
COCCH | 1 | 1 | 51 | 8.89 | 1 | 51
COCCH | 1 | 1 | 54 | 8.04 | 1 | 54
COCCH | 1 | 1 | 78 | 4.5 | 1 | 78
COCCH | 1 | 1 | 74 | 4.48 | 1 | 74
COCCH | 1 | 1 | 81 | 4.91 | 1 | 81
COCCH | 1 | 1 | 69 | 5.99 | 1 | 69
COCCH | 1 | 1 | 54 | 8.46 | 1 | 54
COCCH | 1 | 1 | 79 | 4.88 | 1 | 79
COCCH | 1 | 1 | 66 | 6.86 | 1 | 66
COCCH | 1 | 1 | 76 | 4.95 | 1 | 76
COCCH | 1 | 1 | 70 | 5.14 | 1 | 70
COCCH | 1 | 1 | 73 | 5.66 | 1 | 73
COCCH | 1 | 1 | 69 | 6.21 | 1 | 69
COCCH | 1 | 1 | 78 | 5.17 | 1 | 78
COCCH | 1 | 1 | 62 | 6.84 | 1 | 62
COCCH | 1 | 1 | 66 | 6.01 | 1 | 66
COCCH | 1 | 1 | 72 | 5.01 | 1 | 72
COCCH | 1 | 1 | 76 | 4.63 | 1 | 76
COCCH | 1 | 1 | 58 | 7.58 | 1 | 58
COCCH | 1 | 1 | 78 | 4.44 | 1 | 78
COCCH | 1 | 1 | 80 | 3.54 | 1 | 80
COCCH | 1 | 1 | 81 | 4.31 | 1 | 81
COCCH | 1 | 1 | 76 | 5.27 | 1 | 76
COCCH | 1 | 1 | 69 | 6.46 | 1 | 69
COCCH | 1 | 1 | 73 | 5.58 | 1 | 73
COCCH | 1 | 1 | 67 | 6.66 | 1 | 67
COCCH | 1 | 1 | 61 | 7.24 | 1 | 61
COCCH | 1 | 1 | 57 | 7.56 | 1 | 57
COCCH | 1 | 1 | 58 | 8.15 | 1 | 58
COCCH | 1 | 1 | 63 | 7.36 | 1 | 63
COCCH | 1 | 1 | 65 | 7.53 | 1 | 65
COCCH | 1 | 1 | 50 | 9.31 | 1 | 50
COCCH | 1 | 1 | 60 | 6.8 | 1 | 60
COCCH | 1 | 1 | 56 | 8 | 1 | 56
COCCH | 1 | 1 | 62 | 7.56 | 1 | 62
COCCH | 1 | 1 | 65 | 6.33 | 1 | 65
COCCH | 1 | 1 | 67 | 5.7 | 1 | 67
COCCH | 1 | 1 | 64 | 8.62 | 1 | 64
COCCH | 1 | 1 | 63 | 6.87 | 1 | 63
COCCH | 1 | 1 | 54 | 9.34 | 1 | 54
COCCH | 1 | 1 | 60 | 7.48 | 1 | 60
COCCH | 1 | 1 | 57 | 7.16 | 1 | 57
COCCH | 1 | 1 | 52 | 8.28 | 1 | 52
COCCH | 1 | 1 | 51 | 8.97 | 1 | 51
COCCH | 1 | 1 | 54 | 8.45 | 1 | 54
COCCH | 1 | 1 | 68 | 6.43 | 1 | 68
COCCH | 1 | 1 | 65 | 6.33 | 1 | 65
Kid Kare | 1 | 1 | 41 | 20.69 | 1 | 41
Kid Kare | 1 | 1 | 78 | 7.5 | 1 | 78
Kid Kare | 1 | 1 | 72 | 9.59 | 1 | 72
Kid Kare | 1 | 1 | 68 | 10.17 | 1 | 68
Kid Kare | 1 | 1 | 62 | 11.27 | 1 | 62
Kid Kare | 1 | 1 | 68 | 11.04 | 1 | 68
Kid Kare | 1 | 1 | 43 | 22.64 | 1 | 43
Kid Kare | 1 | 1 | 39 | 20.69 | 1 | 39
Kid Kare | 1 | 1 | 38 | 23.26 | 1 | 38
Kid Kare | 1 | 1 | 35 | 23.28 | 1 | 35
Kid Kare | 1 | 1 | 32 | 18.46 | 1 | 32
Kid Kare | 1 | 1 | 33 | 22.23 | 1 | 33
Kid Kare | 1 | 1 | 63 | 12.61 | 1 | 63
Kid Kare | 1 | 1 | 44 | 19.43 | 1 | 44
Kid Kare | 1 | 1 | 47 | 20.43 | 1 | 47
Kid Kare | 1 | 1 | 51 | 9.5 | 1 | 51
Kid Kare | 1 | 1 | 51 | 9.48 | 1 | 51
Kid Kare | 1 | 1 | 54 | 12.26 | 1 | 54
Kid Kare | 1 | 1 | 56 | 13.89 | 1 | 56
Kid Kare | 1 | 1 | 58 | 11.35 | 1 | 58
Kid Kare | 1 | 1 | 59 | 12.26 | 1 | 59
Kid Kare | 1 | 1 | 62 | 12.26 | 1 | 62
Kid Kare | 1 | 1 | 60 | 11.11 | 1 | 60
Kid Kare | 1 | 1 | 33 | 23.26 | 1 | 33
Kid Kare | 1 | 1 | 62 | 10.31 | 1 | 62
Kid Kare | 1 | 1 | 73 | 9.86 | 1 | 73
Kid Kare | 1 | 1 | 69 | 10.03 | 1 | 69
Kid Kare | 1 | 1 | 68 | 11.18 | 1 | 68
Kid Kare | 1 | 1 | 65 | 11.66 | 1 | 65
Kid Kare | 1 | 1 | 61 | 12.61 | 1 | 61
Kid Kare | 1 | 1 | 59 | 13.78 | 1 | 59
Kid Kare | 1 | 1 | 59 | 13 | 1 | 59
Kid Kare | 1 | 1 | 58 | 13.64 | 1 | 58
Kid Kare | 1 | 1 | 61 | 14.85 | 1 | 61
Kid Kare | 1 | 1 | 77 | 8.39 | 1 | 77
Kid Kare | 1 | 1 | 58 | 15.53 | 1 | 58
Kid Kare | 1 | 1 | 76 | 8.35 | 1 | 76
Kid Kare | 1 | 1 | 48 | 17.38 | 1 | 48
Kid Kare | 1 | 1 | 55 | 14.8 | 1 | 55
Kid Kare | 1 | 1 | 66 | 10.44 | 1 | 66
Kid Kare | 1 | 1 | 66 | 11.75 | 1 | 66
Kid Kare | 1 | 1 | 62 | 12.5 | 1 | 62
Kid Kare | 1 | 1 | 58 | 13.38 | 1 | 58
Kid Kare | 1 | 1 | 52 | 15.88 | 1 | 52
Kid Kare | 1 | 1 | 55 | 11.67 | 1 | 55
Kid Kare | 1 | 1 | 60 | 13.04 | 1 | 60
Kid Kare | 1 | 1 | 64 | 11.97 | 1 | 64
Kid Kare | 1 | 1 | 58 | 22.14 | 1 | 58
Kid Kare | 1 | 1 | 71 | 9.59 | 1 | 71
Kid Kare | 1 | 1 | 64 | 12.42 | 1 | 64
Kid Kare | 1 | 1 | 70 | 10.52 | 1 | 70
Kid Kare | 1 | 1 | 70 | 9.76 | 1 | 70
Kid Kare | 1 | 1 | 65 | 16.86 | 1 | 65
Kid Kare | 1 | 1 | 67 | 10.61 | 1 | 67
Kid Kare | 1 | 1 | 51 | 13.92 | 1 | 51
Kid Kare | 1 | 1 | 65 | 11.38 | 1 | 65
Kid Kare | 1 | 1 | 71 | 8.72 | 1 | 71
Kid Kare | 1 | 1 | 74 | 9.73 | 1 | 74
Kid Kare | 1 | 1 | 63 | 10.92 | 1 | 63
Kid Kare | 1 | 1 | 71 | 9.94 | 1 | 71
Kid Kare | 1 | 1 | 64 | 10.92 | 1 | 64
Kid Kare | 1 | 1 | 72 | 9.14 | 1 | 72
Kid Kare | 1 | 1 | 72 | 9.29 | 1 | 72
Kid Kare | 1 | 1 | 72 | 9.14 | 1 | 72
Kid Kare | 1 | 1 | 74 | 9.34 | 1 | 74
Kid Kare | 1 | 1 | 76 | 8.73 | 1 | 76
Kid Kare | 1 | 1 | 73 | 8.9 | 1 | 73
Kid Kare | 1 | 1 | 71 | 9.34 | 1 | 71
Kid Kare | 1 | 1 | 67 | 10.52 | 1 | 67
Kid Kare | 1 | 1 | 68 | 10.35 | 1 | 68
Kid Kare | 1 | 1 | 67 | 12.09 | 1 | 67
Kid Kare | 1 | 1 | 71 | 9.45 | 1 | 71
Kid Kare | 1 | 1 | 51 | 15.23 | 1 | 51
Kid Kare | 1 | 1 | 62 | 17.43 | 1 | 62
Kid Kare | 1 | 1 | 53 | 14.35 | 1 | 53
Kid Kare | 1 | 1 | 49 | 16.25 | 1 | 49
Kid Kare | 1 | 1 | 49 | 14.87 | 1 | 49
Kid Kare | 1 | 1 | 65 | 12.06 | 1 | 65
Kid Kare | 1 | 1 | 51 | 16.27 | 1 | 51
Kid Kare | 1 | 1 | 65 | 11.38 | 1 | 65
Kid Kare | 1 | 1 | 57 | 13.23 | 1 | 57
Kid Kare | 1 | 1 | 52 | 17.6 | 1 | 52
Kid Kare | 1 | 1 | 42 | 17.22 | 1 | 42
Kid Kare | 1 | 1 | 47 | 16.86 | 1 | 47
Kid Kare | 1 | 1 | 62 | 11.99 | 1 | 62
Kid Kare | 1 | 1 | 50 | 13.25 | 1 | 50
Kid Kare | 1 | 1 | 54 | 14.51 | 1 | 54
Kid Kare | 1 | 1 | 55 | 15.2 | 1 | 55
Kid Kare | 1 | 1 | 58 | 14.01 | 1 | 58
Kid Kare | 1 | 1 | 54 | 14.42 | 1 | 54
Kid Kare | 1 | 1 | 53 | 17.53 | 1 | 53
Kid Kare | 1 | 1 | 53 | 15.06 | 1 | 53
Kid Kare | 1 | 1 | 54 | 14.11 | 1 | 54
Kid Kare | 1 | 1 | 54 | 15.27 | 1 | 54
Kid Kare | 1 | 1 | 52 | 15.61 | 1 | 52
BayView | 3 | 1 | 80 | 8.74 | 1.5 | 120
BayView | 3 | 1 | 68 | 12.23 | 1.5 | 102
BayView | 3 | 1 | 60 | 14.08 | 1.5 | 90
BayView | 3 | 1 | 65 | 15.18 | 1.5 | 97.5
BayView | 3 | 1 | 66 | 15.69 | 1.5 | 99
BayView | 3 | 1 | 64 | 15.84 | 1.5 | 96
BayView | 3 | 1 | 61 | 16.67 | 1.5 | 91.5
BayView | 3 | 1 | 70 | 15.07 | 1.5 | 105
BayView | 3 | 1 | 72 | 13.24 | 1.5 | 108
BayView | 3 | 1 | 63 | 15.04 | 1.5 | 94.5
BayView | 3 | 1 | 68 | 14.34 | 1.5 | 102
BayView | 3 | 1 | 66 | 14.26 | 1.5 | 99
BayView | 3 | 1 | 67 | 15.14 | 1.5 | 100.5
BayView | 3 | 1 | 69 | 13.98 | 1.5 | 103.5
BayView | 3 | 1 | 63 | 16.05 | 1.5 | 94.5
BayView | 3 | 1 | 74 | 11.75 | 1.5 | 111
BayView | 3 | 1 | 48 | 21.14 | 1.5 | 72
BayView | 3 | 1 | 77 | 11.9 | 1.5 | 115.5
BayView | 3 | 1 | 55 | 18.48 | 1.5 | 82.5
BayView | 3 | 1 | 53 | 18.99 | 1.5 | 79.5
BayView | 3 | 1 | 59 | 16.45 | 1.5 | 88.5
BayView | 3 | 1 | 60 | 15.65 | 1.5 | 90
BayView | 3 | 1 | 64 | 14.88 | 1.5 | 96
BayView | 3 | 1 | 70 | 14.07 | 1.5 | 105
BayView | 3 | 1 | 63 | 15.02 | 1.5 | 94.5
BayView | 3 | 1 | 72 | 13.41 | 1.5 | 108
BayView | 3 | 1 | 77 | 12.35 | 1.5 | 115.5
BayView | 3 | 1 | 53 | 18.37 | 1.5 | 79.5
BLDG210 | 2 | 0 | 66 | 22.72 | 3 | 198
BLDG210 | 2 | 0 | 68 | 22.83 | 3 | 204
BLDG210 | 2 | 0 | 63 | 25.24 | 3 | 189
BLDG210 | 2 | 0 | 68 | 24.21 | 3 | 204
BLDG210 | 2 | 0 | 70 | 21.78 | 3 | 210
BLDG210 | 2 | 0 | 61 | 26.47 | 3 | 183
BLDG210 | 2 | 0 | 64 | 25.63 | 3 | 192
BLDG210 | 2 | 0 | 66 | 24.01 | 3 | 198
BLDG210 | 2 | 0 | 74 | 25.43 | 3 | 222
BLDG210 | 2 | 0 | 67 | 22.81 | 3 | 201
BLDG210 | 2 | 0 | 77 | 14.89 | 3 | 231
BLDG210 | 2 | 0 | 59 | 26.25 | 3 | 177
BLDG210 | 2 | 0 | 60 | 22.05 | 3 | 180
BLDG210 | 2 | 0 | 69 | 21.65 | 3 | 207
BLDG210 | 2 | 0 | 80 | 16.75 | 3 | 240
BLDG210 | 2 | 0 | 77 | 19.08 | 3 | 231
BLDG210 | 2 | 0 | 72 | 20.72 | 3 | 216
BLDG210 | 2 | 0 | 63 | 27.04 | 3 | 189
BLDG210 | 2 | 0 | 70 | 22.17 | 3 | 210
BLDG210 | 2 | 0 | 60 | 28.55 | 3 | 180
BLDG210 | 2 | 0 | 63 | 27.9 | 3 | 189
BLDG210 | 2 | 0 | 55 | 31.26 | 3 | 165
BLDG210 | 2 | 0 | 53 | 32.4 | 3 | 159
BLDG210 | 2 | 0 | 48 | 33.31 | 3 | 144
BLDG210 | 2 | 0 | 72 | 17.54 | 3 | 216
BLDG210 | 2 | 0 | 53 | 25.38 | 3 | 159
BLDG210 | 2 | 0 | 64 | 25.29 | 3 | 192
BLDG210 | 2 | 0 | 65 | 24.17 | 3 | 195
BNS GEN | 3 | 1 | 68 | 19.59 | 2.5 | 170
BNS GEN | 3 | 1 | 77 | 18.89 | 2.5 | 192.5
BNS GEN | 3 | 1 | 74 | 18.44 | 2.5 | 185
BNS GEN | 3 | 1 | 80 | 13.56 | 2.5 | 200
BNS GEN | 3 | 1 | 60 | 24.43 | 2.5 | 150
BNS GEN | 3 | 1 | 65 | 25.28 | 2.5 | 162.5
BNS GEN | 3 | 1 | 66 | 27.62 | 2.5 | 165
BNS GEN | 3 | 1 | 64 | 26.73 | 2.5 | 160
BNS GEN | 3 | 1 | 61 | 28.58 | 2.5 | 152.5
BNS GEN | 3 | 1 | 70 | 24.45 | 2.5 | 175
BNS GEN | 3 | 1 | 72 | 23.16 | 2.5 | 180
BNS GEN | 3 | 1 | 63 | 25.76 | 2.5 | 157.5
BNS GEN | 3 | 1 | 68 | 25.53 | 2.5 | 170
BNS GEN | 3 | 1 | 66 | 26.12 | 2.5 | 165
BNS GEN | 3 | 1 | 63 | 30.02 | 2.5 | 157.5
BNS GEN | 3 | 1 | 67 | 24.42 | 2.5 | 167.5
BNS GEN | 3 | 1 | 77 | 20.16 | 2.5 | 192.5
BNS GEN | 3 | 1 | 70 | 24.19 | 2.5 | 175
BNS GEN | 3 | 1 | 64 | 27.54 | 2.5 | 160
BNS GEN | 3 | 1 | 59 | 30.4 | 2.5 | 147.5
BNS GEN | 3 | 1 | 63 | 28.78 | 2.5 | 157.5
BNS GEN | 3 | 1 | 55 | 35 | 2.5 | 137.5
BNS GEN | 3 | 1 | 53 | 36.17 | 2.5 | 132.5
BNS GEN | 3 | 1 | 48 | 40.62 | 2.5 | 120
BNS GEN | 3 | 1 | 53 | 36.65 | 2.5 | 132.5
BNS GEN | 3 | 1 | 69 | 22.37 | 2.5 | 172.5
BNS GEN | 3 | 1 | 72 | 23.45 | 2.5 | 180
BNS GEN | 3 | 1 | 60 | 28.74 | 2.5 | 150
NQ | 4 | 1 | 66 | 68.56 | 10 | 660
NQ | 4 | 1 | 45 | 109.25 | 10 | 450
NQ | 4 | 1 | 45 | 112.09 | 10 | 450
NQ | 4 | 1 | 58 | 80.08 | 10 | 580
NQ | 4 | 1 | 51 | 100.12 | 10 | 510
NQ | 4 | 1 | 56 | 81.13 | 10 | 560
NQ | 4 | 1 | 47 | 108.9 | 10 | 470
NQ | 4 | 1 | 48 | 103.73 | 10 | 480
NQ | 4 | 1 | 52 | 90.78 | 10 | 520
NQ | 4 | 1 | 53 | 91.16 | 10 | 530
NQ | 4 | 1 | 55 | 91.45 | 10 | 550
NQ | 4 | 1 | 43 | 128.86 | 10 | 430
NQ | 4 | 1 | 49 | 103.44 | 10 | 490
NQ | 4 | 1 | 52 | 87.74 | 10 | 520
NQ | 4 | 1 | 60 | 70.99 | 10 | 600
NQ | 4 | 1 | 46 | 107.2 | 10 | 460
NQ | 4 | 1 | 33 | 135.86 | 10 | 330
NQ | 4 | 1 | 53 | 93.8 | 10 | 530
NQ | 4 | 1 | 52 | 93.36 | 10 | 520
NQ | 4 | 1 | 55 | 78.49 | 10 | 550
NQ | 4 | 1 | 43 | 124.67 | 10 | 430
NQ | 4 | 1 | 49 | 102.32 | 10 | 490
NQ | 4 | 1 | 41 | 132.18 | 10 | 410
NQ | 4 | 1 | 46 | 125.94 | 10 | 460
NQ | 4 | 1 | 40 | 138.28 | 10 | 400
NQ | 4 | 1 | 36 | 132.52 | 10 | 360
NQ | 4 | 1 | 37 | 142.15 | 10 | 370
NQ | 4 | 1 | 37 | 124.63 | 10 | 370
NQ | 4 | 1 | 39 | 123 | 10 | 390
NQ | 4 | 1 | 46 | 107.66 | 10 | 460
NQ | 4 | 1 | 47 | 105.97 | 10 | 470
NQ | 4 | 1 | 37 | 140.25 | 10 | 370
NQ | 4 | 1 | 44 | 124.86 | 10 | 440
NQ | 4 | 1 | 39 | 132.78 | 10 | 390
NQ | 4 | 1 | 37 | 129.63 | 10 | 370
NQ | 4 | 1 | 41 | 121.86 | 10 | 410
NQ | 4 | 1 | 44 | 109.08 | 10 | 440
NQ | 4 | 1 | 44 | 116.95 | 10 | 440
NQ | 4 | 1 | 44 | 126.81 | 10 | 440
NQ | 4 | 1 | 41 | 112.37 | 10 | 410

## T1 Size1
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | New Rated Heater Size kW | Heater Size X Temp
TCWWTP | 1 | 1 | 12 | 9.48 | 1 | 12 | SUMMARY OUTPUT
TCWWTP | 1 | 1 | 32 | 7.79 | 1 | 32
TCWWTP | 1 | 1 | 29 | 8.01 | 1 | 29 | Regression Statistics
TCWWTP | 1 | 1 | 38 | 7.82 | 1 | 38 | Multiple R | 0.97077
TCWWTP | 1 | 1 | 34 | 8.02 | 1 | 34 | R Square | 0.94239
TCWWTP | 1 | 1 | 33 | 8.17 | 1 | 33 | Adjusted R Square | 0.94203
TCWWTP | 1 | 1 | 33 | 8.26 | 1 | 33 | Standard Error | 4.2279
TCWWTP | 1 | 1 | 31 | 8.39 | 1 | 31 | Observations | 320
TCWWTP | 1 | 1 | 31 | 8.22 | 1 | 31
TCWWTP | 1 | 1 | 33 | 8.56 | 1 | 33 | ANOVA
TCWWTP | 1 | 1 | 34 | 8.1 | 1 | 34 |  | df | SS | MS | F | Significance F
TCWWTP | 1 | 1 | 35 | 8.48 | 1 | 35 | Regression | 2 | 92698.299 | 46349.1495 | 2592.9769 | 3.4154e-197
TCWWTP | 1 | 1 | 22 | 8.26 | 1 | 22 | Residual | 317 | 5666.3367 | 17.8749
TCWWTP | 1 | 1 | 30 | 8.8 | 1 | 30 | Total | 319 | 98364.6357
TCWWTP | 1 | 1 | 29 | 8.52 | 1 | 29
TCWWTP | 1 | 1 | 31 | 8.56 | 1 | 31 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
TCWWTP | 1 | 1 | 39 | 7.86 | 1 | 39 | Intercept | 3.7032 | 0.349 | 10.6109 | 1.0392e-22 | 3.0165 | 4.3898 | 3.0165 | 4.3898
TCWWTP | 1 | 1 | 22 | 8.58 | 1 | 22 | X Variable 1 | 13.1354 | 0.31426 | 41.7974 | 5.2816e-131 | 12.5171 | 13.7538 | 12.5171 | 13.7538
TCWWTP | 1 | 1 | 22 | 8.38 | 1 | 22 | X Variable 2 | -0.13649 | 0.0069953 | -19.5119 | 2.9953e-56 | -0.15025 | -0.12273 | -0.15025 | -0.12273
TCWWTP | 1 | 1 | 19 | 9.05 | 1 | 19
TCWWTP | 1 | 1 | 27 | 8.4 | 1 | 27
TCWWTP | 1 | 1 | 30 | 8.21 | 1 | 30
TCWWTP | 1 | 1 | 38 | 8.13 | 1 | 38
TCWWTP | 1 | 1 | 34 | 8.15 | 1 | 34
TCWWTP | 1 | 1 | 32 | 8.02 | 1 | 32
TCWWTP | 1 | 1 | 25 | 8.22 | 1 | 25
TCWWTP | 1 | 1 | 19 | 8.66 | 1 | 19
TCWWTP | 1 | 1 | 30 | 7.94 | 1 | 30
TCWWTP | 1 | 1 | 18 | 8.99 | 1 | 18
TCWWTP | 1 | 1 | 34 | 8.21 | 1 | 34
TCWWTP | 1 | 1 | 26 | 8.22 | 1 | 26
TCWWTP | 1 | 1 | 3 | 9.57 | 1 | 3
TCWWTP | 1 | 1 | 5 | 9.52 | 1 | 5
TCWWTP | 1 | 1 | 26 | 8.55 | 1 | 26
TCWWTP | 1 | 1 | 26 | 8.41 | 1 | 26
TCWWTP | 1 | 1 | 40 | 7.94 | 1 | 40
TCWWTP | 1 | 1 | 36 | 7.55 | 1 | 36
TCWWTP | 1 | 1 | 24 | 8.82 | 1 | 24
TCWWTP | 1 | 1 | 22 | 8.55 | 1 | 22
TCWWTP | 1 | 1 | 16 | 9.03 | 1 | 16
TCWWTP | 1 | 1 | 19 | 8.73 | 1 | 19
TCWWTP | 1 | 1 | 39 | 7.17 | 1 | 39
TCWWTP | 1 | 1 | 30 | 7.02 | 1 | 30
TCWWTP | 1 | 1 | 37 | 7.08 | 1 | 37
TCWWTP | 1 | 1 | 28 | 7.83 | 1 | 28
TCWWTP | 1 | 1 | 32 | 8.65 | 1 | 32
TCWWTP | 1 | 1 | 25 | 8.4 | 1 | 25
TCWWTP | 1 | 1 | 16 | 7.7 | 1 | 16
TCWWTP | 1 | 1 | 27 | 8.19 | 1 | 27
TCWWTP | 1 | 1 | 30 | 7.1 | 1 | 30
TCWWTP | 1 | 1 | 15 | 8.83 | 1 | 15
TCWWTP | 1 | 1 | 33 | 8.41 | 1 | 33
TCWWTP | 1 | 1 | 40 | 7.94 | 1 | 40
TCWWTP | 1 | 1 | 38 | 8.06 | 1 | 38
TCWWTP | 1 | 1 | 32 | 7.87 | 1 | 32
TCWWTP | 1 | 1 | 37 | 7.99 | 1 | 37
TCWWTP | 1 | 1 | 35 | 8.99 | 1 | 35
TCWWTP | 1 | 1 | 25 | 8.4 | 1 | 25
TCWWTP | 1 | 1 | 39 | 7.74 | 1 | 39
TCWWTP | 1 | 1 | 15 | 8.89 | 1 | 15
TCWWTP | 1 | 1 | 19 | 8.77 | 1 | 19
TCWWTP | 1 | 1 | 29 | 8.39 | 1 | 29
TCWWTP | 1 | 1 | 35 | 8.57 | 1 | 35
TCWWTP | 1 | 1 | 34 | 7.95 | 1 | 34
TCWWTP | 1 | 1 | 36 | 7.69 | 1 | 36
TCWWTP | 1 | 1 | 23 | 9.35 | 1 | 23
TCWWTP | 1 | 1 | 24 | 8.18 | 1 | 24
TCWWTP | 1 | 1 | 39 | 7.02 | 1 | 39
TCWWTP | 1 | 1 | 42 | 7.72 | 1 | 42
TCWWTP | 1 | 1 | 41 | 8.17 | 1 | 41
TCWWTP | 1 | 1 | 25 | 8.17 | 1 | 25
TCWWTP | 1 | 1 | 36 | 8.28 | 1 | 36
TCWWTP | 1 | 1 | 34 | 8.16 | 1 | 34
TCWWTP | 1 | 1 | 40 | 7.97 | 1 | 40
TCWWTP | 1 | 1 | 32 | 8.14 | 1 | 32
TCWWTP | 1 | 1 | 28 | 7.21 | 1 | 28
TCWWTP | 1 | 1 | 33 | 7.14 | 1 | 33
TCWWTP | 1 | 1 | 27 | 7.16 | 1 | 27
TCWWTP | 1 | 1 | 18 | 9.38 | 1 | 18
HCNW | 1 | 0 | 54 | 37.7 | 6 | 324
HCNW | 1 | 0 | 58 | 19.7 | 6 | 348
HCNW | 1 | 0 | 54 | 29.2 | 6 | 324
HCNW | 1 | 0 | 51 | 41 | 6 | 306
HCNW | 1 | 0 | 51 | 42.2 | 6 | 306
HCNW | 1 | 0 | 44 | 46.2 | 6 | 264
HCNW | 1 | 0 | 38 | 54.9 | 6 | 228
HCNW | 1 | 0 | 34 | 55.2 | 6 | 204
HCNW | 1 | 0 | 43 | 51.4 | 6 | 258
HCNW | 1 | 0 | 55 | 38.2 | 6 | 330
HCNW | 1 | 0 | 60 | 18.8 | 6 | 360
HCNW | 1 | 0 | 52 | 40.3 | 6 | 312
HCNW | 1 | 0 | 43 | 49.5 | 6 | 258
HCNW | 1 | 0 | 35 | 56.8 | 6 | 210
HCNW | 1 | 0 | 32 | 60.8 | 6 | 192
HCNW | 1 | 0 | 32 | 60.8 | 6 | 192
HCNW | 1 | 0 | 47 | 46.9 | 6 | 282
HCNW | 1 | 0 | 44 | 48.8 | 6 | 264
HCNW | 1 | 0 | 34 | 57 | 6 | 204
HCNW | 1 | 0 | 53 | 40.3 | 6 | 318
HCNW | 1 | 0 | 51 | 40 | 6 | 306
HCNW | 1 | 0 | 56 | 35.6 | 6 | 336
HCNW | 1 | 0 | 53 | 37 | 6 | 318
HCNW | 1 | 0 | 54 | 36.3 | 6 | 324
HCNW | 1 | 0 | 54 | 37.2 | 6 | 324
HCNW | 1 | 0 | 50 | 41.5 | 6 | 300
HCNW | 1 | 0 | 47 | 44.3 | 6 | 282
HCNW | 1 | 0 | 42 | 48.1 | 6 | 252
HCNW | 1 | 0 | 52 | 40.3 | 6 | 312
HCNW | 1 | 0 | 59 | 31.8 | 6 | 354
HCNW | 1 | 0 | 57 | 34.4 | 6 | 342
HCNW | 1 | 0 | 62 | 28 | 6 | 372
HCNW | 1 | 0 | 51 | 40.8 | 6 | 306
HCNW | 1 | 0 | 51 | 39.1 | 6 | 306
HCNW | 1 | 0 | 49 | 37.9 | 6 | 294
HCNW | 1 | 0 | 49 | 41.7 | 6 | 294
HCNW | 1 | 0 | 53 | 38.2 | 6 | 318
HCNW | 1 | 0 | 62 | 29.9 | 6 | 372
HCNW | 1 | 0 | 65 | 25.6 | 6 | 390
HCNW | 1 | 0 | 62 | 29.7 | 6 | 372
HCNW | 1 | 0 | 35 | 52.5 | 6 | 210
HCNW | 1 | 0 | 58 | 33.4 | 6 | 348
HCNW | 1 | 0 | 32 | 57.3 | 6 | 192
HCNW | 1 | 0 | 27 | 64.4 | 6 | 162
HCNW | 1 | 0 | 52 | 38.9 | 6 | 312
HCNW | 1 | 0 | 26 | 64.4 | 6 | 156
HCNW | 1 | 0 | 41 | 50.9 | 6 | 246
HCNW | 1 | 0 | 31 | 60.4 | 6 | 186
HCNW | 1 | 0 | 37 | 53.2 | 6 | 222
HCNW | 1 | 0 | 34 | 55.7 | 6 | 204
HCNW | 1 | 0 | 38 | 52.8 | 6 | 228
HCNW | 1 | 0 | 42 | 47.4 | 6 | 252
HCNW | 1 | 0 | 38 | 51 | 6 | 228
HCNW | 1 | 0 | 41 | 51.8 | 6 | 246
HCNW | 1 | 0 | 43 | 47.8 | 6 | 258
HCNW | 1 | 0 | 42 | 47.7 | 6 | 252
HCNW | 1 | 0 | 49 | 43 | 6 | 294
HCNW | 1 | 0 | 40 | 50.6 | 6 | 240
HCNW | 1 | 0 | 35 | 57.8 | 6 | 210
HCNW | 1 | 0 | 33 | 59 | 6 | 198
HCNW | 1 | 0 | 31 | 57.6 | 6 | 186
HCNW | 1 | 0 | 36 | 56.4 | 6 | 216
HCNW | 1 | 0 | 35 | 49.6 | 6 | 210
HCNW | 1 | 0 | 36 | 55.3 | 6 | 216
HCNW | 1 | 0 | 37 | 51.4 | 6 | 222
HCNW | 1 | 0 | 33 | 58.2 | 6 | 198
HCNW | 1 | 0 | 42 | 46.7 | 6 | 252
HCNW | 1 | 0 | 43 | 46.5 | 6 | 258
HCNW | 1 | 0 | 44 | 45.8 | 6 | 264
HCNW | 1 | 0 | 46 | 41.6 | 6 | 276
HCNW | 1 | 0 | 47 | 42.5 | 6 | 282
HCNW | 1 | 0 | 49 | 42.1 | 6 | 294
HCNW | 1 | 0 | 44 | 44.6 | 6 | 264
HCNW | 1 | 0 | 36 | 57.5 | 6 | 216
HCNW | 1 | 0 | 46 | 47.3 | 6 | 276
HCNW | 1 | 0 | 30 | 60.2 | 6 | 180
HCNW | 1 | 0 | 27 | 62.5 | 6 | 162
HCNW | 1 | 0 | 33 | 60.7 | 6 | 198
HCNW | 1 | 0 | 33 | 51.9 | 6 | 198
HCNW | 1 | 0 | 43 | 49.3 | 6 | 258
HCNW | 1 | 0 | 39 | 53 | 6 | 234
HCNW | 1 | 0 | 38 | 54.2 | 6 | 228
HCNW | 1 | 0 | 35 | 57.5 | 6 | 210
HCNW | 1 | 0 | 32 | 48.1 | 6 | 192
HCNW | 1 | 0 | 30 | 61.2 | 6 | 180
HCNW | 1 | 0 | 49 | 43.2 | 6 | 294
HCNW | 1 | 0 | 33 | 53.8 | 6 | 198
COCCH | 1 | 1 | 43 | 10.92 | 1 | 43
COCCH | 1 | 1 | 75 | 5.69 | 1 | 75
COCCH | 1 | 1 | 65 | 6.05 | 1 | 65
COCCH | 1 | 1 | 66 | 6.18 | 1 | 66
COCCH | 1 | 1 | 70 | 5.47 | 1 | 70
COCCH | 1 | 1 | 48 | 9.79 | 1 | 48
COCCH | 1 | 1 | 56 | 8.88 | 1 | 56
COCCH | 1 | 1 | 54 | 8.39 | 1 | 54
COCCH | 1 | 1 | 69 | 5.75 | 1 | 69
COCCH | 1 | 1 | 49 | 9.58 | 1 | 49
COCCH | 1 | 1 | 68 | 6.16 | 1 | 68
COCCH | 1 | 1 | 49 | 9.53 | 1 | 49
COCCH | 1 | 1 | 51 | 8.89 | 1 | 51
COCCH | 1 | 1 | 54 | 8.04 | 1 | 54
COCCH | 1 | 1 | 78 | 4.5 | 1 | 78
COCCH | 1 | 1 | 74 | 4.48 | 1 | 74
COCCH | 1 | 1 | 81 | 4.91 | 1 | 81
COCCH | 1 | 1 | 69 | 5.99 | 1 | 69
COCCH | 1 | 1 | 54 | 8.46 | 1 | 54
COCCH | 1 | 1 | 79 | 4.88 | 1 | 79
COCCH | 1 | 1 | 66 | 6.86 | 1 | 66
COCCH | 1 | 1 | 76 | 4.95 | 1 | 76
COCCH | 1 | 1 | 70 | 5.14 | 1 | 70
COCCH | 1 | 1 | 73 | 5.66 | 1 | 73
COCCH | 1 | 1 | 69 | 6.21 | 1 | 69
COCCH | 1 | 1 | 78 | 5.17 | 1 | 78
COCCH | 1 | 1 | 62 | 6.84 | 1 | 62
COCCH | 1 | 1 | 66 | 6.01 | 1 | 66
COCCH | 1 | 1 | 72 | 5.01 | 1 | 72
COCCH | 1 | 1 | 76 | 4.63 | 1 | 76
COCCH | 1 | 1 | 58 | 7.58 | 1 | 58
COCCH | 1 | 1 | 78 | 4.44 | 1 | 78
COCCH | 1 | 1 | 80 | 3.54 | 1 | 80
COCCH | 1 | 1 | 81 | 4.31 | 1 | 81
COCCH | 1 | 1 | 76 | 5.27 | 1 | 76
COCCH | 1 | 1 | 69 | 6.46 | 1 | 69
COCCH | 1 | 1 | 73 | 5.58 | 1 | 73
COCCH | 1 | 1 | 67 | 6.66 | 1 | 67
COCCH | 1 | 1 | 61 | 7.24 | 1 | 61
COCCH | 1 | 1 | 57 | 7.56 | 1 | 57
COCCH | 1 | 1 | 58 | 8.15 | 1 | 58
COCCH | 1 | 1 | 63 | 7.36 | 1 | 63
COCCH | 1 | 1 | 65 | 7.53 | 1 | 65
COCCH | 1 | 1 | 50 | 9.31 | 1 | 50
COCCH | 1 | 1 | 60 | 6.8 | 1 | 60
COCCH | 1 | 1 | 56 | 8 | 1 | 56
COCCH | 1 | 1 | 62 | 7.56 | 1 | 62
COCCH | 1 | 1 | 65 | 6.33 | 1 | 65
COCCH | 1 | 1 | 67 | 5.7 | 1 | 67
COCCH | 1 | 1 | 64 | 8.62 | 1 | 64
COCCH | 1 | 1 | 63 | 6.87 | 1 | 63
COCCH | 1 | 1 | 54 | 9.34 | 1 | 54
COCCH | 1 | 1 | 60 | 7.48 | 1 | 60
COCCH | 1 | 1 | 57 | 7.16 | 1 | 57
COCCH | 1 | 1 | 52 | 8.28 | 1 | 52
COCCH | 1 | 1 | 51 | 8.97 | 1 | 51
COCCH | 1 | 1 | 54 | 8.45 | 1 | 54
COCCH | 1 | 1 | 68 | 6.43 | 1 | 68
COCCH | 1 | 1 | 65 | 6.33 | 1 | 65
Kid Kare | 1 | 1 | 41 | 20.69 | 1 | 41
Kid Kare | 1 | 1 | 78 | 7.5 | 1 | 78
Kid Kare | 1 | 1 | 72 | 9.59 | 1 | 72
Kid Kare | 1 | 1 | 68 | 10.17 | 1 | 68
Kid Kare | 1 | 1 | 62 | 11.27 | 1 | 62
Kid Kare | 1 | 1 | 68 | 11.04 | 1 | 68
Kid Kare | 1 | 1 | 43 | 22.64 | 1 | 43
Kid Kare | 1 | 1 | 39 | 20.69 | 1 | 39
Kid Kare | 1 | 1 | 38 | 23.26 | 1 | 38
Kid Kare | 1 | 1 | 35 | 23.28 | 1 | 35
Kid Kare | 1 | 1 | 32 | 18.46 | 1 | 32
Kid Kare | 1 | 1 | 33 | 22.23 | 1 | 33
Kid Kare | 1 | 1 | 63 | 12.61 | 1 | 63
Kid Kare | 1 | 1 | 44 | 19.43 | 1 | 44
Kid Kare | 1 | 1 | 47 | 20.43 | 1 | 47
Kid Kare | 1 | 1 | 51 | 9.5 | 1 | 51
Kid Kare | 1 | 1 | 51 | 9.48 | 1 | 51
Kid Kare | 1 | 1 | 54 | 12.26 | 1 | 54
Kid Kare | 1 | 1 | 56 | 13.89 | 1 | 56
Kid Kare | 1 | 1 | 58 | 11.35 | 1 | 58
Kid Kare | 1 | 1 | 59 | 12.26 | 1 | 59
Kid Kare | 1 | 1 | 62 | 12.26 | 1 | 62
Kid Kare | 1 | 1 | 60 | 11.11 | 1 | 60
Kid Kare | 1 | 1 | 33 | 23.26 | 1 | 33
Kid Kare | 1 | 1 | 62 | 10.31 | 1 | 62
Kid Kare | 1 | 1 | 73 | 9.86 | 1 | 73
Kid Kare | 1 | 1 | 69 | 10.03 | 1 | 69
Kid Kare | 1 | 1 | 68 | 11.18 | 1 | 68
Kid Kare | 1 | 1 | 65 | 11.66 | 1 | 65
Kid Kare | 1 | 1 | 61 | 12.61 | 1 | 61
Kid Kare | 1 | 1 | 59 | 13.78 | 1 | 59
Kid Kare | 1 | 1 | 59 | 13 | 1 | 59
Kid Kare | 1 | 1 | 58 | 13.64 | 1 | 58
Kid Kare | 1 | 1 | 61 | 14.85 | 1 | 61
Kid Kare | 1 | 1 | 77 | 8.39 | 1 | 77
Kid Kare | 1 | 1 | 58 | 15.53 | 1 | 58
Kid Kare | 1 | 1 | 76 | 8.35 | 1 | 76
Kid Kare | 1 | 1 | 48 | 17.38 | 1 | 48
Kid Kare | 1 | 1 | 55 | 14.8 | 1 | 55
Kid Kare | 1 | 1 | 66 | 10.44 | 1 | 66
Kid Kare | 1 | 1 | 66 | 11.75 | 1 | 66
Kid Kare | 1 | 1 | 62 | 12.5 | 1 | 62
Kid Kare | 1 | 1 | 58 | 13.38 | 1 | 58
Kid Kare | 1 | 1 | 52 | 15.88 | 1 | 52
Kid Kare | 1 | 1 | 55 | 11.67 | 1 | 55
Kid Kare | 1 | 1 | 60 | 13.04 | 1 | 60
Kid Kare | 1 | 1 | 64 | 11.97 | 1 | 64
Kid Kare | 1 | 1 | 58 | 22.14 | 1 | 58
Kid Kare | 1 | 1 | 71 | 9.59 | 1 | 71
Kid Kare | 1 | 1 | 64 | 12.42 | 1 | 64
Kid Kare | 1 | 1 | 70 | 10.52 | 1 | 70
Kid Kare | 1 | 1 | 70 | 9.76 | 1 | 70
Kid Kare | 1 | 1 | 65 | 16.86 | 1 | 65
Kid Kare | 1 | 1 | 67 | 10.61 | 1 | 67
Kid Kare | 1 | 1 | 51 | 13.92 | 1 | 51
Kid Kare | 1 | 1 | 65 | 11.38 | 1 | 65
Kid Kare | 1 | 1 | 71 | 8.72 | 1 | 71
Kid Kare | 1 | 1 | 74 | 9.73 | 1 | 74
Kid Kare | 1 | 1 | 63 | 10.92 | 1 | 63
Kid Kare | 1 | 1 | 71 | 9.94 | 1 | 71
Kid Kare | 1 | 1 | 64 | 10.92 | 1 | 64
Kid Kare | 1 | 1 | 72 | 9.14 | 1 | 72
Kid Kare | 1 | 1 | 72 | 9.29 | 1 | 72
Kid Kare | 1 | 1 | 72 | 9.14 | 1 | 72
Kid Kare | 1 | 1 | 74 | 9.34 | 1 | 74
Kid Kare | 1 | 1 | 76 | 8.73 | 1 | 76
Kid Kare | 1 | 1 | 73 | 8.9 | 1 | 73
Kid Kare | 1 | 1 | 71 | 9.34 | 1 | 71
Kid Kare | 1 | 1 | 67 | 10.52 | 1 | 67
Kid Kare | 1 | 1 | 68 | 10.35 | 1 | 68
Kid Kare | 1 | 1 | 67 | 12.09 | 1 | 67
Kid Kare | 1 | 1 | 71 | 9.45 | 1 | 71
Kid Kare | 1 | 1 | 51 | 15.23 | 1 | 51
Kid Kare | 1 | 1 | 62 | 17.43 | 1 | 62
Kid Kare | 1 | 1 | 53 | 14.35 | 1 | 53
Kid Kare | 1 | 1 | 49 | 16.25 | 1 | 49
Kid Kare | 1 | 1 | 49 | 14.87 | 1 | 49
Kid Kare | 1 | 1 | 65 | 12.06 | 1 | 65
Kid Kare | 1 | 1 | 51 | 16.27 | 1 | 51
Kid Kare | 1 | 1 | 65 | 11.38 | 1 | 65
Kid Kare | 1 | 1 | 57 | 13.23 | 1 | 57
Kid Kare | 1 | 1 | 52 | 17.6 | 1 | 52
Kid Kare | 1 | 1 | 42 | 17.22 | 1 | 42
Kid Kare | 1 | 1 | 47 | 16.86 | 1 | 47
Kid Kare | 1 | 1 | 62 | 11.99 | 1 | 62
Kid Kare | 1 | 1 | 50 | 13.25 | 1 | 50
Kid Kare | 1 | 1 | 54 | 14.51 | 1 | 54
Kid Kare | 1 | 1 | 55 | 15.2 | 1 | 55
Kid Kare | 1 | 1 | 58 | 14.01 | 1 | 58
Kid Kare | 1 | 1 | 54 | 14.42 | 1 | 54
Kid Kare | 1 | 1 | 53 | 17.53 | 1 | 53
Kid Kare | 1 | 1 | 53 | 15.06 | 1 | 53
Kid Kare | 1 | 1 | 54 | 14.11 | 1 | 54
Kid Kare | 1 | 1 | 54 | 15.27 | 1 | 54
Kid Kare | 1 | 1 | 52 | 15.61 | 1 | 52

## T1 Size2
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | New Rated Heater Size kW | Heater Size X Temp
COCFD | 2 | 1 | 66 | 10.42 | 1 | 66 | SUMMARY OUTPUT
COCFD | 2 | 1 | 48 | 18.38 | 1 | 48
COCFD | 2 | 1 | 70 | 8.26 | 1 | 70 | Regression Statistics
COCFD | 2 | 1 | 76 | 6.77 | 1 | 76 | Multiple R | 0.96247
COCFD | 2 | 1 | 61 | 12.87 | 1 | 61 | R Square | 0.92635
COCFD | 2 | 1 | 67 | 11.41 | 1 | 67 | Adjusted R Square | 0.92583
COCFD | 2 | 1 | 73 | 8.99 | 1 | 73 | Standard Error | 3.7553
COCFD | 2 | 1 | 69 | 10.32 | 1 | 69 | Observations | 282
COCFD | 2 | 1 | 76 | 8.3 | 1 | 76
COCFD | 2 | 1 | 81 | 6.57 | 1 | 81 | ANOVA
COCFD | 2 | 1 | 78 | 6.79 | 1 | 78 |  | df | SS | MS | F | Significance F
COCFD | 2 | 1 | 70 | 8.7 | 1 | 70 | Regression | 2 | 49489.4526 | 24744.7263 | 1754.6913 | 9.2784e-159
COCFD | 2 | 1 | 63 | 13.54 | 1 | 63 | Residual | 279 | 3934.469 | 14.102
COCFD | 2 | 1 | 73 | 8.71 | 1 | 73 | Total | 281 | 53423.9215
COCFD | 2 | 1 | 64 | 15.11 | 1 | 64
COCFD | 2 | 1 | 80 | 4.11 | 1 | 80 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
COCFD | 2 | 1 | 57 | 13.6 | 1 | 57 | Intercept | 5.8599 | 0.3374 | 17.368 | 2.6033e-46 | 5.1957 | 6.5241 | 5.1957 | 6.5241
COCFD | 2 | 1 | 58 | 12.83 | 1 | 58 | X Variable 1 | 13.1949 | 0.3888 | 33.9374 | 4.8565e-101 | 12.4295 | 13.9603 | 12.4295 | 13.9603
COCFD | 2 | 1 | 57 | 12.04 | 1 | 57 | X Variable 2 | -0.13339 | 0.0074641 | -17.8713 | 3.8622e-48 | -0.14809 | -0.1187 | -0.14809 | -0.1187
COCFD | 2 | 1 | 62 | 12.06 | 1 | 62
COCFD | 2 | 1 | 54 | 14.79 | 1 | 54
COCFD | 2 | 1 | 81 | 7.18 | 1 | 81
COCFD | 2 | 1 | 78 | 7.91 | 1 | 78
COCFD | 2 | 1 | 68 | 11.03 | 1 | 68
COCFD | 2 | 1 | 74 | 5.53 | 1 | 74
COCFD | 2 | 1 | 54 | 16.96 | 1 | 54
COCFD | 2 | 1 | 65 | 12.97 | 1 | 65
COCFD | 2 | 1 | 54 | 15.47 | 1 | 54
COCFD | 2 | 1 | 51 | 16.28 | 1 | 51
COCFD | 2 | 1 | 52 | 13.98 | 1 | 52
COCFD | 2 | 1 | 60 | 11.82 | 1 | 60
COCFD | 2 | 1 | 60 | 11.86 | 1 | 60
COCFD | 2 | 1 | 63 | 11.75 | 1 | 63
COCFD | 2 | 1 | 65 | 10.49 | 1 | 65
COCFD | 2 | 1 | 67 | 8.82 | 1 | 67
COCFD | 2 | 1 | 58 | 14.66 | 1 | 58
COCFD | 2 | 1 | 56 | 14.25 | 1 | 56
COCFD | 2 | 1 | 76 | 7.76 | 1 | 76
COCFD | 2 | 1 | 54 | 15.72 | 1 | 54
COCFD | 2 | 1 | 51 | 15.47 | 1 | 51
COCFD | 2 | 1 | 49 | 17.77 | 1 | 49
COCFD | 2 | 1 | 49 | 18.79 | 1 | 49
COCFD | 2 | 1 | 54 | 15.29 | 1 | 54
COCFD | 2 | 1 | 56 | 16.1 | 1 | 56
COCFD | 2 | 1 | 69 | 9.36 | 1 | 69
COCFD | 2 | 1 | 43 | 21.31 | 1 | 43
COCFD | 2 | 1 | 50 | 17.61 | 1 | 50
COCFD | 2 | 1 | 65 | 10.46 | 1 | 65
COCFD | 2 | 1 | 69 | 9.64 | 1 | 69
COCFD | 2 | 1 | 78 | 7.01 | 1 | 78
COCFD | 2 | 1 | 79 | 6.39 | 1 | 79
COCFD | 2 | 1 | 75 | 8.71 | 1 | 75
COCFD | 2 | 1 | 72 | 7.5 | 1 | 72
COCFD | 2 | 1 | 66 | 9.42 | 1 | 66
COCFD | 2 | 1 | 62 | 11.73 | 1 | 62
COCFD | 2 | 1 | 66 | 11.12 | 1 | 66
COCFD | 2 | 1 | 69 | 9.71 | 1 | 69
COCFD | 2 | 1 | 68 | 9.53 | 1 | 68
COCFD | 2 | 1 | 65 | 9.72 | 1 | 65
KE ECAM | 2 | 1 | 68 | 16.93 | 1 | 68
KE ECAM | 2 | 1 | 66 | 12.05 | 1 | 66
KE ECAM | 2 | 1 | 65 | 12.97 | 1 | 65
KE ECAM | 2 | 1 | 70 | 10.35 | 1 | 70
KE ECAM | 2 | 1 | 74 | 8.51 | 1 | 74
KE ECAM | 2 | 1 | 71 | 11.1 | 1 | 71
KE ECAM | 2 | 1 | 66 | 11.65 | 1 | 66
KE ECAM | 2 | 1 | 72 | 12.36 | 1 | 72
KE ECAM | 2 | 1 | 69 | 10.35 | 1 | 69
KE ECAM | 2 | 1 | 69 | 10.5 | 1 | 69
KE ECAM | 2 | 1 | 72 | 10.37 | 1 | 72
KE ECAM | 2 | 1 | 72 | 11.15 | 1 | 72
KE ECAM | 2 | 1 | 75 | 10.83 | 1 | 75
KE ECAM | 2 | 1 | 78 | 7.17 | 1 | 78
KE ECAM | 2 | 1 | 73 | 12.69 | 1 | 73
KE ECAM | 2 | 1 | 66 | 14.54 | 1 | 66
KE ECAM | 2 | 1 | 63 | 12.58 | 1 | 63
KE ECAM | 2 | 1 | 59 | 13.99 | 1 | 59
KE ECAM | 2 | 1 | 60 | 13.88 | 1 | 60
KE ECAM | 2 | 1 | 65 | 13.56 | 1 | 65
KE ECAM | 2 | 1 | 59 | 14.75 | 1 | 59
KE ECAM | 2 | 1 | 60 | 15.37 | 1 | 60
KE ECAM | 2 | 1 | 50 | 20.37 | 1 | 50
KE ECAM | 2 | 1 | 81 | 7.73 | 1 | 81
KE ECAM | 2 | 1 | 71 | 16.36 | 1 | 71
KE ECAM | 2 | 1 | 70 | 11.17 | 1 | 70
KE ECAM | 2 | 1 | 54 | 14.73 | 1 | 54
KE ECAM | 2 | 1 | 79 | 10.78 | 1 | 79
COCTV | 2 | 1 | 79 | 6.47 | 1 | 79
COCTV | 2 | 1 | 66 | 8.82 | 1 | 66
COCTV | 2 | 1 | 75 | 6.72 | 1 | 75
COCTV | 2 | 1 | 69 | 7.28 | 1 | 69
COCTV | 2 | 1 | 65 | 7.09 | 1 | 65
COCTV | 2 | 1 | 70 | 6.24 | 1 | 70
COCTV | 2 | 1 | 66 | 8.71 | 1 | 66
COCTV | 2 | 1 | 62 | 8.78 | 1 | 62
COCTV | 2 | 1 | 69 | 7.62 | 1 | 69
COCTV | 2 | 1 | 68 | 7.36 | 1 | 68
COCTV | 2 | 1 | 73 | 7.39 | 1 | 73
COCTV | 2 | 1 | 66 | 8.88 | 1 | 66
COCTV | 2 | 1 | 76 | 5.31 | 1 | 76
COCTV | 2 | 1 | 73 | 6.52 | 1 | 73
COCTV | 2 | 1 | 78 | 6.54 | 1 | 78
COCTV | 2 | 1 | 81 | 6.89 | 1 | 81
COCTV | 2 | 1 | 74 | 5.81 | 1 | 74
COCTV | 2 | 1 | 61 | 7.77 | 1 | 61
COCTV | 2 | 1 | 76 | 6.11 | 1 | 76
COCTV | 2 | 1 | 63 | 8.66 | 1 | 63
COCTV | 2 | 1 | 72 | 5.25 | 1 | 72
COCTV | 2 | 1 | 69 | 7.89 | 1 | 69
COCTV | 2 | 1 | 64 | 9.89 | 1 | 64
COCTV | 2 | 1 | 70 | 7.76 | 1 | 70
COCTV | 2 | 1 | 58 | 10.48 | 1 | 58
COCTV | 2 | 1 | 57 | 10.26 | 1 | 57
COCTV | 2 | 1 | 67 | 7.51 | 1 | 67
COCTV | 2 | 1 | 78 | 4.96 | 1 | 78
COCTV | 2 | 1 | 78 | 4.93 | 1 | 78
COCTV | 2 | 1 | 76 | 5.97 | 1 | 76
COCTV | 2 | 1 | 81 | 4.98 | 1 | 81
COCTV | 2 | 1 | 80 | 4.56 | 1 | 80
TCWP | 2 | 1 | 45 | 10.17 | 1 | 45
TCWP | 2 | 1 | 35 | 10.82 | 1 | 35
TCWP | 2 | 1 | 37 | 10.57 | 1 | 37
TCWP | 2 | 1 | 37 | 10.64 | 1 | 37
TCWP | 2 | 1 | 31 | 10.96 | 1 | 31
TCWP | 2 | 1 | 31 | 11.14 | 1 | 31
TCWP | 2 | 1 | 33 | 10.77 | 1 | 33
TCWP | 2 | 1 | 44 | 10.73 | 1 | 44
TCWP | 2 | 1 | 28 | 11.01 | 1 | 28
TCWP | 2 | 1 | 34 | 10.58 | 1 | 34
TCWP | 2 | 1 | 33 | 10.71 | 1 | 33
TCWP | 2 | 1 | 38 | 10.75 | 1 | 38
TCWP | 2 | 1 | 37 | 10.92 | 1 | 37
TCWP | 2 | 1 | 30 | 10.54 | 1 | 30
TCWP | 2 | 1 | 32 | 9.94 | 1 | 32
TCWP | 2 | 1 | 37 | 10.42 | 1 | 37
TCWP | 2 | 1 | 34 | 10.4 | 1 | 34
TCWP | 2 | 1 | 50 | 10.27 | 1 | 50
TCWP | 2 | 1 | 29 | 10.54 | 1 | 29
TCWP | 2 | 1 | 51 | 9.15 | 1 | 51
TCWP | 2 | 1 | 35 | 9.89 | 1 | 35
TCWP | 2 | 1 | 33 | 10.34 | 1 | 33
TCWP | 2 | 1 | 40 | 9.99 | 1 | 40
TCWP | 2 | 1 | 34 | 10.71 | 1 | 34
TCWP | 2 | 1 | 34 | 9.68 | 1 | 34
TCWP | 2 | 1 | 50 | 10.4 | 1 | 50
TCWP | 2 | 1 | 29 | 10.73 | 1 | 29
TCWP | 2 | 1 | 44 | 10.78 | 1 | 44
TCWP | 2 | 1 | 41 | 10.68 | 1 | 41
TCWP | 2 | 1 | 39 | 10.71 | 1 | 39
TCWP | 2 | 1 | 35 | 10.66 | 1 | 35
TCWP | 2 | 1 | 32 | 10.73 | 1 | 32
TCWP | 2 | 1 | 39 | 10.46 | 1 | 39
TCWP | 2 | 1 | 43 | 10.08 | 1 | 43
TCWP | 2 | 1 | 35 | 10.91 | 1 | 35
TCWP | 2 | 1 | 32 | 10.45 | 1 | 32
TCWP | 2 | 1 | 32 | 10.51 | 1 | 32
TCWP | 2 | 1 | 30 | 10.78 | 1 | 30
TCWP | 2 | 1 | 40 | 10.71 | 1 | 40
TCWP | 2 | 1 | 29 | 11.05 | 1 | 29
PCDC | 2 | 0 | 56 | 35.7 | 6 | 336
PCDC | 2 | 0 | 35 | 54.4 | 6 | 210
PCDC | 2 | 0 | 49 | 48 | 6 | 294
PCDC | 2 | 0 | 57 | 38.7 | 6 | 342
PCDC | 2 | 0 | 56 | 37.5 | 6 | 336
PCDC | 2 | 0 | 59 | 34.8 | 6 | 354
PCDC | 2 | 0 | 54 | 32.1 | 6 | 324
PCDC | 2 | 0 | 44 | 39.4 | 6 | 264
PCDC | 2 | 0 | 55 | 30.4 | 6 | 330
PCDC | 2 | 0 | 46 | 53.7 | 6 | 276
PCDC | 2 | 0 | 56 | 27.3 | 6 | 336
PCDC | 2 | 0 | 59 | 25.6 | 6 | 354
PCDC | 2 | 0 | 48 | 49 | 6 | 288
PCDC | 2 | 0 | 34 | 63 | 6 | 204
PCDC | 2 | 0 | 51 | 43.2 | 6 | 306
PCDC | 2 | 0 | 44 | 52.7 | 6 | 264
PCDC | 2 | 0 | 57 | 39.8 | 6 | 342
PCDC | 2 | 0 | 42 | 52.7 | 6 | 252
PCDC | 2 | 0 | 49 | 47.7 | 6 | 294
PCDC | 2 | 0 | 58 | 35.4 | 6 | 348
PCDC | 2 | 0 | 59 | 34.3 | 6 | 354
PCDC | 2 | 0 | 59 | 36.2 | 6 | 354
PCDC | 2 | 0 | 63 | 30.7 | 6 | 378
PCDC | 2 | 0 | 62 | 33.8 | 6 | 372
PCDC | 2 | 0 | 60 | 36.5 | 6 | 360
PCDC | 2 | 0 | 38 | 59.1 | 6 | 228
PCDC | 2 | 0 | 38 | 58.9 | 6 | 228
PCDC | 2 | 0 | 37 | 48.4 | 6 | 222
PCDC | 2 | 0 | 48 | 49.1 | 6 | 288
PCDC | 2 | 0 | 44 | 44.4 | 6 | 264
PCDC | 2 | 0 | 34 | 62.4 | 6 | 204
PCDC | 2 | 0 | 45 | 42.2 | 6 | 270
PCDC | 2 | 0 | 57 | 37.1 | 6 | 342
PCDC | 2 | 0 | 64 | 31.3 | 6 | 384
PCDC | 2 | 0 | 57 | 35.6 | 6 | 342
PCDC | 2 | 0 | 44 | 51.3 | 6 | 264
PCDC | 2 | 0 | 31 | 72 | 6 | 186
PCDC | 2 | 0 | 48 | 51.3 | 6 | 288
PCDC | 2 | 0 | 46 | 50.6 | 6 | 276
PCDC | 2 | 0 | 43 | 51 | 6 | 258
PCDC | 2 | 0 | 45 | 50.5 | 6 | 270
PCDC | 2 | 0 | 40 | 59.6 | 6 | 240
PCDC | 2 | 0 | 58 | 36.2 | 6 | 348
PCDC | 2 | 0 | 41 | 57.7 | 6 | 246
PCDC | 2 | 0 | 61 | 33.8 | 6 | 366
PCDC | 2 | 0 | 43 | 53.6 | 6 | 258
PCDC | 2 | 0 | 48 | 48.5 | 6 | 288
PCDC | 2 | 0 | 43 | 45.5 | 6 | 258
PCDC | 2 | 0 | 54 | 39.6 | 6 | 324
PCDC | 2 | 0 | 61 | 32.2 | 6 | 366
PCDC | 2 | 0 | 57 | 37 | 6 | 342
COMW | 2 | 1 | 36 | 18.4 | 1 | 36
COMW | 2 | 1 | 45 | 16.9 | 1 | 45
COMW | 2 | 1 | 52 | 15.3 | 1 | 52
COMW | 2 | 1 | 53 | 15.9 | 1 | 53
COMW | 2 | 1 | 53 | 14.2 | 1 | 53
COMW | 2 | 1 | 50 | 15.1 | 1 | 50
COMW | 2 | 1 | 43 | 15.3 | 1 | 43
COMW | 2 | 1 | 29 | 16.9 | 1 | 29
COMW | 2 | 1 | 40 | 14 | 1 | 40
COMW | 2 | 1 | 44 | 15.6 | 1 | 44
COMW | 2 | 1 | 35 | 16.9 | 1 | 35
COMW | 2 | 1 | 37 | 18.1 | 1 | 37
COMW | 2 | 1 | 32 | 15.8 | 1 | 32
COMW | 2 | 1 | 31 | 16.9 | 1 | 31
COMW | 2 | 1 | 32 | 17.1 | 1 | 32
COMW | 2 | 1 | 35 | 16.6 | 1 | 35
COMW | 2 | 1 | 40 | 16.6 | 1 | 40
COMW | 2 | 1 | 43 | 15.2 | 1 | 43
COMW | 2 | 1 | 43 | 16.2 | 1 | 43
COMW | 2 | 1 | 42 | 14.7 | 1 | 42
COMW | 2 | 1 | 46 | 16.3 | 1 | 46
COMW | 2 | 1 | 34 | 16.5 | 1 | 34
COMKR | 2 | 1 | 40 | 10.9 | 1 | 40
COMKR | 2 | 1 | 43 | 11.1 | 1 | 43
COMKR | 2 | 1 | 50 | 8.7 | 1 | 50
COMKR | 2 | 1 | 53 | 9.3 | 1 | 53
COMKR | 2 | 1 | 53 | 10.8 | 1 | 53
COMKR | 2 | 1 | 52 | 10.6 | 1 | 52
COMKR | 2 | 1 | 35 | 11.9 | 1 | 35
COMKR | 2 | 1 | 36 | 12.5 | 1 | 36
COMKR | 2 | 1 | 32 | 12.8 | 1 | 32
COMKR | 2 | 1 | 45 | 12.7 | 1 | 45
COMKR | 2 | 1 | 29 | 12.8 | 1 | 29
COMKR | 2 | 1 | 34 | 12.3 | 1 | 34
COMKR | 2 | 1 | 46 | 11.8 | 1 | 46
COMKR | 2 | 1 | 37 | 11.4 | 1 | 37
COMKR | 2 | 1 | 32 | 14.7 | 1 | 32
COMKR | 2 | 1 | 31 | 13.4 | 1 | 31
COMKR | 2 | 1 | 35 | 12.9 | 1 | 35
COMKR | 2 | 1 | 43 | 10.6 | 1 | 43
COMKR | 2 | 1 | 43 | 11.7 | 1 | 43
COMKR | 2 | 1 | 42 | 11.2 | 1 | 42
COMKR | 2 | 1 | 44 | 10.1 | 1 | 44
COMKR | 2 | 1 | 40 | 13.5 | 1 | 40
BLDG210 | 2 | 0 | 66 | 22.72 | 3 | 198
BLDG210 | 2 | 0 | 68 | 22.83 | 3 | 204
BLDG210 | 2 | 0 | 63 | 25.24 | 3 | 189
BLDG210 | 2 | 0 | 68 | 24.21 | 3 | 204
BLDG210 | 2 | 0 | 70 | 21.78 | 3 | 210
BLDG210 | 2 | 0 | 61 | 26.47 | 3 | 183
BLDG210 | 2 | 0 | 64 | 25.63 | 3 | 192
BLDG210 | 2 | 0 | 66 | 24.01 | 3 | 198
BLDG210 | 2 | 0 | 74 | 25.43 | 3 | 222
BLDG210 | 2 | 0 | 67 | 22.81 | 3 | 201
BLDG210 | 2 | 0 | 77 | 14.89 | 3 | 231
BLDG210 | 2 | 0 | 59 | 26.25 | 3 | 177
BLDG210 | 2 | 0 | 60 | 22.05 | 3 | 180
BLDG210 | 2 | 0 | 69 | 21.65 | 3 | 207
BLDG210 | 2 | 0 | 80 | 16.75 | 3 | 240
BLDG210 | 2 | 0 | 77 | 19.08 | 3 | 231
BLDG210 | 2 | 0 | 72 | 20.72 | 3 | 216
BLDG210 | 2 | 0 | 63 | 27.04 | 3 | 189
BLDG210 | 2 | 0 | 70 | 22.17 | 3 | 210
BLDG210 | 2 | 0 | 60 | 28.55 | 3 | 180
BLDG210 | 2 | 0 | 63 | 27.9 | 3 | 189
BLDG210 | 2 | 0 | 55 | 31.26 | 3 | 165
BLDG210 | 2 | 0 | 53 | 32.4 | 3 | 159
BLDG210 | 2 | 0 | 48 | 33.31 | 3 | 144
BLDG210 | 2 | 0 | 72 | 17.54 | 3 | 216
BLDG210 | 2 | 0 | 53 | 25.38 | 3 | 159
BLDG210 | 2 | 0 | 64 | 25.29 | 3 | 192
BLDG210 | 2 | 0 | 65 | 24.17 | 3 | 195

## T1 Size3 (hidden)
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | New Rated Heater Size kW | Heater Size X Temp
COCWWTP | 3 | 0 | 81 | 32.05 | 6 | 486 | SUMMARY OUTPUT
COCWWTP | 3 | 0 | 78 | 31.93 | 6 | 468
COCWWTP | 3 | 0 | 79 | 29.67 | 6 | 474 | Regression Statistics
COCWWTP | 3 | 0 | 76 | 28.4 | 6 | 456 | Multiple R | 0.96003
COCWWTP | 3 | 0 | 76 | 30.83 | 6 | 456 | R Square | 0.92165
COCWWTP | 3 | 0 | 62 | 40.46 | 6 | 372 | Adjusted R Square | 0.92025
COCWWTP | 3 | 0 | 54 | 44.24 | 6 | 324 | Standard Error | 3.8637
COCWWTP | 3 | 0 | 67 | 34.75 | 6 | 402 | Observations | 115
COCWWTP | 3 | 0 | 69 | 38.29 | 6 | 414
COCWWTP | 3 | 0 | 68 | 35.65 | 6 | 408 | ANOVA
COCWWTP | 3 | 0 | 65 | 44.66 | 6 | 390 |  | df | SS | MS | F | Significance F
COCWWTP | 3 | 0 | 54 | 55.77 | 6 | 324 | Regression | 2 | 19668.2901 | 9834.145 | 658.7702 | 1.162e-62
COCWWTP | 3 | 0 | 51 | 55.72 | 6 | 306 | Residual | 112 | 1671.9401 | 14.928
COCWWTP | 3 | 0 | 52 | 52.55 | 6 | 312 | Total | 114 | 21340.2302
COCWWTP | 3 | 0 | 60 | 46.88 | 6 | 360
COCWWTP | 3 | 0 | 60 | 42.96 | 6 | 360 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
COCWWTP | 3 | 0 | 50 | 60.42 | 6 | 300 | Intercept | 10.2591 | 0.80485 | 12.7465 | 1.5412e-23 | 8.6643 | 11.8538 | 8.6643 | 11.8538
COCWWTP | 3 | 0 | 65 | 38.29 | 6 | 390 | X Variable 1 | 16.6877 | 0.56831 | 29.3639 | 1.9647e-54 | 15.5616 | 17.8137 | 15.5616 | 17.8137
COCWWTP | 3 | 0 | 64 | 47.7 | 6 | 384 | X Variable 2 | -0.17943 | 0.008452 | -21.2292 | 4.6265e-41 | -0.19618 | -0.16268 | -0.19618 | -0.16268
COCWWTP | 3 | 0 | 65 | 38.9 | 6 | 390
COCWWTP | 3 | 0 | 56 | 50.26 | 6 | 336
COCWWTP | 3 | 0 | 54 | 51.97 | 6 | 324
COCWWTP | 3 | 0 | 54 | 49.76 | 6 | 324
COCWWTP | 3 | 0 | 49 | 61.9 | 6 | 294
COCWWTP | 3 | 0 | 54 | 52.64 | 6 | 324
COCWWTP | 3 | 0 | 56 | 52.56 | 6 | 336
COCWWTP | 3 | 0 | 48 | 60.48 | 6 | 288
COCWWTP | 3 | 0 | 43 | 66.12 | 6 | 258
COCWWTP | 3 | 0 | 63 | 43.44 | 6 | 378
COCWWTP | 3 | 0 | 70 | 35.71 | 6 | 420
COCWWTP | 3 | 0 | 62 | 43.08 | 6 | 372
COCWWTP | 3 | 0 | 78 | 25.51 | 6 | 468
COCWWTP | 3 | 0 | 68 | 35.74 | 6 | 408
COCWWTP | 3 | 0 | 66 | 41.92 | 6 | 396
COCWWTP | 3 | 0 | 66 | 37.87 | 6 | 396
COCWWTP | 3 | 0 | 72 | 30.53 | 6 | 432
COCWWTP | 3 | 0 | 69 | 32.6 | 6 | 414
COCWWTP | 3 | 0 | 75 | 32.73 | 6 | 450
COCWWTP | 3 | 0 | 69 | 37.08 | 6 | 414
COCWWTP | 3 | 0 | 66 | 39.5 | 6 | 396
COCWWTP | 3 | 0 | 51 | 55.2 | 6 | 306
COCWWTP | 3 | 0 | 78 | 26.82 | 6 | 468
COCWWTP | 3 | 0 | 81 | 26.05 | 6 | 486
COCWWTP | 3 | 0 | 76 | 27.53 | 6 | 456
COCWWTP | 3 | 0 | 69 | 35.64 | 6 | 414
COCWWTP | 3 | 0 | 73 | 30.06 | 6 | 438
COCWWTP | 3 | 0 | 67 | 36.65 | 6 | 402
COCWWTP | 3 | 0 | 61 | 44.7 | 6 | 366
COCWWTP | 3 | 0 | 58 | 48.21 | 6 | 348
COCWWTP | 3 | 0 | 63 | 44.13 | 6 | 378
COCWWTP | 3 | 0 | 65 | 36.59 | 6 | 390
COCWWTP | 3 | 0 | 58 | 33.82 | 6 | 348
COCWWTP | 3 | 0 | 57 | 40.95 | 6 | 342
COCWWTP | 3 | 0 | 80 | 16.14 | 6 | 480
COCWWTP | 3 | 0 | 70 | 33.86 | 6 | 420
COCWWTP | 3 | 0 | 73 | 25.06 | 6 | 438
COCWWTP | 3 | 0 | 74 | 29.67 | 6 | 444
COCWWTP | 3 | 0 | 57 | 45.79 | 6 | 342
COCWWTP | 3 | 0 | 49 | 57.41 | 6 | 294
BayView | 3 | 1 | 80 | 8.74 | 1.5 | 120
BayView | 3 | 1 | 68 | 12.23 | 1.5 | 102
BayView | 3 | 1 | 60 | 14.08 | 1.5 | 90
BayView | 3 | 1 | 65 | 15.18 | 1.5 | 97.5
BayView | 3 | 1 | 66 | 15.69 | 1.5 | 99
BayView | 3 | 1 | 64 | 15.84 | 1.5 | 96
BayView | 3 | 1 | 61 | 16.67 | 1.5 | 91.5
BayView | 3 | 1 | 70 | 15.07 | 1.5 | 105
BayView | 3 | 1 | 72 | 13.24 | 1.5 | 108
BayView | 3 | 1 | 63 | 15.04 | 1.5 | 94.5
BayView | 3 | 1 | 68 | 14.34 | 1.5 | 102
BayView | 3 | 1 | 66 | 14.26 | 1.5 | 99
BayView | 3 | 1 | 67 | 15.14 | 1.5 | 100.5
BayView | 3 | 1 | 69 | 13.98 | 1.5 | 103.5
BayView | 3 | 1 | 63 | 16.05 | 1.5 | 94.5
BayView | 3 | 1 | 74 | 11.75 | 1.5 | 111
BayView | 3 | 1 | 48 | 21.14 | 1.5 | 72
BayView | 3 | 1 | 77 | 11.9 | 1.5 | 115.5
BayView | 3 | 1 | 55 | 18.48 | 1.5 | 82.5
BayView | 3 | 1 | 53 | 18.99 | 1.5 | 79.5
BayView | 3 | 1 | 59 | 16.45 | 1.5 | 88.5
BayView | 3 | 1 | 60 | 15.65 | 1.5 | 90
BayView | 3 | 1 | 64 | 14.88 | 1.5 | 96
BayView | 3 | 1 | 70 | 14.07 | 1.5 | 105
BayView | 3 | 1 | 63 | 15.02 | 1.5 | 94.5
BayView | 3 | 1 | 72 | 13.41 | 1.5 | 108
BayView | 3 | 1 | 77 | 12.35 | 1.5 | 115.5
BayView | 3 | 1 | 53 | 18.37 | 1.5 | 79.5
BNS GEN | 3 | 1 | 68 | 19.59 | 2.5 | 170
BNS GEN | 3 | 1 | 77 | 18.89 | 2.5 | 192.5
BNS GEN | 3 | 1 | 74 | 18.44 | 2.5 | 185
BNS GEN | 3 | 1 | 80 | 13.56 | 2.5 | 200
BNS GEN | 3 | 1 | 60 | 24.43 | 2.5 | 150
BNS GEN | 3 | 1 | 65 | 25.28 | 2.5 | 162.5
BNS GEN | 3 | 1 | 66 | 27.62 | 2.5 | 165
BNS GEN | 3 | 1 | 64 | 26.73 | 2.5 | 160
BNS GEN | 3 | 1 | 61 | 28.58 | 2.5 | 152.5
BNS GEN | 3 | 1 | 70 | 24.45 | 2.5 | 175
BNS GEN | 3 | 1 | 72 | 23.16 | 2.5 | 180
BNS GEN | 3 | 1 | 63 | 25.76 | 2.5 | 157.5
BNS GEN | 3 | 1 | 68 | 25.53 | 2.5 | 170
BNS GEN | 3 | 1 | 66 | 26.12 | 2.5 | 165
BNS GEN | 3 | 1 | 63 | 30.02 | 2.5 | 157.5
BNS GEN | 3 | 1 | 67 | 24.42 | 2.5 | 167.5
BNS GEN | 3 | 1 | 77 | 20.16 | 2.5 | 192.5
BNS GEN | 3 | 1 | 70 | 24.19 | 2.5 | 175
BNS GEN | 3 | 1 | 64 | 27.54 | 2.5 | 160
BNS GEN | 3 | 1 | 59 | 30.4 | 2.5 | 147.5
BNS GEN | 3 | 1 | 63 | 28.78 | 2.5 | 157.5
BNS GEN | 3 | 1 | 55 | 35 | 2.5 | 137.5
BNS GEN | 3 | 1 | 53 | 36.17 | 2.5 | 132.5
BNS GEN | 3 | 1 | 48 | 40.62 | 2.5 | 120
BNS GEN | 3 | 1 | 53 | 36.65 | 2.5 | 132.5
BNS GEN | 3 | 1 | 69 | 22.37 | 2.5 | 172.5
BNS GEN | 3 | 1 | 72 | 23.45 | 2.5 | 180
BNS GEN | 3 | 1 | 60 | 28.74 | 2.5 | 150

## T1 Size4 (hidden)
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | New Rated Heater Size kW | Heater Size X Temp
NQ | 4 | 1 | 66 | 68.56 | 10 | 660 | SUMMARY OUTPUT
NQ | 4 | 1 | 45 | 109.25 | 10 | 450
NQ | 4 | 1 | 45 | 112.09 | 10 | 450 | Regression Statistics
NQ | 4 | 1 | 58 | 80.08 | 10 | 580 | Multiple R | 0.94496
NQ | 4 | 1 | 51 | 100.12 | 10 | 510 | R Square | 0.89295
NQ | 4 | 1 | 56 | 81.13 | 10 | 560 | Adjusted R Square | 0.88716
NQ | 4 | 1 | 47 | 108.9 | 10 | 470 | Standard Error | 6.7103
NQ | 4 | 1 | 48 | 103.73 | 10 | 480 | Observations | 40
NQ | 4 | 1 | 52 | 90.78 | 10 | 520
NQ | 4 | 1 | 53 | 91.16 | 10 | 530 | ANOVA
NQ | 4 | 1 | 55 | 91.45 | 10 | 550 |  | df | SS | MS | F | Significance F
NQ | 4 | 1 | 43 | 128.86 | 10 | 430 | Regression | 2 | 13896.9214 | 6948.4607 | 154.3119 | 1.1157e-18
NQ | 4 | 1 | 49 | 103.44 | 10 | 490 | Residual | 37 | 1666.0608 | 45.0287
NQ | 4 | 1 | 52 | 87.74 | 10 | 520 | Total | 39 | 15562.9822
NQ | 4 | 1 | 60 | 70.99 | 10 | 600
NQ | 4 | 1 | 46 | 107.2 | 10 | 460 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
NQ | 4 | 1 | 33 | 135.86 | 10 | 330 | Intercept | 229.5194 | 6.8715 | 33.4016 | 3.1035e-29 | 215.5964 | 243.4424 | 215.5964 | 243.4424
NQ | 4 | 1 | 53 | 93.8 | 10 | 530 | X Variable 1 | 0 | 0 | 65535 | #NUM! | 0 | 0 | 0 | 0
NQ | 4 | 1 | 52 | 93.36 | 10 | 520 | X Variable 2 | -0.25769 | 0.014671 | -17.5644 | #NUM! | -0.28742 | -0.22797 | -0.28742 | -0.22797
NQ | 4 | 1 | 55 | 78.49 | 10 | 550
NQ | 4 | 1 | 43 | 124.67 | 10 | 430
NQ | 4 | 1 | 49 | 102.32 | 10 | 490 | SUMMARY OUTPUT
NQ | 4 | 1 | 41 | 132.18 | 10 | 410
NQ | 4 | 1 | 46 | 125.94 | 10 | 460 | Regression Statistics
NQ | 4 | 1 | 40 | 138.28 | 10 | 400 | Multiple R | 0.94478
NQ | 4 | 1 | 36 | 132.52 | 10 | 360 | R Square | 0.89262
NQ | 4 | 1 | 37 | 142.15 | 10 | 370 | Adjusted R Square | 0.88979
NQ | 4 | 1 | 37 | 124.63 | 10 | 370 | Standard Error | 6.6317
NQ | 4 | 1 | 39 | 123 | 10 | 390 | Observations | 40
NQ | 4 | 1 | 46 | 107.66 | 10 | 460
NQ | 4 | 1 | 47 | 105.97 | 10 | 470 | ANOVA
NQ | 4 | 1 | 37 | 140.25 | 10 | 370 |  | df | SS | MS | F | Significance F
NQ | 4 | 1 | 44 | 124.86 | 10 | 440 | Regression | 1 | 13891.7706 | 13891.7706 | 315.871 | 5.2529e-20
NQ | 4 | 1 | 39 | 132.78 | 10 | 390 | Residual | 38 | 1671.2116 | 43.9793
NQ | 4 | 1 | 37 | 129.63 | 10 | 370 | Total | 39 | 15562.9822
NQ | 4 | 1 | 41 | 121.86 | 10 | 410
NQ | 4 | 1 | 44 | 109.08 | 10 | 440 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
NQ | 4 | 1 | 44 | 116.95 | 10 | 440 | Intercept | 229.5194 | 6.791 | 33.7977 | 5.8085e-30 | 215.7718 | 243.267 | 215.7718 | 243.267
NQ | 4 | 1 | 44 | 126.81 | 10 | 440 | X Variable 1 | -2.5769 | 0.14499 | -17.7728 | 5.2529e-20 | -2.8704 | -2.2834 | -2.8704 | -2.2834
NQ | 4 | 1 | 41 | 112.37 | 10 | 410