## Cost Summary
Updated Cost from HotStart
Capacity of the Generator | Base Cost (Thermosiphon Heater) ($) | Base Case Labor Cost | Total Base Cost | Measure Cost (Forced Circulation Heater) ($) | Measure Labor Cost | Total Measure Cost | Incremental Measure Cost ($)
37-199 kW | 201.25 | 208.8261 | 410.0761 | 700 | 208.8261 | 908.8261 | 498.75
200-799 kW | 717.3485 | 208.8261 | 926.1746 | 804.86 | 208.8261 | 1013.6861 | 87.5115
800-1099 kW | #REF! | 208.8261 | #REF! | #DIV/0! | 208.8261 | #DIV/0! | #DIV/0!
1100-2500 kW | #REF! | 208.8261 | #REF! | #DIV/0! | 208.8261 | #DIV/0! | #DIV/0!
Cost Calculation Methodology
The updated base and measure equipment costs were obtained in 2020 from HotStart®, a major equipment manufacturer for engine heaters who supply components to generator companies like Quinn, CAT and Cummins. The following is the step by step methodology used to calculate the baseline and measure costs from the data provided by HotStart®. • HotStart® representative provided a list of recommended thermosiphon and forced circulation heater models corresponding to engine displacement in liters ranging from 2.4 L and 76.3 L. • These engine displacements in liters are converted to generator capacities in kW using manufacturer websites like Generac and Kohler. The range of generator capacities after the conversion is 30 kW to 2500 kW. These conversions were reviewed with the HotStart® representative. • The engine heaters are designed for different voltages, phases, frequencies and features based on the application. Some variations in features include with-thermostats, adjustable thermostats and without thermostats. A detailed listing of all the different specifications is provided in the References tab of the Cost Analysis attachment. • Pricing information for a variety of HotStart® thermosiphon models was provided. However, for the forced circulation heaters, cost data was available for a few recommended models listed below - Backup Generator 40 to 600 kW – Single phase and 120 Volts Backup Generator 750 to 2000 kW – Single phase and 208 Volts Backup Generator 2500 kW – Three phase and 208 Volts • To provide an accurate cost analysis, the above forced circulation heater models were compared with the thermosiphon counterparts having the same features. • The thermosiphon heaters for generators above 350 kW are assumed to be the with-power cord and without-thermostat models. • The average price for the base and measure equipment was calculated for the (4) categories of the generator capacities identified for measure savings. • Per HotStart representative, there are few if not none thermosiphon (baseline) models available for higher capacity generators.Typically, the customers would use a multiple lower capacity thermosiphon heaters for high capacity generators to maintain temperature or for redunancy in case of failure. This approach resulted in a negative IMC for the larger generator sizes and these measures were removed from the workpaper. • HotStart® representative was not aware of the concept of properly sized and undersized thermosiphon heaters as defined in the calculation methodology. It is assumed that the base case cost is the same for properly sized and undersized. There is no under sizing of the forced circulating heater. Hence, measure cost will always be properly sized circulating block heater. The labor cost is from RSMean Data Year 2020 Quarter 3 Union Labar rate for Electrician ($91.35). This rate was coupled with the labor hours (2.286) for installing a 2 HP size 00 motor, Magnetic FVNR with enclosures and heaters (Line Number 262419400080) - RS Means 2020 Q3. Based on discussion with HotStart®, installing the thermosiphon and circulating block heaters typically takes couple of hours and there is no variation in the installation times.

## Heater to Price Mapping
Thermosiphon Heater |  |  |  | Forced Circulation Heater
Capacity of Generator (kW) | List of Prices for Heater ($) | Thermosiphon Heater Model No. | Phase and Volts | Capacity of Generator (kW) | List of Prices for Heater ($) | Forced Circulation Heater Model No. | Phase and Volts
40, 50, 60 & 80 | 201.25 | TPS101GT8-000 | 1 & 120 | 40, 50, 60 & 80 | 700 | CTM10110-N00 | 1 & 120
40, 50, 60 & 80 | 201.25 | TPS101GT10-000 | 1 & 120 | 200, 250 & 300 | 700 | CTM15110-N00 | 1 & 120
40, 50, 60 & 80 | 201.25 | TPS101GT12-000 | 1 & 120 | 300, 350 & 400 | 700 | CTM25110-N00 | 1 & 120
100, 130, 150 & 175 | 201.25 | TPS151GT8-000 | 1 & 120 | 500 | 700 | CTM25110-N00 | 1 & 120
100, 130, 150 & 175 | 201.25 | TPS151GT10-000 | 1 & 120 | 600 | 700 | CTM25110-N00 | 1 & 120
100, 130, 150 & 175 | 201.25 | TPS151GT12-000 | 1 & 120 | 750 | 1224.3 | CSM10608-000 | 1 & 208
200, 250 & 300 | 209.65 | TPS181GT8-000 | 1 & 120
200, 250 & 300 | 209.65 | TPS181GT10-000 | 1 & 120
200, 250 & 300 | 209.65 | TPS181GT12-000 | 1 & 120
200, 250 & 300 | 628.84 | SB120110-200 | 1 & 120
200, 250 & 300 | 598.75 | CB120110-200 | 1 & 120
300, 350 & 400 | 598.75 | CB125110-200 | 1 & 120
300, 350 & 400 | 628.84 | SB122110-200 | 1 & 120
500 | 769.14 | CL130810-200 | 1 & 208
500 | 791.21 | SL130810-200 | 1 & 208
600 | 769.14 | CL140810-200 | 1 & 208
600 | 791.21 | SL140810-200 | 1 & 208
750 | 1538.28 | CL130810-200 x 2 | 1 & 208 | 1) The different model numbers for each wattage of heater has been obtained from Hotstart product catalog and heater spec sheets. The pdf files have been attached in the next tab, for any additional spec sheets please refer to https://www.hotstart.com/en/home/resources/catalogs/.
750 | 1582.42 | SL130810-200 x 2 | 1 & 208

## Generator kW to Heater Mapping
| Engine kW4 | Engine Manufacturer | Engine Model | Engine Displacement | Recommended Forced Circulation heater2 | Thermosiphon Option2,5 | Other Thermosiphon Option 5
| 2500 | Detroit Diesel/MTU | 16V4000G83L | 76.3L | 12kW CSM | - | -
| 2000 | Mitsubishi | S16R-Y2PTAW2-1 | 64.5L | 9kW CSM | - | -
| 1500 | Mitsubishi | N/A | 65.4L | 9kW CSM | - | -
| 1250 | Mitsubishi | S12R-Y2PTAW-1 | 49.0L | 6kW CSM or CKM | Two 5kW CL/SL1 | -
| 1000 | Mitsubishi | N/A | 37.1L | 6kW CSM or 5KW CKM | Two 4kW CL/SL1 | -
| 900 | Mitsubishi | N/A | 37.1L | 6kW CSM or 5KW CKM | Two 4kW CL/SL1 | -
| 800 | Mitsubishi | N/A | 33.9L | 6kW CSM or 5KW CKM | Two 3Kw CL/SL1 | -
| 750 | Mitsubishi | N/A | 33.9L | 6kW CSM or 5KW CKM | Two 3Kw CL/SL1 | -
| 600 | Perkins | N/A | 18.1L | 3kW CSM or 2.5kW CTM or 3kW CKM | 4kW CL/SL | -
| 500 | Perkins | N/A | 15.2L | 3kW CSM or 2.5kW CTM or 3kW CKM | 3kW CL/SL | -
| 400 | Perkins | N/A | 12.5L | 2.5kW CTM | 2.5kW CB/SB | 2.5kW CB/SB
| 350 | Iveco/FPT | N/A | 12.9L | 2.5kW CTM | 2.5kW CB/SB | 2.5kW CB/SB
| 300 | Iveco/FPT | N/A | 10.3L | 1.5kW CTM | 1.8kW 2kW TPS | 2.5kW CB/SB
| 250 | Iveco/FPT | N/A | 8.7L | 1.5kW CTM | 1.8kW 2kW TPS | 2kW CB/SB
| 200 | Iveco/FPT | N/A | 8.7L | 1.5kW CTM | 1.8kW 2kW TPS | 2kW CB/SB
| 175 | Iveco/FPT | N/A | 6.7L | 1kW CTM | 1.5kW TPS | -
| 150 | Iveco/FPT | N/A | 6.7L | 1kW CTM | 1.5kW TPS | -
| 130 | Iveco/FPT | N/A | 6.7L | 1kW CTM | 1.5kW TPS | -
| 100 | Iveco/FPT | N/A | 6.7L | 1kW CTM | 1.5kW TPS | -
| 80 | Iveco/FPT | N/A | 4.5L | 1kW CTM | 1000W TPS | -
| 60 | Iveco/FPT | N/A | 4.5L | 1kW CTM | 1000W TPS | -
| 50 | Generac | N/A | 3.4L | 1kW CTM | 1000W TPS | -
| 40 | Generac | N/A | 3.4L | 1kW CTM | 1000W TPS | -
| 35 | Generac | N/A | 3.4L | 1kW CTM | 1000W TPS | -
| 30 | Generac | N/A | 2.4L | 1kW CTM | 500W TPS | -
1) Engines with capacities between 33.9L and 76.3L may require two thermosiphon heaters, one on each bank. The cost considered in this analysis is for a per-unit generator basis as per the workpaper. 2) The above recommendations were provided by a Sales Engineer from HotStart. 3) The phase and voltage requirements for each application must be verified. The prices considered here for each heater suggestion is for Single Phase and 120/208 Volts models. 4) The mapping of Liters to Engine kW is from engine manufacturer websites like Generac and Kohler. 5) The CL/SL and CB/SB forced circulation heater models considered here are without thermostats.

## RS Means Labor Cost
The labor cost is from RSMean Data Year 2020 Quarter 3 Union Labar rate for Electrician ($91.35). This rate was coupled with the labor hours (2.286) for installing a 2 HP size 00 motor, Magnetic FVNR with enclosures and heaters (Line Number 262419400080) - RS Means 2020 Q3. Based on discussion with HotStart®, installing the thermosiphon and circulating block heaters typically takes couple of hours and there is no variation in the installation times.
| Labor Rate for Electrician | 91.35
| Est. Labor Hours | 2.286
| Total Baseline/Measure Labor Cost | 208.8261