CPUC Comments on SWRE005-01 Heat Pump Pool Heater, Residential, Fuel Substitution

Lead PA: SCE

Workpaper Submittal Date: 4/5/2021 (Resubmission 07/02/2021)

| CPUC Comment | PA Response |
| --- | --- |
| Why is the output capacity of heat pumps only 110 kBtu? Looking at the baseline demand calculations, it seems the baseline boiler demand can go up to 246,000 Btu/hr. How would a 110,000 Btu/hr output capacity heat pump satisfy this demand? Also, it seems the savings is comparing gas consumption for meeting 246,000 Btu/hr boiler demand with electric consumption of a 110,000 Btu/hr heat pump. | In the calculations, the “Measure Heat Pump Demand (Btu/hr)” and “Baseline Boiler Demand (Btu/hr)” are the heat outputs of the equipment. We have updated the column headers to reflect “output” instead of “demand” for clarity. Furthermore, to better align with how each type of equipment is rated in the market, the “Inputs” tab use input capacity for the gas heater but use output capacity for the HP pool heater. For all hours in which the pool is expected to be “available,” the tool caps the equipment output capacity at the rated HP output capacity and calculated gas heater output capacity. Since the HP pool heater has a lower capacity, it will take more operating hours to reach and maintain the desired pool temperature than the gas pool heater. See next page for calculations on difference in hours for both base case and measure case technologies. As discussed in the workpaper document, natural gas pool heaters are generally oversized for the pool that they are serving, whereas HP pool heaters are usually “right” sized or sized closer to specific load requirements. This calculation does assume that the HP pool heater is of a lower (or right sized) capacity than the base case gas heater. CPUC response 5/12: There is one instance (circled in red below) where the thermal demand is greater than gas heater output capacity. The formulae in the calculator caps the baseline boiler output at maximum rated gas heater output instead of using what the actual thermal load is. The therms savings for that instance compares max gas heater output (240kBtu/hr) with max heat pump output (110kBtu/hr) to calculate the therms savings. Shouldn’t the savings be based on actual load rather than equipment size? Similarly, there is an instance where baseline boiler output is 236.5 kBtu/hr (not capped at maximum rated gas heater output), but the measure case output is only 110 kbtu/hr (measure case output is greater than maximum rated heat pump output. Therefore, the formulae in the calculator caps output at maximum rated heat pump output). Wouldn’t this mean that the measure case output is lower for the same thermal demand because of the cap in the formulae? SCE response to comment from 5/12: The measure case hourly output is the lower than the base case. However, the total annual output of the heater is the same because it must meet the same pool heating load. The measure case pool heater must operate more hours in order to provide the same total heat output as the base case heater. Both the measure and base case heater’s output is the minimum of the required pool heating load and their specific equipment capacities. Notes from 6/24/21 call with CPUC, SCE, and TRC: CPUC is comfortable with how the tool calculates the outputs on an hourly basis. However, SCE/TRC will review the potential interactive effects of additional pool pump operation due to smaller capacity HP pool heaters and either update calculations or add comments to the workpaper document. SCE will include the attached comment sheet to the workpaper submission package. Follow-ups to Meeting on 6/24/21 SCE’s consultant reviewed minimum flow requirements for gas and HP pool heaters and found that the flow varies between type, model, and capacity. However, the average minimum flow found was roughly 30 gpm. From SWRE002 VS Pool Pump workpaper, the estimated minimum flow for both the SFm and MFm pools are 18 gpm and 32 gpm, respectively. Based on this, minimum flow requirements for the heaters are not really expected to impact the MFm pool pump operation. However, to be conservative, we investigated the pool pump power impacts of longer operations for both building types. We exported the base and measure hourly heat pump outputs (in Btu) from the Pool Heater calculator for SFm and MFm for CZ01. CZ01 was selected because it requires the most heating and should show the biggest different in heating hours between base and measure. For each we normalized the Btu outputs by the full load capacity to get a percent output per hour. Since the pool heaters are assumed to operate only at full load, this effectively represents the percent of each hour that each is operating. Next, the difference between the percent operating between the base and measure case was taken for each hour individually to see the additional run time for the measure case. The additional run time was totaled up to find an additional 31.61 hours and 26.60 hours for SFm and MFm, respectively. To estimate the power implications of this extended run time, we used the Power vs Flow regression curves found in SWRE002, which were obtained using analysis on the CEC database of VS pool pumps. We applied the minimum flow assumptions of 30 gpm to find the assumed pool pump power based on the regression curves. Similarly the power associated with the minimum flow assumed by SWRE002 was found. Then we multiplied the difference in power between the previous minimum flow from SWRE002 and the new heat pump minimum flow by the additional operating hours required by the measure case pool heater to find the additional pool pump energy required due to longer run times of the HP pool heater. We provided calculations for all three CEC curves (A, B, C) to show the range of values that could be used. Following the same logic as SWRE002, a flow of 30 gpm could use either Curve A or Curve B. This analysis assumes that the there would be some sort of automatic safety interlock of the pool pump to increase flow to meet the minimum heater flow when required and reduce back down afterward. It also is only looking at run time extended over the natural gas heater run time, not total run time. The findings show a maximum of a 17.51 kWh and minimum of 2.77 kWh penalty on the pool pump operation for SFm. This represents <1% of the total kWh impact for CZ01, and 1.26% of total kWh impact for the average kWh of all CZs. As discussed above, the higher minimum flow of the MFm pools means that there should not be an impact to the pool pump due to longer runtimes since the pool heater minimum flow should be roughly the same or less than the minimum flow of the pool heater. Based on these findings, we suggest that the current analysis not be altered to include the pool pump operations. Please refer to the Pool Heater vs Pump Comparison Analysis.xlsx spreadsheet attached herein. In previous response to CPUC comments on approved WPP, SCE provided calculations that showed that varying the base case pool heater capacity only marginally changed (<0.5%) the natural gas consumption of the base case heater. That is because the pool heating load (i.e. the amount of heat that is needed to heat up the pool) does not change, and the gas pool heaters do not benefit from higher efficiencies at part load or only operate a full load. Thus, the savings are not greatly impacted by using the oversized pool heaters seen in the market. However, using pool heaters sized as seen in the market does correctly (and it is needed to) estimate the incremental cost of the measure. The sizing assumptions and sources for both measure and base case equipment are detailed in the workpaper. |
| Is DEER:RefgFrzr_Recyc-UnConditioned the appropriate electrical impact profile? | The “DEER:RefgFrzr_Recyc-UnConditioned” load shape was used for the previous SWRE002 VSD Pool pump residential measures. Based on the latest impact profiles exported from PEAR this seems to be the most appropriate. Based on previous formal direction, the use of DEER load profiles is required. However, if any profile can be used, the “SCE:Residential:Residential Pool Pumps” would be more appropriate. CPUC response 5/12 – The refrigerator in an unconditioned space “DEER:RefgFrzr_Recyc-UnConditioned“ is OK to use until a better load shape is generated. Load shapes can be generated using pool simulation programs. We suggest generating load shapes in the future, but the current load shape is OK for now. Notes from 6/24/21 call with CPUC, SCE, and TRC: For this version of the workpaper SCE will continue to use DEER:RefgFrzr_Recyc-UnConditioned since there is no better option available. SCE (Andres Fergadiotti) to reach out to Jennifer McWilliams to confirm with her if there is a better option. SCE consultant will also look at the load shapes to see if there are any shapes that only used in the summer SCE/TRC will add a comment in the workpaper that future updates should include (as available) the use a pool heater specific load shape, and a request for CPUC to support the development of such for this measure. Follow-ups to Meeting on 6/24/21 SCE consultant reviewed the DEER load shapes and did not find any load shape more appropriate for this application. Please refer to the DEER Load Shape Analysis_Pool HP.xlsx spreadsheet attached in this document. SCE (Andres Fergadiotti) on 6/25 inquired from Jennifer.McWilliams@dnvgl.com about a more appropriate load shape (either existing and/or under development) for this application with pending response from DNVGL, as 07/02/2021. |
| Have there been more recent studies on residential pool covers? The 52% pool cover usage value comes from a 2004 study on a population of 38 residential homes. We expect the market penetration to be higher compared to 2004; thus, the pool cover usage values are expected to higher than 52%. | During the research phase of this workpaper this was the only study that we could find that addressed pool cover usage. Although the number of pools with covers is expected to have increased since 2004, pool cover usage is customer behavior dependent. The Koeller study shows that, based on customer behavior, only 52% of the pools that had obtained covers from the program actually used them. We also found an EPA WaterSense report about pool covers that came out in 2018, but this document also references the Koeller study for pool cover usage. The study is attached. Proposed adjustments for pool cover used in methodology is determined to be reasonable. Future updates to the workpaper will revisit updated sources of information for this assumption. CPUC Comment 05/06 – For fuel sub measures, the baseline for NR is code according to the fuel sub measures guidance document. Per California Energy Code (CEC T-24) 4) all pools constructed with pool heaters require a pool cover. Should pool cover be an eligibility requirement for the program? SCE response to comment from 5/12: We will require that pools be equipped with pool cover, either existing or newly installed, to be eligible. Notes from 6/24/21 call with CPUC, SCE, and TRC: CPUC is ok with including pool cover requirements in eligibility, but continuing to use the current weighted assumption on pool cover usage in the calculations SCE/TRC will do some additional review to see if any newer assumptions can be used. If not, current assumptions will be maintained. This include: seeing if current Koeller study breaks out SFm vs MFm, reviewing 2015 pool cover disposition, and searching for any pool cover impact evaluations that are applicable Follow-ups to Meeting on 6/24/21 SCG Disposition Notes: The disposition does have some findings about penetration of pool covers in SCG’s area but not about the usage of pool covers by the customers. Furthermore, the disposition is mainly for commercial buildings, with only one measure being for MFm residential. The Koeller study was completed only for SFm participants, so it does not show a breakout between SFm and MFm usage. The Pool Cover Impact Evaluation (2015) for the non-residential pool program includes some site data about the pool covers installed by the program, including the types of covers used. Also, its was noted that for all the sites audited the pool covers were in operation. However, the findings may be skewed as the participants were expecting the auditor. Furthermore, as this is for the non-residential sector, it may not represent the building types in this sector. As such, we recommend using the same assumptions for pool cover usage. |
| SCG implementation IDs are missing. | Not applicable - this is a fuel substitution offering |
| Will the pool pump need to run at full load a longer time if the input from the heater is lower? If not, explain why not. | Based hourly savings calculations, the HP Pool heater is expected to operate (on average) 3.7 hours more for SFm pools and 9 hours more for MFm-Cmn pools per year for the worst case scenario of pools with no cover. (see tables on next page) After conducting research for a sampling of HP and gas models, and equipment specifications, both types of equipment seem to have comparable minimum flow requirements. The heater systems would need to either interlock with the pumps, automatically shut off the heaters below a minimum flow, or the pumps would need to be programmed to operate at the heater minimum flow. Since both HP and gas heaters have similar operating requirements, and HPs only operate at most 25 hours per year (<4%), the impact to pool pump operation and energy consumption is assumed to be negligible. |
| p. 11 talks about the “commercial building type” but elsewhere it seems that this workpaper is primarily for residential. | We have updated language in this section to more generally refer to “CPUC sponsored saturation studies” and removed “commercial” when referring to building types. |
| SCE additional comments 6/23: | SCE will add the following language to the workpaper with addendum based on dispositions for SWWH025. Existing Workpaper Incentive Requirements Deployment of the program may require rebates or financial incentives to participants that exceed the Incremental Measure Cost (IMC). Incentives or rebates that exceed the incremental cost for a measure must be justified by individual PAs and/or third-party implemented programs as applicable and for each instance in addendum to workpaper submissions to document program implementation practice prior to program implementation. |

CPUC Review Date: 04/14/2021

Please note responses to comments in the table below, revise workpaper, and upload the entire package to the WPA. If needed, please reach out to Workpaper Review Team to set up a call to discuss.

Attachments

Comparison of Annual Run Hours

| SFm Measure | Baseline Run Hours | Measure Run Hours | Average Hours Difference | Hours Percent |
| --- | --- | --- | --- | --- |
| No Pool Cover | 744.8 | 748.5 | 3.7 | 0.53% |
| Climate Zone | Baseline Run Hours | Measure Run Hours | Hours Difference from gas baseline per year | Hours Percent |
| CZ01 | 1822 | 1825 | 3 | 0.16% |
| CZ02 | 835 | 836 | 1 | 0.12% |
| CZ03 | 1282 | 1289 | 7 | 0.55% |
| CZ04 | 434 | 434 | 0 | 0.00% |
| CZ05 | 1051 | 1052 | 1 | 0.10% |
| CZ06 | 697 | 705 | 8 | 1.15% |
| CZ07 | 742 | 743 | 1 | 0.13% |
| CZ08 | 385 | 391 | 6 | 1.56% |
| CZ09 | 606 | 606 | 0 | 0.00% |
| CZ10 | 452 | 455 | 3 | 0.66% |
| CZ11 | 692 | 694 | 2 | 0.29% |
| CZ12 | 574 | 577 | 3 | 0.52% |
| CZ13 | 302 | 305 | 3 | 0.99% |
| CZ14 | 735 | 742 | 7 | 0.95% |
| CZ15 | 260 | 260 | 0 | 0.00% |
| CZ16 | 1048 | 1062 | 14 | 1.34% |

| MFm-Cmn Measure | Baseline Run Hours | Measure Run Hours | Average Hours Difference | Hours Percent |
| --- | --- | --- | --- | --- |
| No Pool Cover | 745.9 | 755.1 | 9.1 | 1.48% |
| Climate Zone | Baseline Run Hours | Measure Run Hours | Hours Difference from gas baseline per year | Hours Percent |
| CZ01 | 1823 | 1826 | 3 | 0.16% |
| CZ02 | 835 | 840 | 5 | 0.60% |
| CZ03 | 1287 | 1297 | 10 | 0.78% |
| CZ04 | 437 | 440 | 3 | 0.69% |
| CZ05 | 1051 | 1057 | 6 | 0.57% |
| CZ06 | 701 | 715 | 14 | 2.00% |
| CZ07 | 745 | 751 | 6 | 0.81% |
| CZ08 | 385 | 397 | 12 | 3.12% |
| CZ09 | 605 | 609 | 4 | 0.66% |
| CZ10 | 453 | 461 | 8 | 1.77% |
| CZ11 | 689 | 697 | 8 | 1.16% |
| CZ12 | 573 | 581 | 8 | 1.40% |
| CZ13 | 301 | 309 | 8 | 2.66% |
| CZ14 | 738 | 763 | 25 | 3.39% |
| CZ15 | 259 | 264 | 5 | 1.93% |
| CZ16 | 1053 | 1074 | 21 | 1.99% |