## Summary
Measure | Baseline Total Leakage | Measure Total Leakage
Crossover Duct Replacement | 33.33% | 12.96%
Return Duct Retrofit | 50.72% | 13.69%

## Data
[13 empty] | Mean | 54.51% | [5 empty] | 33.33% | 12.96% | 20.37%
[13 empty] | Min | 7.895% | [5 empty] | 15.64% | 0% | 1.234%
[13 empty] | Max | 100% | [5 empty] | 103.1% | 14.94% | 88.36%
Project Completion Date | Climate Zone | Measure Description | Quantity | System Capacity | System Units | Airflow | Make | Model | CFM Initial | CFM Final | CFM Reduction | Target | Registers | % reduction |  |  | CFM from tonnage | CFM/ton CFM/kBtuh | Target1 | Pre % Loss | Post % Loss | % diff
2018-06-14 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | coleman | unk | 281 | 111 | 170 | 1st Target | 8 | 60.5% | 111 | 170 | 1020 | 400 | 180 | 23.42% | 9.25% | 14.17%
2018-07-11 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | colemn | brccq036bbb | 218 | 163 | 55 | 1st Target | 10 | 25.23% | 163 | 55 | 1020 | 400 | 180 | 18.17% | 13.58% | 4.583%
2018-07-24 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | coleman | brcq0421bdg | 280 | 165 | 115 | 1st Target | 7 | 41.07% | 165 | 115 | 1190 | 400 | 210 | 20% | 11.79% | 8.214%
2018-06-13 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | intertherm | m1mb056abw | 245 | 120 | 125 | 1st Target | 7 | 51.02% | 120 | 125 | 832.5 | 21.7 | 146.475 | 25.09% | 12.29% | 12.8%
2018-03-14 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | COLEMAN | 7842-901 | 1444 | 207 | 1237 | 1st Target | 6 | 85.66% | 207 | 1237 | 1190 | 400 | 210 | 103.1% | 14.79% | 88.36%
2018-03-15 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | DUO-THERM | 750031 | 300 | 150 | 150 | 1st Target | 8 | 50% | 150 | 150 | 1036 | 21.7 | 182.28 | 24.69% | 12.34% | 12.34%
2018-05-25 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | coleman | brcq0361bdg | 285 | 127 | 158 | 1st Target | 10 | 55.44% | 127 | 158 | 1020 | 400 | 180 | 23.75% | 10.58% | 13.17%
2018-07-18 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45.2 | kBTU | 980.84 | coleman | 7656 856 | 170 | 135 | 35 | 1st Target | 8 | 20.59% | 135 | 35 | 836.2 | 21.7 | 147.126 | 17.33% | 13.76% | 3.568%
2018-07-31 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | coleman | brcq0361bd | 465 | 200 | 265 | 1st Target | 10 | 56.99% | 200 | 265 | 1190 | 400 | 210 | 33.21% | 14.29% | 18.93%
2018-05-22 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 64 | kBTU | 1388.8 | COLEMAN PRESIDENTE | 7680a | 419 | 184 | 235 | 1st Target | 10 | 56.09% | 184 | 235 | 1184 | 21.7 | 208.32 | 30.17% | 13.25% | 16.92%
2018-05-22 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 70 | kBTU | 1519 | Coleman | 79700856 | 340 | 200 | 140 | 1st Target | 9 | 41.18% | 200 | 140 | 1295 | 21.7 | 227.85 | 22.38% | 13.17% | 9.217%
2018-05-23 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | coleman | 7970b856 | 190 | 162 | 28 | 1st Target | 8 | 14.74% | 162 | 28 | 1036 | 21.7 | 182.28 | 15.64% | 13.33% | 2.304%
2018-06-07 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 55 | kBTU | 1193.5 | INTERTHERM | mgho55abwn07 | 300 | 163 | 137 | 1st Target | 11 | 45.67% | 163 | 137 | 1017.5 | 21.7 | 179.025 | 25.14% | 13.66% | 11.48%
2018-06-28 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 2 | Ton | 800 | DAY & NIIGHT | n4a524gkc101 | 250 | 102 | 148 | 1st Target | 12 | 59.2% | 102 | 148 | 680 | 400 | 120 | 31.25% | 12.75% | 18.5%
2018-06-13 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | intertherm | m1mb056abw | 245 | 120 | 125 | 1st Target | 7 | 51.02% | 120 | 125 | 832.5 | 21.7 | 146.475 | 25.09% | 12.29% | 12.8%
2018-06-21 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 46 | kBTU | 998.2 | coleman | 7956a856 | 310 | 125 | 185 | 1st Target | 9 | 59.68% | 125 | 185 | 851 | 21.7 | 149.73 | 31.06% | 12.52% | 18.53%
2018-06-27 | Z02 | Cross Over Ducting Replaced ( linear feet ) | 1 | 57 | kBTU | 1236.9 | INTERTHERM | mmhb070abhr06 | 295 | 98 | 197 | 1st Target | 10 | 66.78% | 98 | 197 | 1054.5 | 21.7 | 185.535 | 23.85% | 7.923% | 15.93%
2018-03-27 | Z03 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | COLEMAN | DGAA070BDTB | 824 | 166 | 658 | 1st Target | 7 | 79.85% | 166 | 658 | 1036 | 21.7 | 182.28 | 67.81% | 13.66% | 54.15%
2018-03-29 | Z03 | Cross Over Ducting Replaced ( linear feet ) | 1 | 62 | kBTU | 1345.4 | COLEMAN | DGAH077BBSB | 551 | 200 | 351 | 1st Target | 12 | 63.7% | 200 | 351 | 1147 | 21.7 | 201.81 | 40.95% | 14.87% | 26.09%
2018-07-05 | Z03 | Cross Over Ducting Replaced ( linear feet ) | 1 | 60 | kBTU | 1302 | coleman | m1mc056abw | 400 | 185 | 215 | 1st Target | 10 | 53.75% | 185 | 215 | 1110 | 21.7 | 195.3 | 30.72% | 14.21% | 16.51%
2018-07-18 | Z03 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | coleman | brcs0361bd | 400 | 170 | 230 | 1st Target | 11 | 57.5% | 170 | 230 | 1020 | 400 | 180 | 33.33% | 14.17% | 19.17%
2018-02-13 | Z04 | Cross Over Ducting Replaced ( linear feet ) | 1 | 57 | kBTU | 1236.9 | COLEMAN | DGAT070BDD | 270 | 130 | 140 | 1st Target | 8 | 51.85% | 130 | 140 | 1054.5 | 21.7 | 185.535 | 21.83% | 10.51% | 11.32%
2018-02-20 | Z04 | Cross Over Ducting Replaced ( linear feet ) | 1 | 75 | kBTU | 1627.5 | coleman | 775856 | 400 | 200 | 200 | 1st Target | 10 | 50% | 200 | 200 | 1387.5 | 21.7 | 244.125 | 24.58% | 12.29% | 12.29%
2018-07-30 | Z04 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | EVCON/COLMEN | 8665c867 | 301 | 171 | 130 | 1st Target | 9 | 43.19% | 171 | 130 | 1020 | 400 | 180 | 25.08% | 14.25% | 10.83%
2018-07-30 | Z04 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | COLEMAN/ EVCON | 95767899 | 312 | 168 | 144 | 1st Target | 10 | 46.15% | 168 | 144 | 1020 | 400 | 180 | 26% | 14% | 12%
2018-06-28 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | goodman | 105ana036a | 433 | 165 | 268 | 1st Target | 10 | 61.89% | 165 | 268 | 1020 | 400 | 180 | 36.08% | 13.75% | 22.33%
2018-07-03 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | rheem | RAKA-048-JAZ | 454 | 238 | 216 | 1st Target | 12 | 47.58% | 238 | 216 | 1360 | 400 | 240 | 28.38% | 14.88% | 13.5%
2018-06-28 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 46 | kBTU | 998.2 | coleman | 7956a856 | 654 | 143 | 511 | 1st Target | 9 | 78.13% | 143 | 511 | 851 | 21.7 | 149.73 | 65.52% | 14.33% | 51.19%
2018-07-02 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 46 | kBTU | 998.2 | COLEMAN | 7956A856 | 345 | 130 | 215 | 1st Target | 8 | 62.32% | 130 | 215 | 851 | 21.7 | 149.73 | 34.56% | 13.02% | 21.54%
2018-07-05 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | coleman | dgaa070bdtb | 657 | 176 | 481 | 1st Target | 10 | 73.21% | 176 | 481 | 1036 | 21.7 | 182.28 | 54.07% | 14.48% | 39.58%
2018-06-27 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 60 | kBTU | 1302 | coleman | 7975856 | 286 | 172 | 114 | 1st Target | 9 | 39.86% | 172 | 114 | 1110 | 21.7 | 195.3 | 21.97% | 13.21% | 8.756%
2018-07-03 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 60 | kBTU | 1302 | coleman | 7975856 | 366 | 169 | 197 | 1st Target | 10 | 53.83% | 169 | 197 | 1110 | 21.7 | 195.3 | 28.11% | 12.98% | 15.13%
2018-06-29 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 60 | kBTU | 1302 | coleman | 7680c856 | 453 | 192 | 261 | 1st Target | 9 | 57.62% | 192 | 261 | 1110 | 21.7 | 195.3 | 34.79% | 14.75% | 20.05%
2018-06-29 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 61 | kBTU | 1323.7 | coleman | dgam075bde | 321 | 154 | 167 | 1st Target | 10 | 52.02% | 154 | 167 | 1128.5 | 21.7 | 198.555 | 24.25% | 11.63% | 12.62%
2018-02-15 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 61 | kBTU | 1323.7 | coleman | dt0758de | 299 | 176 | 123 | 1st Target | 9 | 41.14% | 176 | 123 | 1128.5 | 21.7 | 198.555 | 22.59% | 13.3% | 9.292%
2018-02-16 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | carrier | n/a | 270 | 238 | 32 | 1st Target | 10 | 11.85% | 238 | 32 | 1360 | 400 | 240 | 16.88% | 14.88% | 2%
2018-02-21 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | goodman | BRCQ0361BD | 239 | 170 | 69 | 1st Target | 8 | 28.87% | 170 | 69 | 1020 | 400 | 180 | 19.92% | 14.17% | 5.75%
2018-02-23 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | GOODMAN | TCJD48S41S3HA | 289 | 230 | 59 | 1st Target | 10 | 20.42% | 230 | 59 | 1360 | 400 | 240 | 18.06% | 14.37% | 3.688%
2018-04-04 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 2.5 | Ton | 1000 | COLEMAN | ERCS0301BBB | 201 | 149 | 52 | 1st Target | 8 | 25.87% | 149 | 52 | 850 | 400 | 150 | 20.1% | 14.9% | 5.2%
2018-04-10 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 60 | kBTU | 1302 | COLEMAN | 7680C856 | 523 | 186 | 337 | 1st Target | 8 | 64.44% | 186 | 337 | 1110 | 21.7 | 195.3 | 40.17% | 14.29% | 25.88%
2018-04-13 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | RHEEM | RAKA-037JAZ | 324 | 166 | 158 | 1st Target | 10 | 48.77% | 166 | 158 | 1020 | 400 | 180 | 27% | 13.83% | 13.17%
2018-04-17 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 2.5 | Ton | 1000 | COLEMAN | ERCQ0301BBA | 267 | 144 | 123 | 1st Target | 9 | 46.07% | 144 | 123 | 850 | 400 | 150 | 26.7% | 14.4% | 12.3%
2018-04-18 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | CONCORD | 13ACD-036-230-15 | 323 | 157 | 166 | 1st Target | 7 | 51.39% | 157 | 166 | 1020 | 400 | 180 | 26.92% | 13.08% | 13.83%
2018-04-18 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 2.5 | Ton | 1000 | LONNOX | 13ACX-030-230-17 | 948 | 133 | 815 | 1st Target | 9 | 85.97% | 133 | 815 | 850 | 400 | 150 | 94.8% | 13.3% | 81.5%
2018-04-19 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 2.5 | Ton | 1000 | COLEMAN | AM030M1021A | 256 | 144 | 112 | 1st Target | 8 | 43.75% | 144 | 112 | 850 | 400 | 150 | 25.6% | 14.4% | 11.2%
2018-04-18 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | COLEMAN | DGAT056BDD | 350 | 165 | 185 | 1st Target | 7 | 52.86% | 165 | 185 | 1036 | 21.7 | 182.28 | 28.8% | 13.58% | 15.22%
2018-04-30 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | cleman | BRCQ0361BGD | 750 | 180 | 570 | 1st Target | 10 | 76% | 180 | 570 | 1190 | 400 | 210 | 53.57% | 12.86% | 40.71%
2018-05-04 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | allegiance | 7a0042a100a1 | 590 | 165 | 425 | 1st Target | 10 | 72.03% | 165 | 425 | 1190 | 400 | 210 | 42.14% | 11.79% | 30.36%
2018-05-08 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | american standard | 4a7a4037l1000aa | 560 | 200 | 360 | 1st Target | 10 | 64.29% | 200 | 360 | 1360 | 400 | 240 | 35% | 12.5% | 22.5%
2018-05-03 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | RUUD | UAKA-037JAZ | 1137 | 179 | 958 | 1st Target | 14 | 84.26% | 179 | 958 | 1020 | 400 | 180 | 94.75% | 14.92% | 79.83%
2018-05-11 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | CARRIER | NA | 541 | 197 | 344 | 1st Target | 9 | 63.59% | 197 | 344 | 1360 | 400 | 240 | 33.81% | 12.31% | 21.5%
2018-05-10 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | CARRIER | 38TH048320 | 721 | 225 | 496 | 1st Target | 11 | 68.79% | 225 | 496 | 1360 | 400 | 240 | 45.06% | 14.06% | 31%
2018-04-30 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | intertherm | MGHB-056ABFC-09 | 375 | 175 | 200 | 1st Target | 10 | 53.33% | 175 | 200 | 1036 | 21.7 | 182.28 | 30.86% | 14.4% | 16.46%
2018-05-03 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | coleman | pa10ja036-a | 340 | 175 | 165 | 1st Target | 9 | 48.53% | 175 | 165 | 1020 | 400 | 180 | 28.33% | 14.58% | 13.75%
2018-05-15 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | RHEEM | RA1448WJ1NA | 403 | 231 | 172 | 1st Target | 9 | 42.68% | 231 | 172 | 1360 | 400 | 240 | 25.19% | 14.44% | 10.75%
2018-05-17 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | evcon | dgaa070bdtb | 289 | 175 | 114 | 1st Target | 9 | 39.45% | 175 | 114 | 1036 | 21.7 | 182.28 | 23.78% | 14.4% | 9.381%
2018-05-21 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 46 | kBTU | 998.2 | coleman | 756856 | 760 | 145 | 615 | 1st Target | 9 | 80.92% | 145 | 615 | 851 | 21.7 | 149.73 | 76.14% | 14.53% | 61.61%
2018-05-16 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | coleman | CA55480VKD2 | 513 | 234 | 279 | 1st Target | 9 | 54.39% | 234 | 279 | 1360 | 400 | 240 | 32.06% | 14.62% | 17.44%
2018-05-16 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 46 | kBTU | 998.2 | coleman | 756a856 | 280 | 145 | 135 | 1st Target | 7 | 48.21% | 145 | 135 | 851 | 21.7 | 149.73 | 28.05% | 14.53% | 13.52%
2018-05-30 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | guardian | GCGD48S21S2C | 467 | 232 | 235 | 1st Target | 11 | 50.32% | 232 | 235 | 1360 | 400 | 240 | 29.19% | 14.5% | 14.69%
2018-05-15 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 2.5 | Ton | 1000 | York | d1np030n03606a | 180 | 145 | 35 | 1st Target | 7 | 19.44% | 145 | 35 | 850 | 400 | 150 | 18% | 14.5% | 3.5%
2018-05-16 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 70 | kBTU | 1519 | evcon | DGAA070BDTB | 245 | 190 | 55 | 1st Target | 10 | 22.45% | 190 | 55 | 1295 | 21.7 | 227.85 | 16.13% | 12.51% | 3.621%
2018-05-30 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 70 | kBTU | 1519 | evcon | DGAA070BDTB | 250 | 200 | 50 | 1st Target | 10 | 20% | 200 | 50 | 1295 | 21.7 | 227.85 | 16.46% | 13.17% | 3.292%
2018-05-01 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | GOODMAN | CKT361B | 330 | 150 | 180 | 1st Target | 10 | 54.55% | 150 | 180 | 1020 | 400 | 180 | 27.5% | 12.5% | 15%
2018-05-11 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 46 | kBTU | 998.2 | coleman | 7956a856 | 182 | 139 | 43 | 1st Target | 9 | 23.63% | 139 | 43 | 851 | 21.7 | 149.73 | 18.23% | 13.93% | 4.308%
2018-05-10 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | FRIGIDAIRE | es4bd-048kb | 260 | 225 | 35 | 1st Target | 9 | 13.46% | 225 | 35 | 1360 | 400 | 240 | 16.25% | 14.06% | 2.188%
2018-05-16 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | carrier | n4a542gkc101 | 380 | 198 | 182 | 1st Target | 12 | 47.89% | 198 | 182 | 1190 | 400 | 210 | 27.14% | 14.14% | 13%
2018-05-08 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | COLEMAN | DRCS0481BB | 413 | 210 | 203 | 1st Target | 12 | 49.15% | 210 | 203 | 1360 | 400 | 240 | 25.81% | 13.12% | 12.69%
2018-05-08 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | carrier | 3eho36300 | 226 | 160 | 66 | 1st Target | 8 | 29.2% | 160 | 66 | 1020 | 400 | 180 | 18.83% | 13.33% | 5.5%
2018-05-10 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | coleman | tcjf48s41s4a | 255 | 143 | 112 | 1st Target | 10 | 43.92% | 143 | 112 | 1360 | 400 | 240 | 15.94% | 8.938% | 7%
2018-05-11 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | coleman | 2448-901 | 400 | 210 | 190 | 1st Target | 13 | 47.5% | 210 | 190 | 1360 | 400 | 240 | 25% | 13.12% | 11.88%
2018-05-17 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | coleman | gd42s41s3a | 265 | 180 | 85 | 1st Target | 11 | 32.08% | 180 | 85 | 1190 | 400 | 210 | 18.93% | 12.86% | 6.071%
2018-07-17 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 72 | kBTU | 1562.4 | coleman | 7995a856 | 560 | 220 | 340 | 1st Target | 9 | 60.71% | 220 | 340 | 1332 | 21.7 | 234.36 | 35.84% | 14.08% | 21.76%
2018-05-17 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | intertherm | m1mb056abw | 320 | 170 | 150 | 1st Target | 10 | 46.88% | 170 | 150 | 1036 | 21.7 | 182.28 | 26.33% | 13.99% | 12.34%
2018-05-04 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | COLEMAN | BRCQ0301BE | 400 | 160 | 240 | 1st Target | 9 | 60% | 160 | 240 | 1020 | 400 | 180 | 33.33% | 13.33% | 20%
2018-06-19 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | UNK | 14AJM42A01 | 400 | 170 | 230 | 1st Target | 8 | 57.5% | 170 | 230 | 1020 | 400 | 180 | 33.33% | 14.17% | 19.17%
2018-06-25 | Z12 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | unk | s3ba036k | 380 | 170 | 210 | 1st Target | 8 | 55.26% | 170 | 210 | 1020 | 400 | 180 | 31.67% | 14.17% | 17.5%
2018-07-24 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 2.5 | Ton | 1000 | colemen | 7956-856 | 325 | 120 | 205 | 1st Target | 10 | 63.08% | 120 | 205 | 850 | 400 | 150 | 32.5% | 12% | 20.5%
2018-06-06 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | CARRIER | 24AAA536A300 | 295 | 176 | 119 | 1st Target | 8 | 40.34% | 176 | 119 | 1020 | 400 | 180 | 24.58% | 14.67% | 9.917%
2018-06-07 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | COLEMAN | RAC13J364S21A | 476 | 167 | 309 | 1st Target | 12 | 64.92% | 167 | 309 | 1020 | 400 | 180 | 39.67% | 13.92% | 25.75%
2018-06-22 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | BRYANT | N4A336AKB200 | 364 | 167 | 197 | 1st Target | 7 | 54.12% | 167 | 197 | 1020 | 400 | 180 | 30.33% | 13.92% | 16.42%
2018-06-13 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | COLEMAN | AC042X1221G | 273 | 174 | 99 | 1st Target | 9 | 36.26% | 174 | 99 | 1190 | 400 | 210 | 19.5% | 12.43% | 7.071%
2018-06-20 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | COLEMAN | GCGD042S41S3A | 467 | 203 | 264 | 1st Target | 11 | 56.53% | 203 | 264 | 1190 | 400 | 210 | 33.36% | 14.5% | 18.86%
2018-07-11 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | GOODMAN | CK42-1C | 969 | 189 | 780 | 1st Target | 9 | 80.5% | 189 | 780 | 1190 | 400 | 210 | 69.21% | 13.5% | 55.71%
2018-07-10 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | na | 7a2048a100a0 | 489 | 231 | 258 | 1st Target | 9 | 52.76% | 231 | 258 | 1360 | 400 | 240 | 30.56% | 14.44% | 16.12%
2018-07-10 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | american standard | 2a7a3048a100aa | 1200 | 230 | 970 | 1st Target | 10 | 80.83% | 230 | 970 | 1360 | 400 | 240 | 75% | 14.37% | 60.62%
2018-07-03 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | CARRIER | N/A | 987 | 236 | 751 | 1st Target | 9 | 76.09% | 236 | 751 | 1360 | 400 | 240 | 61.69% | 14.75% | 46.94%
2018-07-18 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | COLEMAN | brcq0481bdg | 338 | 198 | 140 | 1st Target | 10 | 41.42% | 198 | 140 | 1360 | 400 | 240 | 21.12% | 12.38% | 8.75%
2018-07-20 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | COLEMAN | 6285B901 | 936 | 235 | 701 | 1st Target | 7 | 74.89% | 235 | 701 | 1360 | 400 | 240 | 58.5% | 14.69% | 43.81%
2018-06-27 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 44 | kBTU | 954.8 | COLEMAN | 755-856 | 390 | 120 | 270 | 1st Target | 11 | 69.23% | 120 | 270 | 814 | 21.7 | 143.22 | 40.85% | 12.57% | 28.28%
2018-06-20 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | coleman | 756f856 | 465 | 132 | 333 | 1st Target | 8 | 71.61% | 132 | 333 | 832.5 | 21.7 | 146.475 | 47.62% | 13.52% | 34.1%
2018-06-21 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | intertherm | m1gb056abw | 170 | 44 | 126 | 1st Target | 10 | 74.12% | 44 | 126 | 832.5 | 21.7 | 146.475 | 17.41% | 4.506% | 12.9%
2018-06-29 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | COLEMAN | 7656B856 | 321 | 133 | 188 | 1st Target | 10 | 58.57% | 133 | 188 | 832.5 | 21.7 | 146.475 | 32.87% | 13.62% | 19.25%
2018-07-11 | Z13 | #REF! | 1 | 45 | kBTU | 976.5 | colemen | dgaa056bdtb | 350 | 130 | 220 | 1st Target | 10 | 62.86% | 130 | 220 | 832.5 | 21.7 | 146.475 | 35.84% | 13.31% | 22.53%
2018-06-22 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | coleman | dgaa070bdta | 487 | 176 | 311 | 1st Target | 10 | 63.86% | 176 | 311 | 1036 | 21.7 | 182.28 | 40.08% | 14.48% | 25.59%
2018-06-26 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | coleman | 7670b856 | 366 | 156 | 210 | 1st Target | 10 | 57.38% | 156 | 210 | 1036 | 21.7 | 182.28 | 30.12% | 12.84% | 17.28%
2018-07-11 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | evcon | dgaa070bdtb | 190 | 175 | 15 | 1st Target | 8 | 7.895% | 175 | 15 | 1036 | 21.7 | 182.28 | 15.64% | 14.4% | 1.234%
2018-06-26 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 57 | kBTU | 1236.9 | coleman | dgat070bdd | 430 | 172 | 258 | 1st Target | 7 | 60% | 172 | 258 | 1054.5 | 21.7 | 185.535 | 34.76% | 13.91% | 20.86%
2018-06-28 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 62 | kBTU | 1345.4 | COLEMAN | DLAS075BDC | 386 | 187 | 199 | 1st Target | 10 | 51.55% | 187 | 199 | 1147 | 21.7 | 201.81 | 28.69% | 13.9% | 14.79%
2018-06-27 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 63 | kBTU | 1367.1 | COLEMEN PRESEDINTAIL | 7663b865 | 440 | 155 | 285 | 1st Target | 10 | 64.77% | 155 | 285 | 1165.5 | 21.7 | 205.065 | 32.18% | 11.34% | 20.85%
2018-06-19 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 64 | kBTU | 1388.8 | coleman | 76580356 | 298 | 186 | 112 | 1st Target | 7 | 37.58% | 186 | 112 | 1184 | 21.7 | 208.32 | 21.46% | 13.39% | 8.065%
2018-06-20 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 64 | kBTU | 1388.8 | colemen | 7680a856 | 319 | 185 | 134 | 1st Target | 10 | 42.01% | 185 | 134 | 1184 | 21.7 | 208.32 | 22.97% | 13.32% | 9.649%
2018-06-29 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 64 | kBTU | 1388.8 | COLEMAN | 7680856 | 377 | 181 | 196 | 1st Target | 8 | 51.99% | 181 | 196 | 1184 | 21.7 | 208.32 | 27.15% | 13.03% | 14.11%
2018-06-07 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 70 | kBTU | 1519 | colemen | DAA070BDTA | 240 | 135 | 105 | 1st Target | 10 | 43.75% | 135 | 105 | 1295 | 21.7 | 227.85 | 15.8% | 8.887% | 6.912%
2018-01-16 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | na | drcs0481beg | 279 | 205 | 74 | 1st Target | 11 | 26.52% | 205 | 74 | 1360 | 400 | 240 | 17.44% | 12.81% | 4.625%
2018-01-17 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | coleman | bcs0421bd | 591 | 201 | 390 | 1st Target | 10 | 65.99% | 201 | 390 | 1190 | 400 | 210 | 42.21% | 14.36% | 27.86%
2018-01-18 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | GOODMAN | CK49-1B | 323 | 0 | 323 |  | 10 | 100% | 0 | 323 | 1360 | 400 | 240 | 20.19% | 0% | 20.19%
2018-01-24 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | corsaire | na | 550 | 213 | 337 | 1st Target | 11 | 61.27% | 213 | 337 | 1360 | 400 | 240 | 34.38% | 13.31% | 21.06%
2018-01-23 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 4 | Ton | 1600 | COLEMAN | 8748-801 | 431 | 183 | 248 | 1st Target | 10 | 57.54% | 183 | 248 | 1360 | 400 | 240 | 26.94% | 11.44% | 15.5%
2018-02-06 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 46 | kBTU | 998.2 | coleman | 7956856 | 216 | 145 | 71 | 1st Target | 9 | 32.87% | 145 | 71 | 851 | 21.7 | 149.73 | 21.64% | 14.53% | 7.113%
2018-02-08 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 62 | kBTU | 1345.4 | coleman | dgaa077bdtb | 365 | 184 | 181 | 1st Target | 11 | 49.59% | 184 | 181 | 1147 | 21.7 | 201.81 | 27.13% | 13.68% | 13.45%
2018-02-09 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | COLEMAN | BRC0421BDG | 461 | 159 | 302 | 1st Target | 10 | 65.51% | 159 | 302 | 1190 | 400 | 210 | 32.93% | 11.36% | 21.57%
2018-01-03 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | LEAR-SEIGER | lsr-42-1 | 1260 | 173 | 1087 | 1st Target | 17 | 86.27% | 173 | 1087 | 1190 | 400 | 210 | 90% | 12.36% | 77.64%
2018-03-02 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | coleman | dgaa056bdtbx | 356 | 127 | 229 | 1st Target | 10 | 64.33% | 127 | 229 | 832.5 | 21.7 | 146.475 | 36.46% | 13.01% | 23.45%
2018-03-05 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | coleman | dgaa056bdtb | 312 | 139 | 173 | 1st Target | 9 | 55.45% | 139 | 173 | 832.5 | 21.7 | 146.475 | 31.95% | 14.23% | 17.72%
2018-03-07 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | coleman | 7656b856 | 432 | 123 | 309 | 1st Target | 13 | 71.53% | 123 | 309 | 832.5 | 21.7 | 146.475 | 44.24% | 12.6% | 31.64%
2018-03-09 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | coleman | daa070b | 321 | 170 | 151 | 1st Target | 9 | 47.04% | 170 | 151 | 1036 | 21.7 | 182.28 | 26.42% | 13.99% | 12.43%
2018-03-09 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 62 | kBTU | 1345.4 | coleman | dgaa077bdtb | 376 | 180 | 196 | 1st Target | 9 | 52.13% | 180 | 196 | 1147 | 21.7 | 201.81 | 27.95% | 13.38% | 14.57%
2018-03-12 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | coleman | 7656a856 | 470 | 132 | 338 | 1st Target | 9 | 71.91% | 132 | 338 | 832.5 | 21.7 | 146.475 | 48.13% | 13.52% | 34.61%
2018-03-12 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | colemAN | dgaa056bdtb | 445 | 123 | 322 | 1st Target | 12 | 72.36% | 123 | 322 | 832.5 | 21.7 | 146.475 | 45.57% | 12.6% | 32.97%
2018-04-24 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 57 | kBTU | 1236.9 | coleman | m1mb070abw | 421 | 172 | 249 | 1st Target | 9 | 59.14% | 172 | 249 | 1054.5 | 21.7 | 185.535 | 34.04% | 13.91% | 20.13%
2018-04-25 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 62 | kBTU | 1345.4 | coleman | m1mb077abw | 365 | 187 | 178 | 1st Target | 9 | 48.77% | 187 | 178 | 1147 | 21.7 | 201.81 | 27.13% | 13.9% | 13.23%
2018-04-24 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | coleman | dgaa070bdtb | 540 | 176 | 364 | 1st Target | 10 | 67.41% | 176 | 364 | 1036 | 21.7 | 182.28 | 44.44% | 14.48% | 29.95%
2018-03-14 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | coleman | TCGD42S21S1HA | 279 | 197 | 82 | 1st Target | 9 | 29.39% | 197 | 82 | 1190 | 400 | 210 | 19.93% | 14.07% | 5.857%
2018-04-27 | Z13 | #REF! | 1 | 4 | Ton | 1600 | NA | C3048VKA1 | 320 | 239 | 81 | 1st Target | 9 | 25.31% | 239 | 81 | 1360 | 400 | 240 | 20% | 14.94% | 5.062%
2018-04-27 | Z13 | #REF! | 1 | 61 | kBTU | 1323.7 | evcon | dgat075bde | 980 | 182 | 798 | 1st Target | 10 | 81.43% | 182 | 798 | 1128.5 | 21.7 | 198.555 | 74.03% | 13.75% | 60.29%
2018-04-30 | Z13 | #REF! | 1 | 3.5 | Ton | 1400 | interthrm | ac0042bcrb | 290 | 168 | 122 | 1st Target | 7 | 42.07% | 168 | 122 | 1190 | 400 | 210 | 20.71% | 12% | 8.714%
2018-04-30 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | na | e061136129 | 455 | 0 | 455 |  | 9 | 100% | 0 | 455 | 1190 | 400 | 210 | 32.5% | 0% | 32.5%
2018-05-01 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3.5 | Ton | 1400 | coleman | dcyzf042n080c | 765 | 0 | 765 |  | 10 | 100% | 0 | 765 | 1190 | 400 | 210 | 54.64% | 0% | 54.64%
2018-05-01 | Z13 | #REF! | 1 | 45 | kBTU | 976.5 | coleman | m1mb056abw | 266 | 132 | 134 | 1st Target | 10 | 50.38% | 132 | 134 | 832.5 | 21.7 | 146.475 | 27.24% | 13.52% | 13.72%
2018-05-02 | Z13 | #REF! | 1 | 3 | Ton | 1200 | coleman | 7670856 | 349 | 179 | 170 | 1st Target | 11 | 48.71% | 179 | 170 | 1020 | 400 | 180 | 29.08% | 14.92% | 14.17%
2018-05-02 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 88 | kBTU | 1909.6 | armstrong | mg64110d2c | 674 | 175 | 499 | 1st Target | 10 | 74.04% | 175 | 499 | 1628 | 21.7 | 286.44 | 35.3% | 9.164% | 26.13%
2018-05-07 | Z13 | #REF! | 1 | 44 | kBTU | 954.8 | coleman | 7655856 | 342 | 105 | 237 | 1st Target | 10 | 69.3% | 105 | 237 | 814 | 21.7 | 143.22 | 35.82% | 11% | 24.82%
2018-05-11 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 3 | Ton | 1200 | goodman | ck361a | 500 | 177 | 323 | 1st Target | 11 | 64.6% | 177 | 323 | 1020 | 400 | 180 | 41.67% | 14.75% | 26.92%
2018-05-11 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 56 | kBTU | 1215.2 | coleman | dgaa0709bdta | 488 | 128 | 360 | 1st Target | 10 | 73.77% | 128 | 360 | 1036 | 21.7 | 182.28 | 40.16% | 10.53% | 29.62%
2018-07-06 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 70 | kBTU | 1519 | coleman | 76708 | 631 | 201 | 430 | 1st Target | 10 | 68.15% | 201 | 430 | 1295 | 21.7 | 227.85 | 41.54% | 13.23% | 28.31%
2018-06-27 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 63 | kBTU | 1367.1 | COLEMEN PRESEDINTAIL | 7663b865 | 440 | 155 | 285 | 1st Target | 10 | 64.77% | 155 | 285 | 1165.5 | 21.7 | 205.065 | 32.18% | 11.34% | 20.85%
2018-07-24 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 2.5 | Ton | 1000 | colemen | 7956-856 | 325 | 120 | 205 | 1st Target | 10 | 63.08% | 120 | 205 | 850 | 400 | 150 | 32.5% | 12% | 20.5%
2018-07-11 | Z13 | Cross Over Ducting Replaced ( linear feet ) | 1 | 45 | kBTU | 976.5 | colemen | dgaa056bdtb | 350 | 130 | 220 | 1st Target | 10 | 62.86% | 130 | 220 | 832.5 | 21.7 | 146.475 | 35.84% | 13.31% | 22.53%
|  | Total | 139 | [5 empty] | 59241 | 23090 | 36151
[13 empty] | Mean | 65.85% | [5 empty] | 50.72% | 13.69% | 37.15%
[13 empty] | Min | 12% | [5 empty] | 0% | 0% | 0%
[13 empty] | Max | 90.12% | [5 empty] | 98.33% | 50% | 84.79%
Project Completion Date | Climate Zone | Measure Description | Quantity | System Capacity | System Units | Airflow | Make | Model | CFM Initial | CFM Final | CFM Reduction | Target | Registers | % reduction |  |  | CFM from tonnage | CFM/ton CFM/kBtuh | Target1 | Pre % Loss | Post % Loss | % diff
2018-07-16 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 2 | Ton | 800 | goodman | GSC130241FC | 976 | 246 | 730 | 2nd Target | 10 | 74.8% | 246 | 730 | 680 | 400 | 120 |  | 30.75%
2018-07-18 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 2.5 | Ton | 1000 | INTERTHEM | ufc-01 | 1137 | 136 | 1001 | 1st Target | 10 | 88.04% | 136 | 1001 | 850 | 400 | 150 |  | 13.6%
2018-06-19 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN | 9536-901 | 1357 | 156 | 1201 | 1st Target | 8 | 88.5% | 156 | 1201 | 1020 | 400 | 180 |  | 13%
2018-07-12 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN | BRCQ036B | 1087 | 175 | 912 | 1st Target | 8 | 83.9% | 175 | 912 | 1020 | 400 | 180 | 90.58% | 14.58% | 76%
2018-07-13 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN/ EVCON | tg8s080b12mp11b | 201 | 176 | 25 | 1st Target | 10 | 12.44% | 176 | 25 | 1020 | 400 | 180 | 16.75% | 14.67% | 2.083%
2018-07-17 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | trane | 4ttr40371000aa | 400 | 170 | 230 | 1st Target | 8 | 57.5% | 170 | 230 | 1020 | 400 | 180 | 33.33% | 14.17% | 19.17%
2018-07-18 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | coleman | es0361bag | 1300 | 170 | 1230 | 1st Target | 10 | 86.92% | 170 | 1130 | 1020 | 400 | 180 |  | 14.17%
2018-07-20 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | colemen | ugab075buh | 1123 | 168 | 955 | 1st Target | 10 | 85.04% | 168 | 955 | 1020 | 400 | 180 | 93.58% | 14% | 79.58%
2018-07-21 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | goodman | CKL36-10 | 987 | 176 | 811 | 1st Target | 10 | 82.17% | 176 | 811 | 1020 | 400 | 180 | 82.25% | 14.67% | 67.58%
2018-07-24 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | GENERAL ELECTRIC | GE036 | 987 | 236 | 751 | 2nd Target | 10 | 76.09% | 236 | 751 | 1020 | 400 | 180 | 82.25% | 19.67% | 62.58%
2018-06-21 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | PAYNE | 561CJ042-B | 1376 | 189 | 1187 | 1st Target | 8 | 86.26% | 189 | 1187 | 1190 | 400 | 210 | 98.29% | 13.5% | 84.79%
2018-07-10 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | COLEMAN | GCGD42S21S2C | 876 | 206 | 670 | 1st Target | 10 | 76.48% | 206 | 670 | 1190 | 400 | 210 | 62.57% | 14.71% | 47.86%
2018-07-09 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | WESTIN HOUSE | FS5BD-042KA | 926 | 203 | 723 | 1st Target | 10 | 78.08% | 203 | 723 | 1190 | 400 | 210 | 66.14% | 14.5% | 51.64%
2018-06-26 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | PAYNE | PA13NR042-J | 976 | 206 | 770 | 1st Target | 10 | 78.89% | 206 | 770 | 1190 | 400 | 210 | 69.71% | 14.71% | 55%
2018-07-10 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | goodman | brcq0421bb | 1272 | 191 | 1081 | 1st Target | 10 | 84.98% | 191 | 1081 | 1190 | 400 | 210 | 90.86% | 13.64% | 77.21%
2018-07-20 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | colemen | 8632A-776 | 1127 | 180 | 947 | 1st Target | 10 | 84.03% | 180 | 947 | 1190 | 400 | 210 | 80.5% | 12.86% | 67.64%
2018-07-18 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | PANYE | PA10JA042000AHAA | 936 | 201 | 735 | 1st Target | 8 | 78.53% | 201 | 735 | 1190 | 400 | 210 | 66.86% | 14.36% | 52.5%
2018-06-29 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | COLEMAN | 9548901 | 1300 | 222 | 1078 | 1st Target | 10 | 82.92% | 222 | 1078 | 1360 | 400 | 240 | 81.25% | 13.88% | 67.38%
2018-07-09 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | goodman | gsc130481ag | 1100 | 231 | 869 | 1st Target | 10 | 79% | 231 | 869 | 1360 | 400 | 240 | 68.75% | 14.44% | 54.31%
2018-07-13 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | na | pa10jao48000ahaa | 1300 | 230 | 1070 | 1st Target | 10 | 82.31% | 230 | 1070 | 1360 | 400 | 240 | 81.25% | 14.37% | 66.88%
2018-07-17 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | coleman | brcq0481bb | 1250 | 230 | 1020 | 1st Target | 10 | 81.6% | 230 | 1020 | 1360 | 400 | 240 | 78.12% | 14.37% | 63.75%
2018-07-18 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | na | 38ckc048300 | 1200 | 234 | 966 | 1st Target | 10 | 80.5% | 234 | 966 | 1360 | 400 | 240 | 75% | 14.62% | 60.38%
2018-07-24 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | GOODMAN | G8X140371KA | 989 | 236 | 753 | 1st Target | 10 | 76.14% | 236 | 753 | 1360 | 400 | 240 | 61.81% | 14.75% | 47.06%
2018-07-25 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | york | p4hub16n06401a | 1080 | 214 | 866 | 1st Target | 10 | 80.19% | 214 | 866 | 1360 | 400 | 240 | 67.5% | 13.38% | 54.12%
2018-07-21 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 5 | Ton | 2000 | COLEMAN | H2RA060S06D | 1232 | 286 | 946 | 1st Target | 12 | 76.79% | 286 | 946 | 1700 | 400 | 300 | 61.6% | 14.3% | 47.3%
2018-07-23 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 60 | kBTU | 1302 | armstrong | 347475328 | 723 | 186 | 537 | 1st Target | 10 | 74.27% | 186 | 537 | 1110 | 21.7 | 195.3 | 55.53% | 14.29% | 41.24%
2018-07-26 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 63 | kBTU | 1367.1 | PAYNE | PG8JAA036070 | 693 | 198 | 495 | 1st Target | 10 | 71.43% | 198 | 495 | 1165.5 | 21.7 | 205.065 | 50.69% | 14.48% | 36.21%
2018-06-27 | Z04 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 64 | kBTU | 1388.8 | COLEMAN | 8631746 | 359 | 200 | 159 | 1st Target | 8 | 44.29% | 200 | 159 | 1184 | 21.7 | 208.32 | 25.85% | 14.4% | 11.45%
2018-07-20 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 64 | kBTU | 1388.8 | coleman | 8631756 | 985 | 235 | 750 | 2nd Target | 8 | 76.14% | 235 | 750 | 1184 | 21.7 | 208.32 | 70.92% | 16.92% | 54%
2018-07-17 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 75 | kBTU | 1627.5 | armstrong | mg64a75d2c | 785 | 222 | 563 | 1st Target | 10 | 71.72% | 222 | 563 | 1387.5 | 21.7 | 244.125 | 48.23% | 13.64% | 34.59%
2018-06-08 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 76 | kBTU | 1649.2 | COLEMAN | 8995A676 | 1172 | 206 | 966 | 1st Target | 10 | 82.42% | 206 | 966 | 1406 | 21.7 | 247.38 | 71.06% | 12.49% | 58.57%
2018-06-28 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 76 | kBTU | 1649.2 | colemen | mgs080c16mp11a | 275 | 165 | 110 | 1st Target | 10 | 40% | 165 | 110 | 1406 | 21.7 | 247.38 | 16.67% | 10% | 6.67%
2018-07-19 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 76 | kBTU | 1649.2 | COLEMAN | 8995-676 | 1176 | 230 | 946 | 1st Target | 10 | 80.44% | 230 | 946 | 1406 | 21.7 | 247.38 | 71.31% | 13.95% | 57.36%
2018-07-25 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 76 | kBTU | 1649.2 | coleman | mg9s080c16mp11a | 454 | 231 | 223 | 1st Target | 10 | 49.12% | 231 | 223 | 1406 | 21.7 | 247.38 | 27.53% | 14.01% | 13.52%
2018-07-26 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 76 | kBTU | 1649.2 | coleman | mg9s080c16mp11a | 657 | 243 | 414 | 1st Target | 10 | 63.01% | 243 | 414 | 1406 | 21.7 | 247.38 | 39.84% | 14.73% | 25.1%
2018-06-12 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | COLEMEN EVCON | ugab100bua | 300 | 200 | 100 | 1st Target | 10 | 33.33% | 200 | 100 | 1480 | 21.7 | 260.4 | 17.28% | 11.52% | 5.76%
2018-06-13 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | colemen | ugab100bua | 300 | 200 | 100 | 1st Target | 10 | 33.33% | 200 | 100 | 1480 | 21.7 | 260.4 | 17.28% | 11.52% | 5.76%
2018-07-03 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | colemen | 8632786 | 1050 | 225 | 825 | 1st Target | 10 | 78.57% | 225 | 825 | 1480 | 21.7 | 260.4 | 60.48% | 12.96% | 47.52%
2018-07-10 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | colemen | 8632776 | 1350 | 215 | 1135 | 1st Target | 10 | 84.07% | 215 | 1135 | 1480 | 21.7 | 260.4 | 77.76% | 12.38% | 65.38%
2018-07-19 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | ugab100bug | 643 | 254 | 389 | 1st Target | 10 | 60.5% | 254 | 389 | 1480 | 21.7 | 260.4 | 37.04% | 14.63% | 22.41%
2018-07-20 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | ugab100bub | 543 | 254 | 289 | 1st Target | 10 | 53.22% | 254 | 289 | 1480 | 21.7 | 260.4 | 31.28% | 14.63% | 16.65%
2018-07-21 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | TDH2C100A9V4VAC | 543 | 251 | 292 | 1st Target | 10 | 53.78% | 251 | 292 | 1480 | 21.7 | 260.4 | 31.28% | 14.46% | 16.82%
2018-07-02 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 88 | kBTU | 1909.6 | armstrong | mg64-110d2c4 | 950 | 235 | 715 | 1st Target | 10 | 75.26% | 235 | 715 | 1628 | 21.7 | 286.44 | 49.75% | 12.31% | 37.44%
2018-07-24 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 93 | kBTU | 2018.1 | york | phuc20l09201a | 600 | 278 | 322 | 1st Target | 10 | 53.67% | 278 | 322 | 1720.5 | 21.7 | 302.715 | 29.73% | 13.78% | 15.96%
2018-07-19 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 100 | kBTU | 2170 | thermal zone | tz80mss100c50xa | 1128 | 161 | 967 | 1st Target | 10 | 85.73% | 161 | 967 | 1850 | 21.7 | 325.5 | 51.98% | 7.419% | 44.56%
2018-01-03 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | LEAR-SEIGER | lsr-42-1 | 1260 | 173 | 1087 | 1st Target | 17 | 86.27% | 173 | 1087 | 1190 | 400 | 210 | 90% | 12.36% | 77.64%
2018-01-04 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | 8632 | 1200 | 240 | 960 | 1st Target | 15 | 80% | 240 | 960 | 1480 | 21.7 | 260.4 | 69.12% | 13.82% | 55.3%
2018-01-05 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | CARRIER620 | 38ck048300 | 1189 | 209 | 980 | 1st Target | 14 | 82.42% | 209 | 980 | 1360 | 400 | 240 | 74.31% | 13.06% | 61.25%
2018-01-04 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | GOODMAN | CMB04811A | 1540 | 233 | 1307 | 1st Target | 10 | 84.87% | 233 | 1307 | 1360 | 400 | 240 | 96.25% | 14.56% | 81.69%
2018-01-05 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | COLEMAN | BRCQ0481BD | 1226 | 238 | 988 | 1st Target | 12 | 80.59% | 238 | 988 | 1360 | 400 | 240 | 76.62% | 14.88% | 61.75%
2018-01-10 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | TEMPSTAR | N4A548GKC101 | 1348 | 186 | 1162 | 1st Target | 10 | 86.2% | 186 | 1162 | 1360 | 400 | 240 | 84.25% | 11.62% | 72.62%
2018-01-12 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 95 | kBTU | 2061.5 | coleman | mg9s100c20mp11a | 1209 | 275 | 934 | 1st Target | 12 | 77.25% | 275 | 934 | 1757.5 | 21.7 | 309.225 | 58.65% | 13.34% | 45.31%
2018-01-16 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | na | mr5136p1 | 0 | 0 | 0 |  | 10 |  |  |  | 1020 | 400 | 180 | 0% | 0% | 0%
2018-01-18 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | TEMPSTAR | N/A | 1179 | 201 | 978 | 1st Target | 10 | 82.95% | 201 | 978 | 1360 | 400 | 240 | 73.69% | 12.56% | 61.12%
2018-01-19 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | coleman | gcgd48s21s2a | 1230 | 238 | 992 | 1st Target | 12 | 80.65% | 238 | 992 | 1360 | 400 | 240 | 76.88% | 14.88% | 62%
2018-01-10 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | na | 38en048320 | 280 | 238 | 42 | 1st Target | 10 | 15% | 238 | 42 | 1360 | 400 | 240 | 17.5% | 14.88% | 2.625%
2018-01-25 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | N/A | HAC042AKA5 | 345 | 230 | 115 | 1st Target | 1 | 33.33% | 230 | 115 | 1360 | 400 | 240 | 21.56% | 14.37% | 7.187%
2018-02-06 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | goodmanj | gsx140431kc | 600 | 200 | 400 | 1st Target | 10 | 66.67% | 200 | 400 | 1360 | 400 | 240 | 37.5% | 12.5% | 25%
2018-02-06 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | coleman | 9541-901 | 1120 | 165 | 955 | 1st Target | 9 | 85.27% | 165 | 955 | 1360 | 400 | 240 | 70% | 10.31% | 59.69%
2018-02-06 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | coleman | CA5548VKD2 | 1132 | 234 | 898 | 1st Target | 9 | 79.33% | 234 | 898 | 1360 | 400 | 240 | 70.75% | 14.62% | 56.12%
2018-02-07 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | COLEMAN | 9541A801 | 465 | 233 | 232 | 1st Target | 10 | 49.89% | 233 | 232 | 1360 | 400 | 240 | 29.06% | 14.56% | 14.5%
2018-02-08 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | COLEMAN | DRCS0481BE | 1476 | 229 | 1247 | 1st Target | 12 | 84.49% | 229 | 1247 | 1360 | 400 | 240 | 92.25% | 14.31% | 77.94%
2018-02-10 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | RUDD | UALB-048JAZ | 1762 | 233 | 1529 | 1st Target | 11 | 86.78% | 233 | 1529 | 1360 | 400 | 240 |  | 14.56%
2018-02-09 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN | 954-901 | 225 | 159 | 66 | 1st Target | 8 | 29.33% | 159 | 66 | 1020 | 400 | 180 | 18.75% | 13.25% | 5.5%
2018-02-12 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | COLEMAN | TCGD48S21S2A | 1235 | 238 | 997 | 1st Target | 8 | 80.73% | 238 | 997 | 1360 | 400 | 240 | 77.19% | 14.88% | 62.31%
2018-02-14 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 76 | kBTU | 1649.2 | COLEMAN | 8632C636 | 1783 | 222 | 1561 | 1st Target | 10 | 87.55% | 222 | 1561 | 1406 | 21.7 | 247.38 |  | 13.46%
2018-02-28 | Z04 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | AMANA | RCB36A2A | 530 | 120 | 410 | 1st Target | 8 | 77.36% | 120 | 410 | 1020 | 400 | 180 | 44.17% | 10% | 34.17%
2018-01-04 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | 8632 | 1200 | 240 | 960 | 1st Target | 15 | 80% | 240 | 960 | 1480 | 21.7 | 260.4 | 69.12% | 13.82% | 55.3%
2018-01-05 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | CARRIER620 | 38ck048300 | 1189 | 209 | 980 | 1st Target | 14 | 82.42% | 209 | 980 | 1360 | 400 | 240 | 74.31% | 13.06% | 61.25%
2018-01-04 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | GOODMAN | CMB04811A | 1540 | 233 | 1307 | 1st Target | 10 | 84.87% | 233 | 1307 | 1360 | 400 | 240 | 96.25% | 14.56% | 81.69%
2018-01-05 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | COLEMAN | BRCQ0481BD | 1226 | 238 | 988 | 1st Target | 12 | 80.59% | 238 | 988 | 1360 | 400 | 240 | 76.62% | 14.88% | 61.75%
2018-01-10 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | TEMPSTAR | N4A548GKC101 | 1348 | 186 | 1162 | 1st Target | 10 | 86.2% | 186 | 1162 | 1360 | 400 | 240 | 84.25% | 11.62% | 72.62%
2018-01-12 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 95 | kBTU | 2061.5 | coleman | mg9s100c20mp11a | 1209 | 275 | 934 | 1st Target | 12 | 77.25% | 275 | 934 | 1757.5 | 21.7 | 309.225 | 58.65% | 13.34% | 45.31%
2018-01-18 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | TEMPSTAR | N/A | 1179 | 201 | 978 | 1st Target | 10 | 82.95% | 201 | 978 | 1360 | 400 | 240 | 73.69% | 12.56% | 61.12%
2018-01-19 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | coleman | gcgd48s21s2a | 1230 | 238 | 992 | 1st Target | 12 | 80.65% | 238 | 992 | 1360 | 400 | 240 | 76.88% | 14.88% | 62%
2018-01-23 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | COLEMAN | 8748-801 | 431 | 183 | 248 | 1st Target | 10 | 57.54% | 183 | 248 | 1360 | 400 | 240 | 26.94% | 11.44% | 15.5%
2018-03-08 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 95 | kBTU | 2061.5 | coleman | mg9s100c16mp11a | 543 | 300 | 243 | 1st Target | 8 | 44.75% | 300 | 243 | 1757.5 | 21.7 | 309.225 | 26.34% | 14.55% | 11.79%
2018-03-08 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | COLEMAN | 684B801 | 1433 | 208 | 1225 | 1st Target | 7 | 85.48% | 208 | 1225 | 1360 | 400 | 240 | 89.56% | 13% | 76.56%
2018-03-15 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | na | 563cn036d | 1145 | 177 | 968 | 1st Target | 10 | 84.54% | 177 | 968 | 1020 | 400 | 180 | 95.42% | 14.75% | 80.67%
2018-03-21 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | COLEMAN | BRCQ0421BD | 530 | 160 | 370 | 1st Target | 11 | 69.81% | 160 | 370 | 1190 | 400 | 210 | 37.86% | 11.43% | 26.43%
2018-03-28 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | SUMMER AIR | R51-48P1AK9 | 1353 | 233 | 1120 | 1st Target | 14 | 82.78% | 233 | 1120 | 1360 | 400 | 240 | 84.56% | 14.56% | 70%
2018-03-29 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | TRANE | T4A336GKA100 | 340 | 165 | 175 | 1st Target | 10 | 51.47% | 165 | 175 | 1020 | 400 | 180 | 28.33% | 13.75% | 14.58%
2018-03-15 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 64 | kBTU | 1388.8 | na | 8631 | 225 | 198 | 27 | 1st Target | 10 | 12% | 198 | 27 | 1184 | 21.7 | 208.32 | 16.2% | 14.26% | 1.944%
2018-04-23 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | ugab100bub | 651 | 250 | 401 | 1st Target | 7 | 61.6% | 250 | 401 | 1480 | 21.7 | 260.4 | 37.5% | 14.4% | 23.1%
2018-04-05 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | coleman | ck361a | 1002 | 179 | 823 | 1st Target | 10 | 82.14% | 179 | 823 | 1020 | 400 | 180 | 83.5% | 14.92% | 68.58%
2018-05-01 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | COLEMAN | AC042X1021A | 340 | 170 | 170 | 1st Target | 9 | 50% | 170 | 170 | 1190 | 400 | 210 | 24.29% | 12.14% | 12.14%
2018-02-05 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | coleman | drcs0421be | 1000 | 700 | 300 | 1st Target | 9 | 30% | 700 | 300 | 1190 | 400 | 210 | 71.43% | 50% | 21.43%
2018-02-07 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | coleman | 9536-901 | 1180 | 206 | 974 | 1st Target | 9 | 82.54% | 206 | 974 | 1020 | 400 | 180 | 98.33% | 17.17% | 81.17%
2018-02-08 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | coleman | drcs0481be | 1278 | 410 | 868 | 1st Target | 10 | 67.92% | 410 | 868 | 1360 | 400 | 240 | 79.88% | 25.62% | 54.25%
2018-05-08 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | payne | PA10JA042 | 1265 | 386 | 879 | 1st Target | 9 | 69.49% | 386 | 879 | 1190 | 400 | 210 | 90.36% | 27.57% | 62.79%
2018-05-17 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 60 | kBTU | 1302 | COLDEMAN | UGAA075BUG | 1782 | 176 | 1606 | 1st Target | 8 | 90.12% | 176 | 1606 | 1110 | 21.7 | 195.3 |  | 13.52%
2018-05-17 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | coleman | ercs0481ca | 1082 | 238 | 844 | 1st Target | 10 | 78% | 238 | 844 | 1360 | 400 | 240 | 67.62% | 14.88% | 52.75%
2018-05-18 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | 8632776 | 654 | 234 | 420 | 1st Target | 10 | 64.22% | 234 | 420 | 1480 | 21.7 | 260.4 | 37.67% | 13.48% | 24.19%
2018-05-30 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | coleman | drcs0481bd | 1019 | 231 | 788 | 1st Target | 10 | 77.33% | 231 | 788 | 1360 | 400 | 240 | 63.69% | 14.44% | 49.25%
2018-05-31 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | RHEEM | RAKA-048JAZ | 837 | 201 | 636 | 1st Target | 10 | 75.99% | 201 | 636 | 1360 | 400 | 240 | 52.31% | 12.56% | 39.75%
2018-05-03 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | RHEEM | RACC048JAS | 405 | 213 | 192 | 1st Target | 8 | 47.41% | 213 | 192 | 1360 | 400 | 240 | 25.31% | 13.31% | 12%
2018-05-09 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN | BRCS0361BB | 283 | 161 | 122 | 1st Target | 8 | 43.11% | 161 | 122 | 1020 | 400 | 180 | 23.58% | 13.42% | 10.17%
2018-07-06 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | goodman | drcs0481be | 931 | 191 | 740 | 1st Target | 10 | 79.48% | 191 | 740 | 1360 | 400 | 240 | 58.19% | 11.94% | 46.25%
2018-07-10 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 76 | kBTU | 1649.2 | coleman | m9s080c16mp11a | 350 | 220 | 130 | 1st Target | 12 | 37.14% | 220 | 130 | 1406 | 21.7 | 247.38 | 21.22% | 13.34% | 7.883%
2018-07-11 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | goodman | gsx130361ba | 300 | 165 | 135 | 1st Target | 6 | 45% | 165 | 135 | 1020 | 400 | 180 | 25% | 13.75% | 11.25%
2018-07-12 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN/ EVCONn | CN36IT6MRSS | 184 | 148 | 36 | 1st Target | 10 | 19.57% | 148 | 36 | 1020 | 400 | 180 | 15.33% | 12.33% | 3%
2018-07-12 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | 8632 | 350 | 200 | 150 | 1st Target | 8 | 42.86% | 200 | 150 | 1480 | 21.7 | 260.4 | 20.16% | 11.52% | 8.641%
2018-07-12 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN/ EVCON | 6716477 | 210 | 168 | 42 | 1st Target | 10 | 20% | 168 | 42 | 1020 | 400 | 180 | 17.5% | 14% | 3.5%
2018-07-13 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN/ EVCON | ugb100bua | 190 | 155 | 35 | 1st Target | 10 | 18.42% | 155 | 35 | 1020 | 400 | 180 | 15.83% | 12.92% | 2.917%
2018-07-16 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | coleman | brcs0421bd | 400 | 165 | 235 | 1st Target | 8 | 58.75% | 165 | 235 | 1020 | 400 | 180 | 33.33% | 13.75% | 19.58%
2018-07-24 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | PG9MABO24060ACSA | 350 | 180 | 170 | 1st Target | 10 | 48.57% | 180 | 170 | 1480 | 21.7 | 260.4 | 20.16% | 10.37% | 9.793%
2018-07-16 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | EVCONTD | DGAA077BDWOK9212393 | 196 | 156 | 40 | 1st Target | 10 | 20.41% | 156 | 40 | 1020 | 400 | 180 | 16.33% | 13% | 3.333%
2018-07-25 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 88 | kBTU | 1909.6 | ARMSTRONG | MG64110D | 350 | 200 | 150 | 1st Target | 8 | 42.86% | 200 | 150 | 1628 | 21.7 | 286.44 | 18.33% | 10.47% | 7.855%
2018-07-24 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 60 | kBTU | 1302 | COLEMAN | UGAA075BUA | 350 | 180 | 170 | 1st Target | 8 | 48.57% | 180 | 170 | 1110 | 21.7 | 195.3 | 26.88% | 13.82% | 13.06%
2018-07-20 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | capf4860c6db | 350 | 200 | 150 | 1st Target | 8 | 42.86% | 200 | 150 | 1480 | 21.7 | 260.4 | 20.16% | 11.52% | 8.641%
2018-07-18 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | INTERNATIO NAL COMFORT | end4x36l17a1 | 295 | 107 | 188 | 1st Target | 17 | 63.73% | 107 | 188 | 1020 | 400 | 180 | 24.58% | 8.917% | 15.67%
2018-07-18 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN | H1RA042S06D | 300 | 170 | 130 | 1st Target | 8 | 43.33% | 170 | 130 | 1020 | 400 | 180 | 25% | 14.17% | 10.83%
2018-07-19 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN PRESITENTIAL II | 6285b901 | 276 | 119 | 157 | 1st Target | 10 | 56.88% | 119 | 157 | 1020 | 400 | 180 | 23% | 9.917% | 13.08%
2018-07-19 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | coleman | 8631 | 296 | 107 | 189 | 1st Target | 10 | 63.85% | 107 | 189 | 1020 | 400 | 180 | 24.67% | 8.917% | 15.75%
2018-07-23 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | RUUD | ra143owj1na | 350 | 195 | 155 | 1st Target | 9 | 44.29% | 195 | 155 | 1190 | 400 | 210 | 25% | 13.93% | 11.07%
2018-07-23 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 88 | kBTU | 1909.6 | ARMSTRONG | MG64110DSC | 350 | 200 | 150 | 1st Target | 8 | 42.86% | 200 | 150 | 1628 | 21.7 | 286.44 | 18.33% | 10.47% | 7.855%
2018-07-24 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | unk | brcs0481bd | 300 | 170 | 130 | 1st Target | 6 | 43.33% | 170 | 130 | 1020 | 400 | 180 | 25% | 14.17% | 10.83%
2018-07-25 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | COLEMAN | UGAB1009BUA | 350 | 180 | 170 | 1st Target | 8 | 48.57% | 180 | 170 | 1480 | 21.7 | 260.4 | 20.16% | 10.37% | 9.793%
2018-07-27 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | COLEMAN | BRCS0421BB | 1231 | 207 | 1024 | 1st Target | 9 | 83.18% | 207 | 1024 | 1190 | 400 | 210 | 87.93% | 14.79% | 73.14%
2018-07-27 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | york | phuc20n08001a | 760 | 243 | 517 | 1st Target | 10 | 68.03% | 243 | 517 | 1480 | 21.7 | 260.4 | 43.78% | 14% | 29.78%
2018-07-26 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | unk | n4a342aka300 | 350 | 170 | 180 | 1st Target | 8 | 51.43% | 170 | 180 | 1020 | 400 | 180 | 29.17% | 14.17% | 15%
2018-07-26 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | coleman | 95414801 | 423 | 117 | 306 | 1st Target | 10 | 72.34% | 117 | 306 | 1020 | 400 | 180 | 35.25% | 9.75% | 25.5%
2018-07-26 | Z02 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | COLEMAN/ EVCON | 6856-9 | 387 | 110 | 277 | 1st Target | 10 | 71.58% | 110 | 277 | 1020 | 400 | 180 | 32.25% | 9.167% | 23.08%
2018-07-27 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 95 | kBTU | 2061.5 | york | 8632c726 | 765 | 287 | 478 | 1st Target | 10 | 62.48% | 287 | 478 | 1757.5 | 21.7 | 309.225 | 37.11% | 13.92% | 23.19%
2018-07-27 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 90 | kBTU | 1953 | TRANE | TUX1C100A9481AB | 350 | 250 | 100 | 1st Target | 8 | 28.57% | 250 | 100 | 1665 | 21.7 | 292.95 | 17.92% | 12.8% | 5.12%
2018-07-27 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 60 | kBTU | 1302 | COLEMAN/ EVCON | BGH07512AX | 250 | 180 | 70 | 1st Target | 10 | 28% | 180 | 70 | 1110 | 21.7 | 195.3 | 19.2% | 13.82% | 5.376%
2018-07-28 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | trane | gsx140431kd | 350 | 170 | 180 | 1st Target | 9 | 51.43% | 170 | 180 | 1020 | 400 | 180 | 29.17% | 14.17% | 15%
2018-07-28 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 64 | kBTU | 1388.8 | coleman | 8638776 | 522 | 200 | 322 | 1st Target | 10 | 61.69% | 200 | 322 | 1184 | 21.7 | 208.32 | 37.59% | 14.4% | 23.19%
2018-07-30 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 64 | kBTU | 1388.8 | coleman | mg6680d2c | 865 | 200 | 665 | 1st Target | 10 | 76.88% | 200 | 665 | 1184 | 21.7 | 208.32 | 62.28% | 14.4% | 47.88%
2018-07-31 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 64 | kBTU | 1388.8 | coleman | mg6680d2c42 | 645 | 198 | 447 | 1st Target | 10 | 69.3% | 198 | 447 | 1184 | 21.7 | 208.32 | 46.44% | 14.26% | 32.19%
2018-07-31 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 60 | kBTU | 1302 | coleman | ugab075bua | 654 | 190 | 464 | 1st Target | 10 | 70.95% | 190 | 464 | 1110 | 21.7 | 195.3 | 50.23% | 14.59% | 35.64%
2018-07-20 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3.5 | Ton | 1400 | colemen | 8632A-776 | 1127 | 180 | 947 | 1st Target | 10 | 84.03% | 180 | 947 | 1190 | 400 | 210 | 80.5% | 12.86% | 67.64%
2018-07-20 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 3 | Ton | 1200 | colemen | ugab075buh | 1123 | 168 | 955 | 1st Target | 10 | 85.04% | 168 | 955 | 1020 | 400 | 180 | 93.58% | 14% | 79.58%
2018-07-25 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4 | Ton | 1600 | york | p4hub16n06401a | 1080 | 214 | 866 | 1st Target | 10 | 80.19% | 214 | 866 | 1360 | 400 | 240 | 67.5% | 13.38% | 54.12%
2018-07-18 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 2.5 | Ton | 1000 | INTERTHEM | ufc-01 | 1137 | 136 | 1001 | 1st Target | 10 | 88.04% | 136 | 1001 | 850 | 400 | 150 |  | 13.6%
2018-07-19 | Z13 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 100 | kBTU | 2170 | thermal zone | tz80mss100c50xa | 1128 | 161 | 967 | 1st Target | 10 | 85.73% | 161 | 967 | 1850 | 21.7 | 325.5 | 51.98% | 7.419% | 44.56%
2018-05-11 | Z12 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 100 | kBTU | 2170 | evcon | UGAB100BUA | 350 | 300 | 50 | 1st Target | 10 | 14.29% | 300 | 50 | 1850 | 21.7 | 325.5 | 16.13% | 13.82% | 2.304%
2018-06-05 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | ugab100buh | 900 | 341 | 559 | 2nd Target | 8 | 62.11% | 341 | 559 | 1480 | 21.7 | 260.4 | 51.84% | 19.64% | 32.2%
2018-06-06 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 45 | kBTU | 976.5 | intertherm | e288746 | 306 | 60 | 246 | 1st Target | 5 | 80.39% | 60 | 246 | 832.5 | 21.7 | 146.475 | 31.34% | 6.144% | 25.19%
2018-06-14 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 80 | kBTU | 1736 | coleman | ub100bub | 401 | 180 | 221 | 1st Target | 8 | 55.11% | 180 | 221 | 1480 | 21.7 | 260.4 | 23.1% | 10.37% | 12.73%
2018-06-19 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 60 | kBTU | 1302 | coleman | ugaa075bua | 350 | 98 | 252 | 1st Target | 8 | 72% | 98 | 252 | 1110 | 21.7 | 195.3 | 26.88% | 7.527% | 19.35%
2018-06-12 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 4.5 | Ton | 1800 | coleman | 9541c901 | 380 | 150 | 230 | 1st Target | 8 | 60.53% | 150 | 230 | 1530 | 400 | 270 | 21.11% | 8.333% | 12.78%
2018-06-13 | Z03 | Return Retrofit ( New Return Installed Yes=1, No=0 ) | 1 | 88 | kBTU | 1909.6 | coleman | mg64-110d2c | 400 | 120 | 280 | 1st Target | 12 | 70% | 120 | 280 | 1628 | 21.7 | 286.44 | 20.95% | 6.284% | 14.66%
|  |  | 143 | [5 empty] | 115676 | 29356 | 86420