CPUC Comments on SWWH016-02: Domestic Hot Water Loop Temperature Controller, Multifamily and Commercial

Lead PA: SCG

Workpaper Submittal Date: 09/03/2020

| CPUC Comment | PA Response |
| --- | --- |
| Test case for transition from eQuest to Open Studio: this issue was not addressed. | CPUC provided the source for “Test case for transition from eQuest to OpenStudio”. The presentation file identified issues, plans, and notes for the consolidation of all statewide workpapers in Feb 2019. This note about “transition to OpenStudio” in the file was only a potential option to be considered for calculation update. The actual analysis for addition of commercial building types utilized eQuest modeling and DEER prototypes as noted in the workpaper update plan submitted (5/1/2020). |
| Some facilities require 140F water to avoid any Legionnaire issues (Nursing Homes). Please address this in the workpaper. | To address the concern for Legionnaires’ disease, SCG will update and resubmit the workpaper with additional limitations for the implementation of the measure and exclude facilities that must keep boiler temperature set to 140 deg F. OSHA Technical Manual suggests hot water to be stored at 140 deg. F and recirculation pump to run continuously to minimize the growth in the system (Link). Data shows that the temperature modulated up to 140 at least for an hour on a daily basis can kill the Legionella bacteria. While temperature is one control strategy, it can also be combined with other prevention strategies. Facilities can also use chemical (chlorine) or UV disinfection for high risk applications. Local, state, and federal regulations must be followed to determine the applicability of this energy efficiency measure to avoid the risk of Legionella growth and scalding. |

CPUC Review Date: 09/22/2020

Please note responses to comments in the table below, revise workpaper, and upload the entire package to the WPA. If needed, please reach out to Workpaper Review Team to set up a call to discuss.