## Survey site 1
Southern California Gas Company Hot Water Survey
Survey Site |  |  | 1
Property Name |  |  | Hotel 1
Property Address |  |  | N/A
Facility Information
|  | Building type | Hotel (4 level w/ basement garage)
|  | Estimate of sq. ft. / Year built | 74,360 sq. ft. / 1982
|  | Avg. Occupancy Rate | 85%
| Number of bathrooms |  | 82
| Number of Kitchens |  | 1
| Number of rooms |  | 80
| Water heater informations |  | heater 1 | heater 2 | heater 3 | heater 4 (laundry only) | heater 5 (laundry only)
|  | Type | Bradford White | Rinnai Corporation | Rinnai Corporation | Rheem | Bradford White
|  | Model | UCG100H2703N | RL94e (HA.CA-004999) | RL94e (GG.CA-073213) | SG60T12YXS10 | 100T88B3N
|  | Efficiency | 82% | 82% | 82% | 80% | 80%
|  | Input rating | 270,000 BTU/HR | 199,000 BTU/HR | 199,000 BTU/HR | 45,000 BTU/HR | 85,000 BTU/HR
|  | Age | 2014 | 2015 | 2016 | 2012 | 2011
|  | Temperature set point | 178F
Faucets (Guest Room)
|  | Number of | 80
|  | Type | double handle
|  | Location | bathroom
|  | Presence of low flow devices(Y/N) | Y
Public restroom faucet
|  | Number of | 2
|  | Type | single/double handle
|  | Location | lobby
|  | Presence of low flow devices(Y/N) | N
Kitchen faucets
|  | Number of | 3
|  | Type | double handle
|  | Location | kitchen
|  | Presence of low flow devices(Y/N) | N
Showerheads
|  | Number of | 80
|  | Type | single handle
|  | Location | guest room
|  | Presence of low flow devices(Y/N) | unknown
| Pre-rinse spray valves | [6 empty] | 1 mL | = | 0.00026417 | gal
|  | Number of | 1 |  |  |  |  | 1 min | = | 60 | s
|  | Type | single handle
|  | Location | kitchen
|  | Presence of low flow devices(Y/N) | unknown |  |  |  |  | Fixture Flow Rates (GPM)
| Flowrate of Fixtures |  | fix. 1 (Rm No. 205/sink) | fix. 2 (Rm No. 205/shower) | fix. 3 (Lobby Men's/sink no.1) | fix. 4 (Lobby Men's/sink no.2) |  |  | Fix. 1 (guest room sink) | Fix. 2 (showerhead) | Fix. 3 (restroom sink) | Fix. 4 (restroom sink) | Fix. 5 (kitchen sink) | Fix. 6 (kitchen sink) | Fix. 7 (kitchen pre-rinse spray)
|  | Max flow rate hot water | 8.71 sec (250ml) | 11.22 sec (2000ml) | 8.66 sec (2000ml) | 19.91 sec (2000ml) |  | Max hot | 0.45 | 2.83 | 3.66 | 1.59 | 6.98 | 7.53 | 1.98
|  | Max flow rate cold water | 8.38 sec (250ml) | 9.97 sec (2000ml) | 11.78 sec (2000ml) | 21.12 sec (2000ml) |  | Max cold | 0.47 | 3.18 | 2.69 | 1.5 | 8.76 | 8.52
| Temperature of water | [6 empty] | Average | 0.46 | 3.005 | 3.175 | 1.545 | 7.87 | 8.025 | 1.98
|  | Time takes to reach hot tempeture | 24.6 sec ("dry" start) |  | 18.09 sec ("dry start) | 4.32 sec ("run" start)
|  | Hot water temp coming out of faucet | 142F | 145.3F | 130.2F | 131.1F
|  | Cold water temp coming out of faucet | 73.5F | 73.2F | 72.8F | 72.6F |  |  |  | 47.09%
|  |  | fix. 5 (Kitchen/sink no.1) | fix. 6 (Kitchen/sink no. 2) | fix. 7 (Kitchen/pre-rinse spray)
|  | Max flow rate hot water | 4.54 sec (2000ml) | 4.21 sec (2000ml) | 16.03 sec (2000ml); single handle spray (hot & cold)
|  | Max flow rate cold water | 3.62 sec (2000ml) | 3.72 sec (2000ml)
|  | Time to reach hot temperature | 16.81 sec ("dry" start) | 19.32 sec ("dry" start)
|  | Hot water temp coming out of faucet | 130.1F | 129.4F
|  | Cold water temp coming out of faucet | 71.8F | 71.5F

## Survey site 2
Southern California Gas Company Hot Water Survey
Survey Site |  |  | 2
Property Name |  |  | Hotel 2
Property Address |  |  | N/A
Facility Information
|  | Building type | Motel (2 level)
|  | Estimate of sq. ft. / Year built | 22,194 sq.ft. / 1970's
|  | Avg, Occupancy Rate | 80%
| Number of bathrooms |  | 61
| Number of Kitchens |  | 0
| Number of rooms |  | 60
| Water heater informations |  | heater 1 | heater 2 | heater 3 (laundry only) | heater 4
|  | Type | Rheem | American Water Heater | Rheem
|  | Model | G100UN | BCN3100T754NV 100 | G100UN
|  | Efficiency | 80% | 80% | 80%
|  | Input rating | 75,100 BTU/HR | 75,100 BTU/HR | 75,100 BTU/HR
|  | Age | 2014 | 2013 | 2014
|  | Temperature set point | 155F | 155F | 145F
Faucets (Guest Room)
|  | Number of | 60 |  | 60
|  | Type | double handle |  | double handle
|  | Location | bathroom |  | bathroom
|  | Presence of low flow devices(Y/N) | N |  | N
Public restroom faucet
|  | Number of | 0 |  | 0
Type
Location
Presence of low flow devices(Y/N)
Kitchen faucets
|  | Number of | 0 |  | 0
Type
Location
Presence of low flow devices(Y/N)
Showerheads
|  | Number of | 60 |  | 60
|  | Type | single handle |  | single handle
|  | Location | guest room |  | guest room
|  | Presence of low flow devices(Y/N) | unknown |  | unknown
| Pre-rinse spray valves | [5 empty] | 1 mL | = | 0.00026417 | gal
|  | Number of | 0 |  | 0 |  | 1 min | = | 60 | s
Type
Location
|  | Presence of low flow devices(Y/N) |  |  |  |  | Fixture Flow Rates (GPM)
| Flowrate of Fixtures |  | fix. 1 (Rm No. 116/sink) | fix. 2 (Rm No. 116/showerhead) | fix. 3 (Rm No. 116/tub faucet) | fixture 4 |  | Fix. 1 (guest room sink) | Fix. 2 (showerhead) | Fix. 3 (tub faucet)
|  | Max flow rate hot water | 2.84 sec (250ml) | 12.75 sec (2000ml) | 3.47 sec (2000ml) |  | Max hot | 1.4 | 2.49 | 9.14
|  | Max flow rate cold water | 1.5 sec (250ml) | 13.16 sec (2000ml) | 3.53 sec (2000ml) |  | Max cold | 2.64 | 2.41 | 8.98
| Temperature of water | [5 empty] | Average | 2.02 | 2.45 | 9.06
|  | Time takes to reach hot tempeture | 28.65 sec ("dry" start) |  | 28.65 sec ("dry" start)
|  | Hot water temp coming out of faucet | 138.2F | 137.8F | 138F
|  | Cold water temp coming out of faucet | 75.1F | 76F | 75.8F |  |  |  | 50.82%

## Survey site 3
Southern California Gas Company Hot Water Survey
Survey Site |  |  | 3
Property Name |  |  | Hotel 3
Property Address |  |  | N/A
Facility Information
|  | Building type | Motel (2 level)
|  | Estimate of sq. ft. / Year built | 22,080 sq.ft. / 1970's
|  | Avg. Occupancy Rate | 80%
| Number of bathrooms |  | 36
| Number of Kitchens |  | 0
| Number of rooms |  | 35
| Water heater informations |  | heater 1 | heater 2 | heater 3 (laundry only) | heater 4
|  | Type | AO Smith | AO Smith | Bradford White
|  | Model | BTL 199 200 | BTN 200 108 | U100T88R3N
|  | Efficiency | 80% | 80% | 80%
|  | Input rating | 199,000 BTU/HR | 199,000 BTU/HR | 85,000 BTU/HR
|  | Age | 2016 | 2009 | 2013
|  | Temperature set point | 140F | 140F | 140F
Faucets (Guest Room)
|  | Number of | 70
|  | Type | double handle
|  | Location | bathroom
|  | Presence of low flow devices(Y/N) | Y and N
Public restroom faucet
|  | Number of | 0
Type
Location
Presence of low flow devices(Y/N)
Kitchen faucets
|  | Number of | 0
Type
Location
Presence of low flow devices(Y/N)
Showerheads
|  | Number of | 35
|  | Type | single handle
|  | Location | guest bathroom
|  | Presence of low flow devices(Y/N) | unknown
| Pre-rinse spray valves | [5 empty] | 1 mL | = | 0.00026417 | gal
|  | Number of | 0 |  |  |  | 1 min | = | 60 | s
Type
Location
|  | Presence of low flow devices(Y/N) |  |  |  |  | Fixture Flow Rates (GPM)
| Flowrate of Fixtures |  | fix. 1 (Guest Rm/sink no.1) | fix. 2 (Rm No. 101/sink no. 2) | fix. 3 (Rm No. 101/Tub faucet) | fix. 4 (Rm No. 101/Showerhead) |  | Fix. 1 (guest room sink) | Fix. 2 (guest room sink) | Fix. 3 (tub faucet) | Fix. 4 (showerhead)
|  | Max flow rate hot water | 2.10 sec (250ml) | 1.72 sec (250ml) | 6.23 sec (2000ml) | 14.75 sec (2000ml); max rate | Max hot | 1.89 | 2.3 | 5.09 | 2.15
|  | Max flow rate cold water | 2.03 sec (250ml) | 1,35 sec (250ml) | 6.10 sec (2000ml) |  | Max cold | 1.95 | 2.94 | 5.2
| Temperature of water | [5 empty] | Average | 1.92 | 2.62 | 5.145
|  | Time takes to reach hot tempeture | 35.8 sec ("dry" start)
|  | Hot water temp coming out of faucet | 128.2F | 128.8F | 129.1F | 129F
|  | Cold water temp coming out of faucet | 70.4F | 71F | 71.3F | 71.6F

## Survey site 4
Southern California Gas Company Hot Water Survey
Survey Site |  |  | 4
Property Name |  |  | Hotel 4
Property Address |  |  | N/A
Facility Information
|  | Building type | Hotel (3 level)
|  | Estimate of sq. ft. / Year built | 68,885 sq.ft. / 1987
|  | Avg. Occupancy Rate | 80%
| Number of bathrooms |  | 146
| Number of Kitchens |  | 1 (not in use)
| Number of rooms |  | 140
| Water heater informations |  | heater 1 | heater 2 | heater 3 | heater 4
|  | Type | Raypack Hi Delta Water Heater | Raypack Raytherm Water Heater
|  | Model | W9-1802 | W2-0824
|  | Efficiency | 85% | 82%
|  | Input rating | 1,800,000 BTU/HR | 825,000 BTU/HR
|  | Age | 2000 | 1997
Temperature set point
Faucets (Guest Room)
|  | Number of | 140
|  | Type | single handle
|  | Location | bathroom
|  | Presence of low flow devices(Y/N) | Y
Public restroom faucet
|  | Number of | 3
|  | Type | double handle
|  | Location | lobby areas
|  | Presence of low flow devices(Y/N) | Y
Kitchen faucets
|  | Number of | 0
Type
Location
Presence of low flow devices(Y/N)
Showerheads
|  | Number of | 140
|  | Type | single handle
|  | Location | bathroom
|  | Presence of low flow devices(Y/N) | unknown
| Pre-rinse spray valves | [5 empty] | 1 mL | = | 0.00026417 | gal
|  | Number of | 0 |  |  |  | 1 min | = | 60 | s
Type
Location
|  | Presence of low flow devices(Y/N) |  |  |  |  | Fixture Flow Rates (GPM)
| Flowrate of Fixtures |  | fix. 1 (Rm No. 131/sink) | fix. 2 (Rm No. 131/Tub faucet) | fix. 3 (Rm No. 131/showerhead) | fix. 4 (Lobby Men's/sink) |  | Fix. 1 (guest room sink) | Fix. 2 (tub faucet) | Fix. 3 (showerhead) | Fix. 4 (restroom sink)
|  | Max flow rate hot water | 2.67 sec (250ml) | 7.81 sec (2000ml) | 14.81 sec (2000ml) | 1.91 sec (250ml) | Max hot | 1.48 | 4.06 | 2.14 | 2.07
|  | Max flow rate cold water | 2.65 sec (250ml) | 8.31 sec (2000ml) | 13.41 sec (2000ml) | 1.83 sec (250ml) | Max cold | 1.5 | 3.81 | 2.36 | 2.17
| Temperature of water | [5 empty] | Average | 1.49 | 3.935 | 2.25 | 2.12
|  | Time takes to reach hot tempeture | 17.8 sec ("dry" start)
|  | Hot water temp coming out of faucet | 124.3F | 124.1F | 123.9F | 125.2F
|  | Cold water temp coming out of faucet | 72.7F | 72.9F | 73F | 72.9F |  |  |  | 47.56%

## Survey site 5
Southern California Gas Company Hot Water Survey
Survey Site |  |  | 5
Property Name |  |  | Hotel 5
Property Address |  |  | N/A
Facility Information
|  | Building type | Hotel (2 level)
|  | Estimate of sq. ft. / Year built | 37,000 sq.ft. / 1970
|  | Avg. Occupancy Rate | 85%
| Number of bathrooms |  | 87
| Number of Kitchens |  | 0
| Number of rooms |  | 86
| Water heater informations |  | heater 1 | heater 2 (laundry only) | heater 3 | heater 4
|  | Type | Raypak | Rheem
|  | Model | WH1-0401 | G76-180
|  | Efficiency | 82% | 80%
|  | Input rating | 399,000 BTU/HR | 180,000 BTU/HR
|  | Age | 2007 | 2011
|  | Temperature set point |  | 135F
Faucets (Guest Room)
|  | Number of | 86
|  | Type | single handle
|  | Location | bathroom
|  | Presence of low flow devices(Y/N) | Y
Public restroom faucet
|  | Number of | 1
|  | Type | single handle
|  | Location | Lobby
|  | Presence of low flow devices(Y/N) | unknown
Kitchen faucets
|  | Number of | 0
Type
Location
Presence of low flow devices(Y/N)
Showerheads
|  | Number of | 86
|  | Type | single handle
|  | Location | guestroom
|  | Presence of low flow devices(Y/N) | unknown
| Pre-rinse spray valves | [5 empty] | 1 mL | = | 0.00026417 | gal
|  | Number of | 0 |  |  |  | 1 min | = | 60 | s
Type
Location
|  | Presence of low flow devices(Y/N) |  |  |  |  | Fixture Flow Rates (GPM)
| Flowrate of Fixtures |  | fix. 1 (Rm No. 104/sink) | fix. 2 (Rm No. 104/tub faucet) | fix. 3 (Rm No. 104/showerhead) | fix. 4 (Lobby Restroom/sink) |  | Fix. 1 (guest room sink) | Fix. 2 (tub faucet) | Fix. 3 (showerhead) | Fix. 4 (restroom sink)
|  | Max flow rate hot water | 1.81 sec (250ml) | 6.10 sec (2000ml) | 12.50 sec (2000ml) | 1.94 sec (250ml) | Max hot | 2.19 | 5.2 | 2.54 | 2.04
|  | Max flow rate cold water | 1.78 sec (250ml) | 7.72 sec (2000ml) | 12.29 sec (2000ml) | 1.62 sec (250ml) | Max cold | 2.23 | 4.11 | 2.58 | 2.45
| Temperature of water | [5 empty] | Average | 2.21 | 4.655 | 2.56 | 2.245
|  | Time takes to reach hot tempeture | 6.85 sec ("run" start)
|  | Hot water temp coming out of faucet | 124.1F | 123.9F | 124F | 87.4F
|  | Cold water temp coming out of faucet | 70.6F | 71.3F | 71.1F | 68.5F |  |  |  | 49.61%