## Summary
[16 empty] | cost cap fraction | 50%
Application Submitted Amounts
Measure ID | Measure Description | Measure Code | Incentive Rates |  |  | Savings |  |  | Incentives |  |  | Measure Cost | Measure Cost Adj. | Total Incentive | Comments
|  |  | Demand ($/kW) | Energy ($/kWh) | Gas ($/therm) | Demand (kW) | Energy (kWh) | Gas (therms) | Demand Reduction | Energy Savings | Gas Savings
1 | Bio-Therm Commercial Dryer Modulation Retrofit | CPL50 | 150 | 0.08 | 1 | 0 | 0 | 3846.1528 | 0 | 0 | 3846.1528 | 4100 | 1796.1528 | 2050
Total | [5 empty] | 0 | 0 | 3846.1528 | 0 | 0 | 3846.1528 | 4100 | 1796.1528 | 2050
Gas Summary
|  | 15056.6099 | Baseline energy consumption (Therms)
|  | 232773 | 12-month total site use (Therms)
|  | 6.468% | Baseline energy use as percentage of 12-month total site use
|  | 25.54% | Energy savings as percentage of baseline energy use

## Energy Savings Calc
System Specifications | Dryer #1 | Dryer #2 | Notes
High Fire Rate/BTU Input (BTU/hr) | 370000 | 300000 | Nameplate
High Fire Gas Manifold Pressure (in w.c.) | 2.5 | 2.5 | Spot measurement
Low Fire Gas Manifold Pressure (in w.c.) | 1.1 | 1.1 | Spot measurement
Avg time per dry cycle (Hrs) | 0.54656 | 0.69768 | Based on 3-weeks data logging (5/15/2015 - 6/5/2015) ON/OFF state of dryer drum motor
Low Fire Rate (BTU/hr) | 245430.2345 | 198997.4874 | Calculated from gas manifold pressure reduction, see 'Low Fire Calculation' tab
Dryer cycles per yr | 5754.6667 | 5546.6667 | Based on 3-weeks data logging (5/15/2015 - 6/5/2015) ON/OFF state of dryer drum motor
Baseline
High Fire Burner ON % | 64.77% | 64.77% | Short term test result, back-calculated to compare same amount of moisture removed as proposed case
Low Fire Burner ON % | 0% | 0% | No modulation
Natural Gas Usage (Therms/yr) | 7537.4636 | 7519.1463 | Therms/yr = (BTU/hr)*(Burner hrs ON/cycle)*(Cycles/yr)*(1 Therm/100,000 BTU)
Proposed
High Fire Burner ON % | 16.95% | 16.95% | Short term test result
Low Fire Burner ON % | 47.14% | 47.14% | Short term test result
Natural Gas Usage (Therms/yr) | 5612.0476 | 5598.4095 | Therms/yr = (BTU/hr)*(Burner hrs ON/cycle)*(Cycles/yr)*(1 Therm/100,000 BTU)
Savings
Natural Gas Savings (Therms/yr) | 1925.4159 | 1920.7369 | Baseline Gas Usage - Proposed Gas Usage

## Short Term Test
PG&E Hilton Field Test | Baseline Measurements | BiO-Therm Measurements
High Fire Time Seconds | 1184 | 356
Low Fire Time Seconds | 0 | 990
Total Burner Time | 1184 | 1346
Dryer Run Time | 30 | 30
Dryer Cool Down | 5 | 5
Load Weight Wet | 77.6 | 77.3
Load Weight Dry | 65.5 | 63.4
Load Weight Difference | 12.1 | 13.9
High Fire Rate | 370000 | 370000
High Fire BTUs Per Second | 102.7778 | 102.7778
Low Fire Rate | 0 | 245430.2345
Low Fire BTUs Per Second | 0 | 68.1751
Gas Used BTUs | 121688.8889 | 104082.2034
% Fuel Reduction | 0 | 14.47%
BTUs Per Load Saved | 0 | 17606.6855
BTUs Per Pound Extracted | 10056.933 | 7487.9283
BTUs Per Pound Difference | 0 | 25.54%
Equivalent High Fire Time Seconds (to achieve same amount of moisture removed as proposed case) | 1360.1322
A short term test was conducted where the exact same load of laundry was washed and dried twice, once in baseline dryer mode and once in modulating dryer mode. Although the load was washed in the exact same washer there is still some variance in the moisture content of the clothes between each drying. This was accounted for by measuring the Btus of gas used per lb of moisture removed during the drying process. The clothes were weighed before and after drying for each mode.

## Low Fire Analysis
Dryer #1
Fill Out Green Cells To Find Low Firing Rate
High Fire Rate BTU/Hr | 370000 | Example - 395000
Low Fire Rate Maifold Pressure (WC) | 1.1 | Example - 1.4
High Fire Rate Maifold Pressure (WC) | 2.5 | Example - 3.5
Your Low Firing Rate = | 245430.2345 | -33.67%
EZ-Efficiency Low Fire Calculator
Dryer #2
Fill Out Green Cells To Find Low Firing Rate
High Fire Rate BTU/Hr | 300000 | Example - 395000
Low Fire Rate Maifold Pressure (WC) | 1.1 | Example - 1.4
High Fire Rate Maifold Pressure (WC) | 2.5 | Example - 3.5
Your Low Firing Rate = | 198997.4874 | -33.67%
EZ-Efficiency Low Fire Calculator
In baseline mode the gas usage was calculated by monitoring the dryer gas valve on time with a current switch and multiplying by the nameplate (high) firing rate of the dryer. For the modulating dryer valve both the high fire and low fire on times were monitored with separate current switches. The low firing rate was determined by measuring the manifold pressure setting of the gas valve with a digital manometer and using the following flow calculation:
New (Low) Firing Rate (Btu/hr) QN = QO * √ ( PN/PO)
Where QN = Low Firing Rate (Btu/hr)
QO = High Firing Rate (Btu/hr)
√ = Square Root
PN = Low Firing Rate Manifold Pressure (inch water column – “WC)
PO = High Firing Rate Manifold Pressure (inch water column – “WC)

## Motor Logger Analysis
|  | Dryer #1 | Dryer #2
| Average cycle time | 0:33 | 0:42
| Total drying time | 181:28 | 223:15
| Average cycles during this period | 332 | 320
Plot Title: 19040 |  |  |  | Plot Title: 19042
# | Date Time, GMT-07:00 | Motor (LGR S/N: 10348430, SEN S/N: 10348430) | Time Interval (min) | # | Date Time, GMT-07:00 | Motor (LGR S/N: 10348432, SEN S/N: 10348432) | Time Interval (min)
1 | 2015-05-15 17:00 | 0 |  | 1 | 2015-05-15 17:00 | 1 | 0:47
2 | 2015-05-15 17:04 | 1 | 0:33 | 2 | 2015-05-15 17:47 | 0
3 | 2015-05-15 17:37 | 0 |  | 3 | 2015-05-15 18:03 | 1 | 0:47
4 | 2015-05-15 18:06 | 1 | 0:36 | 4 | 2015-05-15 18:50 | 0
5 | 2015-05-15 18:42 | 0 |  | 5 | 2015-05-15 18:53 | 1 | 0:54
6 | 2015-05-15 18:59 | 1 | 0:33 | 6 | 2015-05-15 19:47 | 0
7 | 2015-05-15 19:33 | 0 |  | 7 | 2015-05-15 21:08 | 1 | 0:41
8 | 2015-05-15 19:45 | 1 | 0:38 | 8 | 2015-05-15 21:49 | 0
9 | 2015-05-15 20:23 | 0 |  | 9 | 2015-05-15 21:50 | 1 | 1:02
10 | 2015-05-15 21:01 | 1 | 0:43 | 10 | 2015-05-15 22:52 | 0
11 | 2015-05-15 21:44 | 0 |  | 11 | 2015-05-16 11:01 | 1 | 0:35
12 | 2015-05-15 23:15 | 1 | 0:43 | 12 | 2015-05-16 11:36 | 0
13 | 2015-05-15 23:59 | 0 |  | 13 | 2015-05-16 11:41 | 1 | 0:23
14 | 2015-05-16 00:16 | 1 | 0:42 | 14 | 2015-05-16 12:04 | 0
15 | 2015-05-16 00:58 | 0 |  | 15 | 2015-05-16 12:40 | 1 | 0:18
16 | 2015-05-16 11:22 | 1 | 0:18 | 16 | 2015-05-16 12:58 | 0
17 | 2015-05-16 11:40 | 0 |  | 17 | 2015-05-16 12:58 | 1 | 0:06
18 | 2015-05-16 11:40 | 1 | 0:15 | 18 | 2015-05-16 13:04 | 0
19 | 2015-05-16 11:54 | 0 |  | 19 | 2015-05-16 13:06 | 1 | 0:22
20 | 2015-05-16 12:02 | 1 | 0:39 | 20 | 2015-05-16 13:28 | 0
21 | 2015-05-16 12:41 | 0 |  | 21 | 2015-05-16 13:30 | 1 | 0:43
22 | 2015-05-16 12:48 | 1 | 0:14 | 22 | 2015-05-16 14:13 | 0
23 | 2015-05-16 13:02 | 0 |  | 23 | 2015-05-16 14:16 | 1 | 0:32
24 | 2015-05-16 13:03 | 1 | 0:15 | 24 | 2015-05-16 14:48 | 0
25 | 2015-05-16 13:18 | 0 |  | 25 | 2015-05-16 14:59 | 1 | 0:42
26 | 2015-05-16 13:21 | 1 | 0:34 | 26 | 2015-05-16 15:41 | 0
27 | 2015-05-16 13:55 | 0 |  | 27 | 2015-05-16 15:43 | 1 | 0:53
28 | 2015-05-16 13:56 | 1 | 0:21 | 28 | 2015-05-16 16:36 | 0
29 | 2015-05-16 14:17 | 0 |  | 29 | 2015-05-16 16:56 | 1 | 0:48
30 | 2015-05-16 14:18 | 1 | 0:17 | 30 | 2015-05-16 17:44 | 0
31 | 2015-05-16 14:35 | 0 |  | 31 | 2015-05-16 18:20 | 1 | 0:59
32 | 2015-05-16 14:37 | 1 | 0:39 | 32 | 2015-05-16 19:19 | 0
33 | 2015-05-16 15:16 | 0 |  | 33 | 2015-05-16 19:36 | 1 | 0:55
34 | 2015-05-16 15:22 | 1 | 0:35 | 34 | 2015-05-16 20:31 | 0
35 | 2015-05-16 15:57 | 0 |  | 35 | 2015-05-16 20:33 | 1 | 0:51
36 | 2015-05-16 16:00 | 1 | 0:39 | 36 | 2015-05-16 21:23 | 0
37 | 2015-05-16 16:39 | 0 |  | 37 | 2015-05-16 21:47 | 1 | 0:59
38 | 2015-05-16 16:53 | 1 | 0:32 | 38 | 2015-05-16 22:46 | 0
39 | 2015-05-16 17:26 | 0 |  | 39 | 2015-05-16 23:04 | 1 | 0:38
40 | 2015-05-16 17:32 | 1 | 0:43 | 40 | 2015-05-16 23:42 | 0
41 | 2015-05-16 18:15 | 0 |  | 41 | 2015-05-16 23:42 | 1 | 0:21
42 | 2015-05-16 18:27 | 1 | 0:38 | 42 | 2015-05-17 00:03 | 0
43 | 2015-05-16 19:05 | 0 |  | 43 | 2015-05-17 00:04 | 1 | 0:23
44 | 2015-05-16 19:27 | 1 | 0:39 | 44 | 2015-05-17 00:26 | 0
45 | 2015-05-16 20:06 | 0 |  | 45 | 2015-05-17 00:32 | 1 | 0:32
46 | 2015-05-16 20:26 | 1 | 0:16 | 46 | 2015-05-17 01:05 | 0
47 | 2015-05-16 20:43 | 0 |  | 47 | 2015-05-17 01:09 | 1 | 1:10
48 | 2015-05-16 20:45 | 1 | 0:42 | 48 | 2015-05-17 02:20 | 0
49 | 2015-05-16 21:27 | 0 |  | 49 | 2015-05-17 11:33 | 1 | 0:53
50 | 2015-05-16 21:46 | 1 | 0:39 | 50 | 2015-05-17 12:26 | 0
51 | 2015-05-16 22:25 | 0 |  | 51 | 2015-05-17 12:34 | 1 | 0:29
52 | 2015-05-16 23:34 | 1 | 0:32 | 52 | 2015-05-17 13:04 | 0
53 | 2015-05-17 00:06 | 0 |  | 53 | 2015-05-17 13:13 | 1 | 0:20
54 | 2015-05-17 00:07 | 1 | 0:46 | 54 | 2015-05-17 13:33 | 0
55 | 2015-05-17 00:53 | 0 |  | 55 | 2015-05-17 13:33 | 1 | 0:03
56 | 2015-05-17 01:04 | 1 | 0:40 | 56 | 2015-05-17 13:36 | 0
57 | 2015-05-17 01:44 | 0 |  | 57 | 2015-05-17 13:59 | 1 | 0:27
58 | 2015-05-17 08:18 | 1 | 0:38 | 58 | 2015-05-17 14:26 | 0
59 | 2015-05-17 08:56 | 0 |  | 59 | 2015-05-17 14:36 | 1 | 0:17
60 | 2015-05-17 09:10 | 1 | 0:02 | 60 | 2015-05-17 14:52 | 0
61 | 2015-05-17 09:12 | 0 |  | 61 | 2015-05-17 14:52 | 1 | 0:03
62 | 2015-05-17 09:12 | 1 | 0:15 | 62 | 2015-05-17 14:56 | 0
63 | 2015-05-17 09:27 | 0 |  | 63 | 2015-05-17 14:57 | 1 | 0:36
64 | 2015-05-17 11:45 | 1 | 0:38 | 64 | 2015-05-17 15:33 | 0
65 | 2015-05-17 12:23 | 0 |  | 65 | 2015-05-17 15:34 | 1 | 0:48
66 | 2015-05-17 12:42 | 1 | 0:31 | 66 | 2015-05-17 16:22 | 0
67 | 2015-05-17 13:13 | 0 |  | 67 | 2015-05-17 17:23 | 1 | 0:56
68 | 2015-05-17 13:24 | 1 | 0:37 | 68 | 2015-05-17 18:19 | 0
69 | 2015-05-17 14:02 | 0 |  | 69 | 2015-05-17 18:27 | 1 | 0:57
70 | 2015-05-17 14:11 | 1 | 0:33 | 70 | 2015-05-17 19:24 | 0
71 | 2015-05-17 14:44 | 0 |  | 71 | 2015-05-17 19:39 | 1 | 0:46
72 | 2015-05-17 14:52 | 1 | 0:10 | 72 | 2015-05-17 20:25 | 0
73 | 2015-05-17 15:02 | 0 |  | 73 | 2015-05-17 20:28 | 1 | 0:58
74 | 2015-05-17 15:02 | 1 | 0:00 | 74 | 2015-05-17 21:26 | 0
75 | 2015-05-17 15:02 | 0 |  | 75 | 2015-05-17 21:49 | 1 | 1:04
76 | 2015-05-17 15:02 | 1 | 0:01 | 76 | 2015-05-17 22:53 | 0
77 | 2015-05-17 15:03 | 0 |  | 77 | 2015-05-18 01:49 | 1 | 0:50
78 | 2015-05-17 15:04 | 1 | 0:02 | 78 | 2015-05-18 02:39 | 0
79 | 2015-05-17 15:06 | 0 |  | 79 | 2015-05-18 05:27 | 1 | 0:47
80 | 2015-05-17 15:06 | 1 | 0:02 | 80 | 2015-05-18 06:14 | 0
81 | 2015-05-17 15:08 | 0 |  | 81 | 2015-05-18 10:43 | 1 | 0:23
82 | 2015-05-17 15:08 | 1 | 0:02 | 82 | 2015-05-18 11:07 | 0
83 | 2015-05-17 15:10 | 0 |  | 83 | 2015-05-18 11:07 | 1 | 0:02
84 | 2015-05-17 15:11 | 1 | 0:09 | 84 | 2015-05-18 11:09 | 0
85 | 2015-05-17 15:20 | 0 |  | 85 | 2015-05-18 11:10 | 1 | 0:22
86 | 2015-05-17 15:21 | 1 | 0:33 | 86 | 2015-05-18 11:32 | 0
87 | 2015-05-17 15:54 | 0 |  | 87 | 2015-05-18 11:33 | 1 | 0:49
88 | 2015-05-17 15:59 | 1 | 0:40 | 88 | 2015-05-18 12:22 | 0
89 | 2015-05-17 16:39 | 0 |  | 89 | 2015-05-18 12:40 | 1 | 0:30
90 | 2015-05-17 17:15 | 1 | 0:39 | 90 | 2015-05-18 13:11 | 0
91 | 2015-05-17 17:54 | 0 |  | 91 | 2015-05-18 13:16 | 1 | 0:31
92 | 2015-05-17 18:22 | 1 | 0:44 | 92 | 2015-05-18 13:47 | 0
93 | 2015-05-17 19:06 | 0 |  | 93 | 2015-05-18 13:56 | 1 | 0:23
94 | 2015-05-17 19:42 | 1 | 0:30 | 94 | 2015-05-18 14:20 | 0
95 | 2015-05-17 20:12 | 0 |  | 95 | 2015-05-18 14:41 | 1 | 0:52
96 | 2015-05-17 20:25 | 1 | 0:46 | 96 | 2015-05-18 15:33 | 0
97 | 2015-05-17 21:11 | 0 |  | 97 | 2015-05-18 17:33 | 1 | 0:51
98 | 2015-05-17 21:51 | 1 | 0:41 | 98 | 2015-05-18 18:25 | 0
99 | 2015-05-17 22:32 | 0 |  | 99 | 2015-05-18 19:38 | 1 | 0:46
100 | 2015-05-17 23:51 | 1 | 0:39 | 100 | 2015-05-18 20:24 | 0
101 | 2015-05-18 00:29 | 0 |  | 101 | 2015-05-18 20:38 | 1 | 0:58
102 | 2015-05-18 01:47 | 1 | 0:34 | 102 | 2015-05-18 21:36 | 0
103 | 2015-05-18 02:21 | 0 |  | 103 | 2015-05-18 22:16 | 1 | 0:53
104 | 2015-05-18 10:47 | 1 | 0:36 | 104 | 2015-05-18 23:09 | 0
105 | 2015-05-18 11:23 | 0 |  | 105 | 2015-05-18 23:17 | 1 | 1:03
106 | 2015-05-18 11:28 | 1 | 0:40 | 106 | 2015-05-19 00:20 | 0
107 | 2015-05-18 12:07 | 0 |  | 107 | 2015-05-19 03:38 | 1 | 0:47
108 | 2015-05-18 12:44 | 1 | 0:36 | 108 | 2015-05-19 04:25 | 0
109 | 2015-05-18 13:20 | 0 |  | 109 | 2015-05-19 10:17 | 1 | 0:21
110 | 2015-05-18 13:21 | 1 | 0:38 | 110 | 2015-05-19 10:38 | 0
111 | 2015-05-18 13:59 | 0 |  | 111 | 2015-05-19 10:57 | 1 | 0:33
112 | 2015-05-18 14:08 | 1 | 0:39 | 112 | 2015-05-19 11:30 | 0
113 | 2015-05-18 14:47 | 0 |  | 113 | 2015-05-19 11:39 | 1 | 0:52
114 | 2015-05-18 14:49 | 1 | 0:39 | 114 | 2015-05-19 12:30 | 0
115 | 2015-05-18 15:28 | 0 |  | 115 | 2015-05-19 12:50 | 1 | 0:31
116 | 2015-05-18 15:33 | 1 | 0:38 | 116 | 2015-05-19 13:20 | 0
117 | 2015-05-18 16:11 | 0 |  | 117 | 2015-05-19 13:41 | 1 | 0:24
118 | 2015-05-18 17:31 | 1 | 0:36 | 118 | 2015-05-19 14:06 | 0
119 | 2015-05-18 18:06 | 0 |  | 119 | 2015-05-19 14:21 | 1 | 0:50
120 | 2015-05-18 19:27 | 1 | 0:35 | 120 | 2015-05-19 15:11 | 0
121 | 2015-05-18 20:02 | 0 |  | 121 | 2015-05-19 18:22 | 1 | 0:53
122 | 2015-05-18 20:21 | 1 | 0:44 | 122 | 2015-05-19 19:15 | 0
123 | 2015-05-18 21:05 | 0 |  | 123 | 2015-05-19 19:21 | 1 | 0:45
124 | 2015-05-18 21:15 | 1 | 0:41 | 124 | 2015-05-19 20:06 | 0
125 | 2015-05-18 21:56 | 0 |  | 125 | 2015-05-19 20:10 | 1 | 0:51
126 | 2015-05-18 22:14 | 1 | 0:33 | 126 | 2015-05-19 21:02 | 0
127 | 2015-05-18 22:47 | 0 |  | 127 | 2015-05-19 21:06 | 1 | 1:07
128 | 2015-05-18 23:13 | 1 | 0:39 | 128 | 2015-05-19 22:12 | 0
129 | 2015-05-18 23:52 | 0 |  | 129 | 2015-05-19 22:20 | 1 | 0:55
130 | 2015-05-19 00:09 | 1 | 0:35 | 130 | 2015-05-19 23:15 | 0
131 | 2015-05-19 00:43 | 0 |  | 131 | 2015-05-19 23:23 | 1 | 0:52
132 | 2015-05-19 03:41 | 1 | 0:34 | 132 | 2015-05-20 00:14 | 0
133 | 2015-05-19 04:15 | 0 |  | 133 | 2015-05-20 00:38 | 1 | 0:48
134 | 2015-05-19 10:22 | 1 | 0:35 | 134 | 2015-05-20 01:26 | 0
135 | 2015-05-19 10:57 | 0 |  | 135 | 2015-05-20 09:58 | 1 | 0:13
136 | 2015-05-19 11:04 | 1 | 0:28 | 136 | 2015-05-20 10:11 | 0
137 | 2015-05-19 11:31 | 0 |  | 137 | 2015-05-20 10:50 | 1 | 0:46
138 | 2015-05-19 11:31 | 1 | 0:07 | 138 | 2015-05-20 11:36 | 0
139 | 2015-05-19 11:39 | 0 |  | 139 | 2015-05-20 11:47 | 1 | 0:46
140 | 2015-05-19 11:44 | 1 | 0:39 | 140 | 2015-05-20 12:33 | 0
141 | 2015-05-19 12:23 | 0 |  | 141 | 2015-05-20 12:36 | 1 | 0:26
142 | 2015-05-19 12:45 | 1 | 0:33 | 142 | 2015-05-20 13:02 | 0
143 | 2015-05-19 13:19 | 0 |  | 143 | 2015-05-20 13:13 | 1 | 0:35
144 | 2015-05-19 13:49 | 1 | 0:39 | 144 | 2015-05-20 13:48 | 0
145 | 2015-05-19 14:28 | 0 |  | 145 | 2015-05-20 13:55 | 1 | 0:17
146 | 2015-05-19 18:08 | 1 | 0:40 | 146 | 2015-05-20 14:13 | 0
147 | 2015-05-19 18:48 | 0 |  | 147 | 2015-05-20 14:13 | 1 | 0:02
148 | 2015-05-19 18:50 | 1 | 0:37 | 148 | 2015-05-20 14:15 | 0
149 | 2015-05-19 19:27 | 0 |  | 149 | 2015-05-20 14:15 | 1 | 0:01
150 | 2015-05-19 19:51 | 1 | 0:36 | 150 | 2015-05-20 14:16 | 0
151 | 2015-05-19 20:27 | 0 |  | 151 | 2015-05-20 14:16 | 1 | 0:01
152 | 2015-05-19 20:45 | 1 | 0:44 | 152 | 2015-05-20 14:17 | 0
153 | 2015-05-19 21:29 | 0 |  | 153 | 2015-05-20 14:17 | 1 | 0:04
154 | 2015-05-19 21:43 | 1 | 0:38 | 154 | 2015-05-20 14:21 | 0
155 | 2015-05-19 22:21 | 0 |  | 155 | 2015-05-20 14:22 | 1 | 0:14
156 | 2015-05-19 23:07 | 1 | 0:15 | 156 | 2015-05-20 14:36 | 0
157 | 2015-05-19 23:22 | 0 |  | 157 | 2015-05-20 14:37 | 1 | 0:32
158 | 2015-05-19 23:22 | 1 | 0:46 | 158 | 2015-05-20 15:09 | 0
159 | 2015-05-20 00:08 | 0 |  | 159 | 2015-05-20 15:11 | 1 | 0:38
160 | 2015-05-20 04:30 | 1 | 0:35 | 160 | 2015-05-20 15:49 | 0
161 | 2015-05-20 05:06 | 0 |  | 161 | 2015-05-20 15:53 | 1 | 0:09
162 | 2015-05-20 10:54 | 1 | 0:31 | 162 | 2015-05-20 16:03 | 0
163 | 2015-05-20 11:25 | 0 |  | 163 | 2015-05-20 16:05 | 1 | 0:42
164 | 2015-05-20 11:44 | 1 | 0:32 | 164 | 2015-05-20 16:47 | 0
165 | 2015-05-20 12:16 | 0 |  | 165 | 2015-05-20 17:07 | 1 | 0:44
166 | 2015-05-20 12:36 | 1 | 0:30 | 166 | 2015-05-20 17:51 | 0
167 | 2015-05-20 13:06 | 0 |  | 167 | 2015-05-20 18:09 | 1 | 0:54
168 | 2015-05-20 13:15 | 1 | 0:37 | 168 | 2015-05-20 19:04 | 0
169 | 2015-05-20 13:52 | 0 |  | 169 | 2015-05-20 19:12 | 1 | 0:42
170 | 2015-05-20 14:01 | 1 | 0:31 | 170 | 2015-05-20 19:54 | 0
171 | 2015-05-20 14:32 | 0 |  | 171 | 2015-05-20 20:03 | 1 | 0:46
172 | 2015-05-20 15:15 | 1 | 0:31 | 172 | 2015-05-20 20:49 | 0
173 | 2015-05-20 15:45 | 0 |  | 173 | 2015-05-20 20:51 | 1 | 0:38
174 | 2015-05-20 16:08 | 1 | 0:33 | 174 | 2015-05-20 21:29 | 0
175 | 2015-05-20 16:42 | 0 |  | 175 | 2015-05-20 21:45 | 1 | 0:56
176 | 2015-05-20 17:14 | 1 | 0:31 | 176 | 2015-05-20 22:41 | 0
177 | 2015-05-20 17:45 | 0 |  | 177 | 2015-05-20 22:52 | 1 | 1:17
178 | 2015-05-20 18:15 | 1 | 0:35 | 178 | 2015-05-21 00:09 | 0
179 | 2015-05-20 18:50 | 0 |  | 179 | 2015-05-21 05:18 | 1 | 0:45
180 | 2015-05-20 19:07 | 1 | 0:46 | 180 | 2015-05-21 06:03 | 0
181 | 2015-05-20 19:54 | 0 |  | 181 | 2015-05-21 14:07 | 1 | 0:22
182 | 2015-05-20 20:00 | 1 | 0:34 | 182 | 2015-05-21 14:29 | 0
183 | 2015-05-20 20:34 | 0 |  | 183 | 2015-05-21 14:29 | 1 | 0:22
184 | 2015-05-20 20:51 | 1 | 0:47 | 184 | 2015-05-21 14:52 | 0
185 | 2015-05-20 21:38 | 0 |  | 185 | 2015-05-21 15:08 | 1 | 0:44
186 | 2015-05-20 21:50 | 1 | 0:50 | 186 | 2015-05-21 15:52 | 0
187 | 2015-05-20 22:40 | 0 |  | 187 | 2015-05-21 16:08 | 1 | 0:43
188 | 2015-05-20 22:52 | 1 | 0:41 | 188 | 2015-05-21 16:51 | 0
189 | 2015-05-20 23:34 | 0 |  | 189 | 2015-05-21 17:03 | 1 | 0:43
190 | 2015-05-21 05:20 | 1 | 0:33 | 190 | 2015-05-21 17:46 | 0
191 | 2015-05-21 05:53 | 0 |  | 191 | 2015-05-21 18:06 | 1 | 1:00
192 | 2015-05-21 14:14 | 1 | 0:31 | 192 | 2015-05-21 19:06 | 0
193 | 2015-05-21 14:45 | 0 |  | 193 | 2015-05-21 19:13 | 1 | 1:01
194 | 2015-05-21 15:14 | 1 | 0:29 | 194 | 2015-05-21 20:14 | 0
195 | 2015-05-21 15:43 | 0 |  | 195 | 2015-05-21 20:20 | 1 | 0:58
196 | 2015-05-21 16:13 | 1 | 0:29 | 196 | 2015-05-21 21:18 | 0
197 | 2015-05-21 16:42 | 0 |  | 197 | 2015-05-21 21:29 | 1 | 0:44
198 | 2015-05-21 17:07 | 1 | 0:32 | 198 | 2015-05-21 22:13 | 0
199 | 2015-05-21 17:39 | 0 |  | 199 | 2015-05-21 22:50 | 1 | 0:53
200 | 2015-05-21 17:58 | 1 | 0:44 | 200 | 2015-05-21 23:44 | 0
201 | 2015-05-21 18:43 | 0 |  | 201 | 2015-05-21 23:47 | 1 | 0:55
202 | 2015-05-21 19:08 | 1 | 0:45 | 202 | 2015-05-22 00:41 | 0
203 | 2015-05-21 19:53 | 0 |  | 203 | 2015-05-22 00:59 | 1 | 0:44
204 | 2015-05-21 20:22 | 1 | 0:42 | 204 | 2015-05-22 01:43 | 0
205 | 2015-05-21 21:05 | 0 |  | 205 | 2015-05-22 02:24 | 1 | 0:45
206 | 2015-05-21 21:27 | 1 | 0:44 | 206 | 2015-05-22 03:09 | 0
207 | 2015-05-21 22:11 | 0 |  | 207 | 2015-05-22 03:48 | 1 | 0:48
208 | 2015-05-21 22:51 | 1 | 0:36 | 208 | 2015-05-22 04:36 | 0
209 | 2015-05-21 23:27 | 0 |  | 209 | 2015-05-22 04:57 | 1 | 0:43
210 | 2015-05-21 23:50 | 1 | 0:33 | 210 | 2015-05-22 05:39 | 0
211 | 2015-05-22 00:23 | 0 |  | 211 | 2015-05-22 10:38 | 1 | 0:46
212 | 2015-05-22 00:54 | 1 | 0:37 | 212 | 2015-05-22 11:24 | 0
213 | 2015-05-22 01:31 | 0 |  | 213 | 2015-05-22 11:26 | 1 | 0:42
214 | 2015-05-22 02:34 | 1 | 0:36 | 214 | 2015-05-22 12:08 | 0
215 | 2015-05-22 03:10 | 0 |  | 215 | 2015-05-22 12:11 | 1 | 0:45
216 | 2015-05-22 03:46 | 1 | 0:35 | 216 | 2015-05-22 12:55 | 0
217 | 2015-05-22 04:21 | 0 |  | 217 | 2015-05-22 13:00 | 1 | 0:45
218 | 2015-05-22 04:59 | 1 | 0:39 | 218 | 2015-05-22 13:45 | 0
219 | 2015-05-22 05:38 | 0 |  | 219 | 2015-05-22 13:48 | 1 | 0:51
220 | 2015-05-22 10:58 | 1 | 0:37 | 220 | 2015-05-22 14:39 | 0
221 | 2015-05-22 11:35 | 0 |  | 221 | 2015-05-22 14:55 | 1 | 0:46
222 | 2015-05-22 11:42 | 1 | 0:37 | 222 | 2015-05-22 15:41 | 0
223 | 2015-05-22 12:19 | 0 |  | 223 | 2015-05-22 15:49 | 1 | 0:49
224 | 2015-05-22 12:47 | 1 | 0:38 | 224 | 2015-05-22 16:38 | 0
225 | 2015-05-22 13:25 | 0 |  | 225 | 2015-05-22 17:01 | 1 | 0:54
226 | 2015-05-22 13:28 | 1 | 0:35 | 226 | 2015-05-22 17:55 | 0
227 | 2015-05-22 14:04 | 0 |  | 227 | 2015-05-22 19:30 | 1 | 0:53
228 | 2015-05-22 14:12 | 1 | 0:42 | 228 | 2015-05-22 20:23 | 0
229 | 2015-05-22 14:55 | 0 |  | 229 | 2015-05-22 20:32 | 1 | 1:02
230 | 2015-05-22 15:00 | 1 | 0:39 | 230 | 2015-05-22 21:34 | 0
231 | 2015-05-22 15:39 | 0 |  | 231 | 2015-05-22 21:39 | 1 | 0:53
232 | 2015-05-22 15:52 | 1 | 0:37 | 232 | 2015-05-22 22:32 | 0
233 | 2015-05-22 16:29 | 0 |  | 233 | 2015-05-23 00:32 | 1 | 0:46
234 | 2015-05-22 17:04 | 1 | 0:50 | 234 | 2015-05-23 01:19 | 0
235 | 2015-05-22 17:54 | 0 |  | 235 | 2015-05-23 05:34 | 1 | 0:47
236 | 2015-05-22 19:27 | 1 | 0:41 | 236 | 2015-05-23 06:21 | 0
237 | 2015-05-22 20:08 | 0 |  | 237 | 2015-05-23 11:18 | 1 | 0:17
238 | 2015-05-22 20:29 | 1 | 0:47 | 238 | 2015-05-23 11:35 | 0
239 | 2015-05-22 21:16 | 0 |  | 239 | 2015-05-23 11:36 | 1 | 0:12
240 | 2015-05-22 21:21 | 1 | 0:29 | 240 | 2015-05-23 11:48 | 0
241 | 2015-05-22 21:50 | 0 |  | 241 | 2015-05-23 12:06 | 1 | 0:40
242 | 2015-05-23 05:31 | 1 | 0:35 | 242 | 2015-05-23 12:46 | 0
243 | 2015-05-23 06:06 | 0 |  | 243 | 2015-05-23 12:53 | 1 | 0:25
244 | 2015-05-23 11:15 | 1 | 0:19 | 244 | 2015-05-23 13:18 | 0
245 | 2015-05-23 11:34 | 0 |  | 245 | 2015-05-23 13:44 | 1 | 0:28
246 | 2015-05-23 11:34 | 1 | 0:13 | 246 | 2015-05-23 14:12 | 0
247 | 2015-05-23 11:47 | 0 |  | 247 | 2015-05-23 14:19 | 1 | 0:25
248 | 2015-05-23 11:58 | 1 | 0:35 | 248 | 2015-05-23 14:43 | 0
249 | 2015-05-23 12:33 | 0 |  | 249 | 2015-05-23 15:00 | 1 | 0:23
250 | 2015-05-23 12:56 | 1 | 0:25 | 250 | 2015-05-23 15:23 | 0
251 | 2015-05-23 13:22 | 0 |  | 251 | 2015-05-23 15:45 | 1 | 0:53
252 | 2015-05-23 13:39 | 1 | 0:32 | 252 | 2015-05-23 16:37 | 0
253 | 2015-05-23 14:11 | 0 |  | 253 | 2015-05-23 16:40 | 1 | 1:00
254 | 2015-05-23 14:12 | 1 | 0:09 | 254 | 2015-05-23 17:40 | 0
255 | 2015-05-23 14:21 | 0 |  | 255 | 2015-05-23 17:57 | 1 | 0:33
256 | 2015-05-23 14:25 | 1 | 0:26 | 256 | 2015-05-23 18:30 | 0
257 | 2015-05-23 14:51 | 0 |  | 257 | 2015-05-23 18:35 | 1 | 0:58
258 | 2015-05-23 15:10 | 1 | 0:22 | 258 | 2015-05-23 19:33 | 0
259 | 2015-05-23 15:32 | 0 |  | 259 | 2015-05-23 19:48 | 1 | 0:57
260 | 2015-05-23 16:35 | 1 | 0:46 | 260 | 2015-05-23 20:46 | 0
261 | 2015-05-23 17:21 | 0 |  | 261 | 2015-05-23 21:08 | 1 | 0:51
262 | 2015-05-23 17:38 | 1 | 0:37 | 262 | 2015-05-23 21:59 | 0
263 | 2015-05-23 18:15 | 0 |  | 263 | 2015-05-23 23:14 | 1 | 0:51
264 | 2015-05-23 18:33 | 1 | 0:52 | 264 | 2015-05-24 00:06 | 0
265 | 2015-05-23 19:25 | 0 |  | 265 | 2015-05-24 00:16 | 1 | 0:48
266 | 2015-05-23 19:40 | 1 | 0:40 | 266 | 2015-05-24 01:04 | 0
267 | 2015-05-23 20:20 | 0 |  | 267 | 2015-05-24 01:19 | 1 | 0:48
268 | 2015-05-23 20:40 | 1 | 0:53 | 268 | 2015-05-24 02:07 | 0
269 | 2015-05-23 21:33 | 0 |  | 269 | 2015-05-24 03:24 | 1 | 0:50
270 | 2015-05-23 22:17 | 1 | 0:33 | 270 | 2015-05-24 04:14 | 0
271 | 2015-05-23 22:50 | 0 |  | 271 | 2015-05-24 10:51 | 1 | 0:29
272 | 2015-05-23 23:17 | 1 | 0:42 | 272 | 2015-05-24 11:20 | 0
273 | 2015-05-23 23:58 | 0 |  | 273 | 2015-05-24 11:33 | 1 | 0:52
274 | 2015-05-24 00:11 | 1 | 0:34 | 274 | 2015-05-24 12:24 | 0
275 | 2015-05-24 00:45 | 0 |  | 275 | 2015-05-24 12:45 | 1 | 0:29
276 | 2015-05-24 10:56 | 1 | 0:41 | 276 | 2015-05-24 13:15 | 0
277 | 2015-05-24 11:37 | 0 |  | 277 | 2015-05-24 13:26 | 1 | 0:34
278 | 2015-05-24 11:38 | 1 | 0:39 | 278 | 2015-05-24 13:59 | 0
279 | 2015-05-24 12:18 | 0 |  | 279 | 2015-05-24 14:07 | 1 | 0:20
280 | 2015-05-24 12:47 | 1 | 0:31 | 280 | 2015-05-24 14:27 | 0
281 | 2015-05-24 13:18 | 0 |  | 281 | 2015-05-24 14:48 | 1 | 0:22
282 | 2015-05-24 13:19 | 1 | 0:10 | 282 | 2015-05-24 15:10 | 0
283 | 2015-05-24 13:29 | 0 |  | 283 | 2015-05-24 15:36 | 1 | 0:50
284 | 2015-05-24 13:39 | 1 | 0:25 | 284 | 2015-05-24 16:26 | 0
285 | 2015-05-24 14:04 | 0 |  | 285 | 2015-05-24 17:10 | 1 | 0:26
286 | 2015-05-24 14:04 | 1 | 0:08 | 286 | 2015-05-24 17:36 | 0
287 | 2015-05-24 14:13 | 0 |  | 287 | 2015-05-24 17:36 | 1 | 0:22
288 | 2015-05-24 14:19 | 1 | 0:15 | 288 | 2015-05-24 17:58 | 0
289 | 2015-05-24 14:34 | 0 |  | 289 | 2015-05-24 18:04 | 1 | 0:40
290 | 2015-05-24 14:34 | 1 | 0:15 | 290 | 2015-05-24 18:44 | 0
291 | 2015-05-24 14:49 | 0 |  | 291 | 2015-05-24 18:47 | 1 | 1:01
292 | 2015-05-24 15:04 | 1 | 0:40 | 292 | 2015-05-24 19:47 | 0
293 | 2015-05-24 15:44 | 0 |  | 293 | 2015-05-24 19:54 | 1 | 0:57
294 | 2015-05-24 15:48 | 1 | 0:38 | 294 | 2015-05-24 20:51 | 0
295 | 2015-05-24 16:26 | 0 |  | 295 | 2015-05-24 20:59 | 1 | 0:59
296 | 2015-05-24 17:15 | 1 | 0:30 | 296 | 2015-05-24 21:58 | 0
297 | 2015-05-24 17:45 | 0 |  | 297 | 2015-05-24 22:41 | 1 | 0:37
298 | 2015-05-24 17:47 | 1 | 0:11 | 298 | 2015-05-24 23:18 | 0
299 | 2015-05-24 17:58 | 0 |  | 299 | 2015-05-24 23:49 | 1 | 1:04
300 | 2015-05-24 18:08 | 1 | 0:34 | 300 | 2015-05-25 00:53 | 0
301 | 2015-05-24 18:41 | 0 |  | 301 | 2015-05-25 01:13 | 1 | 0:49
302 | 2015-05-24 19:06 | 1 | 0:40 | 302 | 2015-05-25 02:02 | 0
303 | 2015-05-24 19:46 | 0 |  | 303 | 2015-05-25 04:53 | 1 | 0:46
304 | 2015-05-24 20:52 | 1 | 0:39 | 304 | 2015-05-25 05:38 | 0
305 | 2015-05-24 21:32 | 0 |  | 305 | 2015-05-25 09:21 | 1 | 0:01
306 | 2015-05-24 21:50 | 1 | 0:40 | 306 | 2015-05-25 09:22 | 0
307 | 2015-05-24 22:30 | 0 |  | 307 | 2015-05-25 09:26 | 1 | 0:41
308 | 2015-05-24 22:38 | 1 | 0:41 | 308 | 2015-05-25 10:07 | 0
309 | 2015-05-24 23:18 | 0 |  | 309 | 2015-05-25 10:09 | 1 | 0:30
310 | 2015-05-24 23:44 | 1 | 0:36 | 310 | 2015-05-25 10:39 | 0
311 | 2015-05-25 00:20 | 0 |  | 311 | 2015-05-25 11:54 | 1 | 0:46
312 | 2015-05-25 01:08 | 1 | 0:35 | 312 | 2015-05-25 12:40 | 0
313 | 2015-05-25 01:43 | 0 |  | 313 | 2015-05-25 13:12 | 1 | 0:39
314 | 2015-05-25 04:51 | 1 | 0:36 | 314 | 2015-05-25 13:51 | 0
315 | 2015-05-25 05:28 | 0 |  | 315 | 2015-05-25 13:53 | 1 | 0:19
316 | 2015-05-25 12:53 | 1 | 0:23 | 316 | 2015-05-25 14:12 | 0
317 | 2015-05-25 13:16 | 0 |  | 317 | 2015-05-25 14:12 | 1 | 0:21
318 | 2015-05-25 13:55 | 1 | 0:28 | 318 | 2015-05-25 14:32 | 0
319 | 2015-05-25 14:22 | 0 |  | 319 | 2015-05-25 14:35 | 1 | 0:24
320 | 2015-05-25 15:13 | 1 | 0:01 | 320 | 2015-05-25 14:59 | 0
321 | 2015-05-25 15:13 | 0 |  | 321 | 2015-05-25 15:00 | 1 | 0:19
322 | 2015-05-25 15:13 | 1 | 0:21 | 322 | 2015-05-25 15:19 | 0
323 | 2015-05-25 15:35 | 0 |  | 323 | 2015-05-25 15:57 | 1 | 0:23
324 | 2015-05-25 16:08 | 1 | 0:23 | 324 | 2015-05-25 16:20 | 0
325 | 2015-05-25 16:31 | 0 |  | 325 | 2015-05-25 17:57 | 1 | 0:38
326 | 2015-05-25 16:31 | 1 | 0:02 | 326 | 2015-05-25 18:35 | 0
327 | 2015-05-25 16:33 | 0 |  | 327 | 2015-05-25 18:36 | 1 | 0:19
328 | 2015-05-25 16:34 | 1 | 0:06 | 328 | 2015-05-25 18:56 | 0
329 | 2015-05-25 16:40 | 0 |  | 329 | 2015-05-25 18:57 | 1 | 1:03
330 | 2015-05-25 16:48 | 1 | 0:43 | 330 | 2015-05-25 20:00 | 0
331 | 2015-05-25 17:31 | 0 |  | 331 | 2015-05-25 20:03 | 1 | 0:54
332 | 2015-05-25 17:31 | 1 | 0:13 | 332 | 2015-05-25 20:57 | 0
333 | 2015-05-25 17:45 | 0 |  | 333 | 2015-05-25 21:02 | 1 | 0:48
334 | 2015-05-25 18:00 | 1 | 0:48 | 334 | 2015-05-25 21:51 | 0
335 | 2015-05-25 18:49 | 0 |  | 335 | 2015-05-25 21:59 | 1 | 0:49
336 | 2015-05-25 18:53 | 1 | 0:52 | 336 | 2015-05-25 22:48 | 0
337 | 2015-05-25 19:45 | 0 |  | 337 | 2015-05-25 22:57 | 1 | 0:39
338 | 2015-05-25 20:00 | 1 | 0:47 | 338 | 2015-05-25 23:36 | 0
339 | 2015-05-25 20:47 | 0 |  | 339 | 2015-05-25 23:44 | 1 | 0:57
340 | 2015-05-25 21:00 | 1 | 0:51 | 340 | 2015-05-26 00:41 | 0
341 | 2015-05-25 21:51 | 0 |  | 341 | 2015-05-26 00:48 | 1 | 0:48
342 | 2015-05-25 21:56 | 1 | 0:47 | 342 | 2015-05-26 01:35 | 0
343 | 2015-05-25 22:43 | 0 |  | 343 | 2015-05-26 01:39 | 1 | 0:47
344 | 2015-05-25 22:51 | 1 | 0:44 | 344 | 2015-05-26 02:26 | 0
345 | 2015-05-25 23:35 | 0 |  | 345 | 2015-05-26 02:48 | 1 | 0:46
346 | 2015-05-26 00:01 | 1 | 0:35 | 346 | 2015-05-26 03:34 | 0
347 | 2015-05-26 00:36 | 0 |  | 347 | 2015-05-26 03:50 | 1 | 0:46
348 | 2015-05-26 00:46 | 1 | 0:37 | 348 | 2015-05-26 04:36 | 0
349 | 2015-05-26 01:23 | 0 |  | 349 | 2015-05-26 04:41 | 1 | 0:50
350 | 2015-05-26 01:33 | 1 | 0:42 | 350 | 2015-05-26 05:31 | 0
351 | 2015-05-26 02:15 | 0 |  | 351 | 2015-05-26 11:06 | 1 | 0:51
352 | 2015-05-26 03:26 | 1 | 0:44 | 352 | 2015-05-26 11:57 | 0
353 | 2015-05-26 04:11 | 0 |  | 353 | 2015-05-26 12:09 | 1 | 0:47
354 | 2015-05-26 04:40 | 1 | 0:35 | 354 | 2015-05-26 12:56 | 0
355 | 2015-05-26 05:15 | 0 |  | 355 | 2015-05-26 13:20 | 1 | 0:55
356 | 2015-05-26 11:13 | 1 | 0:32 | 356 | 2015-05-26 14:15 | 0
357 | 2015-05-26 11:45 | 0 |  | 357 | 2015-05-26 14:35 | 1 | 0:55
358 | 2015-05-26 12:05 | 1 | 0:38 | 358 | 2015-05-26 15:30 | 0
359 | 2015-05-26 12:43 | 0 |  | 359 | 2015-05-26 17:19 | 1 | 0:48
360 | 2015-05-26 12:56 | 1 | 0:14 | 360 | 2015-05-26 18:07 | 0
361 | 2015-05-26 13:10 | 0 |  | 361 | 2015-05-26 18:34 | 1 | 0:57
362 | 2015-05-26 13:29 | 1 | 0:31 | 362 | 2015-05-26 19:31 | 0
363 | 2015-05-26 14:00 | 0 |  | 363 | 2015-05-26 19:37 | 1 | 0:59
364 | 2015-05-26 14:01 | 1 | 0:08 | 364 | 2015-05-26 20:35 | 0
365 | 2015-05-26 14:09 | 0 |  | 365 | 2015-05-26 21:57 | 1 | 0:45
366 | 2015-05-26 14:13 | 1 | 0:42 | 366 | 2015-05-26 22:42 | 0
367 | 2015-05-26 14:56 | 0 |  | 367 | 2015-05-27 05:14 | 1 | 0:48
368 | 2015-05-26 15:50 | 1 | 0:38 | 368 | 2015-05-27 06:02 | 0
369 | 2015-05-26 16:28 | 0 |  | 369 | 2015-05-27 11:34 | 1 | 0:52
370 | 2015-05-26 17:15 | 1 | 0:35 | 370 | 2015-05-27 12:26 | 0
371 | 2015-05-26 17:50 | 0 |  | 371 | 2015-05-27 12:41 | 1 | 0:40
372 | 2015-05-26 18:37 | 1 | 0:40 | 372 | 2015-05-27 13:21 | 0
373 | 2015-05-26 19:17 | 0 |  | 373 | 2015-05-27 13:42 | 1 | 0:42
374 | 2015-05-26 19:29 | 1 | 0:43 | 374 | 2015-05-27 14:24 | 0
375 | 2015-05-26 20:12 | 0 |  | 375 | 2015-05-27 14:27 | 1 | 0:37
376 | 2015-05-27 05:16 | 1 | 0:36 | 376 | 2015-05-27 15:03 | 0
377 | 2015-05-27 05:52 | 0 |  | 377 | 2015-05-27 15:08 | 1 | 0:56
378 | 2015-05-27 11:41 | 1 | 0:37 | 378 | 2015-05-27 16:04 | 0
379 | 2015-05-27 12:17 | 0 |  | 379 | 2015-05-27 16:09 | 1 | 1:07
380 | 2015-05-27 12:49 | 1 | 0:39 | 380 | 2015-05-27 17:16 | 0
381 | 2015-05-27 13:28 | 0 |  | 381 | 2015-05-27 18:09 | 1 | 0:43
382 | 2015-05-27 13:38 | 1 | 0:38 | 382 | 2015-05-27 18:52 | 0
383 | 2015-05-27 14:17 | 0 |  | 383 | 2015-05-27 19:45 | 1 | 0:48
384 | 2015-05-27 14:30 | 1 | 0:38 | 384 | 2015-05-27 20:33 | 0
385 | 2015-05-27 15:08 | 0 |  | 385 | 2015-05-27 20:35 | 1 | 1:06
386 | 2015-05-27 16:15 | 1 | 0:53 | 386 | 2015-05-27 21:42 | 0
387 | 2015-05-27 17:08 | 0 |  | 387 | 2015-05-27 22:46 | 1 | 0:44
388 | 2015-05-27 17:11 | 1 | 0:37 | 388 | 2015-05-27 23:29 | 0
389 | 2015-05-27 17:48 | 0 |  | 389 | 2015-05-27 23:31 | 1 | 0:50
390 | 2015-05-27 18:42 | 1 | 0:40 | 390 | 2015-05-28 00:21 | 0
391 | 2015-05-27 19:22 | 0 |  | 391 | 2015-05-28 08:08 | 1 | 0:13
392 | 2015-05-27 19:43 | 1 | 0:37 | 392 | 2015-05-28 08:21 | 0
393 | 2015-05-27 20:20 | 0 |  | 393 | 2015-05-28 08:52 | 1 | 0:18
394 | 2015-05-27 20:33 | 1 | 0:07 | 394 | 2015-05-28 09:10 | 0
395 | 2015-05-27 20:39 | 0 |  | 395 | 2015-05-28 11:22 | 1 | 0:33
396 | 2015-05-27 20:40 | 1 | 0:02 | 396 | 2015-05-28 11:56 | 0
397 | 2015-05-27 20:42 | 0 |  | 397 | 2015-05-28 12:22 | 1 | 0:29
398 | 2015-05-27 21:33 | 1 | 0:37 | 398 | 2015-05-28 12:51 | 0
399 | 2015-05-27 22:10 | 0 |  | 399 | 2015-05-28 13:07 | 1 | 0:41
400 | 2015-05-27 22:45 | 1 | 0:52 | 400 | 2015-05-28 13:48 | 0
401 | 2015-05-27 23:37 | 0 |  | 401 | 2015-05-28 13:52 | 1 | 0:34
402 | 2015-05-28 10:28 | 1 | 0:17 | 402 | 2015-05-28 14:26 | 0
403 | 2015-05-28 10:45 | 0 |  | 403 | 2015-05-28 14:54 | 1 | 0:28
404 | 2015-05-28 10:45 | 1 | 0:13 | 404 | 2015-05-28 15:22 | 0
405 | 2015-05-28 10:58 | 0 |  | 405 | 2015-05-28 15:49 | 1 | 0:33
406 | 2015-05-28 11:28 | 1 | 0:30 | 406 | 2015-05-28 16:23 | 0
407 | 2015-05-28 11:58 | 0 |  | 407 | 2015-05-28 16:35 | 1 | 0:38
408 | 2015-05-28 12:26 | 1 | 0:22 | 408 | 2015-05-28 17:13 | 0
409 | 2015-05-28 12:48 | 0 |  | 409 | 2015-05-28 17:27 | 1 | 0:59
410 | 2015-05-28 12:48 | 1 | 0:04 | 410 | 2015-05-28 18:26 | 0
411 | 2015-05-28 12:52 | 0 |  | 411 | 2015-05-28 18:31 | 1 | 0:48
412 | 2015-05-28 12:53 | 1 | 0:17 | 412 | 2015-05-28 19:19 | 0
413 | 2015-05-28 13:09 | 0 |  | 413 | 2015-05-28 19:23 | 1 | 0:47
414 | 2015-05-28 13:11 | 1 | 0:42 | 414 | 2015-05-28 20:10 | 0
415 | 2015-05-28 13:52 | 0 |  | 415 | 2015-05-28 20:13 | 1 | 0:54
416 | 2015-05-28 13:55 | 1 | 0:26 | 416 | 2015-05-28 21:07 | 0
417 | 2015-05-28 14:21 | 0 |  | 417 | 2015-05-28 21:39 | 1 | 0:49
418 | 2015-05-28 14:47 | 1 | 0:44 | 418 | 2015-05-28 22:28 | 0
419 | 2015-05-28 15:31 | 0 |  | 419 | 2015-05-28 22:32 | 1 | 0:59
420 | 2015-05-28 15:56 | 1 | 0:25 | 420 | 2015-05-28 23:31 | 0
421 | 2015-05-28 16:21 | 0 |  | 421 | 2015-05-28 23:51 | 1 | 0:52
422 | 2015-05-28 16:23 | 1 | 0:32 | 422 | 2015-05-29 00:43 | 0
423 | 2015-05-28 16:55 | 0 |  | 423 | 2015-05-29 10:48 | 1 | 0:06
424 | 2015-05-28 17:06 | 1 | 0:29 | 424 | 2015-05-29 10:54 | 0
425 | 2015-05-28 17:36 | 0 |  | 425 | 2015-05-29 10:57 | 1 | 0:38
426 | 2015-05-28 18:23 | 1 | 0:39 | 426 | 2015-05-29 11:35 | 0
427 | 2015-05-28 19:02 | 0 |  | 427 | 2015-05-29 11:44 | 1 | 0:42
428 | 2015-05-28 19:14 | 1 | 0:50 | 428 | 2015-05-29 12:26 | 0
429 | 2015-05-28 20:05 | 0 |  | 429 | 2015-05-29 12:28 | 1 | 0:39
430 | 2015-05-28 21:03 | 1 | 0:40 | 430 | 2015-05-29 13:07 | 0
431 | 2015-05-28 21:43 | 0 |  | 431 | 2015-05-29 13:09 | 1 | 0:14
432 | 2015-05-28 21:46 | 1 | 0:42 | 432 | 2015-05-29 13:23 | 0
433 | 2015-05-28 22:28 | 0 |  | 433 | 2015-05-29 13:24 | 1 | 0:29
434 | 2015-05-28 22:57 | 1 | 0:47 | 434 | 2015-05-29 13:53 | 0
435 | 2015-05-28 23:44 | 0 |  | 435 | 2015-05-29 14:02 | 1 | 0:31
436 | 2015-05-28 23:54 | 1 | 0:37 | 436 | 2015-05-29 14:33 | 0
437 | 2015-05-29 00:31 | 0 |  | 437 | 2015-05-29 14:49 | 1 | 0:11
438 | 2015-05-29 10:58 | 1 | 0:31 | 438 | 2015-05-29 15:00 | 0
439 | 2015-05-29 11:29 | 0 |  | 439 | 2015-05-29 15:00 | 1 | 0:17
440 | 2015-05-29 11:36 | 1 | 0:29 | 440 | 2015-05-29 15:17 | 0
441 | 2015-05-29 12:05 | 0 |  | 441 | 2015-05-29 16:03 | 1 | 0:28
442 | 2015-05-29 12:34 | 1 | 0:26 | 442 | 2015-05-29 16:31 | 0
443 | 2015-05-29 13:00 | 0 |  | 443 | 2015-05-29 16:32 | 1 | 0:37
444 | 2015-05-29 13:06 | 1 | 0:19 | 444 | 2015-05-29 17:09 | 0
445 | 2015-05-29 13:25 | 0 |  | 445 | 2015-05-29 17:11 | 1 | 0:43
446 | 2015-05-29 13:25 | 1 | 0:17 | 446 | 2015-05-29 17:54 | 0
447 | 2015-05-29 13:43 | 0 |  | 447 | 2015-05-29 19:18 | 1 | 0:55
448 | 2015-05-29 13:59 | 1 | 0:22 | 448 | 2015-05-29 20:12 | 0
449 | 2015-05-29 14:21 | 0 |  | 449 | 2015-05-29 20:29 | 1 | 0:54
450 | 2015-05-29 14:27 | 1 | 0:03 | 450 | 2015-05-29 21:22 | 0
451 | 2015-05-29 14:30 | 0 |  | 451 | 2015-05-29 21:25 | 1 | 0:56
452 | 2015-05-29 14:30 | 1 | 0:06 | 452 | 2015-05-29 22:21 | 0
453 | 2015-05-29 14:36 | 0 |  | 453 | 2015-05-29 22:34 | 1 | 1:07
454 | 2015-05-29 14:43 | 1 | 0:18 | 454 | 2015-05-29 23:41 | 0
455 | 2015-05-29 15:00 | 0 |  | 455 | 2015-05-29 23:50 | 1 | 0:29
456 | 2015-05-29 15:02 | 1 | 0:11 | 456 | 2015-05-30 00:20 | 0
457 | 2015-05-29 15:12 | 0 |  | 457 | 2015-05-30 01:01 | 1 | 0:58
458 | 2015-05-29 15:41 | 1 | 0:34 | 458 | 2015-05-30 01:59 | 0
459 | 2015-05-29 16:16 | 0 |  | 459 | 2015-05-30 11:16 | 1 | 0:37
460 | 2015-05-29 17:23 | 1 | 0:32 | 460 | 2015-05-30 11:53 | 0
461 | 2015-05-29 17:55 | 0 |  | 461 | 2015-05-30 12:01 | 1 | 0:45
462 | 2015-05-29 18:10 | 1 | 0:52 | 462 | 2015-05-30 12:46 | 0
463 | 2015-05-29 19:02 | 0 |  | 463 | 2015-05-30 12:55 | 1 | 0:53
464 | 2015-05-29 19:26 | 1 | 0:40 | 464 | 2015-05-30 13:48 | 0
465 | 2015-05-29 20:06 | 0 |  | 465 | 2015-05-30 13:49 | 1 | 0:35
466 | 2015-05-29 20:26 | 1 | 0:50 | 466 | 2015-05-30 14:24 | 0
467 | 2015-05-29 21:16 | 0 |  | 467 | 2015-05-30 14:42 | 1 | 0:24
468 | 2015-05-29 21:31 | 1 | 0:29 | 468 | 2015-05-30 15:05 | 0
469 | 2015-05-29 22:00 | 0 |  | 469 | 2015-05-30 15:13 | 1 | 1:04
470 | 2015-05-29 22:29 | 1 | 0:37 | 470 | 2015-05-30 16:17 | 0
471 | 2015-05-29 23:06 | 0 |  | 471 | 2015-05-30 18:11 | 1 | 0:45
472 | 2015-05-29 23:39 | 1 | 0:52 | 472 | 2015-05-30 18:57 | 0
473 | 2015-05-30 00:31 | 0 |  | 473 | 2015-05-30 19:03 | 1 | 0:47
474 | 2015-05-30 01:01 | 1 | 0:34 | 474 | 2015-05-30 19:50 | 0
475 | 2015-05-30 01:35 | 0 |  | 475 | 2015-05-30 19:59 | 1 | 0:42
476 | 2015-05-30 11:02 | 1 | 0:38 | 476 | 2015-05-30 20:41 | 0
477 | 2015-05-30 11:39 | 0 |  | 477 | 2015-05-30 20:59 | 1 | 0:44
478 | 2015-05-30 11:53 | 1 | 0:39 | 478 | 2015-05-30 21:43 | 0
479 | 2015-05-30 12:32 | 0 |  | 479 | 2015-05-30 21:57 | 1 | 1:04
480 | 2015-05-30 12:54 | 1 | 0:19 | 480 | 2015-05-30 23:01 | 0
481 | 2015-05-30 13:13 | 0 |  | 481 | 2015-05-30 23:18 | 1 | 0:45
482 | 2015-05-30 13:13 | 1 | 0:23 | 482 | 2015-05-31 00:03 | 0
483 | 2015-05-30 13:36 | 0 |  | 483 | 2015-05-31 00:15 | 1 | 0:43
484 | 2015-05-30 13:47 | 1 | 0:33 | 484 | 2015-05-31 00:58 | 0
485 | 2015-05-30 14:20 | 0 |  | 485 | 2015-05-31 01:02 | 1 | 1:08
486 | 2015-05-30 14:29 | 1 | 0:51 | 486 | 2015-05-31 02:10 | 0
487 | 2015-05-30 15:20 | 0 |  | 487 | 2015-05-31 02:54 | 1 | 1:22
488 | 2015-05-30 15:27 | 1 | 0:46 | 488 | 2015-05-31 04:16 | 0
489 | 2015-05-30 16:13 | 0 |  | 489 | 2015-05-31 11:04 | 1 | 0:30
490 | 2015-05-30 18:15 | 1 | 0:48 | 490 | 2015-05-31 11:33 | 0
491 | 2015-05-30 19:03 | 0 |  | 491 | 2015-05-31 11:46 | 1 | 0:51
492 | 2015-05-30 19:07 | 1 | 0:43 | 492 | 2015-05-31 12:37 | 0
493 | 2015-05-30 19:50 | 0 |  | 493 | 2015-05-31 12:44 | 1 | 0:32
494 | 2015-05-30 20:02 | 1 | 0:41 | 494 | 2015-05-31 13:16 | 0
495 | 2015-05-30 20:42 | 0 |  | 495 | 2015-05-31 13:28 | 1 | 0:33
496 | 2015-05-30 21:01 | 1 | 0:41 | 496 | 2015-05-31 14:01 | 0
497 | 2015-05-30 21:43 | 0 |  | 497 | 2015-05-31 14:11 | 1 | 0:34
498 | 2015-05-30 23:21 | 1 | 0:41 | 498 | 2015-05-31 14:45 | 0
499 | 2015-05-31 00:02 | 0 |  | 499 | 2015-05-31 14:55 | 1 | 0:27
500 | 2015-05-31 00:10 | 1 | 0:38 | 500 | 2015-05-31 15:22 | 0
501 | 2015-05-31 00:49 | 0 |  | 501 | 2015-05-31 15:34 | 1 | 0:52
502 | 2015-05-31 01:16 | 1 | 0:43 | 502 | 2015-05-31 16:25 | 0
503 | 2015-05-31 02:00 | 0 |  | 503 | 2015-05-31 16:38 | 1 | 1:02
504 | 2015-05-31 02:54 | 1 | 0:39 | 504 | 2015-05-31 17:40 | 0
505 | 2015-05-31 03:32 | 0 |  | 505 | 2015-05-31 17:58 | 1 | 0:54
506 | 2015-05-31 11:08 | 1 | 0:19 | 506 | 2015-05-31 18:52 | 0
507 | 2015-05-31 11:27 | 0 |  | 507 | 2015-05-31 19:03 | 1 | 0:49
508 | 2015-05-31 11:27 | 1 | 0:15 | 508 | 2015-05-31 19:52 | 0
509 | 2015-05-31 11:42 | 0 |  | 509 | 2015-05-31 19:58 | 1 | 0:48
510 | 2015-05-31 11:53 | 1 | 0:40 | 510 | 2015-05-31 20:46 | 0
511 | 2015-05-31 12:32 | 0 |  | 511 | 2015-05-31 23:36 | 1 | 0:54
512 | 2015-05-31 12:43 | 1 | 0:30 | 512 | 2015-06-01 00:30 | 0
513 | 2015-05-31 13:13 | 0 |  | 513 | 2015-06-01 01:22 | 1 | 0:52
514 | 2015-05-31 13:14 | 1 | 0:31 | 514 | 2015-06-01 02:14 | 0
515 | 2015-05-31 13:45 | 0 |  | 515 | 2015-06-01 10:39 | 1 | 0:36
516 | 2015-05-31 13:55 | 1 | 0:26 | 516 | 2015-06-01 11:15 | 0
517 | 2015-05-31 14:21 | 0 |  | 517 | 2015-06-01 11:35 | 1 | 0:51
518 | 2015-05-31 14:21 | 1 | 0:04 | 518 | 2015-06-01 12:26 | 0
519 | 2015-05-31 14:25 | 0 |  | 519 | 2015-06-01 12:32 | 1 | 0:44
520 | 2015-05-31 14:25 | 1 | 0:03 | 520 | 2015-06-01 13:15 | 0
521 | 2015-05-31 14:28 | 0 |  | 521 | 2015-06-01 13:21 | 1 | 0:28
522 | 2015-05-31 14:36 | 1 | 0:22 | 522 | 2015-06-01 13:49 | 0
523 | 2015-05-31 14:59 | 0 |  | 523 | 2015-06-01 14:02 | 1 | 0:39
524 | 2015-05-31 14:59 | 1 | 0:09 | 524 | 2015-06-01 14:41 | 0
525 | 2015-05-31 15:08 | 0 |  | 525 | 2015-06-01 14:42 | 1 | 0:33
526 | 2015-05-31 15:19 | 1 | 0:42 | 526 | 2015-06-01 15:15 | 0
527 | 2015-05-31 16:01 | 0 |  | 527 | 2015-06-01 15:21 | 1 | 0:55
528 | 2015-05-31 16:36 | 1 | 0:43 | 528 | 2015-06-01 16:16 | 0
529 | 2015-05-31 17:19 | 0 |  | 529 | 2015-06-01 19:11 | 1 | 0:58
530 | 2015-05-31 17:52 | 1 | 0:40 | 530 | 2015-06-01 20:10 | 0
531 | 2015-05-31 18:32 | 0 |  | 531 | 2015-06-01 20:20 | 1 | 0:52
532 | 2015-05-31 18:57 | 1 | 0:39 | 532 | 2015-06-01 21:11 | 0
533 | 2015-05-31 19:36 | 0 |  | 533 | 2015-06-01 21:20 | 1 | 0:50
534 | 2015-05-31 19:56 | 1 | 0:39 | 534 | 2015-06-01 22:10 | 0
535 | 2015-05-31 20:35 | 0 |  | 535 | 2015-06-01 22:41 | 1 | 0:54
536 | 2015-05-31 23:30 | 1 | 0:39 | 536 | 2015-06-01 23:35 | 0
537 | 2015-06-01 00:09 | 0 |  | 537 | 2015-06-01 23:40 | 1 | 1:06
538 | 2015-06-01 00:21 | 1 | 0:35 | 538 | 2015-06-02 00:46 | 0
539 | 2015-06-01 00:55 | 0 |  | 539 | 2015-06-02 01:36 | 1 | 0:45
540 | 2015-06-01 01:25 | 1 | 0:41 | 540 | 2015-06-02 02:21 | 0
541 | 2015-06-01 02:07 | 0 |  | 541 | 2015-06-02 03:12 | 1 | 0:47
542 | 2015-06-01 04:58 | 1 | 0:35 | 542 | 2015-06-02 03:59 | 0
543 | 2015-06-01 05:34 | 0 |  | 543 | 2015-06-02 04:59 | 1 | 0:46
544 | 2015-06-01 10:56 | 1 | 0:40 | 544 | 2015-06-02 05:46 | 0
545 | 2015-06-01 11:36 | 0 |  | 545 | 2015-06-02 11:10 | 1 | 0:38
546 | 2015-06-01 11:42 | 1 | 0:34 | 546 | 2015-06-02 11:48 | 0
547 | 2015-06-01 12:17 | 0 |  | 547 | 2015-06-02 11:56 | 1 | 0:28
548 | 2015-06-01 12:39 | 1 | 0:30 | 548 | 2015-06-02 12:24 | 0
549 | 2015-06-01 13:08 | 0 |  | 549 | 2015-06-02 12:24 | 1 | 0:10
550 | 2015-06-01 13:25 | 1 | 0:01 | 550 | 2015-06-02 12:34 | 0
551 | 2015-06-01 13:26 | 0 |  | 551 | 2015-06-02 13:06 | 1 | 0:39
552 | 2015-06-01 13:27 | 1 | 0:30 | 552 | 2015-06-02 13:45 | 0
553 | 2015-06-01 13:57 | 0 |  | 553 | 2015-06-02 13:46 | 1 | 0:41
554 | 2015-06-01 14:15 | 1 | 0:34 | 554 | 2015-06-02 14:27 | 0
555 | 2015-06-01 14:49 | 0 |  | 555 | 2015-06-02 14:29 | 1 | 0:53
556 | 2015-06-01 14:51 | 1 | 0:40 | 556 | 2015-06-02 15:22 | 0
557 | 2015-06-01 15:31 | 0 |  | 557 | 2015-06-02 16:06 | 1 | 0:54
558 | 2015-06-01 19:15 | 1 | 0:48 | 558 | 2015-06-02 17:00 | 0
559 | 2015-06-01 20:03 | 0 |  | 559 | 2015-06-02 17:02 | 1 | 0:43
560 | 2015-06-01 20:14 | 1 | 0:36 | 560 | 2015-06-02 17:45 | 0
561 | 2015-06-01 20:50 | 0 |  | 561 | 2015-06-02 17:48 | 1 | 1:05
562 | 2015-06-01 21:19 | 1 | 0:36 | 562 | 2015-06-02 18:53 | 0
563 | 2015-06-01 21:55 | 0 |  | 563 | 2015-06-02 19:42 | 1 | 0:55
564 | 2015-06-01 22:44 | 1 | 0:46 | 564 | 2015-06-02 20:37 | 0
565 | 2015-06-01 23:30 | 0 |  | 565 | 2015-06-02 20:38 | 1 | 0:55
566 | 2015-06-01 23:42 | 1 | 0:49 | 566 | 2015-06-02 21:33 | 0
567 | 2015-06-02 00:31 | 0 |  | 567 | 2015-06-02 23:45 | 1 | 0:47
568 | 2015-06-02 00:46 | 1 | 0:37 | 568 | 2015-06-03 00:31 | 0
569 | 2015-06-02 01:23 | 0 |  | 569 | 2015-06-03 00:43 | 1 | 0:46
570 | 2015-06-02 11:15 | 1 | 0:33 | 570 | 2015-06-03 01:30 | 0
571 | 2015-06-02 11:48 | 0 |  | 571 | 2015-06-03 10:39 | 1 | 0:48
572 | 2015-06-02 12:01 | 1 | 0:37 | 572 | 2015-06-03 11:27 | 0
573 | 2015-06-02 12:37 | 0 |  | 573 | 2015-06-03 11:33 | 1 | 0:51
574 | 2015-06-02 13:13 | 1 | 0:40 | 574 | 2015-06-03 12:24 | 0
575 | 2015-06-02 13:53 | 0 |  | 575 | 2015-06-03 12:29 | 1 | 0:51
576 | 2015-06-02 13:55 | 1 | 0:39 | 576 | 2015-06-03 13:20 | 0
577 | 2015-06-02 14:34 | 0 |  | 577 | 2015-06-03 13:22 | 1 | 0:31
578 | 2015-06-02 14:36 | 1 | 0:39 | 578 | 2015-06-03 13:53 | 0
579 | 2015-06-02 15:15 | 0 |  | 579 | 2015-06-03 13:55 | 1 | 0:19
580 | 2015-06-02 15:16 | 1 | 0:40 | 580 | 2015-06-03 14:14 | 0
581 | 2015-06-02 15:56 | 0 |  | 581 | 2015-06-03 14:15 | 1 | 0:40
582 | 2015-06-02 16:09 | 1 | 0:44 | 582 | 2015-06-03 14:54 | 0
583 | 2015-06-02 16:53 | 0 |  | 583 | 2015-06-03 14:56 | 1 | 0:50
584 | 2015-06-02 17:12 | 1 | 0:42 | 584 | 2015-06-03 15:46 | 0
585 | 2015-06-02 17:54 | 0 |  | 585 | 2015-06-03 17:53 | 1 | 1:15
586 | 2015-06-02 18:11 | 1 | 0:42 | 586 | 2015-06-03 19:08 | 0
587 | 2015-06-02 18:52 | 0 |  | 587 | 2015-06-03 19:27 | 1 | 0:54
588 | 2015-06-02 19:39 | 1 | 0:39 | 588 | 2015-06-03 20:21 | 0
589 | 2015-06-02 20:18 | 0 |  | 589 | 2015-06-03 20:40 | 1 | 1:03
590 | 2015-06-02 23:43 | 1 | 0:40 | 590 | 2015-06-03 21:43 | 0
591 | 2015-06-03 00:23 | 0 |  | 591 | 2015-06-03 21:45 | 1 | 0:57
592 | 2015-06-03 06:19 | 1 | 0:36 | 592 | 2015-06-03 22:42 | 0
593 | 2015-06-03 06:55 | 0 |  | 593 | 2015-06-03 23:34 | 1 | 0:31
594 | 2015-06-03 10:41 | 1 | 0:38 | 594 | 2015-06-04 00:05 | 0
595 | 2015-06-03 11:19 | 0 |  | 595 | 2015-06-04 05:38 | 1 | 0:48
596 | 2015-06-03 11:27 | 1 | 0:41 | 596 | 2015-06-04 06:26 | 0
597 | 2015-06-03 12:08 | 0 |  | 597 | 2015-06-04 10:18 | 1 | 0:21
598 | 2015-06-03 12:35 | 1 | 0:38 | 598 | 2015-06-04 10:39 | 0
599 | 2015-06-03 13:13 | 0 |  | 599 | 2015-06-04 11:07 | 1 | 0:41
600 | 2015-06-03 13:14 | 1 | 0:34 | 600 | 2015-06-04 11:48 | 0
601 | 2015-06-03 13:49 | 0 |  | 601 | 2015-06-04 12:06 | 1 | 0:37
602 | 2015-06-03 13:53 | 1 | 0:17 | 602 | 2015-06-04 12:43 | 0
603 | 2015-06-03 14:10 | 0 |  | 603 | 2015-06-04 13:09 | 1 | 0:23
604 | 2015-06-03 14:10 | 1 | 0:02 | 604 | 2015-06-04 13:32 | 0
605 | 2015-06-03 14:12 | 0 |  | 605 | 2015-06-04 13:42 | 1 | 0:38
606 | 2015-06-03 14:12 | 1 | 0:05 | 606 | 2015-06-04 14:21 | 0
607 | 2015-06-03 14:17 | 0 |  | 607 | 2015-06-04 14:27 | 1 | 0:22
608 | 2015-06-03 14:34 | 1 | 0:32 | 608 | 2015-06-04 14:50 | 0
609 | 2015-06-03 15:07 | 0 |  | 609 | 2015-06-04 15:19 | 1 | 0:30
610 | 2015-06-03 15:16 | 1 | 0:40 | 610 | 2015-06-04 15:49 | 0
611 | 2015-06-03 15:56 | 0 |  | 611 | 2015-06-04 17:23 | 1 | 0:48
612 | 2015-06-03 19:18 | 1 | 0:40 | 612 | 2015-06-04 18:11 | 0
613 | 2015-06-03 19:58 | 0 |  | 613 | 2015-06-04 18:12 | 1 | 0:48
614 | 2015-06-03 21:00 | 1 | 0:43 | 614 | 2015-06-04 19:00 | 0
615 | 2015-06-03 21:42 | 0 |  | 615 | 2015-06-04 19:02 | 1 | 1:20
616 | 2015-06-03 21:44 | 1 | 0:44 | 616 | 2015-06-04 20:22 | 0
617 | 2015-06-03 22:28 | 0 |  | 617 | 2015-06-04 21:07 | 1 | 1:03
618 | 2015-06-03 22:37 | 1 | 0:18 | 618 | 2015-06-04 22:09 | 0
619 | 2015-06-03 22:55 | 0 |  | 619 | 2015-06-04 23:01 | 1 | 1:02
620 | 2015-06-03 22:55 | 1 | 0:16 | 620 | 2015-06-05 00:03 | 0
621 | 2015-06-03 23:11 | 0 |  | 621 | 2015-06-05 09:57 | 1 | 0:33
622 | 2015-06-03 23:35 | 1 | 0:33 | 622 | 2015-06-05 10:30 | 0
623 | 2015-06-04 00:08 | 0 |  | 623 | 2015-06-05 10:44 | 1 | 0:38
624 | 2015-06-04 10:16 | 1 | 0:17 | 624 | 2015-06-05 11:22 | 0
625 | 2015-06-04 10:33 | 0 |  | 625 | 2015-06-05 11:25 | 1 | 0:51
626 | 2015-06-04 10:34 | 1 | 0:11 | 626 | 2015-06-05 12:16 | 0
627 | 2015-06-04 10:45 | 0 |  | 627 | 2015-06-05 12:22 | 1 | 0:09
628 | 2015-06-04 12:09 | 1 | 0:21 | 628 | 2015-06-05 12:32 | 0
629 | 2015-06-04 12:30 | 0 |  | 629 | 2015-06-05 12:32 | 1 | 0:06
630 | 2015-06-04 12:53 | 1 | 0:29 | 630 | 2015-06-05 12:38 | 0
631 | 2015-06-04 13:22 | 0 |  | 631 | 2015-06-05 12:45 | 1 | 0:41
632 | 2015-06-04 13:53 | 1 | 0:35 | 632 | 2015-06-05 13:26 | 0
633 | 2015-06-04 14:27 | 0 |  | 633 | 2015-06-05 13:41 | 1 | 0:34
634 | 2015-06-04 14:39 | 1 | 0:31 | 634 | 2015-06-05 14:15 | 0
635 | 2015-06-04 15:10 | 0 |  | 635 | 2015-06-05 14:24 | 1 | 0:33
636 | 2015-06-04 15:25 | 1 | 0:17 | 636 | 2015-06-05 14:57 | 0
637 | 2015-06-04 15:42 | 0 |  | 637 | 2015-06-05 15:05 | 1 | 0:53
638 | 2015-06-04 15:43 | 1 | 0:19 | 638 | 2015-06-05 15:58 | 0
639 | 2015-06-04 16:02 | 0 |  | 639 | 2015-06-05 16:06 | 1 | 0:56
640 | 2015-06-04 17:20 | 1 | 0:49 | 640 | 2015-06-05 17:02 | 0
641 | 2015-06-04 18:09 | 0
642 | 2015-06-04 18:10 | 1 | 0:38
643 | 2015-06-04 18:49 | 0
644 | 2015-06-04 19:06 | 1 | 0:44
645 | 2015-06-04 19:49 | 0
646 | 2015-06-04 20:04 | 1 | 0:40
647 | 2015-06-04 20:45 | 0
648 | 2015-06-04 22:59 | 1 | 0:44
649 | 2015-06-04 23:43 | 0
650 | 2015-06-05 10:09 | 1 | 0:42
651 | 2015-06-05 10:51 | 0
652 | 2015-06-05 10:55 | 1 | 0:40
653 | 2015-06-05 11:35 | 0
654 | 2015-06-05 11:41 | 1 | 0:40
655 | 2015-06-05 12:21 | 0
656 | 2015-06-05 12:27 | 1 | 0:40
657 | 2015-06-05 13:08 | 0
658 | 2015-06-05 13:21 | 1 | 0:39
659 | 2015-06-05 14:00 | 0
660 | 2015-06-05 14:02 | 1 | 0:28
661 | 2015-06-05 14:30 | 0
662 | 2015-06-05 14:39 | 1 | 0:40
663 | 2015-06-05 15:19 | 0
664 | 2015-06-05 16:11 | 1 | 0:35
665 | 2015-06-05 16:47 | 0

## Usage History
Usage Name | Period EndSorted Descending | Max kW Demand | kWh Usage | Therm (Thru-Put) | Total Electric Bill Amount | Total Gas Bill Amount | Blended Electric Rate (kWh) | Blended Gas Rate (Therm)
1825222005:06/01/2015 | 2015-06-01 |  | 0 | 6392 | 0 | 2542.16 | 0 | 0.3977
1825222005:04/30/2015 | 2015-04-30 |  | 0 | 6340 | 0 | 2528.54 | 0 | 0.3988
1825222005:03/31/2015 | 2015-03-31 |  | 0 | 14975 | 0 | 5407.94 | 0 | 0.3611
1825222005:03/02/2015 | 2015-03-02 |  | 0 | 24936 | 0 | 8053.34 | 0 | 0.323
1825222005:01/29/2015 | 2015-01-29 |  | 0 | 25128 | 0 | 8126.72 | 0 | 0.3234
1825222005:12/30/2014 | 2014-12-30 |  | 0 | 25570 | 0 | 8139.7 | 0 | 0.3183
1825222005:12/01/2014 | 2014-12-01 |  | 0 | 28491 | 0 | 8853.94 | 0 | 0.3108
1825222005:10/29/2014 | 2014-10-29 |  | 0 | 24670 | 0 | 6581.86 | 0 | 0.2668
1825222005:09/30/2014 | 2014-09-30 |  | 0 | 20962 | 0 | 5694.31 | 0 | 0.2716
1825222005:08/29/2014 | 2014-08-29 |  | 0 | 17029 | 0 | 4343.61 | 0 | 0.2551
1825222005:07/30/2014 | 2014-07-30 |  | 0 | 17863 | 0 | 4535.66 | 0 | 0.2539
1825222005:06/30/2014 | 2014-06-30 |  | 0 | 20417 | 0 | 5083.73 | 0 | 0.249

## Raw Motor Logger Data
Plot Title: 19040 |  |  | Plot Title: 19042
# | Date Time, GMT-07:00 | Motor (LGR S/N: 10348430, SEN S/N: 10348430) | # | Date Time, GMT-07:00 | Motor (LGR S/N: 10348432, SEN S/N: 10348432)
1 | 2015-05-15 17:00 | 0 | 1 | 2015-05-15 17:00 | 1
2 | 2015-05-15 17:04 | 1 | 2 | 2015-05-15 17:47 | 0
3 | 2015-05-15 17:37 | 0 | 3 | 2015-05-15 18:03 | 1
4 | 2015-05-15 18:06 | 1 | 4 | 2015-05-15 18:50 | 0
5 | 2015-05-15 18:42 | 0 | 5 | 2015-05-15 18:53 | 1
6 | 2015-05-15 18:59 | 1 | 6 | 2015-05-15 19:47 | 0
7 | 2015-05-15 19:33 | 0 | 7 | 2015-05-15 21:08 | 1
8 | 2015-05-15 19:45 | 1 | 8 | 2015-05-15 21:49 | 0
9 | 2015-05-15 20:23 | 0 | 9 | 2015-05-15 21:50 | 1
10 | 2015-05-15 21:01 | 1 | 10 | 2015-05-15 22:52 | 0
11 | 2015-05-15 21:44 | 0 | 11 | 2015-05-16 11:01 | 1
12 | 2015-05-15 23:15 | 1 | 12 | 2015-05-16 11:36 | 0
13 | 2015-05-15 23:59 | 0 | 13 | 2015-05-16 11:41 | 1
14 | 2015-05-16 00:16 | 1 | 14 | 2015-05-16 12:04 | 0
15 | 2015-05-16 00:58 | 0 | 15 | 2015-05-16 12:40 | 1
16 | 2015-05-16 11:22 | 1 | 16 | 2015-05-16 12:58 | 0
17 | 2015-05-16 11:40 | 0 | 17 | 2015-05-16 12:58 | 1
18 | 2015-05-16 11:40 | 1 | 18 | 2015-05-16 13:04 | 0
19 | 2015-05-16 11:54 | 0 | 19 | 2015-05-16 13:06 | 1
20 | 2015-05-16 12:02 | 1 | 20 | 2015-05-16 13:28 | 0
21 | 2015-05-16 12:41 | 0 | 21 | 2015-05-16 13:30 | 1
22 | 2015-05-16 12:48 | 1 | 22 | 2015-05-16 14:13 | 0
23 | 2015-05-16 13:02 | 0 | 23 | 2015-05-16 14:16 | 1
24 | 2015-05-16 13:03 | 1 | 24 | 2015-05-16 14:48 | 0
25 | 2015-05-16 13:18 | 0 | 25 | 2015-05-16 14:59 | 1
26 | 2015-05-16 13:21 | 1 | 26 | 2015-05-16 15:41 | 0
27 | 2015-05-16 13:55 | 0 | 27 | 2015-05-16 15:43 | 1
28 | 2015-05-16 13:56 | 1 | 28 | 2015-05-16 16:36 | 0
29 | 2015-05-16 14:17 | 0 | 29 | 2015-05-16 16:56 | 1
30 | 2015-05-16 14:18 | 1 | 30 | 2015-05-16 17:44 | 0
31 | 2015-05-16 14:35 | 0 | 31 | 2015-05-16 18:20 | 1
32 | 2015-05-16 14:37 | 1 | 32 | 2015-05-16 19:19 | 0
33 | 2015-05-16 15:16 | 0 | 33 | 2015-05-16 19:36 | 1
34 | 2015-05-16 15:22 | 1 | 34 | 2015-05-16 20:31 | 0
35 | 2015-05-16 15:57 | 0 | 35 | 2015-05-16 20:33 | 1
36 | 2015-05-16 16:00 | 1 | 36 | 2015-05-16 21:23 | 0
37 | 2015-05-16 16:39 | 0 | 37 | 2015-05-16 21:47 | 1
38 | 2015-05-16 16:53 | 1 | 38 | 2015-05-16 22:46 | 0
39 | 2015-05-16 17:26 | 0 | 39 | 2015-05-16 23:04 | 1
40 | 2015-05-16 17:32 | 1 | 40 | 2015-05-16 23:42 | 0
41 | 2015-05-16 18:15 | 0 | 41 | 2015-05-16 23:42 | 1
42 | 2015-05-16 18:27 | 1 | 42 | 2015-05-17 00:03 | 0
43 | 2015-05-16 19:05 | 0 | 43 | 2015-05-17 00:04 | 1
44 | 2015-05-16 19:27 | 1 | 44 | 2015-05-17 00:26 | 0
45 | 2015-05-16 20:06 | 0 | 45 | 2015-05-17 00:32 | 1
46 | 2015-05-16 20:26 | 1 | 46 | 2015-05-17 01:05 | 0
47 | 2015-05-16 20:43 | 0 | 47 | 2015-05-17 01:09 | 1
48 | 2015-05-16 20:45 | 1 | 48 | 2015-05-17 02:20 | 0
49 | 2015-05-16 21:27 | 0 | 49 | 2015-05-17 11:33 | 1
50 | 2015-05-16 21:46 | 1 | 50 | 2015-05-17 12:26 | 0
51 | 2015-05-16 22:25 | 0 | 51 | 2015-05-17 12:34 | 1
52 | 2015-05-16 23:34 | 1 | 52 | 2015-05-17 13:04 | 0
53 | 2015-05-17 00:06 | 0 | 53 | 2015-05-17 13:13 | 1
54 | 2015-05-17 00:07 | 1 | 54 | 2015-05-17 13:33 | 0
55 | 2015-05-17 00:53 | 0 | 55 | 2015-05-17 13:33 | 1
56 | 2015-05-17 01:04 | 1 | 56 | 2015-05-17 13:36 | 0
57 | 2015-05-17 01:44 | 0 | 57 | 2015-05-17 13:59 | 1
58 | 2015-05-17 08:18 | 1 | 58 | 2015-05-17 14:26 | 0
59 | 2015-05-17 08:56 | 0 | 59 | 2015-05-17 14:36 | 1
60 | 2015-05-17 09:10 | 1 | 60 | 2015-05-17 14:52 | 0
61 | 2015-05-17 09:12 | 0 | 61 | 2015-05-17 14:52 | 1
62 | 2015-05-17 09:12 | 1 | 62 | 2015-05-17 14:56 | 0
63 | 2015-05-17 09:27 | 0 | 63 | 2015-05-17 14:57 | 1
64 | 2015-05-17 11:45 | 1 | 64 | 2015-05-17 15:33 | 0
65 | 2015-05-17 12:23 | 0 | 65 | 2015-05-17 15:34 | 1
66 | 2015-05-17 12:42 | 1 | 66 | 2015-05-17 16:22 | 0
67 | 2015-05-17 13:13 | 0 | 67 | 2015-05-17 17:23 | 1
68 | 2015-05-17 13:24 | 1 | 68 | 2015-05-17 18:19 | 0
69 | 2015-05-17 14:02 | 0 | 69 | 2015-05-17 18:27 | 1
70 | 2015-05-17 14:11 | 1 | 70 | 2015-05-17 19:24 | 0
71 | 2015-05-17 14:44 | 0 | 71 | 2015-05-17 19:39 | 1
72 | 2015-05-17 14:52 | 1 | 72 | 2015-05-17 20:25 | 0
73 | 2015-05-17 15:02 | 0 | 73 | 2015-05-17 20:28 | 1
74 | 2015-05-17 15:02 | 1 | 74 | 2015-05-17 21:26 | 0
75 | 2015-05-17 15:02 | 0 | 75 | 2015-05-17 21:49 | 1
76 | 2015-05-17 15:02 | 1 | 76 | 2015-05-17 22:53 | 0
77 | 2015-05-17 15:03 | 0 | 77 | 2015-05-18 01:49 | 1
78 | 2015-05-17 15:04 | 1 | 78 | 2015-05-18 02:39 | 0
79 | 2015-05-17 15:06 | 0 | 79 | 2015-05-18 05:27 | 1
80 | 2015-05-17 15:06 | 1 | 80 | 2015-05-18 06:14 | 0
81 | 2015-05-17 15:08 | 0 | 81 | 2015-05-18 10:43 | 1
82 | 2015-05-17 15:08 | 1 | 82 | 2015-05-18 11:07 | 0
83 | 2015-05-17 15:10 | 0 | 83 | 2015-05-18 11:07 | 1
84 | 2015-05-17 15:11 | 1 | 84 | 2015-05-18 11:09 | 0
85 | 2015-05-17 15:20 | 0 | 85 | 2015-05-18 11:10 | 1
86 | 2015-05-17 15:21 | 1 | 86 | 2015-05-18 11:32 | 0
87 | 2015-05-17 15:54 | 0 | 87 | 2015-05-18 11:33 | 1
88 | 2015-05-17 15:59 | 1 | 88 | 2015-05-18 12:22 | 0
89 | 2015-05-17 16:39 | 0 | 89 | 2015-05-18 12:40 | 1
90 | 2015-05-17 17:15 | 1 | 90 | 2015-05-18 13:11 | 0
91 | 2015-05-17 17:54 | 0 | 91 | 2015-05-18 13:16 | 1
92 | 2015-05-17 18:22 | 1 | 92 | 2015-05-18 13:47 | 0
93 | 2015-05-17 19:06 | 0 | 93 | 2015-05-18 13:56 | 1
94 | 2015-05-17 19:42 | 1 | 94 | 2015-05-18 14:20 | 0
95 | 2015-05-17 20:12 | 0 | 95 | 2015-05-18 14:41 | 1
96 | 2015-05-17 20:25 | 1 | 96 | 2015-05-18 15:33 | 0
97 | 2015-05-17 21:11 | 0 | 97 | 2015-05-18 17:33 | 1
98 | 2015-05-17 21:51 | 1 | 98 | 2015-05-18 18:25 | 0
99 | 2015-05-17 22:32 | 0 | 99 | 2015-05-18 19:38 | 1
100 | 2015-05-17 23:51 | 1 | 100 | 2015-05-18 20:24 | 0
101 | 2015-05-18 00:29 | 0 | 101 | 2015-05-18 20:38 | 1
102 | 2015-05-18 01:47 | 1 | 102 | 2015-05-18 21:36 | 0
103 | 2015-05-18 02:21 | 0 | 103 | 2015-05-18 22:16 | 1
104 | 2015-05-18 10:47 | 1 | 104 | 2015-05-18 23:09 | 0
105 | 2015-05-18 11:23 | 0 | 105 | 2015-05-18 23:17 | 1
106 | 2015-05-18 11:28 | 1 | 106 | 2015-05-19 00:20 | 0
107 | 2015-05-18 12:07 | 0 | 107 | 2015-05-19 03:38 | 1
108 | 2015-05-18 12:44 | 1 | 108 | 2015-05-19 04:25 | 0
109 | 2015-05-18 13:20 | 0 | 109 | 2015-05-19 10:17 | 1
110 | 2015-05-18 13:21 | 1 | 110 | 2015-05-19 10:38 | 0
111 | 2015-05-18 13:59 | 0 | 111 | 2015-05-19 10:57 | 1
112 | 2015-05-18 14:08 | 1 | 112 | 2015-05-19 11:30 | 0
113 | 2015-05-18 14:47 | 0 | 113 | 2015-05-19 11:39 | 1
114 | 2015-05-18 14:49 | 1 | 114 | 2015-05-19 12:30 | 0
115 | 2015-05-18 15:28 | 0 | 115 | 2015-05-19 12:50 | 1
116 | 2015-05-18 15:33 | 1 | 116 | 2015-05-19 13:20 | 0
117 | 2015-05-18 16:11 | 0 | 117 | 2015-05-19 13:41 | 1
118 | 2015-05-18 17:31 | 1 | 118 | 2015-05-19 14:06 | 0
119 | 2015-05-18 18:06 | 0 | 119 | 2015-05-19 14:21 | 1
120 | 2015-05-18 19:27 | 1 | 120 | 2015-05-19 15:11 | 0
121 | 2015-05-18 20:02 | 0 | 121 | 2015-05-19 18:22 | 1
122 | 2015-05-18 20:21 | 1 | 122 | 2015-05-19 19:15 | 0
123 | 2015-05-18 21:05 | 0 | 123 | 2015-05-19 19:21 | 1
124 | 2015-05-18 21:15 | 1 | 124 | 2015-05-19 20:06 | 0
125 | 2015-05-18 21:56 | 0 | 125 | 2015-05-19 20:10 | 1
126 | 2015-05-18 22:14 | 1 | 126 | 2015-05-19 21:02 | 0
127 | 2015-05-18 22:47 | 0 | 127 | 2015-05-19 21:06 | 1
128 | 2015-05-18 23:13 | 1 | 128 | 2015-05-19 22:12 | 0
129 | 2015-05-18 23:52 | 0 | 129 | 2015-05-19 22:20 | 1
130 | 2015-05-19 00:09 | 1 | 130 | 2015-05-19 23:15 | 0
131 | 2015-05-19 00:43 | 0 | 131 | 2015-05-19 23:23 | 1
132 | 2015-05-19 03:41 | 1 | 132 | 2015-05-20 00:14 | 0
133 | 2015-05-19 04:15 | 0 | 133 | 2015-05-20 00:38 | 1
134 | 2015-05-19 10:22 | 1 | 134 | 2015-05-20 01:26 | 0
135 | 2015-05-19 10:57 | 0 | 135 | 2015-05-20 09:58 | 1
136 | 2015-05-19 11:04 | 1 | 136 | 2015-05-20 10:11 | 0
137 | 2015-05-19 11:31 | 0 | 137 | 2015-05-20 10:50 | 1
138 | 2015-05-19 11:31 | 1 | 138 | 2015-05-20 11:36 | 0
139 | 2015-05-19 11:39 | 0 | 139 | 2015-05-20 11:47 | 1
140 | 2015-05-19 11:44 | 1 | 140 | 2015-05-20 12:33 | 0
141 | 2015-05-19 12:23 | 0 | 141 | 2015-05-20 12:36 | 1
142 | 2015-05-19 12:45 | 1 | 142 | 2015-05-20 13:02 | 0
143 | 2015-05-19 13:19 | 0 | 143 | 2015-05-20 13:13 | 1
144 | 2015-05-19 13:49 | 1 | 144 | 2015-05-20 13:48 | 0
145 | 2015-05-19 14:28 | 0 | 145 | 2015-05-20 13:55 | 1
146 | 2015-05-19 18:08 | 1 | 146 | 2015-05-20 14:13 | 0
147 | 2015-05-19 18:48 | 0 | 147 | 2015-05-20 14:13 | 1
148 | 2015-05-19 18:50 | 1 | 148 | 2015-05-20 14:15 | 0
149 | 2015-05-19 19:27 | 0 | 149 | 2015-05-20 14:15 | 1
150 | 2015-05-19 19:51 | 1 | 150 | 2015-05-20 14:16 | 0
151 | 2015-05-19 20:27 | 0 | 151 | 2015-05-20 14:16 | 1
152 | 2015-05-19 20:45 | 1 | 152 | 2015-05-20 14:17 | 0
153 | 2015-05-19 21:29 | 0 | 153 | 2015-05-20 14:17 | 1
154 | 2015-05-19 21:43 | 1 | 154 | 2015-05-20 14:21 | 0
155 | 2015-05-19 22:21 | 0 | 155 | 2015-05-20 14:22 | 1
156 | 2015-05-19 23:07 | 1 | 156 | 2015-05-20 14:36 | 0
157 | 2015-05-19 23:22 | 0 | 157 | 2015-05-20 14:37 | 1
158 | 2015-05-19 23:22 | 1 | 158 | 2015-05-20 15:09 | 0
159 | 2015-05-20 00:08 | 0 | 159 | 2015-05-20 15:11 | 1
160 | 2015-05-20 04:30 | 1 | 160 | 2015-05-20 15:49 | 0
161 | 2015-05-20 05:06 | 0 | 161 | 2015-05-20 15:53 | 1
162 | 2015-05-20 10:54 | 1 | 162 | 2015-05-20 16:03 | 0
163 | 2015-05-20 11:25 | 0 | 163 | 2015-05-20 16:05 | 1
164 | 2015-05-20 11:44 | 1 | 164 | 2015-05-20 16:47 | 0
165 | 2015-05-20 12:16 | 0 | 165 | 2015-05-20 17:07 | 1
166 | 2015-05-20 12:36 | 1 | 166 | 2015-05-20 17:51 | 0
167 | 2015-05-20 13:06 | 0 | 167 | 2015-05-20 18:09 | 1
168 | 2015-05-20 13:15 | 1 | 168 | 2015-05-20 19:04 | 0
169 | 2015-05-20 13:52 | 0 | 169 | 2015-05-20 19:12 | 1
170 | 2015-05-20 14:01 | 1 | 170 | 2015-05-20 19:54 | 0
171 | 2015-05-20 14:32 | 0 | 171 | 2015-05-20 20:03 | 1
172 | 2015-05-20 15:15 | 1 | 172 | 2015-05-20 20:49 | 0
173 | 2015-05-20 15:45 | 0 | 173 | 2015-05-20 20:51 | 1
174 | 2015-05-20 16:08 | 1 | 174 | 2015-05-20 21:29 | 0
175 | 2015-05-20 16:42 | 0 | 175 | 2015-05-20 21:45 | 1
176 | 2015-05-20 17:14 | 1 | 176 | 2015-05-20 22:41 | 0
177 | 2015-05-20 17:45 | 0 | 177 | 2015-05-20 22:52 | 1
178 | 2015-05-20 18:15 | 1 | 178 | 2015-05-21 00:09 | 0
179 | 2015-05-20 18:50 | 0 | 179 | 2015-05-21 05:18 | 1
180 | 2015-05-20 19:07 | 1 | 180 | 2015-05-21 06:03 | 0
181 | 2015-05-20 19:54 | 0 | 181 | 2015-05-21 14:07 | 1
182 | 2015-05-20 20:00 | 1 | 182 | 2015-05-21 14:29 | 0
183 | 2015-05-20 20:34 | 0 | 183 | 2015-05-21 14:29 | 1
184 | 2015-05-20 20:51 | 1 | 184 | 2015-05-21 14:52 | 0
185 | 2015-05-20 21:38 | 0 | 185 | 2015-05-21 15:08 | 1
186 | 2015-05-20 21:50 | 1 | 186 | 2015-05-21 15:52 | 0
187 | 2015-05-20 22:40 | 0 | 187 | 2015-05-21 16:08 | 1
188 | 2015-05-20 22:52 | 1 | 188 | 2015-05-21 16:51 | 0
189 | 2015-05-20 23:34 | 0 | 189 | 2015-05-21 17:03 | 1
190 | 2015-05-21 05:20 | 1 | 190 | 2015-05-21 17:46 | 0
191 | 2015-05-21 05:53 | 0 | 191 | 2015-05-21 18:06 | 1
192 | 2015-05-21 14:14 | 1 | 192 | 2015-05-21 19:06 | 0
193 | 2015-05-21 14:45 | 0 | 193 | 2015-05-21 19:13 | 1
194 | 2015-05-21 15:14 | 1 | 194 | 2015-05-21 20:14 | 0
195 | 2015-05-21 15:43 | 0 | 195 | 2015-05-21 20:20 | 1
196 | 2015-05-21 16:13 | 1 | 196 | 2015-05-21 21:18 | 0
197 | 2015-05-21 16:42 | 0 | 197 | 2015-05-21 21:29 | 1
198 | 2015-05-21 17:07 | 1 | 198 | 2015-05-21 22:13 | 0
199 | 2015-05-21 17:39 | 0 | 199 | 2015-05-21 22:50 | 1
200 | 2015-05-21 17:58 | 1 | 200 | 2015-05-21 23:44 | 0
201 | 2015-05-21 18:43 | 0 | 201 | 2015-05-21 23:47 | 1
202 | 2015-05-21 19:08 | 1 | 202 | 2015-05-22 00:41 | 0
203 | 2015-05-21 19:53 | 0 | 203 | 2015-05-22 00:59 | 1
204 | 2015-05-21 20:22 | 1 | 204 | 2015-05-22 01:43 | 0
205 | 2015-05-21 21:05 | 0 | 205 | 2015-05-22 02:24 | 1
206 | 2015-05-21 21:27 | 1 | 206 | 2015-05-22 03:09 | 0
207 | 2015-05-21 22:11 | 0 | 207 | 2015-05-22 03:48 | 1
208 | 2015-05-21 22:51 | 1 | 208 | 2015-05-22 04:36 | 0
209 | 2015-05-21 23:27 | 0 | 209 | 2015-05-22 04:57 | 1
210 | 2015-05-21 23:50 | 1 | 210 | 2015-05-22 05:39 | 0
211 | 2015-05-22 00:23 | 0 | 211 | 2015-05-22 10:38 | 1
212 | 2015-05-22 00:54 | 1 | 212 | 2015-05-22 11:24 | 0
213 | 2015-05-22 01:31 | 0 | 213 | 2015-05-22 11:26 | 1
214 | 2015-05-22 02:34 | 1 | 214 | 2015-05-22 12:08 | 0
215 | 2015-05-22 03:10 | 0 | 215 | 2015-05-22 12:11 | 1
216 | 2015-05-22 03:46 | 1 | 216 | 2015-05-22 12:55 | 0
217 | 2015-05-22 04:21 | 0 | 217 | 2015-05-22 13:00 | 1
218 | 2015-05-22 04:59 | 1 | 218 | 2015-05-22 13:45 | 0
219 | 2015-05-22 05:38 | 0 | 219 | 2015-05-22 13:48 | 1
220 | 2015-05-22 10:58 | 1 | 220 | 2015-05-22 14:39 | 0
221 | 2015-05-22 11:35 | 0 | 221 | 2015-05-22 14:55 | 1
222 | 2015-05-22 11:42 | 1 | 222 | 2015-05-22 15:41 | 0
223 | 2015-05-22 12:19 | 0 | 223 | 2015-05-22 15:49 | 1
224 | 2015-05-22 12:47 | 1 | 224 | 2015-05-22 16:38 | 0
225 | 2015-05-22 13:25 | 0 | 225 | 2015-05-22 17:01 | 1
226 | 2015-05-22 13:28 | 1 | 226 | 2015-05-22 17:55 | 0
227 | 2015-05-22 14:04 | 0 | 227 | 2015-05-22 19:30 | 1
228 | 2015-05-22 14:12 | 1 | 228 | 2015-05-22 20:23 | 0
229 | 2015-05-22 14:55 | 0 | 229 | 2015-05-22 20:32 | 1
230 | 2015-05-22 15:00 | 1 | 230 | 2015-05-22 21:34 | 0
231 | 2015-05-22 15:39 | 0 | 231 | 2015-05-22 21:39 | 1
232 | 2015-05-22 15:52 | 1 | 232 | 2015-05-22 22:32 | 0
233 | 2015-05-22 16:29 | 0 | 233 | 2015-05-23 00:32 | 1
234 | 2015-05-22 17:04 | 1 | 234 | 2015-05-23 01:19 | 0
235 | 2015-05-22 17:54 | 0 | 235 | 2015-05-23 05:34 | 1
236 | 2015-05-22 19:27 | 1 | 236 | 2015-05-23 06:21 | 0
237 | 2015-05-22 20:08 | 0 | 237 | 2015-05-23 11:18 | 1
238 | 2015-05-22 20:29 | 1 | 238 | 2015-05-23 11:35 | 0
239 | 2015-05-22 21:16 | 0 | 239 | 2015-05-23 11:36 | 1
240 | 2015-05-22 21:21 | 1 | 240 | 2015-05-23 11:48 | 0
241 | 2015-05-22 21:50 | 0 | 241 | 2015-05-23 12:06 | 1
242 | 2015-05-23 05:31 | 1 | 242 | 2015-05-23 12:46 | 0
243 | 2015-05-23 06:06 | 0 | 243 | 2015-05-23 12:53 | 1
244 | 2015-05-23 11:15 | 1 | 244 | 2015-05-23 13:18 | 0
245 | 2015-05-23 11:34 | 0 | 245 | 2015-05-23 13:44 | 1
246 | 2015-05-23 11:34 | 1 | 246 | 2015-05-23 14:12 | 0
247 | 2015-05-23 11:47 | 0 | 247 | 2015-05-23 14:19 | 1
248 | 2015-05-23 11:58 | 1 | 248 | 2015-05-23 14:43 | 0
249 | 2015-05-23 12:33 | 0 | 249 | 2015-05-23 15:00 | 1
250 | 2015-05-23 12:56 | 1 | 250 | 2015-05-23 15:23 | 0
251 | 2015-05-23 13:22 | 0 | 251 | 2015-05-23 15:45 | 1
252 | 2015-05-23 13:39 | 1 | 252 | 2015-05-23 16:37 | 0
253 | 2015-05-23 14:11 | 0 | 253 | 2015-05-23 16:40 | 1
254 | 2015-05-23 14:12 | 1 | 254 | 2015-05-23 17:40 | 0
255 | 2015-05-23 14:21 | 0 | 255 | 2015-05-23 17:57 | 1
256 | 2015-05-23 14:25 | 1 | 256 | 2015-05-23 18:30 | 0
257 | 2015-05-23 14:51 | 0 | 257 | 2015-05-23 18:35 | 1
258 | 2015-05-23 15:10 | 1 | 258 | 2015-05-23 19:33 | 0
259 | 2015-05-23 15:32 | 0 | 259 | 2015-05-23 19:48 | 1
260 | 2015-05-23 16:35 | 1 | 260 | 2015-05-23 20:46 | 0
261 | 2015-05-23 17:21 | 0 | 261 | 2015-05-23 21:08 | 1
262 | 2015-05-23 17:38 | 1 | 262 | 2015-05-23 21:59 | 0
263 | 2015-05-23 18:15 | 0 | 263 | 2015-05-23 23:14 | 1
264 | 2015-05-23 18:33 | 1 | 264 | 2015-05-24 00:06 | 0
265 | 2015-05-23 19:25 | 0 | 265 | 2015-05-24 00:16 | 1
266 | 2015-05-23 19:40 | 1 | 266 | 2015-05-24 01:04 | 0
267 | 2015-05-23 20:20 | 0 | 267 | 2015-05-24 01:19 | 1
268 | 2015-05-23 20:40 | 1 | 268 | 2015-05-24 02:07 | 0
269 | 2015-05-23 21:33 | 0 | 269 | 2015-05-24 03:24 | 1
270 | 2015-05-23 22:17 | 1 | 270 | 2015-05-24 04:14 | 0
271 | 2015-05-23 22:50 | 0 | 271 | 2015-05-24 10:51 | 1
272 | 2015-05-23 23:17 | 1 | 272 | 2015-05-24 11:20 | 0
273 | 2015-05-23 23:58 | 0 | 273 | 2015-05-24 11:33 | 1
274 | 2015-05-24 00:11 | 1 | 274 | 2015-05-24 12:24 | 0
275 | 2015-05-24 00:45 | 0 | 275 | 2015-05-24 12:45 | 1
276 | 2015-05-24 10:56 | 1 | 276 | 2015-05-24 13:15 | 0
277 | 2015-05-24 11:37 | 0 | 277 | 2015-05-24 13:26 | 1
278 | 2015-05-24 11:38 | 1 | 278 | 2015-05-24 13:59 | 0
279 | 2015-05-24 12:18 | 0 | 279 | 2015-05-24 14:07 | 1
280 | 2015-05-24 12:47 | 1 | 280 | 2015-05-24 14:27 | 0
281 | 2015-05-24 13:18 | 0 | 281 | 2015-05-24 14:48 | 1
282 | 2015-05-24 13:19 | 1 | 282 | 2015-05-24 15:10 | 0
283 | 2015-05-24 13:29 | 0 | 283 | 2015-05-24 15:36 | 1
284 | 2015-05-24 13:39 | 1 | 284 | 2015-05-24 16:26 | 0
285 | 2015-05-24 14:04 | 0 | 285 | 2015-05-24 17:10 | 1
286 | 2015-05-24 14:04 | 1 | 286 | 2015-05-24 17:36 | 0
287 | 2015-05-24 14:13 | 0 | 287 | 2015-05-24 17:36 | 1
288 | 2015-05-24 14:19 | 1 | 288 | 2015-05-24 17:58 | 0
289 | 2015-05-24 14:34 | 0 | 289 | 2015-05-24 18:04 | 1
290 | 2015-05-24 14:34 | 1 | 290 | 2015-05-24 18:44 | 0
291 | 2015-05-24 14:49 | 0 | 291 | 2015-05-24 18:47 | 1
292 | 2015-05-24 15:04 | 1 | 292 | 2015-05-24 19:47 | 0
293 | 2015-05-24 15:44 | 0 | 293 | 2015-05-24 19:54 | 1
294 | 2015-05-24 15:48 | 1 | 294 | 2015-05-24 20:51 | 0
295 | 2015-05-24 16:26 | 0 | 295 | 2015-05-24 20:59 | 1
296 | 2015-05-24 17:15 | 1 | 296 | 2015-05-24 21:58 | 0
297 | 2015-05-24 17:45 | 0 | 297 | 2015-05-24 22:41 | 1
298 | 2015-05-24 17:47 | 1 | 298 | 2015-05-24 23:18 | 0
299 | 2015-05-24 17:58 | 0 | 299 | 2015-05-24 23:49 | 1
300 | 2015-05-24 18:08 | 1 | 300 | 2015-05-25 00:53 | 0
301 | 2015-05-24 18:41 | 0 | 301 | 2015-05-25 01:13 | 1
302 | 2015-05-24 19:06 | 1 | 302 | 2015-05-25 02:02 | 0
303 | 2015-05-24 19:46 | 0 | 303 | 2015-05-25 04:53 | 1
304 | 2015-05-24 20:52 | 1 | 304 | 2015-05-25 05:38 | 0
305 | 2015-05-24 21:32 | 0 | 305 | 2015-05-25 09:21 | 1
306 | 2015-05-24 21:50 | 1 | 306 | 2015-05-25 09:22 | 0
307 | 2015-05-24 22:30 | 0 | 307 | 2015-05-25 09:26 | 1
308 | 2015-05-24 22:38 | 1 | 308 | 2015-05-25 10:07 | 0
309 | 2015-05-24 23:18 | 0 | 309 | 2015-05-25 10:09 | 1
310 | 2015-05-24 23:44 | 1 | 310 | 2015-05-25 10:39 | 0
311 | 2015-05-25 00:20 | 0 | 311 | 2015-05-25 11:54 | 1
312 | 2015-05-25 01:08 | 1 | 312 | 2015-05-25 12:40 | 0
313 | 2015-05-25 01:43 | 0 | 313 | 2015-05-25 13:12 | 1
314 | 2015-05-25 04:51 | 1 | 314 | 2015-05-25 13:51 | 0
315 | 2015-05-25 05:28 | 0 | 315 | 2015-05-25 13:53 | 1
316 | 2015-05-25 12:53 | 1 | 316 | 2015-05-25 14:12 | 0
317 | 2015-05-25 13:16 | 0 | 317 | 2015-05-25 14:12 | 1
318 | 2015-05-25 13:55 | 1 | 318 | 2015-05-25 14:32 | 0
319 | 2015-05-25 14:22 | 0 | 319 | 2015-05-25 14:35 | 1
320 | 2015-05-25 15:13 | 1 | 320 | 2015-05-25 14:59 | 0
321 | 2015-05-25 15:13 | 0 | 321 | 2015-05-25 15:00 | 1
322 | 2015-05-25 15:13 | 1 | 322 | 2015-05-25 15:19 | 0
323 | 2015-05-25 15:35 | 0 | 323 | 2015-05-25 15:57 | 1
324 | 2015-05-25 16:08 | 1 | 324 | 2015-05-25 16:20 | 0
325 | 2015-05-25 16:31 | 0 | 325 | 2015-05-25 17:57 | 1
326 | 2015-05-25 16:31 | 1 | 326 | 2015-05-25 18:35 | 0
327 | 2015-05-25 16:33 | 0 | 327 | 2015-05-25 18:36 | 1
328 | 2015-05-25 16:34 | 1 | 328 | 2015-05-25 18:56 | 0
329 | 2015-05-25 16:40 | 0 | 329 | 2015-05-25 18:57 | 1
330 | 2015-05-25 16:48 | 1 | 330 | 2015-05-25 20:00 | 0
331 | 2015-05-25 17:31 | 0 | 331 | 2015-05-25 20:03 | 1
332 | 2015-05-25 17:31 | 1 | 332 | 2015-05-25 20:57 | 0
333 | 2015-05-25 17:45 | 0 | 333 | 2015-05-25 21:02 | 1
334 | 2015-05-25 18:00 | 1 | 334 | 2015-05-25 21:51 | 0
335 | 2015-05-25 18:49 | 0 | 335 | 2015-05-25 21:59 | 1
336 | 2015-05-25 18:53 | 1 | 336 | 2015-05-25 22:48 | 0
337 | 2015-05-25 19:45 | 0 | 337 | 2015-05-25 22:57 | 1
338 | 2015-05-25 20:00 | 1 | 338 | 2015-05-25 23:36 | 0
339 | 2015-05-25 20:47 | 0 | 339 | 2015-05-25 23:44 | 1
340 | 2015-05-25 21:00 | 1 | 340 | 2015-05-26 00:41 | 0
341 | 2015-05-25 21:51 | 0 | 341 | 2015-05-26 00:48 | 1
342 | 2015-05-25 21:56 | 1 | 342 | 2015-05-26 01:35 | 0
343 | 2015-05-25 22:43 | 0 | 343 | 2015-05-26 01:39 | 1
344 | 2015-05-25 22:51 | 1 | 344 | 2015-05-26 02:26 | 0
345 | 2015-05-25 23:35 | 0 | 345 | 2015-05-26 02:48 | 1
346 | 2015-05-26 00:01 | 1 | 346 | 2015-05-26 03:34 | 0
347 | 2015-05-26 00:36 | 0 | 347 | 2015-05-26 03:50 | 1
348 | 2015-05-26 00:46 | 1 | 348 | 2015-05-26 04:36 | 0
349 | 2015-05-26 01:23 | 0 | 349 | 2015-05-26 04:41 | 1
350 | 2015-05-26 01:33 | 1 | 350 | 2015-05-26 05:31 | 0
351 | 2015-05-26 02:15 | 0 | 351 | 2015-05-26 11:06 | 1
352 | 2015-05-26 03:26 | 1 | 352 | 2015-05-26 11:57 | 0
353 | 2015-05-26 04:11 | 0 | 353 | 2015-05-26 12:09 | 1
354 | 2015-05-26 04:40 | 1 | 354 | 2015-05-26 12:56 | 0
355 | 2015-05-26 05:15 | 0 | 355 | 2015-05-26 13:20 | 1
356 | 2015-05-26 11:13 | 1 | 356 | 2015-05-26 14:15 | 0
357 | 2015-05-26 11:45 | 0 | 357 | 2015-05-26 14:35 | 1
358 | 2015-05-26 12:05 | 1 | 358 | 2015-05-26 15:30 | 0
359 | 2015-05-26 12:43 | 0 | 359 | 2015-05-26 17:19 | 1
360 | 2015-05-26 12:56 | 1 | 360 | 2015-05-26 18:07 | 0
361 | 2015-05-26 13:10 | 0 | 361 | 2015-05-26 18:34 | 1
362 | 2015-05-26 13:29 | 1 | 362 | 2015-05-26 19:31 | 0
363 | 2015-05-26 14:00 | 0 | 363 | 2015-05-26 19:37 | 1
364 | 2015-05-26 14:01 | 1 | 364 | 2015-05-26 20:35 | 0
365 | 2015-05-26 14:09 | 0 | 365 | 2015-05-26 21:57 | 1
366 | 2015-05-26 14:13 | 1 | 366 | 2015-05-26 22:42 | 0
367 | 2015-05-26 14:56 | 0 | 367 | 2015-05-27 05:14 | 1
368 | 2015-05-26 15:50 | 1 | 368 | 2015-05-27 06:02 | 0
369 | 2015-05-26 16:28 | 0 | 369 | 2015-05-27 11:34 | 1
370 | 2015-05-26 17:15 | 1 | 370 | 2015-05-27 12:26 | 0
371 | 2015-05-26 17:50 | 0 | 371 | 2015-05-27 12:41 | 1
372 | 2015-05-26 18:37 | 1 | 372 | 2015-05-27 13:21 | 0
373 | 2015-05-26 19:17 | 0 | 373 | 2015-05-27 13:42 | 1
374 | 2015-05-26 19:29 | 1 | 374 | 2015-05-27 14:24 | 0
375 | 2015-05-26 20:12 | 0 | 375 | 2015-05-27 14:27 | 1
376 | 2015-05-27 05:16 | 1 | 376 | 2015-05-27 15:03 | 0
377 | 2015-05-27 05:52 | 0 | 377 | 2015-05-27 15:08 | 1
378 | 2015-05-27 11:41 | 1 | 378 | 2015-05-27 16:04 | 0
379 | 2015-05-27 12:17 | 0 | 379 | 2015-05-27 16:09 | 1
380 | 2015-05-27 12:49 | 1 | 380 | 2015-05-27 17:16 | 0
381 | 2015-05-27 13:28 | 0 | 381 | 2015-05-27 18:09 | 1
382 | 2015-05-27 13:38 | 1 | 382 | 2015-05-27 18:52 | 0
383 | 2015-05-27 14:17 | 0 | 383 | 2015-05-27 19:45 | 1
384 | 2015-05-27 14:30 | 1 | 384 | 2015-05-27 20:33 | 0
385 | 2015-05-27 15:08 | 0 | 385 | 2015-05-27 20:35 | 1
386 | 2015-05-27 16:15 | 1 | 386 | 2015-05-27 21:42 | 0
387 | 2015-05-27 17:08 | 0 | 387 | 2015-05-27 22:46 | 1
388 | 2015-05-27 17:11 | 1 | 388 | 2015-05-27 23:29 | 0
389 | 2015-05-27 17:48 | 0 | 389 | 2015-05-27 23:31 | 1
390 | 2015-05-27 18:42 | 1 | 390 | 2015-05-28 00:21 | 0
391 | 2015-05-27 19:22 | 0 | 391 | 2015-05-28 08:08 | 1
392 | 2015-05-27 19:43 | 1 | 392 | 2015-05-28 08:21 | 0
393 | 2015-05-27 20:20 | 0 | 393 | 2015-05-28 08:52 | 1
394 | 2015-05-27 20:33 | 1 | 394 | 2015-05-28 09:10 | 0
395 | 2015-05-27 20:39 | 0 | 395 | 2015-05-28 11:22 | 1
396 | 2015-05-27 20:40 | 1 | 396 | 2015-05-28 11:56 | 0
397 | 2015-05-27 20:42 | 0 | 397 | 2015-05-28 12:22 | 1
398 | 2015-05-27 21:33 | 1 | 398 | 2015-05-28 12:51 | 0
399 | 2015-05-27 22:10 | 0 | 399 | 2015-05-28 13:07 | 1
400 | 2015-05-27 22:45 | 1 | 400 | 2015-05-28 13:48 | 0
401 | 2015-05-27 23:37 | 0 | 401 | 2015-05-28 13:52 | 1
402 | 2015-05-28 10:28 | 1 | 402 | 2015-05-28 14:26 | 0
403 | 2015-05-28 10:45 | 0 | 403 | 2015-05-28 14:54 | 1
404 | 2015-05-28 10:45 | 1 | 404 | 2015-05-28 15:22 | 0
405 | 2015-05-28 10:58 | 0 | 405 | 2015-05-28 15:49 | 1
406 | 2015-05-28 11:28 | 1 | 406 | 2015-05-28 16:23 | 0
407 | 2015-05-28 11:58 | 0 | 407 | 2015-05-28 16:35 | 1
408 | 2015-05-28 12:26 | 1 | 408 | 2015-05-28 17:13 | 0
409 | 2015-05-28 12:48 | 0 | 409 | 2015-05-28 17:27 | 1
410 | 2015-05-28 12:48 | 1 | 410 | 2015-05-28 18:26 | 0
411 | 2015-05-28 12:52 | 0 | 411 | 2015-05-28 18:31 | 1
412 | 2015-05-28 12:53 | 1 | 412 | 2015-05-28 19:19 | 0
413 | 2015-05-28 13:09 | 0 | 413 | 2015-05-28 19:23 | 1
414 | 2015-05-28 13:11 | 1 | 414 | 2015-05-28 20:10 | 0
415 | 2015-05-28 13:52 | 0 | 415 | 2015-05-28 20:13 | 1
416 | 2015-05-28 13:55 | 1 | 416 | 2015-05-28 21:07 | 0
417 | 2015-05-28 14:21 | 0 | 417 | 2015-05-28 21:39 | 1
418 | 2015-05-28 14:47 | 1 | 418 | 2015-05-28 22:28 | 0
419 | 2015-05-28 15:31 | 0 | 419 | 2015-05-28 22:32 | 1
420 | 2015-05-28 15:56 | 1 | 420 | 2015-05-28 23:31 | 0
421 | 2015-05-28 16:21 | 0 | 421 | 2015-05-28 23:51 | 1
422 | 2015-05-28 16:23 | 1 | 422 | 2015-05-29 00:43 | 0
423 | 2015-05-28 16:55 | 0 | 423 | 2015-05-29 10:48 | 1
424 | 2015-05-28 17:06 | 1 | 424 | 2015-05-29 10:54 | 0
425 | 2015-05-28 17:36 | 0 | 425 | 2015-05-29 10:57 | 1
426 | 2015-05-28 18:23 | 1 | 426 | 2015-05-29 11:35 | 0
427 | 2015-05-28 19:02 | 0 | 427 | 2015-05-29 11:44 | 1
428 | 2015-05-28 19:14 | 1 | 428 | 2015-05-29 12:26 | 0
429 | 2015-05-28 20:05 | 0 | 429 | 2015-05-29 12:28 | 1
430 | 2015-05-28 21:03 | 1 | 430 | 2015-05-29 13:07 | 0
431 | 2015-05-28 21:43 | 0 | 431 | 2015-05-29 13:09 | 1
432 | 2015-05-28 21:46 | 1 | 432 | 2015-05-29 13:23 | 0
433 | 2015-05-28 22:28 | 0 | 433 | 2015-05-29 13:24 | 1
434 | 2015-05-28 22:57 | 1 | 434 | 2015-05-29 13:53 | 0
435 | 2015-05-28 23:44 | 0 | 435 | 2015-05-29 14:02 | 1
436 | 2015-05-28 23:54 | 1 | 436 | 2015-05-29 14:33 | 0
437 | 2015-05-29 00:31 | 0 | 437 | 2015-05-29 14:49 | 1
438 | 2015-05-29 10:58 | 1 | 438 | 2015-05-29 15:00 | 0
439 | 2015-05-29 11:29 | 0 | 439 | 2015-05-29 15:00 | 1
440 | 2015-05-29 11:36 | 1 | 440 | 2015-05-29 15:17 | 0
441 | 2015-05-29 12:05 | 0 | 441 | 2015-05-29 16:03 | 1
442 | 2015-05-29 12:34 | 1 | 442 | 2015-05-29 16:31 | 0
443 | 2015-05-29 13:00 | 0 | 443 | 2015-05-29 16:32 | 1
444 | 2015-05-29 13:06 | 1 | 444 | 2015-05-29 17:09 | 0
445 | 2015-05-29 13:25 | 0 | 445 | 2015-05-29 17:11 | 1
446 | 2015-05-29 13:25 | 1 | 446 | 2015-05-29 17:54 | 0
447 | 2015-05-29 13:43 | 0 | 447 | 2015-05-29 19:18 | 1
448 | 2015-05-29 13:59 | 1 | 448 | 2015-05-29 20:12 | 0
449 | 2015-05-29 14:21 | 0 | 449 | 2015-05-29 20:29 | 1
450 | 2015-05-29 14:27 | 1 | 450 | 2015-05-29 21:22 | 0
451 | 2015-05-29 14:30 | 0 | 451 | 2015-05-29 21:25 | 1
452 | 2015-05-29 14:30 | 1 | 452 | 2015-05-29 22:21 | 0
453 | 2015-05-29 14:36 | 0 | 453 | 2015-05-29 22:34 | 1
454 | 2015-05-29 14:43 | 1 | 454 | 2015-05-29 23:41 | 0
455 | 2015-05-29 15:00 | 0 | 455 | 2015-05-29 23:50 | 1
456 | 2015-05-29 15:02 | 1 | 456 | 2015-05-30 00:20 | 0
457 | 2015-05-29 15:12 | 0 | 457 | 2015-05-30 01:01 | 1
458 | 2015-05-29 15:41 | 1 | 458 | 2015-05-30 01:59 | 0
459 | 2015-05-29 16:16 | 0 | 459 | 2015-05-30 11:16 | 1
460 | 2015-05-29 17:23 | 1 | 460 | 2015-05-30 11:53 | 0
461 | 2015-05-29 17:55 | 0 | 461 | 2015-05-30 12:01 | 1
462 | 2015-05-29 18:10 | 1 | 462 | 2015-05-30 12:46 | 0
463 | 2015-05-29 19:02 | 0 | 463 | 2015-05-30 12:55 | 1
464 | 2015-05-29 19:26 | 1 | 464 | 2015-05-30 13:48 | 0
465 | 2015-05-29 20:06 | 0 | 465 | 2015-05-30 13:49 | 1
466 | 2015-05-29 20:26 | 1 | 466 | 2015-05-30 14:24 | 0
467 | 2015-05-29 21:16 | 0 | 467 | 2015-05-30 14:42 | 1
468 | 2015-05-29 21:31 | 1 | 468 | 2015-05-30 15:05 | 0
469 | 2015-05-29 22:00 | 0 | 469 | 2015-05-30 15:13 | 1
470 | 2015-05-29 22:29 | 1 | 470 | 2015-05-30 16:17 | 0
471 | 2015-05-29 23:06 | 0 | 471 | 2015-05-30 18:11 | 1
472 | 2015-05-29 23:39 | 1 | 472 | 2015-05-30 18:57 | 0
473 | 2015-05-30 00:31 | 0 | 473 | 2015-05-30 19:03 | 1
474 | 2015-05-30 01:01 | 1 | 474 | 2015-05-30 19:50 | 0
475 | 2015-05-30 01:35 | 0 | 475 | 2015-05-30 19:59 | 1
476 | 2015-05-30 11:02 | 1 | 476 | 2015-05-30 20:41 | 0
477 | 2015-05-30 11:39 | 0 | 477 | 2015-05-30 20:59 | 1
478 | 2015-05-30 11:53 | 1 | 478 | 2015-05-30 21:43 | 0
479 | 2015-05-30 12:32 | 0 | 479 | 2015-05-30 21:57 | 1
480 | 2015-05-30 12:54 | 1 | 480 | 2015-05-30 23:01 | 0
481 | 2015-05-30 13:13 | 0 | 481 | 2015-05-30 23:18 | 1
482 | 2015-05-30 13:13 | 1 | 482 | 2015-05-31 00:03 | 0
483 | 2015-05-30 13:36 | 0 | 483 | 2015-05-31 00:15 | 1
484 | 2015-05-30 13:47 | 1 | 484 | 2015-05-31 00:58 | 0
485 | 2015-05-30 14:20 | 0 | 485 | 2015-05-31 01:02 | 1
486 | 2015-05-30 14:29 | 1 | 486 | 2015-05-31 02:10 | 0
487 | 2015-05-30 15:20 | 0 | 487 | 2015-05-31 02:54 | 1
488 | 2015-05-30 15:27 | 1 | 488 | 2015-05-31 04:16 | 0
489 | 2015-05-30 16:13 | 0 | 489 | 2015-05-31 11:04 | 1
490 | 2015-05-30 18:15 | 1 | 490 | 2015-05-31 11:33 | 0
491 | 2015-05-30 19:03 | 0 | 491 | 2015-05-31 11:46 | 1
492 | 2015-05-30 19:07 | 1 | 492 | 2015-05-31 12:37 | 0
493 | 2015-05-30 19:50 | 0 | 493 | 2015-05-31 12:44 | 1
494 | 2015-05-30 20:02 | 1 | 494 | 2015-05-31 13:16 | 0
495 | 2015-05-30 20:42 | 0 | 495 | 2015-05-31 13:28 | 1
496 | 2015-05-30 21:01 | 1 | 496 | 2015-05-31 14:01 | 0
497 | 2015-05-30 21:43 | 0 | 497 | 2015-05-31 14:11 | 1
498 | 2015-05-30 23:21 | 1 | 498 | 2015-05-31 14:45 | 0
499 | 2015-05-31 00:02 | 0 | 499 | 2015-05-31 14:55 | 1
500 | 2015-05-31 00:10 | 1 | 500 | 2015-05-31 15:22 | 0
501 | 2015-05-31 00:49 | 0 | 501 | 2015-05-31 15:34 | 1
502 | 2015-05-31 01:16 | 1 | 502 | 2015-05-31 16:25 | 0
503 | 2015-05-31 02:00 | 0 | 503 | 2015-05-31 16:38 | 1
504 | 2015-05-31 02:54 | 1 | 504 | 2015-05-31 17:40 | 0
505 | 2015-05-31 03:32 | 0 | 505 | 2015-05-31 17:58 | 1
506 | 2015-05-31 11:08 | 1 | 506 | 2015-05-31 18:52 | 0
507 | 2015-05-31 11:27 | 0 | 507 | 2015-05-31 19:03 | 1
508 | 2015-05-31 11:27 | 1 | 508 | 2015-05-31 19:52 | 0
509 | 2015-05-31 11:42 | 0 | 509 | 2015-05-31 19:58 | 1
510 | 2015-05-31 11:53 | 1 | 510 | 2015-05-31 20:46 | 0
511 | 2015-05-31 12:32 | 0 | 511 | 2015-05-31 23:36 | 1
512 | 2015-05-31 12:43 | 1 | 512 | 2015-06-01 00:30 | 0
513 | 2015-05-31 13:13 | 0 | 513 | 2015-06-01 01:22 | 1
514 | 2015-05-31 13:14 | 1 | 514 | 2015-06-01 02:14 | 0
515 | 2015-05-31 13:45 | 0 | 515 | 2015-06-01 10:39 | 1
516 | 2015-05-31 13:55 | 1 | 516 | 2015-06-01 11:15 | 0
517 | 2015-05-31 14:21 | 0 | 517 | 2015-06-01 11:35 | 1
518 | 2015-05-31 14:21 | 1 | 518 | 2015-06-01 12:26 | 0
519 | 2015-05-31 14:25 | 0 | 519 | 2015-06-01 12:32 | 1
520 | 2015-05-31 14:25 | 1 | 520 | 2015-06-01 13:15 | 0
521 | 2015-05-31 14:28 | 0 | 521 | 2015-06-01 13:21 | 1
522 | 2015-05-31 14:36 | 1 | 522 | 2015-06-01 13:49 | 0
523 | 2015-05-31 14:59 | 0 | 523 | 2015-06-01 14:02 | 1
524 | 2015-05-31 14:59 | 1 | 524 | 2015-06-01 14:41 | 0
525 | 2015-05-31 15:08 | 0 | 525 | 2015-06-01 14:42 | 1
526 | 2015-05-31 15:19 | 1 | 526 | 2015-06-01 15:15 | 0
527 | 2015-05-31 16:01 | 0 | 527 | 2015-06-01 15:21 | 1
528 | 2015-05-31 16:36 | 1 | 528 | 2015-06-01 16:16 | 0
529 | 2015-05-31 17:19 | 0 | 529 | 2015-06-01 19:11 | 1
530 | 2015-05-31 17:52 | 1 | 530 | 2015-06-01 20:10 | 0
531 | 2015-05-31 18:32 | 0 | 531 | 2015-06-01 20:20 | 1
532 | 2015-05-31 18:57 | 1 | 532 | 2015-06-01 21:11 | 0
533 | 2015-05-31 19:36 | 0 | 533 | 2015-06-01 21:20 | 1
534 | 2015-05-31 19:56 | 1 | 534 | 2015-06-01 22:10 | 0
535 | 2015-05-31 20:35 | 0 | 535 | 2015-06-01 22:41 | 1
536 | 2015-05-31 23:30 | 1 | 536 | 2015-06-01 23:35 | 0
537 | 2015-06-01 00:09 | 0 | 537 | 2015-06-01 23:40 | 1
538 | 2015-06-01 00:21 | 1 | 538 | 2015-06-02 00:46 | 0
539 | 2015-06-01 00:55 | 0 | 539 | 2015-06-02 01:36 | 1
540 | 2015-06-01 01:25 | 1 | 540 | 2015-06-02 02:21 | 0
541 | 2015-06-01 02:07 | 0 | 541 | 2015-06-02 03:12 | 1
542 | 2015-06-01 04:58 | 1 | 542 | 2015-06-02 03:59 | 0
543 | 2015-06-01 05:34 | 0 | 543 | 2015-06-02 04:59 | 1
544 | 2015-06-01 10:56 | 1 | 544 | 2015-06-02 05:46 | 0
545 | 2015-06-01 11:36 | 0 | 545 | 2015-06-02 11:10 | 1
546 | 2015-06-01 11:42 | 1 | 546 | 2015-06-02 11:48 | 0
547 | 2015-06-01 12:17 | 0 | 547 | 2015-06-02 11:56 | 1
548 | 2015-06-01 12:39 | 1 | 548 | 2015-06-02 12:24 | 0
549 | 2015-06-01 13:08 | 0 | 549 | 2015-06-02 12:24 | 1
550 | 2015-06-01 13:25 | 1 | 550 | 2015-06-02 12:34 | 0
551 | 2015-06-01 13:26 | 0 | 551 | 2015-06-02 13:06 | 1
552 | 2015-06-01 13:27 | 1 | 552 | 2015-06-02 13:45 | 0
553 | 2015-06-01 13:57 | 0 | 553 | 2015-06-02 13:46 | 1
554 | 2015-06-01 14:15 | 1 | 554 | 2015-06-02 14:27 | 0
555 | 2015-06-01 14:49 | 0 | 555 | 2015-06-02 14:29 | 1
556 | 2015-06-01 14:51 | 1 | 556 | 2015-06-02 15:22 | 0
557 | 2015-06-01 15:31 | 0 | 557 | 2015-06-02 16:06 | 1
558 | 2015-06-01 19:15 | 1 | 558 | 2015-06-02 17:00 | 0
559 | 2015-06-01 20:03 | 0 | 559 | 2015-06-02 17:02 | 1
560 | 2015-06-01 20:14 | 1 | 560 | 2015-06-02 17:45 | 0
561 | 2015-06-01 20:50 | 0 | 561 | 2015-06-02 17:48 | 1
562 | 2015-06-01 21:19 | 1 | 562 | 2015-06-02 18:53 | 0
563 | 2015-06-01 21:55 | 0 | 563 | 2015-06-02 19:42 | 1
564 | 2015-06-01 22:44 | 1 | 564 | 2015-06-02 20:37 | 0
565 | 2015-06-01 23:30 | 0 | 565 | 2015-06-02 20:38 | 1
566 | 2015-06-01 23:42 | 1 | 566 | 2015-06-02 21:33 | 0
567 | 2015-06-02 00:31 | 0 | 567 | 2015-06-02 23:45 | 1
568 | 2015-06-02 00:46 | 1 | 568 | 2015-06-03 00:31 | 0
569 | 2015-06-02 01:23 | 0 | 569 | 2015-06-03 00:43 | 1
570 | 2015-06-02 11:15 | 1 | 570 | 2015-06-03 01:30 | 0
571 | 2015-06-02 11:48 | 0 | 571 | 2015-06-03 10:39 | 1
572 | 2015-06-02 12:01 | 1 | 572 | 2015-06-03 11:27 | 0
573 | 2015-06-02 12:37 | 0 | 573 | 2015-06-03 11:33 | 1
574 | 2015-06-02 13:13 | 1 | 574 | 2015-06-03 12:24 | 0
575 | 2015-06-02 13:53 | 0 | 575 | 2015-06-03 12:29 | 1
576 | 2015-06-02 13:55 | 1 | 576 | 2015-06-03 13:20 | 0
577 | 2015-06-02 14:34 | 0 | 577 | 2015-06-03 13:22 | 1
578 | 2015-06-02 14:36 | 1 | 578 | 2015-06-03 13:53 | 0
579 | 2015-06-02 15:15 | 0 | 579 | 2015-06-03 13:55 | 1
580 | 2015-06-02 15:16 | 1 | 580 | 2015-06-03 14:14 | 0
581 | 2015-06-02 15:56 | 0 | 581 | 2015-06-03 14:15 | 1
582 | 2015-06-02 16:09 | 1 | 582 | 2015-06-03 14:54 | 0
583 | 2015-06-02 16:53 | 0 | 583 | 2015-06-03 14:56 | 1
584 | 2015-06-02 17:12 | 1 | 584 | 2015-06-03 15:46 | 0
585 | 2015-06-02 17:54 | 0 | 585 | 2015-06-03 17:53 | 1
586 | 2015-06-02 18:11 | 1 | 586 | 2015-06-03 19:08 | 0
587 | 2015-06-02 18:52 | 0 | 587 | 2015-06-03 19:27 | 1
588 | 2015-06-02 19:39 | 1 | 588 | 2015-06-03 20:21 | 0
589 | 2015-06-02 20:18 | 0 | 589 | 2015-06-03 20:40 | 1
590 | 2015-06-02 23:43 | 1 | 590 | 2015-06-03 21:43 | 0
591 | 2015-06-03 00:23 | 0 | 591 | 2015-06-03 21:45 | 1
592 | 2015-06-03 06:19 | 1 | 592 | 2015-06-03 22:42 | 0
593 | 2015-06-03 06:55 | 0 | 593 | 2015-06-03 23:34 | 1
594 | 2015-06-03 10:41 | 1 | 594 | 2015-06-04 00:05 | 0
595 | 2015-06-03 11:19 | 0 | 595 | 2015-06-04 05:38 | 1
596 | 2015-06-03 11:27 | 1 | 596 | 2015-06-04 06:26 | 0
597 | 2015-06-03 12:08 | 0 | 597 | 2015-06-04 10:18 | 1
598 | 2015-06-03 12:35 | 1 | 598 | 2015-06-04 10:39 | 0
599 | 2015-06-03 13:13 | 0 | 599 | 2015-06-04 11:07 | 1
600 | 2015-06-03 13:14 | 1 | 600 | 2015-06-04 11:48 | 0
601 | 2015-06-03 13:49 | 0 | 601 | 2015-06-04 12:06 | 1
602 | 2015-06-03 13:53 | 1 | 602 | 2015-06-04 12:43 | 0
603 | 2015-06-03 14:10 | 0 | 603 | 2015-06-04 13:09 | 1
604 | 2015-06-03 14:10 | 1 | 604 | 2015-06-04 13:32 | 0
605 | 2015-06-03 14:12 | 0 | 605 | 2015-06-04 13:42 | 1
606 | 2015-06-03 14:12 | 1 | 606 | 2015-06-04 14:21 | 0
607 | 2015-06-03 14:17 | 0 | 607 | 2015-06-04 14:27 | 1
608 | 2015-06-03 14:34 | 1 | 608 | 2015-06-04 14:50 | 0
609 | 2015-06-03 15:07 | 0 | 609 | 2015-06-04 15:19 | 1
610 | 2015-06-03 15:16 | 1 | 610 | 2015-06-04 15:49 | 0
611 | 2015-06-03 15:56 | 0 | 611 | 2015-06-04 17:23 | 1
612 | 2015-06-03 19:18 | 1 | 612 | 2015-06-04 18:11 | 0
613 | 2015-06-03 19:58 | 0 | 613 | 2015-06-04 18:12 | 1
614 | 2015-06-03 21:00 | 1 | 614 | 2015-06-04 19:00 | 0
615 | 2015-06-03 21:42 | 0 | 615 | 2015-06-04 19:02 | 1
616 | 2015-06-03 21:44 | 1 | 616 | 2015-06-04 20:22 | 0
617 | 2015-06-03 22:28 | 0 | 617 | 2015-06-04 21:07 | 1
618 | 2015-06-03 22:37 | 1 | 618 | 2015-06-04 22:09 | 0
619 | 2015-06-03 22:55 | 0 | 619 | 2015-06-04 23:01 | 1
620 | 2015-06-03 22:55 | 1 | 620 | 2015-06-05 00:03 | 0
621 | 2015-06-03 23:11 | 0 | 621 | 2015-06-05 09:57 | 1
622 | 2015-06-03 23:35 | 1 | 622 | 2015-06-05 10:30 | 0
623 | 2015-06-04 00:08 | 0 | 623 | 2015-06-05 10:44 | 1
624 | 2015-06-04 10:16 | 1 | 624 | 2015-06-05 11:22 | 0
625 | 2015-06-04 10:33 | 0 | 625 | 2015-06-05 11:25 | 1
626 | 2015-06-04 10:34 | 1 | 626 | 2015-06-05 12:16 | 0
627 | 2015-06-04 10:45 | 0 | 627 | 2015-06-05 12:22 | 1
628 | 2015-06-04 12:09 | 1 | 628 | 2015-06-05 12:32 | 0
629 | 2015-06-04 12:30 | 0 | 629 | 2015-06-05 12:32 | 1
630 | 2015-06-04 12:53 | 1 | 630 | 2015-06-05 12:38 | 0
631 | 2015-06-04 13:22 | 0 | 631 | 2015-06-05 12:45 | 1
632 | 2015-06-04 13:53 | 1 | 632 | 2015-06-05 13:26 | 0
633 | 2015-06-04 14:27 | 0 | 633 | 2015-06-05 13:41 | 1
634 | 2015-06-04 14:39 | 1 | 634 | 2015-06-05 14:15 | 0
635 | 2015-06-04 15:10 | 0 | 635 | 2015-06-05 14:24 | 1
636 | 2015-06-04 15:25 | 1 | 636 | 2015-06-05 14:57 | 0
637 | 2015-06-04 15:42 | 0 | 637 | 2015-06-05 15:05 | 1
638 | 2015-06-04 15:43 | 1 | 638 | 2015-06-05 15:58 | 0
639 | 2015-06-04 16:02 | 0 | 639 | 2015-06-05 16:06 | 1
640 | 2015-06-04 17:20 | 1 | 640 | 2015-06-05 17:02 | 0
641 | 2015-06-04 18:09 | 0
642 | 2015-06-04 18:10 | 1
643 | 2015-06-04 18:49 | 0
644 | 2015-06-04 19:06 | 1
645 | 2015-06-04 19:49 | 0
646 | 2015-06-04 20:04 | 1
647 | 2015-06-04 20:45 | 0
648 | 2015-06-04 22:59 | 1
649 | 2015-06-04 23:43 | 0
650 | 2015-06-05 10:09 | 1
651 | 2015-06-05 10:51 | 0
652 | 2015-06-05 10:55 | 1
653 | 2015-06-05 11:35 | 0
654 | 2015-06-05 11:41 | 1
655 | 2015-06-05 12:21 | 0
656 | 2015-06-05 12:27 | 1
657 | 2015-06-05 13:08 | 0
658 | 2015-06-05 13:21 | 1
659 | 2015-06-05 14:00 | 0
660 | 2015-06-05 14:02 | 1
661 | 2015-06-05 14:30 | 0
662 | 2015-06-05 14:39 | 1
663 | 2015-06-05 15:19 | 0
664 | 2015-06-05 16:11 | 1
665 | 2015-06-05 16:47 | 0