Workpaper WPSCGNRHC120206A

Revision 4

Southern California Gas Company

Customer Programs Department

Space Heating Boilers

Revision History

| Revision No. | Date | Description | Author |
| --- | --- | --- | --- |
| 0 | Mar. 20, 2006 | Original release | Stu Knoke (EEA) |
| 2 | May 18, 2012 | Updated cost and efficiency data | Stu Knoke (ICF) |
| 3 | January 29, 2014 | Updated cost and Deer 2014 efficiency data | Raad Bashar (SCG) |
| 4 | March 17, 2014 | Removed Boilers with Atmospheric type Combustion from the rebate list of boilers. Adjusted the measure efficiency to fit the minimum requirement in SCG’s rebate program for 2014-2015. | Chan Paek / Raad Bashar (SCG) |

| Measure ID | Measure Name | Program Application Type (RE, NC, ROB, ER, etc) | EUR/RUL (yr) | CZ | Building Type | Building Vintage | Unit Definition | NTG IMC | NTG Savings | Program Delivery Method (CustIncent, PreReb, Dirinstall, etc) | Gross Realization Rate (GRR) | % Eligible for TOU AC Adjustment |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | RobNc | 20 | 1 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 2 | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | RobNc | 20 | 2 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 17 | NG-HVAC-Blr-HW-300to2500kBtuh-85p0ET-Drft | RobNc | 20 | 1 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 18 | NG-HVAC-Blr-HW-300to2500kBtuh-85p0ET-Drft | RobNc | 20 | 2 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 33 | NG-HVAC-Blr-HW-gt2500kBtuh-85p0EC-Drft | RobNc | 20 | 1 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 34 | NG-HVAC-Blr-HW-gt2500kBtuh-85p0EC-Drft | RobNc | 20 | 2 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 49 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-Cnd | RobNc | 20 | 1 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 50 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-Cnd | RobNc | 20 | 2 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 65 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0ET-Cnd | RobNc | 20 | 1 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 66 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0ET-Cnd | RobNc | 20 | 2 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 81 | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft | RobNc | 20 | 1 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 82 | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft | RobNc | 20 | 2 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 97 | NG-HVAC-Blr-Stm-300to2500kBtuh-85p0ET-Drft | RobNc | 20 | 1 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 98 | NG-HVAC-Blr-Stm-300to2500kBtuh-85p0ET-Drft | RobNc | 20 | 2 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 113 | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0EC-Drft | RobNc | 20 | 1 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |
| 114 | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0EC-Drft | RobNc | 20 | 2 | Com | Ex | Mbtuh | 0.6 | 0.6 | PreReb | 1 | N/A |

Measure Summary Table

| Measure ID |  | Measure Name |  | 1st Baseline |  |  |  |  |  |  |  | 2nd Baseline |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Gas Savings (therms) |  | Base Total Cost ($/unit) |  | Measure Total Cost ($/unit) |  | Incremental Measure Cost ($/unit) |  | Gas Savings (therms) |  | Base Total Cost ($/unit) |  | Measure Total Cost ($/unit) |  | Incremental Measure Cost ($/unit) |  |
| 1 |  | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft |  | 1.67 |  | $20.04 |  | $29.22 |  | $9.18 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 2 |  | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft |  | 1.34 |  | $19.02 |  | $27.74 |  | $8.71 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 17 |  | NG-HVAC-Blr-HW-300to2500kBtuh-85p0ET-Drft |  | 1.57 |  | $10.72 |  | $12.84 |  | $2.12 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 18 |  | NG-HVAC-Blr-HW-300to2500kBtuh-85p0ET-Drft |  | 1.27 |  | $10.18 |  | $12.19 |  | $2.01 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 33 |  | NG-HVAC-Blr-HW-gt2500kBtuh-85p0EC-Drft |  | 2.20 |  | $9.07 |  | $10.07 |  | $1.00 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 34 |  | NG-HVAC-Blr-HW-gt2500kBtuh-85p0EC-Drft |  | 1.76 |  | $8.61 |  | $9.56 |  | $0.95 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 49 |  | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-Cnd |  | 2.01 |  | $20.69 |  | $26.65 |  | $5.96 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 50 |  | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-Cnd |  | 1.62 |  | $19.64 |  | $25.31 |  | $5.66 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 65 |  | NG-HVAC-Blr-HW-300to2500kBtuh-94p0ET-Cnd |  | 2.56 |  | $18.97 |  | $22.40 |  | $22.40 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 66 |  | NG-HVAC-Blr-HW-300to2500kBtuh-94p0ET-Cnd |  | 2.07 |  | $18.01 |  | $21.27 |  | $21.27 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 81 |  | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft |  | 2.04 |  | $21.10 |  | $22.58 |  | $1.48 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 82 |  | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft |  | 1.63 |  | $20.03 |  | $21.44 |  | $1.41 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 97 |  | NG-HVAC-Blr-Stm-300to2500kBtuh-85p0ET-Drft |  | 0.94 |  | $10.55 |  | $12.84 |  | $2.28 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 98 |  | NG-HVAC-Blr-Stm-300to2500kBtuh-85p0ET-Drft |  | 0.76 |  | $10.02 |  | $12.19 |  | $2.17 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 113 |  | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0EC-Drft |  | 3.89 |  | $11.20 |  | $11.98 |  | $0.78 |  | N/A |  | N/A |  | N/A |  | N/A |  |
| 114 |  | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0EC-Drft |  | 3.10 |  | $10.63 |  | $11.37 |  | $0.74 |  | N/A |  | N/A |  | N/A |  | N/A |  |

# Table of Contents

Revision History	i

Measure Summary Table	ii

List of Figures	viii

List of Tables	viii

SECTION 1 - General Measure & Baseline Data	1

1.01	Measure & Delivery Description	1

1.02	DEER Differences Analysis	2

1.03	Code Analysis	3

1.04	Measure Effective Useful Life	3

1.05	Net-to-Gross Ratios for Different Program Strategies	3

1.06	Gross Realization Rate	3

1.07	Time-of-Use Adjustment Factor	4

SECTION 2 - Energy Savings & Demand Reduction Calculations	5

2.01	Load Shapes	5

2.02	Energy Savings	5

SECTION 3 - Base Case & Measure Costs	13

3.01	Base Case Cost	13

3.02	Gross Measure Cost	13

3.03	Incremental Measure Cost	13

3.04	Cost Adjustment for the 16 weather zones in CAlifornia	14

Attachments	16

References	17

List of Figures

Figure 1 -	Distribution of Annual Fuel Utilization Efficiencies for Hot Water Boilers ( <300 MBtu/hr) in the CEC Appliance Efficiency Database	8

Figure 2 -	Distribution of Thermal Efficiencies for Hot Water Boilers (300-2,500 MBtu/hr) in the CEC Appliance Efficiency Database	8

Figure 3 -	Distribution of Combustion Efficiencies for Hot Water Boilers( ≥2,500 MBtu/hr) in the CEC Appliance Efficiency Database	9

Figure 4 -	Distribution of Annual Fuel Utilization Efficiencies for Steam Water Boilers ( <300 MBtu/hr) in the CEC Appliance Efficiency Database	9

Figure 5 -	Distribution of Thermal Efficiencies for Steam Boilers (300-2,500 MBtu/hr) in the CEC Appliance Efficiency Database	10

Figure 6 -	Distribution of Combustion Efficiencies for Steam Boilers ( ≥2,500 MBtu/hr) in the CEC Appliance Efficiency Database	10

List of Tables

Table 1 -	Base and Measure Space Heating Boiler Efficiencies in DEER 2014	5

Table 2 -	Boiler Efficiency Ranges from CEC Appliance Efficiency Database	5

Table 3 -	2013 California Titles 20 and 24 Energy Code Standards2,	6

Table 4 -	Baseline and Measure Efficiency by Equipment Type	11

Table 5 -	Adjusted Baseline and Measure Efficiencies	12

Table 6 -	Gross and Incremental Measure Cost by Equipment Type	14

Table 7 -	Adjustment Factor for Material Cost by Cities in CA	14

General Measure & Baseline Data

Measure & Delivery Description

Measure description

Space heating boilers are pressure vessels that produce hot water or steam for space heating applications.  In most boilers, a heat exchanger separates the combustion products from the water.  Boilers can be configured as an integrated packaged boiler, or in some cases, the boiler may be connected to a separate tank that contains an internal heat exchanger.  Energy efficient units may have one or more of the following features:  high efficiency/low NOx burners, power burners, water tubes, relatively large heat exchange surfaces, and flue exhaust heat recovery systems.

Measures covered in this document exclude atmospheric/natural draft boilers.

According to ASHRAE, there are following types of boilers:

Natural draft boiler: It is designed to operate with a negative pressure in the combustion chamber and in the flue connection. The pressure difference is created by the tendency of hot gases to rise up a chimney or by the height of the boiler up to the draft control device.

Mechanical draft boiler: a fan or blower or other machinery creates the required pressure difference. These boilers may be either forced draft or induced draft.

Forced-draft boiler: air is forced into the combustion chamber to maintain a positive pressure in the combustion chamber and/or the space between the tubing and the jacket (breaching).

Induced draft boiler: air is drawn into the combustion chamber to maintain a negative pressure in the combustion chamber.

The 2006 Space Heating Boilers Workpaper includes a more detailed technology description in its Appendix A.

The 2012 Space Heating Boilers Workpaper for the average gas savings in SCG territories is also attached1.

Market Applicability

These measures are applicable to boilers used primarily for space heating in commercial buildings.

Applicable building/business types include (but are not limited to) offices, restaurants, retail establishments, schools, colleges, hotels, motels, and recreational facilities.

Boilers used primarily for process end uses or domestic hot water do not qualify.

Terms & Conditions

Boiler rebates cannot exceed $25,000 per unit.

Only boilers used primarily for space heating for human comfort uses qualify, as defined by California Titles 20 and 24 standards,

The rebate applies to gas-for-gas equipment replacements on burnout or to new installations in existing buildings.

The rebate does not apply to new construction (NC).

Boilers used for pool or spa heating do not qualify.

The manufacturer’s name and equipment model number must be provided.

If necessary, customers must provide proof of unit efficiency (e.g., manufacturer’s equipment specification sheet).

Delivery Methods

The preferred delivery method is a downstream prescriptive rebate offered to the gas customer purchasing the new boiler.

However, a midstream point-of-sale rebate or an upstream manufacturer rebate strategy may also be implemented.

Boiler Efficiency Type

- The full load efficiency of a boiler is expressed as one of the following2:

- • 	Annual Fuel Utilization Efficiency (AFUE) is a measure of the boiler’s efficiency over a predefined heating season.

- • 	Thermal Efficiency (TE) is the ratio of the heat transferred to the water divided by the heat input of the fuel.

- • 	Combustion Efficiency (CE) is the measure of how much energy is extracted from the fuel and is the ratio of heat transferred to the combustion air divided by the heat input of the fuel.

Qualifying Efficiency

Test methods for determining boiler efficiencies are referenced in the California Title 20 and the new 2013 Title-24 standards.  Following are the minimum qualifying efficiencies for space heating boiler measures.

Minimum qualifying annual fuel utilization efficiency (AFUE) for small (<300 MBtuh) space heating boilers:

- 84% for Tier 1 hot water boilers (non-condensing)

- 90% for Tier 2 hot water boilers (condensing)

- 82% for steam boilers

Minimum qualifying thermal efficiency (TE) for medium (300-2500 MBtuh) space heating boilers:

- 83% TE for Tier 1 hot water boilers (non-condensing)

- 90% TE for Tier 2 hot water boilers (condensing)

- 81% TE for steam boilers

Minimum qualifying combustion efficiency (TE or CE) for large (≥2500 MBtuh) space heating boilers:

- 85% CE (or 83% TE) for Tier 1 hot water boilers (non-condensing)

- 83% CE (or 81% TE) for steam boilers

The SoCalGas Energy Efficiency Rebates for Business Rebate Guide and Application 2013-2014 lists the minimum qualifying boiler efficiencies as follows:

- 82% AFUE for steam boilers <300 MBtuh

- 83% CE for steam boiler ≥300 MBtuh

- 84% AFUE for Tier-1 hot water boilers <300 MBtuh (non-condensing)

- 85% CE for Tier-1 hot water boilers ≥300 MBtuh (non-condensing)

- 90% AFUE for Tier-2 hot water boilers <300 MBtuh (condensing)

- 90% CE for Tier-2 hot water boilers ≥300 MBtuh (condensing)

DEER Differences Analysis

Measure Efficiency

The minimum qualifying measure efficiencies are similar to the “2014 Database for Energy-Efficient Resources (DEER) for Use in the California IOU 2013-14 Energy Efficiency Planning”, with some exceptions.  The following measure efficiencies are adopted after consideration of the high-efficiency boilers listed in the California Energy Commission Energy Efficiency Appliance Database3:

Small (<300 MBtu/hr) Tier 1 hot water boiler -- the DEER 2014 value of 84.5% AFUE is rounded to 84%.  This change increases the number of qualifying models with minimal change in energy savings.

Small (<300 MBtu/hr) Tier 2 hot water boiler -- the DEER 2014 value of 94% AFUE for small condensing hot water boilers is adjusted to 90% for the measure to be consistent across all types of boilers and water heaters (90% efficiency can only be achieved with condensing boilers).

Medium and large Tier 1 hot water boilers – the DEER 2014 value of 85%TE for small HW boiler is adopted in this workpaper.  However, the efficiency criterion for medium Tier 1 hot water boilers is changed from thermal efficiency (TE) to combustion efficiency (CE).

Combustion efficiency is a measure of the energy extracted from the products of combustion.  Combustion efficiency does not account for energy losses from the boiler jacket to ambient.

Thermal efficiency is a measure of the energy transferred from the combustion of gas to the water or steam.  Thermal efficiency is generally 1-3% lower than combustion efficiency.  The conversion from TE to CE is made by assuming 2% drop in efficiency due to the jacket loss.

Medium and large Tier 2 hot water boilers – the DEER 2014 value of 94% TE for medium condensing hot water boilers is set to 90% to be consistent across all types of boilers and water heaters.

Small (<300 MBtu/hr) steam boiler – the DEER 2014 value of 82% AFUE is used in this workpaper.

Medium and large steam boilers – The DEER 2014 values of 85% TE for medium and 80% CE for large steam boilers were simplified to 83% CE for both size ranges.  The value of 83% is chosen due to the limited availability of medium and large steam boilers with CE above 83% in the CEC Appliance Database5.

Baseline Efficiency

The minimum baseline efficiencies match the California Titles 20 and 24 standards2,3, which are similar to the “2014 Database for Energy-Efficient Resources (DEER) for use in the California IOU 2013-14 Energy Efficiency Planning5”.

Small (<300 MBtu/hr) hot water boiler – the DEER 2014 value of 82% AFUE is used in this workpaper.

Medium and large hot water boilers – the baseline efficiency of 80% CE matches the Titles 20 and 24 value for gas packaged boiler (the DEER 2014 values are lower than Titles 20 and 24).

Small (<300 MBtu/hr) steam boiler – the DEER 2014 value of 80% AFUE is used in this workpaper.

Medium and large steam boilers – the baseline efficiency of 80% CE matches the Titles 20 and 24 value for gas packaged boilers (the DEER 2014 values are lower than Titles 20 and 24).

Incremental Measure Cost

Since the efficiencies used here are different from DEER 2014, the incremental measure costs were adjusted as well.

Data were collected through a survey of vendors that sell hot water and steam space heating boilers in California for each of the categories of boiler type, rated input, and efficiency used in this workpaper.

Code Analysis

The minimum baseline efficiencies match the California Titles 20 and 24 standards2,3.  The minimum qualifying measure efficiencies exceed the California Titles 20 and 24 standards2,3.

Measure Effective Useful Life

The effective useful life (EUL) for space heating boilers of 20 years is taken from the DEER 2014 Update

Net-to-Gross Ratios for Different Program Strategies

DEER 2014 recommends a net-to-gross ratio (NTGR) of 0.60 for all energy efficiency measures (EEMs) covered under this program.  The referenced NTGR table suggests the 0.60 value for NTGR for the category labeled “All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years”.  Space-heating boilers fall into this category for Tier-1 high efficiency and Tier-2 condensing boilers.

Gross Realization Rate

Gross realization rate of 1.00 is applied to measures in this document.

Time-of-Use Adjustment Factor

N/A

Energy Savings & Demand Reduction Calculations

Load Shapes

N/A

Energy Savings

Annual Gas Energy Savings.

The annual gas energy savings are based on DEER 20145.  Table 1 list the baseline efficiencies and qualifying measure efficiencies for space heating boilers in the “2014 DEER for Use in the California IOU 2013-14 Energy Efficiency Planning”5.

- Base and Measure Space Heating Boiler Efficiencies in DEER 20145

| Equipment Type | Combustion Type | Rated Input (MBtu/hr) | Efficiency Units | Base Efficiency | Qualifying Efficiency |
| --- | --- | --- | --- | --- | --- |
| Space Heating Hot Water Boilers | Draft | < 300 | AFUE | 82% | 84.5% |
|  | Condensing | < 300 | AFUE | 82% | 94% |
|  | DraftAtmospheric | 300 – 2,500300 – 2,500 | TETE | 80%80% | 85%85% |
|  | CondensingDraft | 300 – 2,500300 – 2,500 | TETE | 80%80% | 94%85% |
|  | DraftAtmosphericCondensing | > 2,500> 2,500300 – 2,500 | CECETE | 82%82%80% | 85%85%94% |
|  | DraftAtmosphericDraftAtmospheric | < 300< 300> 2,500> 2,500 | AFUEAFUECECE | 80%80%82%82% | 82%82%85%85% |
|  | DraftAtmosphericDraftAtmosphericDraft | 300 – 2,500300 – 2,500< 300< 300> 2,500 | TETEAFUEAFUECE | 79%77%80%80%82% | 85%85%82%82%85% |
|  | DraftAtmosphericDraftAtmosphericDraftAtmospheric | > 2,500> 2,500300 – 2,500300 – 2,500< 300< 300 | CECETETEAFUEAFUE | 79%77%79%77%80%80% | 80%80%85%85%82%82% |
| Space Heating Steam Boilers | DraftAtmosphericDraftAtmosphericDraft | > 2,500> 2,500300 – 2,500300 – 2,500< 300 | CECETETEAFUE | 79%77%79%77%80% | 80%80%85%85%82% |
|  | DraftAtmosphericDraftAtmospheric | > 2,500> 2,500300 – 2,500300 – 2,500 | CECETETE | 79%77%79%77% | 80%80%85%85% |
|  | DraftAtmosphericDraft | > 2,500> 2,500300 – 2,500 | CECETE | 79%77%79% | 80%80%85% |
|  | DraftAtmospheric | > 2,500> 2,500 | CECE | 79%77% | 80%80% |
|  | Draft | > 2,500 | CE | 79% | 80% |

Boiler Efficiencies.

Table 2 shows the range of space heating boiler efficiencies found in the CEC Appliance Database as specified by the Air-Conditioning, Heating, and

- Refrigeration Institute (AHRI) standard rating conditions. The AHRI database6 has very similar ranges (Attachment B).  In several categories, several boilers were found that met the DEER 2014 qualifying efficiency standards, except for one category (medium size steam boiler), there were very few.

- Boiler Efficiency Ranges from CEC Appliance Efficiency Database6

| Equipment Type | Rated Input (MBtu/hr) | Efficiency Units | Minimum Efficiency | Maximum Efficiency |
| --- | --- | --- | --- | --- |
| Heating Products, Hot Water Boilers, Non-condensing | 30 – 299 | AFUE | 80.0% | 88.0% |
|  | 300 – 2,500 | TE | 77.0% | 87.0% |
|  |  | CE | 80.0% | 87.0% |
|  | 2,547 – 4,930 | TE | 79.2% | 84.9% |
|  |  | CE | 80.0% | 85.8% |
| Heating Products, Hot Water Boilers, Condensing | 50 – 299 | AFUE | 88.1% | 98.0% |
|  | 300 – 2,500 | TE | 83.8% | 96.8% |
|  |  | CE | 85.3% | 96.8% |
|  | 2,600 – 5,650 | TE | 91.1% | 96.6% |
|  |  | CE | 85.8% | 96.6% |
| Heating Products, Steam Boilers | 62 – 299 | AFUE | 75.8% | 83.2% |
|  | 300 – 2,500 | TE | 75.8% | 81.7% |
|  |  | CE | 80.0% | 84.9% |
|  | 2,511 – 5,650 | TE | 79.2% | 84.2% |
|  |  | CE | 80.0% | 85.5% |

Standard Efficiencies.

Table 3 lists the California Titles 20 standards for 2013 (CEC-140-2013-002.pdf) and (CEC-400-2013-002-CMF.pdf) posted on August and June of 2013, respectively (Attachment C).  In these standards, the efficiency units for all boilers with rated inputs exceeding 300 MBtuh is thermal efficiency, unlike the efficiency units found in DEER 2014.which uses combustion efficiency for boilers with rated input >2500 MBtuh..

- 2013 California Titles 20 Energy Code Standards2,3

| Equipment Type | Rated Input (MBtuh) | Efficiency Units | Minimum Efficiency (T-20) |
| --- | --- | --- | --- |
| Space Heating Hot Water Boilers | < 300 | AFUE | 82% |
|  | ≥ 300 and ≤ 2500 | TE | 80% |
|  | > 2500 | CE | 82% |
| Space Heating Steam Boilers | < 300 | AFUE | 80% |
|  | ≥ 300 and ≤ 2500 (except natural draft) | TE | 79% |
|  | > 2500 (except natural draft) | TE | 79% |

Baseline and Measure Efficiencies.

- Space heating boiler efficiency values – both baseline and high efficiency – were calculated based on efficiency listings published by the California Energy Commission (CEC), (Attachment-B).  The CEC listing included over 9,000 boilers smaller than 10 MMBtuh.  These boilers were divided into six groups:

- •	Space heating, hot water:	< 300 MBtuh

- •	Space heating, hot water:	300-2,500 MBtuh

- •	Space heating, hot water:	> 2,500 MBtuh

- •	Space heating, steam:		< 300 MBtuh

- •	Space heating, steam:		300-2,500 MBtuh

- •	Space heating, steam		> 2,500 MBtuh

- The resulting data were sorted in order of increasing efficiency.  The results are plotted in Figure 1, Figure 2, Figure 3, Figure 4, Figure 5 and Figure 6. The plots provided the following information:

- Figure 1 show the distribution of annual fuel utilization efficiencies for the 1058 small size water heating boiler products found in the CEC Database.  About 50% of the products are considered baseline (<84.5% AFUE) while 20% of the products meet the minimum efficiency for Tier 2 (>94% AFUE).  By changing the minimum required efficiency for Tier-2 condensing boilers (from 94% to 90% AFUE), the number of qualified units increased to 35%.

- Figure 2 shows the distribution of thermal efficiencies for the 557 medium size water heating boiler products found in the CEC Database.   About 50% of the products are considered Baseline (<85% TE) and only 10% of the products meet the minimum efficiency of Tier 2 (>94% TE).  With the reduced minimum efficiency requirement for the condensing type boiler s (from 94% to 90% TE), the number of qualified boilers increased to over 30%.

- Figure 3 shows the distribution of combustion efficiencies for the 179 large size water heating boiler products found in the CEC Database.  About 27% of the products are considered baseline (<85% CE) while 73% of the products meet the minimum efficiency for Tier 1 (>85% CE).

- Figure 4 shows the distribution of annual fuel utilization efficiencies for the 248 small size steam heating boiler products found in the CEC Database.   About 75% of the products are considered baseline (<82% AFUE) while 25% of the products meet the minimum efficiency for Tier 1 (>82% AFUE).

- Figure 5 shows the distribution of thermal efficiencies for the 98 medium size steam heating boiler products found in the CEC Database.  Over 96% of the products are considered baseline (<85% TE) while only 4% of the products meet the minimum efficiency for Tier 1 (>85% TE).  Lowering Tier-1 to 81% TE will double the number of qualified units.

- Figure 6 shows the distribution of combustion efficiencies for the 679 large size steam heating boiler products found in the CEC Database.  Only 4% of the products are considered baseline (<80% CE) while 96% of the products meet the minimum efficiency for Tier 1 (80% CE).  For consistency, if Tier-1 increased to 83% CE the number of qualified units drop to 10%.

- Distribution of Annual Fuel Utilization Efficiencies for Hot Water Boilers ( <300 MBtu/hr) in the CEC Appliance Efficiency Database

- Distribution of Thermal Efficiencies for Hot Water Boilers (300-2,500 MBtu/hr) in the CEC Appliance Efficiency Database

- Distribution of Combustion Efficiencies for Hot Water Boilers( ≥2,500 MBtu/hr) in the CEC Appliance Efficiency Database

- Distribution of Annual Fuel Utilization Efficiencies for Steam Water Boilers ( <300 MBtu/hr) in the CEC Appliance Efficiency Database

- Distribution of Thermal Efficiencies for Steam Boilers (300-2,500 MBtu/hr) in the CEC Appliance Efficiency Database

- Distribution of Combustion Efficiencies for Steam Boilers ( ≥2,500 MBtu/hr) in the CEC Appliance Efficiency Database

Energy Savings Calculation.

For calculating energy savings, the following assumptions are used:

The energy savings calculated for DEER 2014 are correct except for the base and measure efficiency values.

The energy savings calculated for DEER 2014 are averaged across building types, building vintages, equipment type and burner types to produce a single value for each of the (16) weather zone in California.

The average efficiency for the baseline products is the minimum base efficiency.  The average of the baseline efficiencies is not the average efficiencies of the universe of boilers of this type, nor is it the average efficiencies of boilers replace in the rebate program, but it is the bare minimum baseline efficiency.

The average efficiency for the qualifying products is the minimum measure efficiency.  The average of the measure efficiencies is not the average efficiencies of the universe of boilers of this type, nor is it the average efficiencies of new boilers rebated, but it is the bare minimum qualifying efficiency.

To convert from combustion efficiency to thermal efficiency, the corresponding combustion efficiency is assumed to be 2% greater than the thermal efficiency.

Gas savings was reported in fuel consumption per equipment rated input, therms/MBtuh.

Electric parasitic load were recorded in annual kWh and kW use per unit (MBtuh).  Negative sign for the additional load on the system.

With these assumptions, the energy saved by a high-efficiency measure boiler can be calculated as follows:

∆Q3-4 = ∆Q1-2 x (1/E3-1/E4) / (1/E1-1/E2)									Eqn-1

- where

∆Q – Energy Saved (therms/yr).  Savings which results from installing the high-efficiency measure equipment for each boiler category and weather zone.

E – Efficiency (%).  Efficiency of equipment in appropriate efficiency units (annual fuel utilization efficiency, combustion efficiency, etc.).

Subscript 1 = DEER 2014 baseline (reference) equipment

Subscript 2 = DEER 2014 measure (new high-efficiency) equipment

Subscript 3 = Adjusted baseline equipment value

Subscript 4 = Adjusted measure equipment value

Table 4 shows the baseline and measure efficiencies for each type of boilers as provided in DEER 2014. However, Table-5 shows the adjusted values used in SoCal Gas Company’s rebate program.

- Baseline and Measure Efficiency by Equipment Type

| Equipment Type | Hot Water Boiler, Non-condensing |  |  | Hot Water Boiler, Condensing |  | Steam Boiler |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated Input (MBtu/hr) | <300 | 300-2,500 | ≥2,500 | <300 | ≥300 | <300 | 300-2,500 (draft) | ≥2,500 (draft) |
| DEER 2014 |  |  |  |  |  |  |  |  |
| Efficiency units | AFUE | TE | CE | AFUE | TE | AFUE | TE | CE |
| Base Efficiency | 82% | 80% | 82% | 82% | 80% | 80% | 79% | 79% |
| Measure Efficiency | 84.5% | 85% | 85% | 94% | 94% | 82.0% | 85% | 80% |
| Annual Energy Savings (therms/yr/KBtuh) | 1.309 | 1.622 | 1.391 | 1.864 | 2.223 | 1.283 | 1.713 | 1.238 |

- Adjusted Baseline and Measure Efficiencies

| Requirements for rebate application |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Equipment Type | Hot Water Boiler, Non-condensing |  |  | Hot Water Boiler, Condensing |  | Steam Boiler |  |  |
| Rated Input (MBtu/hr) | <300 (draft) | 300-2,500 (draft) | ≥2,500 (draft) | <300 | ≥300 | <300 (draft) | 300-2,500 (draft) | ≥2,500 (draft) |
| Adjusted Values |  |  |  |  |  |  |  |  |
| Efficiency units | AFUE | TE | TE | AFUE | TE | AFUE | TE | TE |
| Base Efficiency | 82% | 80% | 80% | 82% | 80% | 80% | 79% | 79% |
| Measure Efficiency | 84% | 83% | 83% | 90% | 90% | 82% | 81% | 81% |
| Adjusted Annual Energy Savings (therms/yr/KBtuh)* | 1.05 | 1.00 | 1.39 | 1.30 | 1.66 | 1.28 | 0.60 | 2.44 |

*Savings are averaged for all 16 weather zones and building vintages in each equipment category.

The expanded data and calculations for all 16 weather zones in CA are included in an Excel file embedded as Attachment A.  And the results are presented in the “Measure Summary Table” of this workpaper.

Base Case & Measure Costs

Base Case Cost

When the customer is replacing equipment on burnout (ROB) or buying new equipment (NEW), the customer must buy a new boiler to continue operating, so the base case cost is that of a baseline (standard) boiler.

The base case costs are shown in Table 6 below.

The upper section of the table lists the 2008 DEER cost data taken from the “2011 Database for Energy-Efficient Resources (DEER) for Use in the California IOU 2013-14 Energy Efficiency Planning”6.  The average base case costs are the average of the measure cost for boilers with atmospheric burners and forced draft burners.  The equipment efficiency ranges used for the DEER cost data matched the equipment efficiency ranges used in this workpaper.

The middle section of the table lists the results of a survey of equipment vendors that sell hot water and steam space heating boilers in California.  The vendor calls in the year 2013 produced data for all of the categories of boiler type, rated input, and efficiency used in this workpaper.  The base measure costs shown in Table 6 represent an arithmetic average of the equipment cost per MBtuh in each category.

The lower section of the table lists the average of DEER cost data and the survey data.  The data and calculations are included in an Excel file embedded as Attachment D.  The average base case cost of DEER cost and Survey cost is used for IMC calculation.

Gross Measure Cost

The gross measure costs include the cost of the equipment, excluding installation and start-up costs.  For the purposes of determining incremental measure costs, the installation and start-up costs are assumed to be the same for the base case and measure equipment.

The gross measure costs are shown in Table 6 below.

The upper section of the table lists the 2008 DEER cost data taken from the “2011 Database for Energy-Efficient Resources (DEER) for Use in the California IOU 2013-14 Energy Efficiency Planning”6.  The average base case costs are the average of the measure cost for boilers with atmospheric burners and forced draft burners.

The middle section of the table lists the results of a survey of equipment vendors that sell hot water and steam space heating boilers in California.  Data were collected in 2013 for this updated version of the workpaper. The gross measure costs shown in Table 6 represent an arithmetic average of the equipment cost per MBtuh in each category.

The lower section of the table lists the average of DEER cost data and the survey data.  The cost data and calculations are included in an Excel file embedded as Attachment D.

Incremental Measure Cost

The incremental measure cost (IMC) is the difference between the average base case cost and the average gross measure cost.

The incremental measure costs are shown in Table 6 below.

- Gross and Incremental Measure Cost by Equipment Type

| Equipment Type | Small Hot Water (Draft) | Small Hot Water (Condensing) | Medium Hot Water (Draft) | Medium Hot Water (Condensing) | Large Hot Water (Draft) | Small Steam (Draft) | Medium Steam (Draft) |  | Large Steam (Draft) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated Input (MBtuh) | <300 | <300 | 300-2,500 | 300-2500 | >2,500 | <300 | 300-2,500 |  | >2,500 |  |
| 2008 DEER Cost Data ($/MBtuh) |  |  |  |  |  |  |  |  |  |
| Average Base Cost | $22.09 | $21.76 | $10.98 | $16.46 | $9.17 | $21.33 | $10.98 | $11.32 |  |
| Average Gross Measure Cost | $29.54 | $26.66 | $12.98 | $19.60 | $10.18 | $22.83 | $12.98 | $12.11 |  |
| Average Incremental Measure Cost | $7.45 | $4.90 | $2.00 | $3.14 | $1.01 | $1.50 | $2.0 | $0.79 |  |
| 2013 Vendor Survey Data ($/MBtuh) |  |  |  |  |  |  |  |  |  |
| Average Base Cost | $18.43 | $20.08 | $10.71 | $21.90 |  |  | $10.36 |  |  |
| Average Gross Measure Cost |  | $27.23 |  | $25.71 |  |  |  |  |  |
| Average Incremental Measure Cost |  | $7.15 |  | $3.81 |  |  |  |  |  |
| Average of DEER and 2013 Vendor Survey Data ($/MBtuh) |  |  |  |  |  |  |  |  |  |
| Average Base Cost | $20.26 | $20.92 | $10.84 | $19.18 | $9.17 | $21.33 | $10.67 | $11.32 |  |
| Average Gross Measure Cost | $29.54 | $26.95 | $12.98 | $22.65 | $10.18 | $22.83 | $12.98 | $12.11 |  |
| Average Incremental Measure Cost | $9.28 | $6.03 | $2.14 | $3.48 | $1.01 | $1.50 | $2.31 | $0.79 |  |

Cost Adjustment for the 16 weather zones in CAlifornia

The average Incremental Measure Cost for each equipment category was then multiplied by adjustment factors for the 16 weather zones in California.  A climate multiplier factors given in DEER 2014 are used to adjust labor and material costs for HVAC measures (code HVAC50) by location (Climate Zone) for various types of labor categories, as shown in Table-7 and in Attachment E.

- Adjustment Factor for Material Cost by Cities in CA

| Climate Zone | Reference City | Material | Installation* |
| --- | --- | --- | --- |
| 1 | Arcata | 0.989 | 0.962 |
| 2 | Santa Rosa | 0.939 | 1.150 |
| 3 | Oakland | 1.027 | 1.513 |
| 4 | Sunnyvale | 1.024 | 1.378 |
| 5 | Santa Maria | 0.880 | 0.993 |
| 6 | Los Angeles | 0.870 | 1.072 |
| 7 | San Diego | 1.000 | 0.978 |
| 8 | El Toro | 0.936 | 1.050 |
| 9 | Pasadena | 0.963 | 1.138 |
| 10 | Riverside | 0.904 | 1.029 |
| 11 | Red Bluff | 0.984 | 1.048 |
| 12 | Sacramento | 0.973 | 1.048 |
| 13 | Fresno | 0.894 | 0.944 |
| 14 | China Lake | 0.879 | 0.979 |
| 15 | El Centro | 0.936 | 1.029 |
| 16 | Mount Shasta | 0.987 | 1.048 |
| Average |  | 0.949 | 1.085 |

*Installation Cost was assumed the same for both baseline and measure; therefore it was ignored in the IMC.

Attachments

Attachment A – Energy Savings Data and Calculations

Attachment B – The CEC Appliance Equipment Efficiency Database

Attachment C – California Titles 20 and 24 standards for 2013

Attachment D – Vendor Survey Cost Data and Calculations

Attachment E – DEER 2014 Cost Adjustment for HVAC Equipment

References

Space Heating Boilers Workpaper, Revision A, EEA Report No. B-REP-06-599-01A, March 20, 2006.

Space Heating Boilers Workpaper, Revision 2, WPSCGNRHC120206A_Rev.2.

California Code of Regulations, Title 20. Public Utilities and Energy, Division 2. State Energy Resources Conservation and Development Commission, California Energy Commission, CEC-140-2013-002, posted August 2013 (Accessed November 14 at http://www.energy.ca.gov/2013publications/CEC-140-2013-002/CEC-140-2013-002.pdf).

2013 Building Energy Efficiency Standards, Nonresidential Compliance Manual, Title 24, California Energy Commission, CEC-400-2013-002-CMF, posted June 2013 (Accessed Jan 20, 2014 at http://www.energy.ca.gov/title24/).

4 Energy Efficiency Rebates for Business Rebate Guide and Application 2013-2014 (Accessed December 12, 2013 at http://socalgas.com/documents/business/rebates/EERBGuideandApp.pdf)

5 DEER Database for Energy-Efficient Resources, Deer2013 database tables: Energy Impacts (Accessed Sep. 20, 2013 and Jan 15, 2014 at ftp://ftp.deeresources.com/).

6 California Energy Commission Appliance Efficiency Database (Accessed November 7, 2013 at

http://www.appliances.energy.ca.gov/AdvancedSearch.aspx)

7 Technology and Measure Cost Data/Effective and Remaining Useful Life (EUL/RUL) Values.  (“DEER2014 Database for Energy-Efficiency Resources, READI_v1.0.4, Updated for 2014 Codes (Accessed Jan. 10, 2014 at http://www.deeresources.com/).

8 DEER 2014 Net-To-Gross Ratios.  (“DEER2013 Database for Energy-Efficiency Resources, READI_v1.0.4, Updated for 2014 Codes (Accessed Jan 10, 2014 at http://www.deeresources.com).