Work Paper WPSCGNRWH160726A

Revision 0

Southern California Gas Company

Heat-Recovery Rooftop Unit

(HR-RTU)

# At-a-Glance Summary

| Measure Codes | HvcHtr001: HR-RTU unit for fast food service venues. |
| --- | --- |
| Measure Description | Heat-Recovery Rooftop Units (HR-RTU) reduce a commercial building’s energy for hot water load by capturing the waste heat from the RTU’s air conditioning circuit and use it via the refrigerant-to-water heat exchanger to preheat the water from the main prior to entering the water heater. The waste heat, originating in the building’s interior, is typically rejected via an air-cooled condenser in the RTU to the outdoors. Currently this technology is only offered in a 10 and 15 ton cooling capacity, the results presented in this measure are reflected from a 10 ton system. |
| Base Case Description | Rooftop unit with no heat exchanger. Heat is rejected to the outdoor condensing coil for atmospheric dissipation. |
| Units | Water Heating Savings: Each, System is only available in two sizes, 10 and 15 ton cooling capacity. The savings in this Workpaper reflect the performance of a 10 ton cooling unit. |
| Energy Savings | Refer to Excel Calculation Attachment (CZ9: 612 Therms) |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment ($17,100) |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment ($5,500) |
| Effective Useful Life | 15 years DEER READI 2.4.5 (EUL ID: HVAC-airAC) |
| Measure Installation Type | Replacement on Burnout (ROB) |
| Net-to-Gross Ratio | 0.85 ET-Default |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 11/17/2016 | Carlos Pineda(SCG) | Original work paper |

Table of Contents

At-a-Glance Summary	2

Revision History	3

Section 1. General Measure & Baseline Data	6

1.1 Measure Description & Background	6

1.3 Installation Types and Delivery Mechanisms	7

1.4 Measure Parameters	8

1.4.1 DEER Data	8

1.4.2 Codes and Standards Analysis	9

1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information	9

1.5.1 Portfolio of the Future: Field Testing Report - Rheem H2AC at a Quick-Serve Restaurant	9

1.6 Data Quality and Future Data Needs	10

Section 2. Calculation Methodology	10

2.1 Monitored Period Savings	10

2.2 Annual Savings	11

Section 3. Load Shapes	13

Section 4. Costs	13

4.1 Base Case Cost	13

4.3 Measure Case Cost	14

4.4 Full and Incremental Measure Cost	14

Attachments	15

References	16

List of Figures

Figure 1: Typical HR-RTU System Architecture	7

Figure 2: Savings VS CDD	12

Figure 3: 16 CZ Savings	13

List of Tables

Table I: Base, Standard and Measure Cases	6

Table II: Measures and Codes	6

Table III: Installation Type Description	7

Table IV: Delivery Method Descriptions	8

Table V: Incentive Method Descriptions	8

Table VI: Deer Difference Summary	8

Table VII: NTGR ID	8

Table VIII: GSIA ID	9

Table IX: EUL ID	9

Table X: Code Summary	9

Table XI: Regression Analysis	11

Table XII: Building Type and Load Shapes	13

Table XIII: Base Cost Breakdown	13

Table XIV: Measure Case Cost Breakdown	14

Table XV: Full and Incremental Measure Cost Equations for HR-RTU in Fast Food Venues	14

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper outlines the energy saving from installing a roof top unit system with an air to water heat-recovery feature. This advantage has not been available until recently in which the system uses the AC load to heat incoming water from the main. This will offset the work required by the water heater resulting in energy savings in water heating. This measure is a replacement on burnout (ROB) type.

Table I: Base, Standard and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Installation of a RTU that is equipped with an air-to-water heat exchanger to preheat service hot water. |
| Existing Condition | RTU unit which dissipates the waste heat through condensing coil into the atmosphere. |
| Code/Standard | RTU with no heat recovery. |
| Industry Standard Practice | RTU with no heat recovery. |

Table II: Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
| HvcHtr001 |  |  |  | Heat Recover RTU unit for fast food service venues. |

- Eligibility Requirements: This workpaper only applies to rooftop air conditioner units operating in fast food restaurants locations with a gas water heating system. The venue must be within the IOU service territory.

- Implementation Requirements: This work paper allows the installation of any air to water roof top air conditioner unit in fast food restaurants venues that are capable of utilizing waste heat to preheat incoming water from the main.

1.2 Technical Description

Heat-Recovery Rooftop Units (HR-RTU) reduce the energy required for water heating in fast food restaurants through the use of the waste heat from the RTU’s air conditioning cycle. The waste heat is used to preheat the incoming water from the main; once the water has been preheated it is directed into a storage tank where it will be available upon demand. When there is a hot water demand, the preheated water will route into the water heater to be raised to set point temperature.

In a typical setting, waste heat originating in the building’s interior is rejected via an air-cooled condenser in the RTU to the atmosphere.  With a heat-recovery-capable RTU, the heat is instead transferred via a refrigerant-to-water heat exchanger to the incoming water. This offsets the water heater’s natural gas consumption by having the RTU increase the main water temperature prior to entering the water heater.

The energy savings are proportional to the change in temperature between the water main and the water heater inlet; this is the “free” heat from the RTU that would have been rejected into the environment. While the equipment itself is integrated in an RTU for space conditioning, this is a water heating measure.  Savings in this measure are directly dependent to the cooling demand which makes this a weather sensitive measure. Currently, there is only a 10 and 15 ton cooling capacity systems available, this workpaper is model after a 10 ton cooling RTU unit.  Below is a diagram of the cycle.

Figure 1: Typical HR-RTU System Architecture

Additional benefits include:

- Increased water heating capacity – an HR-RTU increases the total hot water that can be provided by the existing hot water heater.

- Backup water heating capabilities – should the building’s hot water heater fail, the HR-RTU can provide hot water at up to ~125°F  between 80 and 220 kBtu/hr, providing there is sufficient space cooling demand.

## 1.3 Installation Types and Delivery Mechanisms

The HR-RTU will be offered through Third-Party Programs or as a downstream rebate.

Table III: Installation Type Description

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Replacement on Burnout (ROB) | Code | N/A | RTU EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Table IV: Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |

Table V: Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

There are currently no DEER measures that apply to this type of technology.

Table VI: Deer Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | No |
| DEER Measure Case | No |
| DEER Building Types | Yes |
| DEER Operating Hours | No |
| DEER eQUEST Prototypes | No |
| DEER Version | DEER 2016 |
| Reason for Deviation from DEER | DEER does not contain any type of this measure |
| DEER Measure IDs Used | N/A |

Net-to-Gross Ratio

The NTG values were obtained from the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

Table VII: NTGR ID

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| ET-Default | Emerging Technologies approved by ED through work paper review | Any | Any | Any | 0.85 |

* ET Report is embedded in ATTACHMENST section.

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained from the DEER READI tool. The relevant IR values for the measures in this workpaper are in the table below.

Table VIII: GSIA ID

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained by using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

Table IX: EUL ID

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HVAC-airAC | Air Conditioners (air-cooled, split and unitary) | COM | HVAC | 15 | 5 |

### 1.4.2 Codes and Standards Analysis

There are currently no federal, state, or regional codes that impact HR-RTU units.

Table X: Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2016) | Section: 110.2, Pg. 87 | 01/01/2016 |
| Title 20 (2016) | N/A | N/A |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

To establish savings, empirical data from Emerging Technology study report and conservative values and assumptions were used.

### 1.5.1 Portfolio of the Future: Field Testing Report - Rheem H2AC at a Quick-Serve Restaurant

- Field Test Report prepared by Navigant Consulting Inc.

- Fast Food Service Restaurants.

- On site evaluation of HR-RTU unit performed in a Fast Food Service Restaurant located in Anaheim, California.

- Data from the report was directly used for this work paper to create a savings regression.

## 1.6 Data Quality and Future Data Needs

- Due to this technology being new, there are currently no studies outlining the benefits of preheating water with an air to water heat exchanger in an RTU.   “Portfolio of the Future: Field Testing Report - Rheem H2AC at a Quick-Serve Restaurant” is a field test report in which an HR-RTU unit was installed and data was monitored and recorded for 114 days.

- Further research is needed to associate a relation between hot water demand and air-conditioning load to increase the accuracy of savings.

- The data recorded in the study above is of good quality and accuracy, outlining all values required to yield an empirical savings value over the monitored period.

# Section 2. Calculation Methodology

### 2.1 Monitored Period Savings

During the monitored test period of 114 days at a Fast Food Restaurant located in Anaheim California, measurements for water main temperature, storage tank outlet temperature, water heater outlet temperature and water use were taken. These values were used along with convective principles to estimate daily savings. The following equation was used.

Equation 1:

Qtherm=m*Cp*ΔTη*100,000

Where,

- m=water(lbm)=gallons*8.33lbmgallons

- Cp=Water Specific Heat Capacity=1 BTUlbm*°F

- ΔT=Temperature difference=Water Heater outlet-Storage Tank Outlet

- η=Water Heater Efficiency=80%

- 1 therm=100,000 Btu

For a sample calculation, consider a recording on the date of March 22, 2014 with the following values (Energy Savings).

- Water use = 4 gallons = 4 gallons*8.33lbmgallons=33.32 lbm

- Water Inlet Main Temperature = 67 °F

- Water Heater ΔT = (144 – 67)  °F = 77 °F (No HR-RTU)

- Water Heater ΔT = (144 – 90 )  °F = 54 °F (With HR-RTU)

For this instance, the heat recovery- roof top unit increased the water main temp by 23 °F, applying equation 1, the savings are as follows:

Qtherm: No HR-RTU-Qtherm: HR-RTU=m*Cp*ΔTη*100,000= 33.32 lbm*1 BTUlbm*°F*  77 °F0.80*100,000-33.32 lbm*1 BTUlbm*°F*  54 °F0.80*100,000= 0.032-0.022=0.010 therm.

All the recordings for March 22, 2014 were calculated as shown in the example and aggregated to yield a daily savings value. During this day 4.2 therms were used, 1.80 were accounted to the HR-RTU as savings from pre heating water by taking advantage of the AC cooling load.

For the entire test period of 114 days, the amount of energy saved was estimated to 237 therms (Energy Savings). The amount of energy used would have been 437 therms, 200 therms were accounted to the water heater. For this test period, the energy consumption was reduced by 54%.

### 2.2 Annual Savings

A regression as a function of Cooling Degree Days (CCD) was made to estimate the annual savings. The regression was made from the data collected over the 114 day test period. The respective energy-therm savings was plotted versus Cooling Degree Days. The following was generated.

Table XI: Regression Analysis

| CDD42 |  |
| --- | --- |
| sloped section: |  |
| slope: | 0.08 |
| Intercept: | -0.05 |
| Inflection: | 28 |
| RSQ | 0.35 |
| Y=0.08X-0.05 |  |
| Flat Section: |  |
| slope | -0.01 |
| intercept | 2.53 |
| Average | 2.30 |
| Y=2.3 |  |

A Cooling Degree base of 42 was used to generate the regression. This base was chosen for the following reasons.

- The typical 65 degree base is driven by outside temperatures. However, in a fast food environment, the thermostat will call for cooling prior to the outside temperature exceeding 65 degrees.  This is due to various internal loads in a fast food setting (i.e. multiple people, cooking equipment, electronics, and constant traffic opening doors).

- The Y-intercept in this mathematical model is very close to zero with an inflection point of 28 CCD. This implies that at zero degree days, there will be no savings. This is true for this measure. If the AC is off, savings are nonexistent.

- Weather data (KFUL_CDD_65F) shows that for a base of CDD65 on March 25, 2014 there was zero CDD. This implies that there should be no AC activity. However, there were savings and therefore AC load must have been present. From the 114 day test data, 1.67 therms were saved on March 25, 2014. Applying the regression generated and the CDD days from a base of 42 Degrees (KFUL_CDD_42F), the following is observed:

Y = 0.08*19.3 – 0.05 = 1.5 Therm, a conservative value which shows the mathematical model is approximate to the actual savings.

- During a major interval during the test pilot, AC status was recorded and it was observed that it would cycle ON and OFF. There was not a single day in which the AC was OFF for the entire day (Test Pilot Raw Data).

However, the regression savings are limited to an inflection point of 28 CDD. This point value was chosen to  force the Y-intercept to be close to a value of zero for zero savings at zero CDD.   Any value of CDD exceeding 28 will yield the same energy savings as 28 CDD. This was done to limit the amount of energy saved otherwise savings will indefinitely increase linearly with CDD. This limitation was set in place due to the hot water demand, which depends on the facility’s daily traffic. During the monitor period, 28 CDD was the maximum value that produced savings and the most occurred CDD. This relates water demand that needs heating and available heat to preheat it. Beyond this CDD value, the hot water demand volume and available heat are not modeled by the current data. The hot water demand could be much more than the amount of heating that could be provided by this measure, therefore savings past 28CDD are uniform. This is done by having two sections in the regression (slope, flat). The following plot represents the linear regression against CDD:

Figure 2: Savings VS CDD

The regression was applied to weather approved data by the CPUC “Compare Weather data” file attached to yield annual savings for all California Climate Zones “Energy Savings”. Below is a plot showing natural gas savings for all California Climate Zones:

Figure 3: 16 CZ Savings

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Table XII: Building Type and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Commercial : Restaurant- Fast-Food(RFF) | DHW HtPmp | COM |

# Section 4. Costs

Costs were calculated for the Heat-Recovery Roof Top Unit. Due to the uniqueness and different costs for any installation, costs were gathered from manufacturer, contractor discussions, and from research, in which a price per ton was established.  In addition, the costs of the equipment and material used in the “POF Rheem H2AC Field Testing Report” were also used to establish a measure cost.  The “Cost Analysis” document attached shows how the cost was determined.

## 4.1 Base Case Cost

The table below shows the Base Case Cost breakdown.

Table XIII: Base Cost Breakdown

|  | Baseline Unit (10T) |  |
| --- | --- | --- |
|  | per unit | per ton |
| Materials – RTU | $5,000 | $500 |
| Materials – Curb adapter | $900 | $90 |
| Materials – storage tank | N/A | N/A |
| Materials – piping, other misc. | N/A | N/A |
| Labor – Rigging/placing/reconnecting power/etc. | $5,700 | $570 |
| Labor – additional H2AC plumbing labor | N/A | N/A |
| Total Labor | $5,700 | $570 |
| Total | $11,600 | $1,160 |

Research was performed to evaluate the baseline cost. The price from manufacturer discussions and typical installed cost from research presented in the “Cost Analysis” document attached are within a consistent  range of each other.

## 4.3 Measure Case Cost

There is no available cost data for this measure. Costs for this measure were taken from the installation in the test pilot. In addition, equipment, labor and installation cost were taken from discussions with contractors and equipment manufacturers.

Table XIV: Measure Case Cost Breakdown

|  | Rheem H2AC (10T) |  |
| --- | --- | --- |
|  | per unit | per ton |
| Materials – RTU | $7,000 | $700 |
| Materials – Curb adapter | $900 | $90 |
| Materials – storage tank | $1,000 | $100 |
| Materials – piping, other misc. | $2,500 | $250 |
|  | (inc. labor) | (inc. labor) |
| Labor – Rigging/placing/reconnecting power/etc. | $5,700 | $570 |
| Labor – additional H2AC plumbing labor | See above | See above |
| Total Labor | $8,200 | $820 |
| Total | $17,100 | $1,710 |

Make changes to Ex-Ante table to diffuse labor cost and material cost.

Add a row before final “total” to include total for labor.

## 4.4 Full and Incremental Measure Cost

Table XV: Full and Incremental Measure Cost Equations for HR-RTU in Fast Food Venues

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| ROB | ($5,000 + $900+5700)-($7,000+$900+$1000+$2500+$5700) = $5,500 | ($5,000 + $900+5700)-($7,000+$900+$1000+$2500+$5700) = $5,500 | N/A |

# Attachments

# References

http://www.rheem.com/h2ac. n.d.

http://www.advancedrtu.org/uploads/7/4/8/7/7487823/advanced_rtu_campaign_webinar_6-17-2013.pdf

https://blog.builtspace.com/2014/11/16/the-economics-of-rooftop-units-rtu-energy-efficiency-depends-on-your-choices/

www.vadakin.com/articles/rtu.doc

http://procure.ohio.gov/pricelist/800195revpricelist.pdf

http://bookstore.ashrae.biz/journal/download.php?file=RooftopACs.pdf.

http://www.rushingco.com/assets/Uploads/Mindshare/Documents/HVAC-Basics-10.16.12.pdf

http://www.owen.kyschools.us/userfiles/272/November%2018,%202013/Bid%20Proposal.pdf

http://www.allcostdata.info/detail.html/157702006/Rooftop-Pkgd-HVAC-Units,-10-Ton-Elec-Heat-Approx-1/2-Cooling-Cap

(http://www.rheem.com/h2ac)