## Savings Summary
Faucet Aerators for Commercial Buildings Savings Summary
Measure | Climate Zone | Units | Annual Therm Savings per Public Lavatory Faucet | Annual Therm Savings per Private Lavatory Faucet
0.5 GPM Aerator | 1 | therm/yr | 12.487 | 4.018
0.5 GPM Aerator | 2 | therm/yr | 10.9006 | 3.5075
0.5 GPM Aerator | 3 | therm/yr | 10.9651 | 3.5283
0.5 GPM Aerator | 4 | therm/yr | 10.3047 | 3.3158
0.5 GPM Aerator | 5 | therm/yr | 11.2925 | 3.6336
0.5 GPM Aerator | 6 | therm/yr | 9.7035 | 3.1223
0.5 GPM Aerator | 7 | therm/yr | 9.4887 | 3.0532
0.5 GPM Aerator | 8 | therm/yr | 9.1693 | 2.9505
0.5 GPM Aerator | 9 | therm/yr | 9.1478 | 2.9435
0.5 GPM Aerator | 10 | therm/yr | 9.0593 | 2.915
0.5 GPM Aerator | 11 | therm/yr | 9.317 | 2.998
0.5 GPM Aerator | 12 | therm/yr | 9.937 | 3.1975
0.5 GPM Aerator | 13 | therm/yr | 9.0727 | 2.9194
0.5 GPM Aerator | 14 | therm/yr | 9.4565 | 3.0429
0.5 GPM Aerator | 15 | therm/yr | 6.0207 | 1.9373
0.5 GPM Aerator | 16 | therm/yr | 12.3877 | 3.986
1.0 GPM Aerator | 1 | therm/yr | 7.1507 | 2.3009
1.0 GPM Aerator | 2 | therm/yr | 6.2422 | 2.0086
1.0 GPM Aerator | 3 | therm/yr | 6.2791 | 2.0205
1.0 GPM Aerator | 4 | therm/yr | 5.901 | 1.8988
1.0 GPM Aerator | 5 | therm/yr | 6.4667 | 2.0808
1.0 GPM Aerator | 6 | therm/yr | 5.5567 | 1.788
1.0 GPM Aerator | 7 | therm/yr | 5.4337 | 1.7484
1.0 GPM Aerator | 8 | therm/yr | 5.2508 | 1.6896
1.0 GPM Aerator | 9 | therm/yr | 5.2385 | 1.6856
1.0 GPM Aerator | 10 | therm/yr | 5.1878 | 1.6693
1.0 GPM Aerator | 11 | therm/yr | 5.3353 | 1.7168
1.0 GPM Aerator | 12 | therm/yr | 5.6904 | 1.831
1.0 GPM Aerator | 13 | therm/yr | 5.1955 | 1.6718
1.0 GPM Aerator | 14 | therm/yr | 5.4153 | 1.7425
1.0 GPM Aerator | 15 | therm/yr | 3.4478 | 1.1094
1.0 GPM Aerator | 16 | therm/yr | 7.0938 | 2.2826

## Public Faucet Energy Calcs
|  | 1.0 GPM Aerator |  |  |  |  | 0.5 GPM Aerator
Values | Units / Description | Existing | Measure |  | Values | Units / Description | Existing | Measure
V_dot | [gal/min] | 1.67 | 1 |  | V_dot | [gal/min] | 1.67 | 0.5
ρ | [lbm/gal] | 8.33 | 8.33 |  | ρ | [lbm/gal] | 8.33 | 8.33
m_dot | [lbm/min] | 13.9111 | 8.33 |  | m_dot | [lbm/min] | 13.9111 | 4.165
Conversion | [min/hr] | 60 | 60 |  | Conversion | [min/hr] | 60 | 60
cp | [Btu/(lbm*°F)] | 1 | 1 |  | cp | [Btu/(lbm*°F)] | 1 | 1
Conversion | [therm/Btu] | 1e-05 | 1e-05 |  | Conversion | [therm/Btu] | 1e-05 | 1e-05
Tmixed | [°F] | 97.9 | 97.9 |  | Tmixed | [°F] | 97.9 | 97.9
Usage time | [min/day] | 12.4 |  |  | Usage time | [min/day] | 12.4
Annual Usage Time (τ) | [hr/yr] | 34.886 |  |  | Annual Usage Time (τ) | [hr/yr] | 34.886
ξ | Efficiency | 0.76 | 0.76 |  | ξ | Efficiency | 0.76 | 0.76
Consumption | Climate Zone | Make-up Water Temperature (°F) | Q_Faucet (therms/yr) | Q_aerator (therms/yr) | Consumption | Climate Zone | Make-up Water Temperature (°F) | Q_Faucet (therms/yr) | Q_aerator (therms/yr)
Q | 1 | 51.38 | 17.8234 | 10.6727 | Q | 1 | 51.38 | 17.8234 | 5.3363
Q | 2 | 57.29 | 15.559 | 9.3168 | Q | 2 | 57.29 | 15.559 | 4.6584
Q | 3 | 57.05 | 15.651 | 9.3719 | Q | 3 | 57.05 | 15.651 | 4.6859
Q | 4 | 59.51 | 14.7085 | 8.8075 | Q | 4 | 59.51 | 14.7085 | 4.4037
Q | 5 | 55.83 | 16.1184 | 9.6517 | Q | 5 | 55.83 | 16.1184 | 4.8259
Q | 6 | 61.75 | 13.8503 | 8.2936 | Q | 6 | 61.75 | 13.8503 | 4.1468
Q | 7 | 62.55 | 13.5438 | 8.11 | Q | 7 | 62.55 | 13.5438 | 4.055
Q | 8 | 63.74 | 13.0878 | 7.837 | Q | 8 | 63.74 | 13.0878 | 3.9185
Q | 9 | 63.82 | 13.0572 | 7.8187 | Q | 9 | 63.82 | 13.0572 | 3.9093
Q | 10 | 64.15 | 12.9307 | 7.743 | Q | 10 | 64.15 | 12.9307 | 3.8715
Q | 11 | 63.19 | 13.2986 | 7.9632 | Q | 11 | 63.19 | 13.2986 | 3.9816
Q | 12 | 60.88 | 14.1836 | 8.4932 | Q | 12 | 60.88 | 14.1836 | 4.2466
Q | 13 | 64.1 | 12.9499 | 7.7544 | Q | 13 | 64.1 | 12.9499 | 3.8772
Q | 14 | 62.67 | 13.4978 | 8.0825 | Q | 14 | 62.67 | 13.4978 | 4.0413
Q | 15 | 75.47 | 8.5937 | 5.1459 | Q | 15 | 75.47 | 8.5937 | 2.573
Q | 16 | 51.75 | 17.6816 | 10.5878 | Q | 16 | 51.75 | 17.6816 | 5.2939
| Climate Zone | Therms/yr |  |  |  | Climate Zone | Therms/yr
Fuel Saved | 1 | 7.1507 |  |  | Fuel Saved | 1 | 12.487
Fuel Saved | 2 | 6.2422 |  |  | Fuel Saved | 2 | 10.9006
Fuel Saved | 3 | 6.2791 |  |  | Fuel Saved | 3 | 10.9651
Fuel Saved | 4 | 5.901 |  |  | Fuel Saved | 4 | 10.3047
Fuel Saved | 5 | 6.4667 |  |  | Fuel Saved | 5 | 11.2925
Fuel Saved | 6 | 5.5567 |  |  | Fuel Saved | 6 | 9.7035
Fuel Saved | 7 | 5.4337 |  |  | Fuel Saved | 7 | 9.4887
Fuel Saved | 8 | 5.2508 |  |  | Fuel Saved | 8 | 9.1693
Fuel Saved | 9 | 5.2385 |  |  | Fuel Saved | 9 | 9.1478
Fuel Saved | 10 | 5.1878 |  |  | Fuel Saved | 10 | 9.0593
Fuel Saved | 11 | 5.3353 |  |  | Fuel Saved | 11 | 9.317
Fuel Saved | 12 | 5.6904 |  |  | Fuel Saved | 12 | 9.937
Fuel Saved | 13 | 5.1955 |  |  | Fuel Saved | 13 | 9.0727
Fuel Saved | 14 | 5.4153 |  |  | Fuel Saved | 14 | 9.4565
Fuel Saved | 15 | 3.4478 |  |  | Fuel Saved | 15 | 6.0207
Fuel Saved | 16 | 7.0938 |  |  | Fuel Saved | 16 | 12.3877

## Private Faucet Energy Calcs
|  | 1.0 GPM Aerator |  |  |  |  | 0.5 GPM Aerator
Values | Units / Description | Existing | Measure |  | Values | Units / Description | Existing | Measure
V_dot | [gal/min] | 1.67 | 1 |  | V_dot | [gal/min] | 1.67 | 0.5
ρ | [lbm/gal] | 8.33 | 8.33 |  | ρ | [lbm/gal] | 8.33 | 8.33
m_dot | [lbm/min] | 13.9111 | 8.33 |  | m_dot | [lbm/min] | 13.9111 | 4.165
Conversion | [min/hr] | 60 | 60 |  | Conversion | [min/hr] | 60 | 60
cp | [Btu/(lbm*°F)] | 1 | 1 |  | cp | [Btu/(lbm*°F)] | 1 | 1
Conversion | [therm/Btu] | 1e-05 | 1e-05 |  | Conversion | [therm/Btu] | 1e-05 | 1e-05
Tmixed | [°F] | 97.9 | 97.9 |  | Tmixed | [°F] | 97.9 | 97.9
Usage time | [min/day] | 3.99 |  |  | Usage time | [min/day] | 3.99
Annual Usage Time (τ) | [hr/yr] | 11.2254 |  |  | Annual Usage Time (τ) | [hr/yr] | 11.2254
ξ | Efficiency | 0.76 | 0.76 |  | ξ | Efficiency | 0.76 | 0.76
Consumption | Climate Zone | Make-up Water Temperature (°F) | Q_Faucet (therms/yr) | Q_aerator (therms/yr) | Consumption | Climate Zone | Make-up Water Temperature (°F) | Q_Faucet (therms/yr) | Q_aerator (therms/yr)
Q | 1 | 51.38 | 5.7351 | 3.4342 | Q | 1 | 51.38 | 5.7351 | 1.7171
Q | 2 | 57.29 | 5.0065 | 2.9979 | Q | 2 | 57.29 | 5.0065 | 1.499
Q | 3 | 57.05 | 5.0361 | 3.0156 | Q | 3 | 57.05 | 5.0361 | 1.5078
Q | 4 | 59.51 | 4.7328 | 2.834 | Q | 4 | 59.51 | 4.7328 | 1.417
Q | 5 | 55.83 | 5.1865 | 3.1057 | Q | 5 | 55.83 | 5.1865 | 1.5528
Q | 6 | 61.75 | 4.4567 | 2.6687 | Q | 6 | 61.75 | 4.4567 | 1.3343
Q | 7 | 62.55 | 4.358 | 2.6096 | Q | 7 | 62.55 | 4.358 | 1.3048
Q | 8 | 63.74 | 4.2113 | 2.5218 | Q | 8 | 63.74 | 4.2113 | 1.2609
Q | 9 | 63.82 | 4.2015 | 2.5158 | Q | 9 | 63.82 | 4.2015 | 1.2579
Q | 10 | 64.15 | 4.1608 | 2.4915 | Q | 10 | 64.15 | 4.1608 | 1.2457
Q | 11 | 63.19 | 4.2791 | 2.5624 | Q | 11 | 63.19 | 4.2791 | 1.2812
Q | 12 | 60.88 | 4.5639 | 2.7329 | Q | 12 | 60.88 | 4.5639 | 1.3664
Q | 13 | 64.1 | 4.1669 | 2.4952 | Q | 13 | 64.1 | 4.1669 | 1.2476
Q | 14 | 62.67 | 4.3432 | 2.6007 | Q | 14 | 62.67 | 4.3432 | 1.3004
Q | 15 | 75.47 | 2.7652 | 1.6558 | Q | 15 | 75.47 | 2.7652 | 0.82791
Q | 16 | 51.75 | 5.6895 | 3.4069 | Q | 16 | 51.75 | 5.6895 | 1.7034
| Climate Zone | Therms/yr |  |  |  | Climate Zone | Therms/yr
Fuel Saved | 1 | 2.3009 |  |  | Fuel Saved | 1 | 4.018
Fuel Saved | 2 | 2.0086 |  |  | Fuel Saved | 2 | 3.5075
Fuel Saved | 3 | 2.0205 |  |  | Fuel Saved | 3 | 3.5283
Fuel Saved | 4 | 1.8988 |  |  | Fuel Saved | 4 | 3.3158
Fuel Saved | 5 | 2.0808 |  |  | Fuel Saved | 5 | 3.6336
Fuel Saved | 6 | 1.788 |  |  | Fuel Saved | 6 | 3.1223
Fuel Saved | 7 | 1.7484 |  |  | Fuel Saved | 7 | 3.0532
Fuel Saved | 8 | 1.6896 |  |  | Fuel Saved | 8 | 2.9505
Fuel Saved | 9 | 1.6856 |  |  | Fuel Saved | 9 | 2.9435
Fuel Saved | 10 | 1.6693 |  |  | Fuel Saved | 10 | 2.915
Fuel Saved | 11 | 1.7168 |  |  | Fuel Saved | 11 | 2.998
Fuel Saved | 12 | 1.831 |  |  | Fuel Saved | 12 | 3.1975
Fuel Saved | 13 | 1.6718 |  |  | Fuel Saved | 13 | 2.9194
Fuel Saved | 14 | 1.7425 |  |  | Fuel Saved | 14 | 3.0429
Fuel Saved | 15 | 1.1094 |  |  | Fuel Saved | 15 | 1.9373
Fuel Saved | 16 | 2.2826 |  |  | Fuel Saved | 16 | 3.986

## Water Savings
Water Consumption/Savings
| Units/Description | Existing | Measure
V_dot | [gal/min] | 1.67 | 1
0.5
|  | Public | Private
Usage time | [min/day] | 12.4 | 3.99
Annual Usage Time (τ) | [hr/yr] | 34.886 | 11.2254
Conversion | [min/hr] | 60
Consumption | Units/Description | Original Faucet | Faucet with Aerator
| Flow Rate | 1.67 GPM | 1.0 GPM | 0.5 GPM
| Public (gal per faucet per year) | 3495.5732 | 2093.1576 | 1046.5788
| Private (gal per faucet per year) | 1124.7852 | 673.5241 | 336.762
Savings | Units | 1.0 GMP | 0.5 GPM
| Public (gal per faucet per year) | 1402.4156 | 2448.9944
| Private (gal per faucet per year) | 451.2611 | 788.0232

## Assumptions & Terms
Assumptions:
1. Supply piping losses considered insignificant
2. Density of water at 120°F= 62.3 lbm/cubic foot
a. 1 gallon of water = 8.33 lbm
3. cp of water at temperature range from 50-212°F = 1 BTU/(lbm*°F)
4. 1 therm = 100,000 BTU
5. Thermal efficiency of water heating equipment assumed to be 76% (including losses)
6. Hand washing (mixed water) temperature of 97.9°F | See "Calculated Assumptions" tab
7. Faucet usage time:
a. Public: 12.4 min/day
b. Private: 3.99 min/day
8. Average existing flow rate of faucet: 1.67 gpm
Equations Used
q = m_dot*cp*Δt | Energy, 1st Law
Q = (m_dot*cp*(Tmixed-Tmu)*τ)/ξ | Energy consumed
m_dot = V_dot*ρ | Mass flow rate
Description of Terms
| Description | Unit
Tmixed | Temperature of mixed water (temperature of water coming out of faucet, mixed hot and cold water streams) | [°F]
Tmu (Tcold ) | Temperature of make up water (climate zone dependent) | [°F]
cp | Specific heat at constant pressure | [BTU/(lbm*°F)]
ρ | Density | [lbm/gal]
V_dot | Volumetric flow rate | [gal/min]
m_dot | Mass flow rate | [lbm/min]
ξ | Efficiency of water heating equipment | Factor
τ | Annual hand washing time (Based on Assumption #1) | [hr/yr]
Q_faucet | Energy consumption of bare faucet with no flow restrictor installed | [therm/yr]
Q_aerator | Energy consumption for faucet with low flow aerator installed | [therm/yr]
Control Volume:

## Calculated Assumptions
Faucet | Measured flow rate (gpm) | Max flow rate (gpm) | Faucets without aerators
1 | 1.65 | 1.99 | measured flow rate from metered data
2 | 1.57 | 2.04 | Max flow rate from spot check using bag/timer method or digital flow meter
3 | 2.74 | 5
4 | 1.47 | 4.8
5 | 1.4 | 2.03
6 | 1.68 | 5.63
7 | 1.18 | 2.34
8 | 1.16 | 2.06
9 | 2.17 | 6.35
Average | 1.6689 | 3.5822
Behavioral Factor | 0.46588
Public lavatories
Faucet | Usage (min/day) | Length of average usage instance (s) | Average Number of Usage Instances per Day | Usage per day (s) | Usage per day (min)
1 | 16.78 | 6.56 | 147.6 | 968.256 | 16.1376
2 | 7.1 | 6.18 | 65.6 | 405.408 | 6.7568
3 | 20.68 | 6.59 | 177 | 1166.43 | 19.4405
4 | 10.07 | 5.04 | 105.22 | 530.3088 | 8.8385
5 | 15.98 | 18.08 | 53.1 | 960.048 | 16.0008
6 | 14.23 | 10.44 | 79.7 | 832.068 | 13.8678
7 | 5.22 | 10.57 | 36.9 | 390.033 | 6.5006
8 | 7.81 | 18.06 | 29.4 | 530.964 | 8.8494
9 | 13.95 | 14.27 | 62.7 | 894.729 | 14.9122
Average | 12.4244 |  |  |  | 12.3671
Average of both calculation methods | 12.3958 | min/day
Private lavatories
Faucet | Usage (min/day) | Length of average usage instance (s) | Average Number of Usage Instances per Day | Usage per day (s) | Usage per day (min)
1 | 7.96 | 26.91 | 20.9 | 562.419 | 9.3736
2 | 1.18 | 8.12 | 8 | 64.96 | 1.0827
3 | 2.06 | 10.61 | 13.07 | 138.6727 | 2.3112
Average | 3.7333 |  |  |  | 4.2558
Average of both calculation methods | 3.9946
Faucet | Mixed Water Temperature (F)
1 | 108
2 | 112
3 | 98
4 | 99
5 | 94
6 | 90
7 | 97
8 | 106
9 | 104
10 | 90
11 | 102.1
12 | 92.1
13 | 96.4
14 | 81.3
Average | 97.85

## Com Operating Hours
Operating Hours of Commercial Buildings |  |  |  | Source: | http://www.eia.gov/consumption/commercial/data/2012/bc/cfm/pba1.php
Building Type | Average Hours/Week | Hours/Year | Days/Year
Education | 53 | 2756 | 114.8333
Food Sales | 121 | 6292 | 262.1667
Food Service | 82 | 4264 | 177.6667
Lodging | 165 | 8580 | 357.5
Mercantile | 64 | 3328 | 138.6667
Office | 55 | 2860 | 119.1667
Public Assembly | 56 | 2912 | 121.3333
Public Order and Safety | 113 | 5876 | 244.8333
Religious Worship | 31 | 1612 | 67.1667
Service | 56 | 2912 | 121.3333
Other | 61 | 3172 | 132.1667
Average of Commercial Sector: | 77.9091 | 4051.2727 | 168.803