Workpaper WPSCGREWH130613A

Revision 1

Southern California Gas Company

Customer Programs Department

Central Storage Water Heaters for 
Multifamily Residential Applications

Revision History

| Revision No. | Date | Description | Author |
| --- | --- | --- | --- |
| 0 | November 27, 2013 | Original Release | Ali Bozorgi (ICF) |
| 1 | September 08, 2016 | - Updates per Water Heater Disposition (Attachment G) - Adjust cost to include installation (Labor and Material) - Added air quality emission requirements | Miguel Urrea (SCG) |

Measure Summary Table A

| Measure Name | Program Application Type (RE, NC, ROB, ER) | EUL or RUL (yr) | CZ | Building Type | Building Vintage | Unit Definition | NTGR | Program Delivery Method (CustIncent, PreReb, DirInstall) | Gross Realization Rate (GRR) | % Eligible for TOU AC Adjustment |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MF Central Storage Water Heater >75 kBtuh, Tier 1 (83% TE) | ROB | 15 | 9 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2 (90% TE) | ROB | 15 | 9 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |

Measure Summary Table B

| Measure Name | Gas Savings (therms/yr/kBtu) | User Entered kW Savings per unit (kW/unit) | Gross Unit Annual Electricity Savings (kWh/unit) | Measure Electric End Use Shape (Load Shape) | Incremental Measure Cost ($/kBtu) |
| --- | --- | --- | --- | --- | --- |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 9 | 1.01 | N/A | N/A | N/A | $2.56 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 9 | 3.09 | N/A | N/A | N/A | $8.81 |

Note: For the complete list of Measures, refer to the accompanying calculation spreadsheet

# Table of Contents

Revision History	i

Measure Summary Table A	ii

Measure Summary Table B	ii

List of Tables	iv

List of Figures	iv

SECTION 1 - General Measure & Baseline Data	1

1.01	Measure & Delivery Description	1

1.02	DEER Differences Analysis	3

1.03	Code Analysis	4

1.04	Measure Effective Useful Life	7

1.05	Net-to-Gross Ratios for Different Program Strategies	7

1.06	Gross Realization Rate	7

1.07	Time-of-Use Adjustment Factor	7

SECTION 2 - Energy Savings & Demand Reduction Calculations	7

2.01	Load Shapes	7

2.02	Energy Savings	7

SECTION 3 - Base Case & Measure Costs	12

3.02	Base Case Cost	13

3.03	Gross Measure Cost	13

3.04	Incremental Measure Cost	13

Attachments	14

References	15

List of Tables

Table 1 -	Commercial Storage Water Heater Thermal Efficiencies in DEER2013	3

Table 2 -	Code Summary	4

Table 3 -	Code Summary - NOxRequirements for AQMDs	5

Table 4 -	Annual Gas Consumption and Savings by Tier and Climate Zone	10

Table 5 -	Annual Gas Savings per Water Heater System	11

Table 6 -	Gross and Incremental Measure Cost by Equipment Type	13

List of Figures

Figure 1 - Distribution of Thermal Efficiencies for Non-condensing Large Storage Water Heaters in the CEC Appliance Efficiency Database	2

Figure 2 - Distribution of Thermal Efficiencies for Condensing Large Storage Water Heaters in the CEC Appliance Efficiency Database	2

Figure 3 - California Counties Subject to Ultra Low NOx Requirements	6

Figure 4 - California Energy Commission Forecast Climate Zones	8

Figure 5 - Water Heater Gas Consumption Adjustment Factors for the California 16 Climate Zones	9

General Measure & Baseline Data

Measure & Delivery Description

Measure Description

- A typical gas-fired storage water heater is a large vertical insulated tank with a gas burner located under the tank.  When hot water is drawn from the tank, cold water flows into the bottom of the tank.  When the water temperature in the tank gets too low, a thermostat sensing the water temperature (often called an aquastat) calls for heat from the burner.  When the water temperature in the tank reaches the set point, the thermostat turns off the burner.  The burner may be ignited by an electronic spark ignition, glow plug, or, in some models, by a standing pilot light.

- The rated input for a natural gas fueled storage water heater for this multifamily residential measure must exceed 75,000 Btuh (75 kBtuh).  Qualifying storage water heaters must also have a storage tank that holds at least 80 gallons of water. This measure will have two tiers of incentive: Tier 1 is for large natural gas non-condensing storage water heaters and Tier 2 is for large natural gas condensing storage water heaters.  Tier 2 water heaters will often require flu modifications.  These modifications may increase or decrease installation costs.  Tier 2 systems also receive higher rebates than Tier 1 systems. Relative to standard models, energy efficient units typically have features such as no standing pilot light, larger heat exchange surfaces, additional tank insulation, and the capability to condense moisture in the flue gas.

- The test method for measuring storage water heater thermal efficiency (TE) is ANSI Z21.10.3-1998 §2.9, as referenced in the California Title 20 standard.  A parameter for determining the thermal efficiency and energy consumption of water heaters is the cold water temperature at the inlet to the storage water heater. The nominal ANSI standard temperature of the supply water entering the water heater is 70 F. The actual inlet water temperature in California varies with climate zone and season, so adjustment factors were created based on ground temperature data for each climate zone to account for varying water heater consumption due to inlet water temperature. More information regarding these adjustment factors are included in Section 2.02. The California Title 20 standard defines a minimum TE of 80% for the baseline large storage water heaters. The qualifying measure efficiencies for large storage water heaters are the following with an emission limit of 14ng/J or 20 ppm NOx @3% O2 dry:

Minimum TE of 83% for Tier 1 (non-condensing) large storage water heaters.

Minimum TE of 90% for Tier 2 (condensing) large storage water heaters.

Baseline and Measure Efficiencies

- These measure efficiencies are adopted after consideration of the availability of high-efficiency storage water heaters listed in the California Energy Commission Energy Efficiency Appliance Database (CEC Database).  Figure 1 shows the distribution of thermal efficiencies for the 965 large non-condensing storage water heater products found in the CEC Database.  About 80% of the products are considered baseline while 20% of the products meet the minimum TE for Tier 1.  Figure 2 shows the distribution of thermal efficiencies for the 266 large condensing storage water heater products found in the CEC Database.   Over 90% of the products meet the minimum TE for Tier 2.  Note: The CEC Appliance Database does not consider emission compliance which would reduce the number of available water heaters for more than 77% of California’s populations.

- Figure 1 - Distribution of Thermal Efficiencies for Non-condensing Large Storage Water Heaters in the CEC Appliance Efficiency Database

- Figure 2 - Distribution of Thermal Efficiencies for Condensing Large Storage Water Heaters in the CEC Appliance Efficiency Database

Market Applicability

- These measures are applicable to multifamily properties.  The large natural gas central water heaters must serve two or more dwelling units (households) to be eligible for incentives.

Terms & Conditions

The rebate applies to gas-for-gas equipment replacements on burnout (ROB).

Qualifying storage water heaters must have an input rate of at least 75 kBtuh and a storage tank size of at least 80 gallons.

Tankless water heaters or hot water boilers with a separate storage tank that are factory mounted on the same skid do not qualify as a storage water heater.

Storage water heaters used for space heating applications do not qualify.

Water heaters used for pools or spas do not qualify.

The manufacturer’s name and equipment model number must be provided.

If necessary, customer must provide proof of unit efficiency (e.g., manufacturer’s equipment specification sheet).

The equipment model must be listed on California Energy Commission Energy Efficiency Appliance Database (CEC Database) to qualify for the rebate.

The equipment must meet the minimum emission requirements per air district.

Delivery Method

- The preferred delivery method is a downstream prescriptive rebate offered to the gas customer purchasing the storage water heater.  However, a midstream point-of-sale rebate or an upstream manufacturer rebate strategy may also be implemented.

DEER Differences Analysis

    - Baseline and Measure Efficiency

- Large storage water heaters for multifamily residential applications are not specified in the 2013 Database for Energy-Efficiency Resources (DEER2013) Update for 2014 Codes.  Table 1 lists the baseline and measure efficiencies for commercial storage water heaters found in the DEER2013.  This workpaper uses commercial storage water heaters because they are typically found in multifamily buildings. All of these storage water heaters have standby losses of 0.56% per hour.  Standby losses are expressed as a percentage of the energy stored in the hot water relative to the average ambient air temperature.  The minimum baseline DEER efficiencies listed in Table 1 were applied to the baseline large storage water heaters for multifamily residential applications.  The minimum qualifying DEER measure efficiencies listed in Table 1 were applied to the Tier 1 and Tier 2 large storage water heater measures for multifamily residential applications.

Commercial Storage Water Heater Thermal Efficiencies in DEER2013

| Equipment Type | DEER Baseline | DEER Measure |
| --- | --- | --- |
| Commercial Storage Water Heater >75 kBtuh, Tier 1 (non-condensing), Readi ID: NG-WtrHt-LrgStrg-Gas-gte75kBtuh-0p83Et | 80% | 83% |
| Commercial Storage Water Heater >75 kBtuh, Tier 2 (condensing), Readi ID: NG-WtrHt-LrgStrg-Gas-gte75kBtuh-0p90Et | 80% | 90% |

Equipment Useful Life

- DEER2013 includes equipment useful life (EUL) values for water heaters. The EUL is 11 years for residential natural gas storage water heaters (WtrHt-SmlStrg-Gas-Res). The EUL is 15 years for large natural gas storage water heaters (WtrHt-LrgStrg-Gas). Because commercial storage water heaters are used as central storage water heaters in multifamily residential applications, the appropriate EUL for use in this workpaper is 15 years (see Section 1.04).

Net to Gross Ratio

- The DEER2013 values for net-to-gross (NTG) ratio are used in this workpaper (see Section 1.05).

Incremental Measure Cost

- The DEER2013 contains a measure for large storage water heaters with a TE of 82% and a baseline of 80%.  Although the baseline of 80% is the same, DEER does not contain cost data for large storage water heaters with a TE of 83% or 90% in the 2008, 2011, or 2013 databases. Since the efficiencies used here are different from those used for the DEER2013 database, the incremental measure costs found in DEER2013 do not apply.  Cost was data derived from Technical Support Document (TSD) “Commercial Water heating Equipment (EERE-2014-BT-STD-0042)”. The incremental measure costs used in this workpaper are based on the cost data provided by the TSD.

Code Analysis

- The minimum baseline efficiency is consistent with the California Title 20 standard for large gas storage water heaters with less than 4,000 Btuh of rated input per gallon of measured storage volume2. The minimum qualifying measure efficiencies exceed the California Title 20 standard for large gas storage water heaters with less than 4,000 Btuh of rated input per gallon of measured storage volume2.

Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | Section 110.3 | 11/26/2013 |
| Title 20 (2014) | Section 1605.3(f) | 1/20/2004 |
| Code of Federal Regulations | 10 CFR 430.32(d) | 04/16/2015 |
| South Coast AQMD | Rule 1121, Rule 1146.2 | See Rule |
| Bay Area AQMD | Regulation 9, Rule 6 | See Rule |
| San Joaquin Valley APCD | Rule 4902 | See Rule |
| Sacramento Metropolitan AQMD | Rule 414 | See Rule |
| Yolo-Solano AQMD | Regulation II, Rule 2.37 | See Rule |
| Ventura County Air Pollution Control District | Rule 74.11 | See Rule |

Code Summary - NOxRequirements for AQMDs

| Category | Rated heat input capacity | Rule | Emission Limit |
| --- | --- | --- | --- |
| Mobile Home Water Heater | All | YSAQMD-2.37, SJVUAPCD-4902, BAAQMD-Reg 9-Rule 6, SMAQMD- 414, VCAPCD-74.11 | 40ng/J or 55 ppm NOx @3% O2 dry |
| Small Water Heater | <75,000 Btu/hr | YSAQMD-2.37, SJVUAPCD-4902 , SCAQMD-1121, BAAQMD-Reg 9-Rule 6, SMAQMD-414, SBCAPCD-352, VCAPCD-74.11 | 10ng/J or 15 ppm NOx @3% O2 dry |
| Large Water Heater | 75,000 - 400,000 Btu/hr | YSAQMD-2.37, BAAQMD-Reg 9-Rule 6, SMAQMD-414, VCAPCD-74.11.1, SCAQMD-1146.2 | 14ng/J or 20 ppm NOx @3% O2 dry |
| Small Boiler | 400,000-1,000,000 Btu/hr | YSAQMD-2.37, BAAQMD-Reg 9-Rule 6*, SMAQMD-414, VCAPCD-74.11.1, SCAQMD-1146.2 | 14ng/J or 20 ppm NOx @3% O2 dry |
| Pool/Spa Heater | 400,000-1,000,000 Btu/hr | YSAQMD-2.37, BAAQMD-Reg 9-Rule 6, SMAQMD-414** | 14ng/J or 20 ppm NOx @3% O2 dry |
| Instantaneous Water Heater*** | Unspecified | SJVUAPCD-4902, BAAQMD-Reg 9-Rule 6, SMAQMD-414, SCAQMD-1146.2***, YSAQMD-2.37*** | 14ng/J or 20 ppm NOx @3% O2 dry |

*BAAQMD Defines Small Boiler input capacity as 400,000 - 2,000,000 Btu/hr

**SMAQMD regulates Pool/spa heaters at 40 ng/J

***SCAQMD does not set emission requirements for instantaneous water heaters, but any instantaneous water heaters within Type 1 water heaters (75,001 Btu/h – 400,000 Btu/h) rated input capacity must meet this requirement. YSAQMD requirements are based on small and large water heaters ( < 75,000 and 75,001 – 400,000 btu/h).  Any instantaneous water heater within this rated input capacity must meet this requirement.

- Figure 3 - California Counties Subject to Ultra Low NOx Requirements

The minimum baseline efficiencies are consistent with the Code of Federal Regulations standards.

The minimum qualifying measure efficiencies exceed the California Titles 20 and Code of Federal Regulations standards.

Measure Effective Useful Life

- The effective useful life (EUL) WtrHt-Com of 15 years for central storage water heaters for multifamily residential applications is taken from the value for large storage water heaters for commercial applications in DEER 2014 update.

Net-to-Gross Ratios for Different Program Strategies

- The DEER2014 documents recommend a net-to-gross ratio (NTGR) Res-Default>2  of 0.55 for all other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years.

Gross Realization Rate

- Gross realization rate of 1.00 is applied to the measures in this document.

Time-of-Use Adjustment Factor

- N/A

Energy Savings & Demand Reduction Calculations

Load Shapes

- N/A

Energy Savings

- The energy savings estimates for measures in this workpaper were calculated for each CA climate zones as shown in Measure Summary Table.  The 16 California Energy Commission forecast climate zones are shown in Figure 4. These areas are grouped according to California Title 24 and “represent a geographic area for which an energy budget is established.” Title 24 also states,

- “The Energy Commission originally developed weather data for each climate zone by using unmodified (but error-screened) data for a representative city and weather year (representative months from various years). The Energy Commission analyzed weather data from weather stations selected for (1) reliability of data, (2) currency of data, (3) proximity to population centers, and (4) non-duplication of stations within a climate zone.”

- Figure 4 - California Energy Commission Forecast Climate Zones

Annual Electric Energy Savings

- No electric energy savings will result from this measure.

Electric Demand Reduction

- No electric demand reduction will result from this measure

Annual Gas Energy Savings

The annual water heater gas energy use for the 16 California Energy Commission are established by applying 16 adjustment factors to the state average storage water heater gas consumption for multifamily apartments/units from the 2009 California Residential Appliance Saturation Study (RASS).

The adjustment factors were developed using 2013 ground temperature data and the “Building America Multi-Family Central Water Heating Evaluation Tool” from the Department of Energy’s Office of Energy Efficiency and Renewable Energy to model the annual water heater gas consumption for the 16 climate zones. The annual consumption associated with each climate zone was then divided by the median of consumptions in all 16 climate zones to estimate the adjustment factor for each climate zone, which are presented in Figure 5. The adjustment factor calculations are included in an Excel file embedded as Attachment A.

- Figure 5 - Water Heater Gas Consumption Adjustment Factors for the California 16 Climate Zones

- The calculated adjustment factors are applied to the state average gas consumption for multi-family apartment unit from RASS to establish the baseline water heater gas consumption for the 16 climate zones.

- The following steps were then taken to derive the gas savings per unit of water heater capacity (kBtuh):

Determine average rated input of central storage water heater per dwelling unit along with average number of occupants per dwelling unit. These resources can be found in Attachment E.

Calculate gas savings per kBtuh rated input from the baseline thermal efficiency and the measure thermal efficiency.

For calculating energy savings, the following assumptions are used:

The average efficiency for the baseline products is a minimum TE of 80% based on California Title 20 code standard.

The average efficiencies for the qualifying products are: 1) a minimum TE of 83% for Tier 1 (non-condensing) large storage water heaters, 2) a minimum TE of 90% for Tier 2 (condensing) large storage water heaters.

With these assumptions, the energy saved by a high-efficiency measure storage water heater can be calculated as follows:

∆Q = Qb x (1 - Eb/Em)											Eqn-1

- where

∆Q – Gas Saved (therms/yr).  Savings which results from installing the high-efficiency measure equipment.

E – Efficiency (%).  Efficiency of equipment in appropriate efficiency units (thermal efficiency).

Subscript b = Baseline (or base case) equipment

Subscript m = Measure (new high-efficiency) equipment

The gas savings are calculated for each or climate zone.  The energy savings data and calculations are included in an Excel file embedded as Attachment B.

- The calculated gas consumption and savings per climate zone and tier are summarized in Table 4:

Annual Gas Consumption and Savings by Tier and Climate Zone

| Climate Zone | Tier | Annual Gas Consumption per Apartment Unit (Therms/Yr/Dwelling Unit) | Annual Gas Savings (Therms/Yr/Dwelling Unit) | Annual GasSavings (Therms/Yr/ kBtuh) |
| --- | --- | --- | --- | --- |
| 1 | 1 | 196 | 7.1 | 1.09 |
| 2 | 1 | 189 | 6.8 | 1.05 |
| 3 | 1 | 189 | 6.8 | 1.05 |
| 4 | 1 | 186 | 6.7 | 1.03 |
| 5 | 1 | 190 | 6.9 | 1.06 |
| 6 | 1 | 183 | 6.6 | 1.02 |
| 7 | 1 | 182 | 6.6 | 1.01 |
| 8 | 1 | 181 | 6.5 | 1.01 |
| 9 | 1 | 181 | 6.5 | 1.01 |
| 10 | 1 | 181 | 6.5 | 1.00 |
| 11 | 1 | 182 | 6.6 | 1.01 |
| 12 | 1 | 185 | 6.7 | 1.03 |
| 13 | 1 | 181 | 6.5 | 1.01 |
| 14 | 1 | 183 | 6.6 | 1.02 |
| 15 | 1 | 168 | 6.1 | 0.93 |
| 16 | 1 | 195 | 7.1 | 1.09 |
| 1 | 2 | 196 | 21.7 | 3.34 |
| 2 | 2 | 189 | 21.0 | 3.22 |
| 3 | 2 | 189 | 21.0 | 3.23 |
| 4 | 2 | 186 | 20.7 | 3.18 |
| 5 | 2 | 190 | 21.1 | 3.25 |
| 6 | 2 | 183 | 20.4 | 3.13 |
| 7 | 2 | 182 | 20.3 | 3.12 |
| 8 | 2 | 181 | 20.1 | 3.09 |
| 9 | 2 | 181 | 20.1 | 3.09 |
| 10 | 2 | 181 | 20.1 | 3.09 |
| 11 | 2 | 182 | 20.2 | 3.11 |
| 12 | 2 | 185 | 20.5 | 3.15 |
| 13 | 2 | 181 | 20.1 | 3.09 |
| 14 | 2 | 183 | 20.3 | 3.12 |
| 15 | 2 | 168 | 18.6 | 2.87 |
| 16 | 2 | 195 | 21.7 | 3.34 |

The savings are also calculated for two sizes of central water heaters, smaller than or equal to 200,000 kBtuh and larger than 200,000 kBtuh. Based on the SoCal Gas rebate application data for central storage water heaters in multifamily buildings, the average capacity of water heaters smaller than or equal to 200,000 kBtuh is about 150,000 kBtuh and average capacity of water heaters larger than 200,000 kBtuh is about 265,000 kBtuh. These average sizes are multiplied by the Annual Gas Savings per kBtu (Therms/Yr/kBtuh) for each climate zone from Table 4 to estimate the gas savings per system for the 16 climate zones.  The annual gas savings per water heater system are summarized in Table 5:

Annual Gas Savings per Water Heater System

| Climate Zone | Tier | Annual Gas Savings (Therm/Yr) per Water Heater System <= 200 kBtuh | Annual Gas Savings (Therm/Yr) per Water Heater System > 200 kBtuh |
| --- | --- | --- | --- |
| 1 | 1 | 163 | 288 |
| 2 | 1 | 157 | 278 |
| 3 | 1 | 157 | 279 |
| 4 | 1 | 155 | 274 |
| 5 | 1 | 159 | 281 |
| 6 | 1 | 153 | 270 |
| 7 | 1 | 152 | 269 |
| 8 | 1 | 151 | 267 |
| 9 | 1 | 151 | 267 |
| 10 | 1 | 150 | 266 |
| 11 | 1 | 152 | 268 |
| 12 | 1 | 154 | 272 |
| 13 | 1 | 151 | 267 |
| 14 | 1 | 152 | 269 |
| 15 | 1 | 140 | 247 |
| 16 | 1 | 163 | 288 |
| 1 | 2 | 501 | 887 |
| 2 | 2 | 483 | 855 |
| 3 | 2 | 484 | 856 |
| 4 | 2 | 476 | 843 |
| 5 | 2 | 487 | 863 |
| 6 | 2 | 470 | 831 |
| 7 | 2 | 467 | 827 |
| 8 | 2 | 464 | 821 |
| 9 | 2 | 463 | 820 |
| 10 | 2 | 463 | 819 |
| 11 | 2 | 466 | 825 |
| 12 | 2 | 473 | 837 |
| 13 | 2 | 463 | 820 |
| 14 | 2 | 468 | 828 |
| 15 | 2 | 430 | 761 |
| 16 | 2 | 500 | 886 |

Base Case & Measure Costs

Cost was data derived from Technical Support Document (TSD) “Commercial Water heating Equipment (EERE-2014-BT-STD-0042)”.  This data includes both labor and material cost.  Condensing water heaters typically use pvc for venting flue exhaust which is cheaper and easier to install than sheet metal used for non-condensing water heaters10.  The cost difference in venting material and installation is captured in the above referenced documents.  The cost data and calculations are included in an Excel file embedded as Attachment C.  Summary of cost data captured from the TSDs are included in Attachment F.

Both online vendor cost survey and the Ex Ante Measure Cost Study were taken into consideration while developing the cost data.  Vendor cost survey provided a reference point for product cost, but did not provide sufficient data for installation cost due to the various installation set-ups.  The Measure Cost Study did not appear to take ultra-low NOx production cost into consideration for gas storage water heaters.  Citing the CEC’s Appliance Database as the source for qualifying water heaters (CEC’s Appliance Database does not take air quality regulations into consideration). Air quality regulations were only mentioned in the study in reference to boiler projects.  Due to thorough investigation of storage water heater cost and installation set-ups, including updated cost for large storage water heaters, the TSD’s were used for final cost data.  Both the Measure Cost Study and online vendor study are included in the cost data Attachment D for reference.

TSD “Commercial Water heating Equipment (EERE-2014-BT-STD-0042)”11 reports the total installed cost for large storage water heaters as the sum of equipment retail price and the installation cost, but does not present the exact equipment retail and installation cost values used in the summation.  The large storage water heaters are reported as one single cost value.

Base Case Cost

When the customer is replacing equipment on burnout (ROB) or buying new equipment (NC), the customer must buy a new storage water heater to continue operating, so the base case cost is that of a baseline storage water heater.  The base case costs are shown in Table 6 - below.

Gross Measure Cost

The gross measure costs include the cost of the equipment, installation and start-up costs.

Venting material used with non-condensing water heaters are not suitable for condensing due to material properties.  Plastics used for condensing water heaters have lower vent temperatures limits and are not suitable for non-condensing water heaters.  The cost differences in these set-ups are taken into consideration in the cost analysis.  The gross measure costs are shown in Table 6 - below.

Incremental Measure Cost

The incremental measure cost (IMC) is the difference between the cost of the average baseline unit and the average high efficiency measure.  The incremental measure costs are shown in Table 6.

Gross and Incremental Measure Cost by Equipment Type

| Equipment Type | Large Tier 1 | Large Tier 2 |
| --- | --- | --- |
| Rated Input (kBtuh) | > 75 | > 75 |
| DOE Technical Support Document |  |  |
| Base Cost ($/kBtuh) | $23.29 | $23.29 |
| Gross Measure Cost ($/kBtuh) | $25.85 | $32.10 |
| Incremental Measure Cost ($/kBtuh) | $2.56 | $8.81 |

Attachments

Attachment A –Storage Water Heater Gas Consumption Modeling and Adjustment Factors Calculation

Attachment B – Storage Water Heater Energy Savings Calculations

Attachment C – Storage Water Heater Vendor Cost Data

Attachment D – Explanation of DOE Building America Multi-family Water Heater Tool (See Section 2.1.7 for Tool Methodology)

Attachment E – kBtuh per Dwelling Unit Derivation

Attachment F – Water Heater & Boiler Cost Summary

Attachment G – Water Heater Disposition

References

Gas Water Heaters - Volume III, Storage Water Heaters With Input Ratings Above 75,000 Btu Per Hour, Circulating and Instantaneous, ANSI Z21.10.3-2011/CSA 4.3-2011 (Replaces ANSI Z21.10.3-1998) (http://webstore.ansi.org/RecordDetail.aspx?sku=ANSI+Z21.10.3-2011%2FCSA+4.3-2011).

California Code of Regulations, Title 20. Public Utilities and Energy, Division 2. State Energy Resources Conservation and Development Commission, California Energy Commission, CEC-140-2012-002, November 2012 (Accessed July 24, 2013 at http://www.energy.ca.gov/2012publications/CEC-140-2012-002/CEC-140-2012-002.pdf.

California Energy Commission Appliance Efficiency Database (Accessed March 7, 2012 at http://www.appliances.energy.ca.gov/AdvancedSearch.aspx).

(Team, 2011)

http://www.energy.ca.gov/title24/2013standards/prerulemaking/documents/current/Reports/Residential/Water_Heating/2013_CASE_WH2.WH5_WaterHeaterReady-10.28.2011.pdf

California Energy Commission Appliance Efficiency Database (Accessed March 7, 2012 at http://www.appliances.energy.ca.gov/AdvancedSearch.aspx).

DEER2013 Database for Energy-Efficiency Resources, READI_v1.0.1, Updated for 2014 Codes (Accessed October 1, 2013 at http://www.deeresources.com/).

(DOE, Docket ID: EERE-2014-BT-STD-0042, 2016)

https://www.regulations.gov/#!docketDetail;D=EERE-2014-BT-STD-0042

(EUL Table Update, 2014), http://deeresources.com/files/DEER2013codeUpdate/download/DEER2014-EUL-table-update_2014-02-05.xlsx

(DEER2011 Update Net-To-Gross table, 2012), http://deeresources.com/files/DEER2011/download/DEER2011_NTGR_2012-05-16.xls

California Energy Commission Climate Zone Map, http://www.energy.ca.gov/maps/renewable/building_climate_zones.html.

2009 California Residential Appliance Saturation Study, by KEMA, Inc., for California Energy Commission, CEC‐ 200‐ 2010‐004‐ES, October 2010 (Accessed June 25, 2013 at http://websafe.kemainc.com/rass2009/Default.aspx).

(DOE, Docket ID: EERE-2014-BT-STD-0042, 2016)

https://www.regulations.gov/#!docketDetail;D=EERE-2014-BT-STD-0042

(Itron, Inc, 2014)

http://www.calmac.org/publications/2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report.pdf