Workpaper WPSCGREWH130613A

Revision 0

Southern California Gas Company

Customer Programs Department

Central Storage Water Heaters for 
Multifamily Residential Applications

Revision History

| Revision No. | Date | Description | Author |
| --- | --- | --- | --- |
| 0 | November 27, 2013 | Original Release | Ali Bozorgi (ICF) |

Measure Summary Table A

| Measure Name | Program Application Type (RE, NC, ROB, ER) | EUL or RUL (yr) | CZ | Building Type | Building Vintage | Unit Definition | NTGR | Program Delivery Method (CustIncent, PreReb, DirInstall) | Gross Realization Rate (GRR) | % Eligible for TOU AC Adjustment |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 1 | NC, ROB | 15 | 1 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 2 | NC, ROB | 15 | 2 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 3 | NC, ROB | 15 | 3 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 4 | NC, ROB | 15 | 4 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 5 | NC, ROB | 15 | 5 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 6 | NC, ROB | 15 | 6 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 7 | NC, ROB | 15 | 7 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 8 | NC, ROB | 15 | 8 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 9 | NC, ROB | 15 | 9 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 10 | NC, ROB | 15 | 10 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 11 | NC, ROB | 15 | 11 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 12 | NC, ROB | 15 | 12 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 13 | NC, ROB | 15 | 13 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 14 | NC, ROB | 15 | 14 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 15 | NC, ROB | 15 | 15 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 16 | NC, ROB | 15 | 16 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 1 | NC, ROB | 15 | 1 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 2 | NC, ROB | 15 | 2 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 3 | NC, ROB | 15 | 3 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 4 | NC, ROB | 15 | 4 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 5 | NC, ROB | 15 | 5 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 6 | NC, ROB | 15 | 6 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 7 | NC, ROB | 15 | 7 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 8 | NC, ROB | 15 | 8 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 9 | NC, ROB | 15 | 9 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 10 | NC, ROB | 15 | 10 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 11 | NC, ROB | 15 | 11 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 12 | NC, ROB | 15 | 12 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 13 | NC, ROB | 15 | 13 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 14 | NC, ROB | 15 | 14 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 15 | NC, ROB | 15 | 15 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 16 | NC, ROB | 15 | 16 | MF Residential | N/A | MBtuh | 0.70 | PreReb | 1.00 | N/A |

Measure Summary Table B

| Measure Name | Gas Savings (therms/yr/kBtu) | User Entered kW Savings per unit (kW/unit) | Gross Unit Annual Electricity Savings (kWh/unit) | Measure Electric End Use Shape (Load Shape) | Incremental Measure Cost ($/kBtu) |
| --- | --- | --- | --- | --- | --- |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 1 | 1.09 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 2 | 1.05 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 3 | 1.05 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 4 | 1.03 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 5 | 1.06 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 6 | 1.02 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 7 | 1.01 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 8 | 1.01 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 9 | 1.01 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 10 | 1.00 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 11 | 1.01 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 12 | 1.03 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 13 | 1.01 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 14 | 1.02 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 15 | 0.93 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 1, CZ 16 | 1.09 | N/A | N/A | N/A | $2.98 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 1 | 3.34 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 2 | 3.22 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 3 | 3.23 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 4 | 3.18 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 5 | 3.25 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 6 | 3.13 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 7 | 3.12 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 8 | 3.09 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 9 | 3.09 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 10 | 3.09 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 11 | 3.11 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 12 | 3.15 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 13 | 3.09 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 14 | 3.12 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 15 | 2.87 | N/A | N/A | N/A | $9.52 |
| MF Central Storage Water Heater >75 kBtuh, Tier 2, CZ 16 | 3.34 | N/A | N/A | N/A | $9.52 |

# Table of Contents

Revision History	i

Measure Summary Table A	ii

Measure Summary Table B	iv

List of Tables	vii

List of Figures	vii

SECTION 1 - General Measure & Baseline Data	1

1.01	Measure & Delivery Description	1

1.02	DEER Differences Analysis	3

1.03	Code Analysis	4

1.04	Measure Effective Useful Life	4

1.05	Net-to-Gross Ratios for Different Program Strategies	4

1.06	Gross Realization Rate	4

1.07	Time-of-Use Adjustment Factor	4

SECTION 2 - Energy Savings & Demand Reduction Calculations	5

2.01	Load Shapes	5

2.02	Energy Savings	5

SECTION 3 - Base Case & Measure Costs	10

3.01	Base Case Cost	10

3.02	Gross Measure Cost	10

3.03	Incremental Measure Cost	11

Attachments	13

References	14

List of Tables

Table 1 - Commercial Storage Water Heater Thermal Efficiencies in DEER2013	3

Table 2 - Annual Gas Consumption and Savings by Tier and Climate Zone	8

Table 3 – Annual Gas Savings per Water Heater System	9

Table 4 - Gross and Incremental Measure Cost by Equipment Type	12

List of Figures

Figure 1 - Distribution of Thermal Efficiencies for Non-condensing Large Storage Water Heaters in the CEC Appliance Efficiency Database	2

Figure 2 - Distribution of Thermal Efficiencies for Condensing Large Storage Water Heaters in the CEC Appliance Efficiency Database	2

Figure 3 - California Energy Commission Forecast Climate Zones	6

Figure 4 – Water Heater Gas Consumption Adjustment Factors for the California 16 Climate Zones	7

General Measure & Baseline Data

Measure & Delivery Description

Measure Description

- A typical gas-fired storage water heater is a large vertical insulated tank with a gas burner located under the tank.  When hot water is drawn from the tank, cold water flows into the bottom of the tank.  When the water temperature in the tank gets too low, a thermostat sensing the water temperature (often called an aquastat) calls for heat from the burner.  When the water temperature in the tank reaches the set point, the thermostat turns off the burner.  The burner may be ignited by an electronic spark ignition, glow plug, or, in some models, by a standing pilot light.

- The rated input for a natural gas fueled storage water heater for this multifamily residential measure must exceed 75,000 Btuh (75 kBtuh).  Qualifying storage water heaters must also have a storage tank that holds at least 80 gallons of water. This measure will have two tiers of incentive: Tier 1 is for large natural gas non-condensing storage water heaters and Tier 2 is for large natural gas condensing storage water heaters.  Tier 2 water heaters will often require flu modifications in order to condensate which may raise installation costs. Tier 2 systems also receive higher rebates than Tier 1 systems. Relative to standard models, energy efficient units typically have features such as no standing pilot light, larger heat exchange surfaces, additional tank insulation, and the capability to condense moisture in the flue gas.

- The test method for measuring storage water heater thermal efficiency (TE) is ANSI Z21.10.3-1998 §2.9, as referenced in the California Title 20 standard.  A parameter for determining the thermal efficiency and energy consumption of water heaters is the cold water temperature at the inlet to the storage water heater. The nominal ANSI standard temperature of the supply water entering the water heater is 70 F. The actual inlet water temperature in California varies with climate zone and season, so adjustment factors were created based on ground temperature data for each climate zone to account for varying water heater consumption due to inlet water temperature. More information regarding these adjustment factors are included in Section 2.02. The California Title 20 standard defines a minimum TE of 80% for the baseline large storage water heaters. The qualifying measure efficiencies for large storage water heaters are the following:

Minimum TE of 83% for Tier 1 (non-condensing) large storage water heaters.

Minimum TE of 90% for Tier 2 (condensing) large storage water heaters.

Baseline and Measure Efficiencies

- These measure efficiencies are adopted after consideration of the availability of high-efficiency storage water heaters listed in the California Energy Commission Energy Efficiency Appliance Database (CEC Database).  Figure 1 shows the distribution of thermal efficiencies for the 965 large non-condensing storage water heater products found in the CEC Database.  About 80% of the products are considered baseline while 20% of the products meet the minimum TE for Tier 1.  Figure 2 shows the distribution of thermal efficiencies for the 266 large condensing storage water heater products found in the CEC Database.   Over 90% of the products meet the minimum TE for Tier 2.

- Figure 1 - Distribution of Thermal Efficiencies for Non-condensing Large Storage Water Heaters in the CEC Appliance Efficiency Database

- Figure 2 - Distribution of Thermal Efficiencies for Condensing Large Storage Water Heaters in the CEC Appliance Efficiency Database

Market Applicability

- These measures are applicable to multifamily properties.  The large natural gas central water heaters must serve two or more dwelling units (households) to be eligible for incentives.

Terms & Conditions

The rebate applies to gas-for-gas equipment replacements on burnout (ROB) as well as new construction (NC).

Qualifying storage water heaters must have an input rate of at least 75 kBtuh and a storage tank size of at least 80 gallons.

Tankless water heaters or hot water boilers with a separate storage tank that are factory mounted on the same skid do not qualify as a storage water heater.

Storage water heaters used for space heating applications do not qualify.

Water heaters used for pools or spas do not qualify.

The manufacturer’s name and equipment model number must be provided.

If necessary, customer must provide proof of unit efficiency (e.g., manufacturer’s equipment specification sheet).

The equipment model must be listed on California Energy Commission Energy Efficiency Appliance Database (CEC Database) to qualify for the rebate.

Delivery Method

- The preferred delivery method is a downstream prescriptive rebate offered to the gas customer purchasing the storage water heater.  However, a midstream point-of-sale rebate or an upstream manufacturer rebate strategy may also be implemented.

DEER Differences Analysis

    - Baseline and Measure Efficiency

- Large storage water heaters for multifamily residential applications are not specified in the 2013 Database for Energy-Efficiency Resources (DEER2013) Update for 2014 Codes.  Table 1 lists the baseline and measure efficiencies for commercial storage water heaters found in the DEER2013.  This workpaper uses commercial storage water heaters because they are typically found in multifamily buildings. All of these storage water heaters have standby losses of 0.56% per hour.  Standby losses are expressed as a percentage of the energy stored in the hot water relative to the average ambient air temperature.  The minimum baseline DEER efficiencies listed in Table 1 were applied to the baseline large storage water heaters for multifamily residential applications.  The minimum qualifying DEER measure efficiencies listed in Table 1 were applied to the Tier 1 and Tier 2 large storage water heater measures for multifamily residential applications.

- Table 1 - Commercial Storage Water Heater Thermal Efficiencies in DEER2013

| Equipment Type | DEER Baseline | DEER Measure |
| --- | --- | --- |
| Commercial Storage Water Heater >75 kBtuh, Tier 1 (non-condensing), Readi ID: NG-WtrHt-LrgStrg-Gas-gte75kBtuh-0p83Et | 80% | 83% |
| Commercial Storage Water Heater >75 kBtuh, Tier 2 (condensing), Readi ID: NG-WtrHt-LrgStrg-Gas-gte75kBtuh-0p90Et | 80% | 90% |

Equipment Useful Life

- DEER2013 includes equipment useful life (EUL) values for water heaters. The EUL is 11 years for residential natural gas storage water heaters (WtrHt-SmlStrg-Gas-Res). The EUL is 15 years for large natural gas storage water heaters (WtrHt-LrgStrg-Gas). Because commercial storage water heaters are used as central storage water heaters in multifamily residential applications, the appropriate EUL for use in this workpaper is 15 years (see Section 1.04).

Net to Gross Ratio

- The DEER2013 values for net-to-gross (NTG) ratio are used in this workpaper (see Section 1.05).

Incremental Measure Cost

- The DEER2013 contains a measure for large storage water heaters with a TE of 82% and a baseline of 80%.  Although the baseline of 80% is the same, DEER does not contain cost data for large storage water heaters with a TE of 83% or 90% in the 2008, 2011, or 2013 databases. Since the efficiencies used here are different from those used for the DEER2013 database, the incremental measure costs found in DEER2013 do not apply.  Cost data were collected through 1) a survey of vendors that sell large storage water heaters in California and 2) SoCal Gas rebate applications for large storage water heater measures. The incremental measure costs used in this workpaper are based on the arithmetic average of the survey cost data per kBtuh for the baseline and measures covered by this workpaper.

Code Analysis

- The minimum baseline efficiency is consistent with the California Title 20 standard for large gas storage water heaters with less than 4,000 Btuh of rated input per gallon of measured storage volume.2  The minimum qualifying measure efficiencies exceed the California Title 20 standard for large gas storage water heaters with less than 4,000 Btuh of rated input per gallon of measured storage volume.2

Measure Effective Useful Life

- The effective useful life (EUL) of 15 years for central storage water heaters for multifamily residential applications is taken from the value for large storage water heaters for commercial applications in DEER2013.

Net-to-Gross Ratios for Different Program Strategies

- The DEER2013 documents recommend a net-to-gross ratio (NTGR) of 0.55 for “All other EEM with no evaluated NTGR; existing EEM with same delivery mechanism for more than 2 years”, which includes the Tier 1 storage water heaters covered under this workpaper.  The DEER2013 documents recommend a net-to-gross ratio (NTGR) of 0.70 for “All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years”, which includes the Tier 2 condensing storage water heaters covered under this workpaper.7

Gross Realization Rate

- Gross realization rate of 1.00 is applied to the measures in this document.

Time-of-Use Adjustment Factor

- N/A

Energy Savings & Demand Reduction Calculations

Load Shapes

- N/A

Energy Savings

- The energy savings estimates for measures in this workpaper were calculated for each CA climate zones as shown in Measure Summary Table.  The 16 California Energy Commission forecast climate zones are shown in Figure 3. These areas are grouped according to California Title 24 and “represent a geographic area for which an energy budget is established.” Title 24 also states,

- “The Energy Commission originally developed weather data for each climate zone by using unmodified (but error-screened) data for a representative city and weather year (representative months from various years). The Energy Commission analyzed weather data from weather stations selected for (1) reliability of data, (2) currency of data, (3) proximity to population centers, and (4) non-duplication of stations within a climate zone.”

- Figure 3 - California Energy Commission Forecast Climate Zones

Annual Electric Energy Savings

- No electric energy savings will result from this measure.

Electric Demand Reduction

- No electric demand reduction will result from this measure

Annual Gas Energy Savings

The annual water heater gas energy use for the 16 California Energy Commission are established by applying 16 adjustment factors to the state average storage water heater gas consumption for multifamily apartments/units from the 2009 California Residential Appliance Saturation Study (RASS).

The adjustment factors were developed using 2013 ground temperature data and the “Building America Multi-Family Central Water Heating Evaluation Tool” from the Department of Energy’s Office of Energy Efficiency and Renewable Energy to model the annual water heater gas consumption for the 16 climate zones. The annual consumption associated with each climate zone was then divided by the median of consumptions in all 16 climate zones to estimate the adjustment factor for each climate zone, which are presented in Figure 4. The adjustment factor calculations are included in an Excel file embedded as Attachment A.

- Figure 4 – Water Heater Gas Consumption Adjustment Factors for the California 16 Climate Zones

- The calculated adjustment factors are applied to the state average gas consumption for multi-family apartment unit from RASS to establish the baseline water heater gas consumption for the 16 climate zones.

- The following steps were then taken to derive the gas savings per unit of water heater capacity (kBtuh):

Determine average rated input of central storage water heater per dwelling unit along with average number of occupants per dwelling unit. These resources can be found in Attachment E.

Calculate gas savings per kBtuh rated input from the baseline thermal efficiency and the measure thermal efficiency.

For calculating energy savings, the following assumptions are used:

The average efficiency for the baseline products is a minimum TE of 80% based on California Title 20 code standard.

The average efficiencies for the qualifying products are: 1) a minimum TE of 83% for Tier 1 (non-condensing) large storage water heaters, 2) a minimum TE of 90% for Tier 2 (condensing) large storage water heaters.

With these assumptions, the energy saved by a high-efficiency measure storage water heater can be calculated as follows:

∆Q = Qb x (1 - Eb/Em)											Eqn-1

- where

∆Q – Gas Saved (therms/yr).  Savings which results from installing the high-efficiency measure equipment.

E – Efficiency (%).  Efficiency of equipment in appropriate efficiency units (thermal efficiency).

Subscript b = Baseline (or base case) equipment

Subscript m = Measure (new high-efficiency) equipment

The gas savings are calculated for each or climate zone.  The energy savings data and calculations are included in an Excel file embedded as Attachment B.

- The calculated gas consumption and savings per climate zone and tier are summarized in Table 2:

- Table 2 - Annual Gas Consumption and Savings by Tier and Climate Zone

| Climate Zone | Tier | Annual Gas Consumption per Apartment Unit (Therms/Yr/Dwelling Unit) | Annual Gas Savings (Therms/Yr/Dwelling Unit) | Annual GasSavings (Therms/Yr/ kBtuh) |
| --- | --- | --- | --- | --- |
| 1 | 1 | 196 | 7.1 | 1.09 |
| 2 | 1 | 189 | 6.8 | 1.05 |
| 3 | 1 | 189 | 6.8 | 1.05 |
| 4 | 1 | 186 | 6.7 | 1.03 |
| 5 | 1 | 190 | 6.9 | 1.06 |
| 6 | 1 | 183 | 6.6 | 1.02 |
| 7 | 1 | 182 | 6.6 | 1.01 |
| 8 | 1 | 181 | 6.5 | 1.01 |
| 9 | 1 | 181 | 6.5 | 1.01 |
| 10 | 1 | 181 | 6.5 | 1.00 |
| 11 | 1 | 182 | 6.6 | 1.01 |
| 12 | 1 | 185 | 6.7 | 1.03 |
| 13 | 1 | 181 | 6.5 | 1.01 |
| 14 | 1 | 183 | 6.6 | 1.02 |
| 15 | 1 | 168 | 6.1 | 0.93 |
| 16 | 1 | 195 | 7.1 | 1.09 |
| 1 | 2 | 196 | 21.7 | 3.34 |
| 2 | 2 | 189 | 21.0 | 3.22 |
| 3 | 2 | 189 | 21.0 | 3.23 |
| 4 | 2 | 186 | 20.7 | 3.18 |
| 5 | 2 | 190 | 21.1 | 3.25 |
| 6 | 2 | 183 | 20.4 | 3.13 |
| 7 | 2 | 182 | 20.3 | 3.12 |
| 8 | 2 | 181 | 20.1 | 3.09 |
| 9 | 2 | 181 | 20.1 | 3.09 |
| 10 | 2 | 181 | 20.1 | 3.09 |
| 11 | 2 | 182 | 20.2 | 3.11 |
| 12 | 2 | 185 | 20.5 | 3.15 |
| 13 | 2 | 181 | 20.1 | 3.09 |
| 14 | 2 | 183 | 20.3 | 3.12 |
| 15 | 2 | 168 | 18.6 | 2.87 |
| 16 | 2 | 195 | 21.7 | 3.34 |

The savings are also calculated for two sizes of central water heaters, smaller than or equal to 200,000 kBtuh and larger than 200,000 kBtuh. Based on the SoCal Gas rebate application data for central storage water heaters in multifamily buildings, the average capacity of water heaters smaller than or equal to 200,000 kBtuh is about 150,000 kBtuh and average capacity of water heaters larger than 200,000 kBtuh is about 265,000 kBtuh. These average sizes are multiplied by the Annual Gas Savings per kBtu (Therms/Yr/kBtuh) for each climate zone from Table 2 to estimate the gas savings per system for the 16 climate zones.  The annual gas savings per water heater system are summarized in Table 3:

- Table 3 – Annual Gas Savings per Water Heater System

| Climate Zone | Tier | Annual Gas Savings (Therm/Yr) per Water Heater System <= 200 kBtuh | Annual Gas Savings (Therm/Yr) per Water Heater System > 200 kBtuh |
| --- | --- | --- | --- |
| 1 | 1 | 163 | 288 |
| 2 | 1 | 157 | 278 |
| 3 | 1 | 157 | 279 |
| 4 | 1 | 155 | 274 |
| 5 | 1 | 159 | 281 |
| 6 | 1 | 153 | 270 |
| 7 | 1 | 152 | 269 |
| 8 | 1 | 151 | 267 |
| 9 | 1 | 151 | 267 |
| 10 | 1 | 150 | 266 |
| 11 | 1 | 152 | 268 |
| 12 | 1 | 154 | 272 |
| 13 | 1 | 151 | 267 |
| 14 | 1 | 152 | 269 |
| 15 | 1 | 140 | 247 |
| 16 | 1 | 163 | 288 |
| 1 | 2 | 501 | 887 |
| 2 | 2 | 483 | 855 |
| 3 | 2 | 484 | 856 |
| 4 | 2 | 476 | 843 |
| 5 | 2 | 487 | 863 |
| 6 | 2 | 470 | 831 |
| 7 | 2 | 467 | 827 |
| 8 | 2 | 464 | 821 |
| 9 | 2 | 463 | 820 |
| 10 | 2 | 463 | 819 |
| 11 | 2 | 466 | 825 |
| 12 | 2 | 473 | 837 |
| 13 | 2 | 463 | 820 |
| 14 | 2 | 468 | 828 |
| 15 | 2 | 430 | 761 |
| 16 | 2 | 500 | 886 |

Base Case & Measure Costs

Base Case Cost

- Cost data were collected through two following sources: a survey of vendors that sell storage water heaters in California for each of the categories of storage water heater type, rated input, and efficiency used in this workpaper and SoCal Gas rebate applications for large storage water heater measures for commercial applications.

- When the customer is replacing equipment on burnout (ROB) or buying new equipment (NC), the customer must buy a new storage water heater to continue operating, so the base case cost is that of a baseline (standard) storage water heater.  The cost data and calculations are included in an Excel file embedded as Attachment C.

Gross Measure Cost

- DEER2013 cost data are reported as the cost per storage water heater, not the cost per MBtuh.  Because the input rates are not provided in DEER cost data, cost/kBtuh cannot be calculated, and thus these DEER data are not used for determining the incremental measure cost.

- The results of a survey of equipment vendors that sell storage water heaters in California as well as the cost estimates from SoCal Gas rebate applications are included in the “database” tab of the embedded workbook as attachment C.  The table provides the cost per MBtuh.  The gross measure costs represent an arithmetic average of the equipment cost per kBtuh in each category.

Incremental Measure Cost

- The incremental measure cost (IMC) is the difference between the cost of the average baseline unit and the average high efficiency measure.  The incremental measure costs are shown in Table 4.

- Table 4 - Gross and Incremental Measure Cost by Equipment Type

| Equipment Type | Large Tier 1 | Large Tier 2 |
| --- | --- | --- |
| Rated Input (kBtuh) | > 75 | > 75 |
| 2012 Vendor Survey Data per kBtuh |  |  |
| Average Base Cost ($/kBtuh) | $22.37 | $22.37 |
| Average Gross Measure Cost ($/kBtuh) | $25.36 | $31.89 |
| Average Incremental Measure Cost ($/kBtuh) | $2.98 | $9.52 |

Attachments

Attachment A –Storage Water Heater Gas Consumption Modeling and Adjustment Factors Calculation

Attachment B – Storage Water Heater Energy Savings Calculations

Attachment C – Storage Water Heater Vendor Cost Data

Attachment D – Explanation of DOE Building America Multi-family Water Heater Tool (See Section 2.1.7 for Tool Methodology)

Attachment E – kBtuh per Dwelling Unit Derivation

References

Gas Water Heaters - Volume III, Storage Water Heaters With Input Ratings Above 75,000 Btu Per Hour, Circulating and Instantaneous, ANSI Z21.10.3-2011/CSA 4.3-2011 (Replaces ANSI Z21.10.3-1998) (http://webstore.ansi.org/RecordDetail.aspx?sku=ANSI+Z21.10.3-2011%2FCSA+4.3-2011).

California Code of Regulations, Title 20. Public Utilities and Energy, Division 2. State Energy Resources Conservation and Development Commission, California Energy Commission, CEC-140-2012-002, November 2012 (Accessed July 24, 2013 at http://www.energy.ca.gov/2012publications/CEC-140-2012-002/CEC-140-2012-002.pdf.

California Energy Commission Appliance Efficiency Database (Accessed March 7, 2012 at http://www.appliances.energy.ca.gov/AdvancedSearch.aspx).

California Energy Commission Appliance Efficiency Database (Accessed March 7, 2012 at http://www.appliances.energy.ca.gov/AdvancedSearch.aspx).

DEER2013 Database for Energy-Efficiency Resources, READI_v1.0.1, Updated for 2014 Codes (Accessed October 1, 2013 at http://www.deeresources.com/).

Technology and Measure Cost Data/Effective and Remaining Useful Life (EUL/RUL) Values, http://www.deeresources.com/index. “EUL_Summary_10-1-08.xls”

DEER2013 Net-To-Gross Ratios, http://www.deeresources.com, “READI v1.0.1”,

California Energy Commission Climate Zone Map, http://www.energy.ca.gov/maps/renewable/building_climate_zones.html.

2009 California Residential Appliance Saturation Study, by KEMA, Inc., for California Energy Commission, CEC‐ 200‐ 2010‐004‐ES, October 2010 (Accessed June 25, 2013 at http://websafe.kemainc.com/rass2009/Default.aspx).