Work Paper WPSCGREWH161128A

Revision 0

Southern California Gas Company

Recirculation Pump Control for Multifamily Residential

# At-a-Glance Summary

| Measure Codes | ShwFtc001 |
| --- | --- |
| Measure Description | Demand-controlled DHW recirculation pump in multifamily residential building. The measure includes pumps installed with variable frequency drives, integrated or remote sensors, and control systems that respond to hot water loop temperature. The energy savings are estimated using hot water loop temperature as a single-controlled variable. Water heater is natural gas storage with recovery efficiency = 80%. - Sector: Res - Use Category: SHW - Use Sub-Category: Liquid Circ - Tech Type: Flow TempCtrl |
| Base Case Description | Industry Standard - constant flow DHW recirculation pump, operates uncontrolled 24 hours per day. |
| Units | Pump savings are provided in kWh/dwelling unit Domestic hot water savings are provided in Therms/dwelling unit |
| Energy Savings | Values averaged for all California Building Climate Zone Areas - Pump Savings = 38.54 kWh/dwelling unit - Domestic Hot Water Savings = 13.54 Therms/dwelling unit Refer to Building Energy Model Results Attachment |
| Full Measure Cost ($/unit) | $108.33 per dwelling unit |
| Incremental Measure Cost ($/unit) | $108.33 per dwelling unit (same as full measure cost) |
| Effective Useful Life | 15 years (DEER EUL ID: Wtr-Ht-Timeclock) |
| Measure Installation Type | Retrofit Add-on (REA) |
| Net-to-Gross Ratio | 0.55 (DEER NTGR ID: Res-Default>2 years) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 12/2/16 | Travis Michalke, PE (ICF) | Original workpaper |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

Table of Contents

At-a-Glance Summary	2

Revision History	3

Commission Staff and Cal TF Comments	3

Section 1. General Measure & Baseline Data	5

1.1 Measure Description & Background	5

1.2 Technical Description	6

1.3 Installation Types and Delivery Mechanisms	8

1.4 Measure Parameters	9

1.4.1 DEER Data	9

1.4.2 Codes and Standards Analysis	12

1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information	15

1.5.1 VFD Hot Water Recirculation Pump Controller	15

1.5.2 On-Demand Pump Controller Workpaper	16

1.5.3 High Performance Circulator Pumps	16

1.5.4 Commercial Smart Hot Water Recirculators	17

1.5.5 AutoHot Demand Controller	17

1.6 Data Quality and Future Data Needs	18

Section 2. Calculation Methodology	19

Section 3. Load Shapes	29

Section 4. Costs	30

4.1 Base Case Cost	30

4.2 Measure Case Cost	30

4.3 Full and Incremental Measure Cost	30

Attachments	31

References	32

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This workpaper details the base case and energy efficiency measure case for an on-demand hot water recirculation pump in existing multifamily residential buildings. The base case is a centralized gas-fired domestic hot water system with a recirculation pump that operates continuously. The measure case is a retrofit add-on measure that replaces the base case pump with a pump that utilizes flow control methods (e.g. VFD, on/off control), which responds to demand by controlling the hot water recirculation loop temperature.

Annual energy measure savings are provided on a per-dwelling unit basis for pump (kWh) and hot water heating (Therms) for each of the 16 California Building Climate Zone Areas. Energy demand reduction is provided on a per-dwelling unit basis for pump power only. Whole-building energy savings have also been derived; they are included in the Building Energy Model Results attachment.

Table 1 and Table 2 provide summaries of the base case, measure case, and of the relevant DEER measures and their Source Descriptions as taken from DEER READI v.2.4.7.

Table 1 - Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Demand-controlled DHW recirculation pump in multifamily residential building. The measure includes pumps installed with variable frequency drives, integrated or remote sensors, and control systems that respond to hot water loop temperature. The energy savings are estimated using hot water loop temperature as a single-controlled variable. Water heater is natural gas storage with recovery efficiency = 80%. - Sector: Res - Use Category: SHW - Use Sub-Category: Liquid Circ - Tech Type: Flow TempCtrl |
| Existing Condition | N/A |
| Code/Standard | N/A |
| Industry Standard Practice | Constant flow DHW recirculation pump, operates uncontrolled 24 hours per day. |

Table 2 - Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
| ShwFtc001 | TBD | TBD | TBD | Demand-controlled DHW recirculation pump in multifamily residential building. The measure includes pumps installed with variable frequency drives, integrated or remote sensors, and control systems that respond to hot water loop temperature. The energy savings are estimated using hot water loop temperature as a single-controlled variable. Water heater is natural gas storage with recovery efficiency = 80%. - Sector: Res - Use Category: SHW - Use Sub-Category: Liquid Circ - Tech Type: Flow TempCtrl |

Eligibility requirements:

- The energy efficiency measure is applicable to existing multifamily residential buildings that have a centralized, gas-fired, domestic hot water system with constant volume, fractional horsepower, and an uncontrolled recirculation pump.

- This measure is only applicable to buildings with systems that utilize stand-alone domestic hot water systems. Hot water generation systems must be used primarily for domestic hot-water heating uses. Hot-water generation systems used for pool or spa heating are not eligible for this measure.

- The energy efficiency measure applies to all California Building Climate Zone Areas.

Other program restrictions and guidelines:

- The hot water supply and hot water return lines of the recirculation loop must maintain a temperature difference of at least 20°F.  For example, for the energy modeling purposes of this workpaper, the supply temperature was set at 135°F and the return temperature was maintained at 105°F.

## 1.2 Technical Description

This workpaper details an on-demand domestic hot water recirculation pump for multifamily residential buildings. The pump is integrated with flow control capabilities such as a variable frequency drive (VFD) controller or on/off controls. This technology controls the recirculating pump in order to provide a flow rate necessary to maintain a set-point recirculation loop temperature. Reducing system flow rate to meet demand reduces pumping power, heat loss in the recirculation loop, and boiler input gas consumption.

Figure 1 – Hot Water System and Corresponding Energy and Heat Transfer Flows

Figure 2 – Average Energy Flows in Central DHW Systems

The illustrations in Figure 1 and Figure 2 demonstrate the various paths in which the domestic hot water system loses energy to the surrounding environment. This measure reduces heat loss in the hot water recirculation loop and is directly affected by the loop characteristics such as hot water supply temperature, minimum desired loop temperature, indoor ambient temperature, as well as piping system characteristics and length.

Hot water recirculation loops are common in multifamily residential buildings with centralized, domestic hot water systems. Hot water demand in multifamily buildings varies throughout the day, with peaks occurring in the morning and evening hours, as illustrated in Figure 3. Demand also varies according building size, demographics, and the number and type of hot water fixtures. When the hot water demand is reduced during off-peak hours, heat in the hot water distribution system is lost to the surrounding space. This reduces the hot water supply temperature and availability of hot water at the fixtures.

Figure 3 – Domestic Hot Water Hourly Flow Profile

A recirculation loop increases the availability of fixture hot water by pumping hot water through the distribution system – albeit at the expense of additional pump energy consumption and increased distribution system heat losses. This measure then reduces the average hot water loop temperature while maintaining a minimum hot water loop temperature required to service connected fixtures.

The baseline case for this workpaper is a continuously operating and uncontrolled recirculation pump that operates on a 24-hour-per-day, 7-day-per-week schedule. It ensures hot water is always available at the fixture, irrespective of hot water loop temperature or system demand. The energy efficiency measure is an on-demand controlled pump that activates or adjust the performance of the hot water circulation pump when the return loop temperature sensor indicates a need for the pump to run in order to maintain delivered hot water temperature; this saves both pumping and water heating energy. The measure includes pumps installed with variable frequency drives, integrated or remote sensors, and control systems that respond to hot water loop temperature. The energy savings are estimated using hot water loop temperature as a single-controlled variable.

## 1.3 Installation Types and Delivery Mechanisms

The installation type for this energy efficiency measure, indicated in Table 3, is a Retrofit Add-on (REA). The measure replaces and upgrades the existing uncontrolled domestic hot water recirculation pump (before the end of its effective useful life) with an on-demand hot water recirculation pump that exceeds federal and state codes and industry standard practice.

Table 3 - Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

Applicable delivery types are described in Table 4.

Table 4 - Delivery Type Descriptions

| Incentive Method | Description |
| --- | --- |
| Direct Install (DirInstall) | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |
| Prescriptive Rebate (PreReb) | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

The energy efficiency measure detailed in this workpaper is not included in the Database of Energy Efficiency Resources (DEER) READI v2.4.7. There are two relevant DEER Technology Types, Flow Plus Temperature Control and Time Clock that are briefly discussed below.

DEER contains two similar Flow Plus Temperature Control measures (DemandCtl-WtrHt-Gas-44unitMFbldg and DemandCtl-WtrHt-Gas-88unitMFbldg), which were developed from the IOU workpaper WPSCGODE091116 Rev4. These measures are applicable for centralized gas-fired domestic hot water systems in multifamily residential buildings of 44 (low-rise) and 88 (high-rise) dwelling units. The primary similarities between these DEER measures and the measure case detailed in this workpaper include

- Base Case: They use a similar base case condition, which is defined as a multifamily residential building with a central gas-fired domestic hot water system, recirculation loop, and an uncontrolled pump that operates continuously. The Codes and Standards Enhancement Initiative (CASE) Multifamily Central DHW and Solar Water Heating study  is the basis for the baseline condition.

- Applicability: They are applicable to low and high-rise multifamily residential buildings in all of the California Building Climate Zone Areas.

- Water Heater: The recovery efficiency of a natural gas-fired storage tank type water heater is assumed to be 80% per recommendations from the CA Energy Division.

The primary differences between the DEER measures and the measure detailed in this workpaper include

- Pump Controller: The DEER measures use an on/off demand based pump controller that operates a constant flow pump about 2 hours per day. The pump controller is activated when temperature sensors indicate flow is required to maintain a minimum temperature in the hot water return loop. In contrast, the on-demand pump controller detailed in this workpaper expands upon the on/off technology to include variable frequency drives (VFDs) that further reduce hot water flow during periods of low demand, thereby reducing pumping power and hot water distribution system heat losses.

- Energy Calculation Methodology: Measure energy savings in DEER are described in the On-Demand Pump Control for Central Domestic Hot Water Systems workpaper. They were developed using the methodologies, research, and results from field measured data and assumptions outlined in the CASE study. In contrast, measure case energy savings detailed in this workpaper are developed by simulating prototypical DEER building energy models, which account for interactive affects between building systems in order to derive annual energy consumption by end use and whole building.

- Climate Zone Impacts: The measures detailed in this workpaper are sensitive to changes in ambient temperatures. Domestic hot water systems located in buildings in colder climate zones exhibit higher hot water heating consumption due to the increased temperature difference between indoor ambient and hot water loop temperatures.

DEER contains a second similar measure: Time Clock (D03-095 – Circulation Pump Timeclock Retrofit). This measure adds a time clock to the existing circulation pump, which provides on/off pump control based on building occupancy and meets the requirements of the California Building Energy Efficiency Standards. The measure within this workpaper, however, uses demand-based controls that control pump operation based on the hot water return loop temperature and exceeds California state code requirements. A summary of DEER differences is presented in Table 5.

Table 5 - DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | No |
| DEER Measure Case | No |
| DEER Building Types | No |
| DEER Operating Hours | No |
| DEER eQUEST Prototypes | Yes, DEER 2003 eQUEST Prototypes |
| DEER Version | DEER 2016, READI v2.4.7 |
| Reason for Deviation from DEER | DEER does not contain this type of measure. |
| DEER Measure IDs Used | N/A |

Net-to-Gross Ratio

The Net-to-Gross (NTG) Ratio value was obtained using the DEER READI tool, version v.2.4.7. Note that this measure technology type is not brand new and has been documented in workpaper form since 2009 with a similar on-demand pump control measure in DEER. The relevant NTG value for the measure in this workpaper is provided in Table 6 and applies to both electric (kWh) and natural gas (Therms) savings in all 16 California Building Climate Zone Areas. These values are consistent with the On-Demand Pump Control for Central Domestic Hot Water Systems workpaper.

Table 6 - Net-to-Gross Ratio

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| Res-Default>2 years | All other EEM with no evaluated NTGR; existing EEM with same delivery mechanism for more than 2 years | Res | Any | Any | 0.55 |

Note: Direct install measures that are not hard-to-reach will use the default NTG value.

Spillage Rate

Spillage rates are not tracked in workpapers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool, version v.2.4.7. The relevant IR values for the measures in this workpaper are in Table 7.

Table 7 – Installation Rate

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool, version v.2.4.7. The two similar on-demand hot water measures in DEER (DemandCtl-WtrHt-Gas-44unitMFbldg and DemandCtl-WtrHt-Gas-88unitMFbldg) were developed from the IOU workpaper WPSCGODE091116 Rev4 and use the WtrHt-Timeclock EUL/RUL ID, which corresponds to 15 and 5 years, respectively.

DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this workpaper are in Table 8.

Table 8 - Effective Useful Life

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| Wtr-Ht-Timeclock | Circulation Pump Timeclock Retrofit | Com | SHW | 15 | 5 |

### 1.4.2 Codes and Standards Analysis

There are no federal, state, or regional codes or standards that regulate domestic hot-water recirculation pumps in existing buildings. Recirculation systems are regulated by California’s Building Energy Efficiency Standards for both new construction and building alterations and therefore inform, but do not impact, this Retrofit Add-on (REA) measure. Table 9 outlines the codes and standards researched, and it is followed by a summary of the relevant code and its requirements.

Table 9 - Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | Building Energy Efficiency Standards | July 1, 2014 |
| Title 24 (2016) | Building Energy Efficiency Standards | January 1, 2017 |
| Title 20 (2015) | Appliance Efficiency Regulations | July 1, 2014 |
| DOE 10 CFR Part 430 | Federal Register | January 20, 2004 |

California’s Title 24 Building Energy Efficiency Standards (2013)

The California Building Energy Efficiency Standard provides mandatory, prescriptive and performance requirements for domestic hot water recirculation systems in newly constructed buildings, additions to existing buildings, and alterations to existing buildings. Both the mandatory and prescriptive sections are relevant for informing this measure; they include: automatic shut off pump controls, general system installation, pipe insulation requirements for all building types, and pipe insulation requirements and demand based controls for newly constructed low-rise residential buildings. These code requirements are summarized below:

- Section 110.3(c) 2, Page 92: This section requires domestic hot water systems with recirculation pumps in all building types have automatic shut off controls to turn off the service hot water system.

- Section 110.3(c) 5, Page 92-93: This section applies to all building types. It provides mandatory requirements for the installation of how water recirculation systems but does not address recirculation pump control.

- Section 120, Page 120: This section provides requirements for hot water pipe insulation in all building types. It requires service hot water systems above 105°F be insulated with a material meeting a minimum level of thermal conductivity, based on nominal pipe diameter. This section is relevant insomuch as assumptions used to develop prototypical hot water systems and corresponding building energy model inputs assume that hot water circulation loop is insulated. The insulating requirements and thermal conductivity values used in development of the measure case correspond to the requirements consistent with the DEER 2003 vintage.

- Section 150.0(j) 2.iii, Page 216: This section requires that all domestic hot water recirculation loop piping in low-rise residential buildings be insulated.

- Section 150.1(c) 8.C.ii, Page 232: This section prescribes, as a compliance approach, that domestic hot water systems in newly constructed low-rise residential buildings that serve multiple dwelling units have a recirculation loop with hot water demand control, similar to the energy efficiency measure detailed in this workpaper.

California’s Title 24 Building Energy Efficiency Standards (2016)

No material differences for hot water recirculation pump control requirements were identified between the 2013 and 2016 Building Energy Efficiency Standards.

Title 10 of Electronic Code of Federal Regulations

There are no federal regulations for hot water recirculation pumps.

California’s Title 20 Appliance Efficiency Regulations (2015)

The California appliance efficiency standards do not regulate hot water recirculation pumps.

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

Emerging technology reports, available vendor and manufacturer reports, and California workpapers were reviewed and assessed in development of this workpaper. The purpose was to understand the nuanced differences between each technology to assist in defining the energy efficiency measure(s) to be analyzed. Specifically, documents were reviewed for five manufacturers / technologies, which ranged from commercialized (where a workpaper has already been developed, or multiple manufacturers may be serving the market) to emerging technologies (that are commercially available but may not be as market-ready). These included

- VFD Hot Water Recirculation Pump Controller

- On-Demand Pump Controller Workpaper

- High Performance Circulator Pumps

- Commercial Smart Hot Water Recirculates

- AutoHot Demand Controller

Each technology was cataloged in seven categories for more than 30 operating characteristics (refer to the On-Demand Pump Controller Technology Comparison attachment). A summary of the key attributes are detailed in the sections below. This summary is limited to information that varies only between the technologies that may be most useful in highlighting key technological differences represented in this workpaper. The sections below provide an overview of the studies that influenced development of this workpaper. They are organized around on-demand pump controller technology and manufacturer.

### 1.5.1 VFD Hot Water Recirculation Pump Controller

- Tech Source 1 (power point): Southern California Gas Company, Engineering Analysis Center – Applied Technologies, VFD Controller for Fractional Horse-power Hot Water Recirculators, ET12SCG0003, November 2015.

- Tech Source 2 (emerging technologies report): Southern California Gas Company, Engineering Analysis Center – Applied Technologies, Appendix Project Test Report - Effects of Bi-Level Temperature Controller on Variable Frequency Drive Recirculation Pump Controller Performance, ET12SCG0003, October 2014.

- Tech Source 3 (emerging technologies report): Southern California Gas Company, Engineering Analysis Center – Applied Technologies, Project Test Report - Variable Frequency Drive Hot Water Recirculation Pump Controller, January 2014.

- Market Covered: Residential and Commercial; Multifamily, Apartments, Dormitory, Gym, Office Building, Hotel, Motel

- Timeframe: 10-week period during the summer time.

- Techniques used: On/off testing performed over 10-week period during the summer time when the ground water temperatures and Tmain are highest (about 75 °F). IPMVP Option B w/control volume around hot water heater, pump, and distribution system.

- Technology: VFD Controller for Fractional Horsepower Hot Water Recirculators - VFD pumps (using pulse with modulation technology) controlled by hot water recirculation loop return temperature.

- Relevance: This technology exceeds Title 24 requirements for hot water recirculation loops. It uses a variable frequency drive to reduce hot water loop recirculation based on return water temperature. Savings are achieved from reduction in pump power, but more specifically from reduction in average recirculation loop temperature.

- Concerns: Several potentially confounding results were identified or noted in the documents reviewed. These include increases in hot water consumption and large variances in savings increasing performance risk. This is an emerging technology and may be proprietary, limiting market availability and procurement.

### 1.5.2 On-Demand Pump Controller Workpaper

- Tech Source 1 (workpaper): Southern California Gas Company, Multifamily Domestic Hot Water Temperature Reset Controller, Workpaper SCGWP100315A, Revision 1, May 2014.

- Tech Source 2 (workpaper): Southern California Gas Company, On-Demand Pump Control for Central Domestic Hot Water Systems, Workpaper WPSCGODEO91116, Revision 4, December 2013.

- Tech Source 3 (workpaper disposition): California Public Utilities Commission, Energy Division, Workpaper Disposition for On-Demand Pump Control for Central Domestic Hot Water Systems, February 2013.

- Tech Source 4 (workpaper): Southern California Gas Company, On-Demand Pump Control for Central Domestic Hot Water Systems, Workpaper WPSCGODEO91116, Revision 3, January 2010.

- Market Covered: Residential and Commercial; Multifamily, Apartment, Condominium, Campus Housing

- Timeframe: N/A

- Techniques used: Demand control savings pump operational cycles were validated using field monitored data.

- Technology: Demand Control Recirculation Pump Gas Water Heater Low/High Rise Building - On/off pump controller reduces recirculation loop operation from continuous operation (24/7/365) to 2 hours per day.

- Relevance: This technology meets (but does not exceed) minimum Title 24 requirements for hot water recirculation loops using an on/off pump controller.

- Assessment: An existing workpaper already describes the deemed savings for this technology.

### 1.5.3 High Performance Circulator Pumps

- Tech Source 1 (power point): High Performance Circulator (HPC) Pumps, California Technical Forum, September 2016.

- Tech Source 2 (workpaper): High Performance Circulator (HPC) Pumps, California Technical Forum, Revision 1, September 2016.

- Tech Source 2 (power point): High Efficiency Pumping Systems, California Technical Forum, January 2016.

- Tech Source 3 (workpaper abstract): Workpaper Abstract - High Efficiency Pumping Systems, Revision 1, California Technical Forum, September 2016.

- Market Covered: Residential; Single Family, All

- Timeframe: N/A

- Techniques Used: References and comparisons with work performed by EPRI. Pumps tested under identical operating conditions to EPRI tests. Power meter used to collect system performance data. Savings calculated based on difference in results in power meter.

- Technology: On-Demand High Performance Circulator (HPC) - Pumps include electrically communicated motors (ECM) with integrated variable frequency drives (VFD) with on board pump controlling logic with self-optimizing programming allowing the pump to operate at the most efficient point on the pump curve.

- Relevance: This technology appears to exceed the minimum Title 24 requirements for hot water recirculation loops. It uses prepacked and integrated controls with VFD and optimization algorithms.

- Assessment: The workpaper is focused on market and potential for residential single family homes, however it may also be applicable to the commercial sector.

### 1.5.4 Commercial Smart Hot Water Recirculators

- Tech Source 1 (market analysis power point slide): N/A.

- Market Covered: Commercial

- Timeframe: N/A

- Techniques used: N/A

- Technology: Smart HW Recirculators - Smart pumps prepackaged with controls to save gas and electricity using a high efficiency motor and pump with sensor wiring points and system performance visualization screens to optimize pump speed according to the intersect of system curve and pump performance curve.  Uses remotely controlled and interfaces with building automation system. Saves gas by reducing overall chilled/hot water waste over single speed or uncontrolled

- Relevance: This technology exceeds the minimum Title 24 requirements for hot water recirculation loops. It uses a smart controller that includes VFD and optimization algorithms, which are integrated into the hot water circulation pump.

- Assessment: The technology is similar and maybe identical to the High Performance Circulator Pumps but is focused on the commercial sector. The innovative technology has application beyond hot water systems and recirculation loops. The low cost to install and potential savings are likely to make result in favorable economics and good market potential. Although an emerging technology, there are several companies that manufacture similar technologies.

### 1.5.5 AutoHot Demand Controller

- Tech Source 1 (manufacturer spec sheet): AutoHot Submittal | Specifications.

- Tech Source 2 (manufacturer brochure): AutoHot Demand Controlled Circulation for Central Domestic Hot Water.

- Tech Source 3 (manufacturer proposal): EGI Monitoring Protocol, 2016

- Market Covered: Residential; Campus Housing

- Timeframe: N/A

- Techniques used: Proposed techniques include two weeks of field data collection

- Technology: On-demand pump that is controlled on both return loop water temperature set point and hot water demand. Pump is de-energized when return loop water temperature is above set point regardless of hot water demand. Pump is energized when both the hot water temperature is below set point and there is a demand for hot water.

- Relevance: This technology exceeds the minimum Title 24 requirements for hot water recirculation loops.

- Assessment: The technology is relevant to domestic hot water systems in multifamily residential buildings. Using the two controlled variables (flow and temperature) may reduce energy consumption when compared to existing DEER measures and current code mandatory requirements.

## 1.6 Data Quality and Future Data Needs

The various emerging technology reports and studies assessed in development of this workpaper did not measure energy savings performance over a full year. Generally, energy savings estimates have been developed over a shorter time frame, with data being extrapolated to estimate annual savings. Furthermore, none of the studies reviewed detailed savings in each of the California Building Code Zone Areas. Because hot water system performance is affected by ambient temperatures, future studies may look to test over longer durations and consider performing multiple demonstrations that include a greater number of climate zones.

# Section 2. Calculation Methodology

Energy efficiency measure savings were developed through a combination of research, engineering calculations, and building energy models. The approach used to develop the deemed savings estimates in this workpaper is described below.

Base and Measure Case Underlying Parameters

The measure case is based on an analysis that made use of the prototypical DEER 2003 vintage building models to represent an average cross section of the existing building stock to which this measure may apply.

The multifamily buildings in these models consist of 4 residential stories with 24 dwelling units, all of which have the same hot water fixture make-up and demand.

Measure savings were developed by simulating a single building per climate zone. Savings may be extrapolated to larger and smaller cohorts of high-rise and low-rise multifamily residential buildings, but no range of acceptable sizes that deviate from the base case model has been quantified. Variances in building floor area, number of dwelling units, configuration of hot water fixtures, and hot water piping loop characteristics are some of the site-specific factors that may substantially affect energy consumption. Savings, for example, may not scale linearly with building floor area or number of dwelling units as documented in the CASE study, and they may therefore produce variations between deemed savings and actual results.

The base case and measure case recirculation loop is located exclusively within the building envelope’s conditioned space, consistent with the On-Demand Pump Control for Central Domestic Hot Water Systems workpaper. Placement of the recirculation loop will affect energy performance and interactive effects with other building end uses, including space heating and space cooling systems.

The measure case hot water heater supply temperature and the recirculation loop return temperature are set to 135°F and 105°F, respectively. These temperatures were derived by researching a combination of existing workpapers, codes and standards documents, and industry standards. The temperatures drive the hot water heating recirculation loop heat losses, energy consumption, and amount of energy savings potential.

Define Baseline Performance

Secondary literature research was performed to define an industry standard baseline condition for domestic hot water recirculation pump control in multifamily residential buildings. The purpose was to understand what opportunity may exist for energy savings through the installation of enhanced system controls that reduce both pumping energy and hot water recirculation loop heat loss. Domestic hot water studies, codes and standards reports, and existing utility program deemed savings workpapers were reviewed to identify what system control schemes have been documented through field testing, survey data, and empirical studies.

A majority of resources referred back to the Public Interest Energy Research (PIER) Program Study as their primary data source. These include the CASE Study and various emerging technology reports and multifamily deemed savings workpapers documented and referenced in Section 1.5. These studies consistently defined the baseline condition as a hot water recirculation system with an uncontrolled, constant-speed pump that operates continuously (with a flat load curve).

This baseline was compared with the Database of Energy Efficiency Resources (DEER) and California Building Energy Efficiency Standard to understand the relative opportunity for energy savings. DEER contains two similar measures for central gas-fired hot water system in multifamily residential buildings. These measures use an on/off demand based control scheme and were developed as an outcome of the PIER Study and subsequent workpapers, and use the same baseline operating condition. The California Building Energy Efficiency Standard regulates domestic hot water systems for new construction and existing building alteration and does not apply to this building retrofit measure; however, relevant mandatory and prescriptive requirements inform the minimum level of measure efficiency. The energy code provides general installation requirements for domestic hot water recirculation loops. It requires that they be insulated, have automatic system shut off controls and prescribes demand controls that respond to the recirculation loop temperature in newly constructed low-rise residential buildings. These requirements are detailed in Section 1.4.2.

Based on research of available studies, the base case for this workpaper is defined as a multifamily residential building with a central gas-fired hot water recirculation system that consists of an uncontrolled, constant-speed, fractional horsepower pump that operates continuously. Furthermore, a compliant system is limited to servicing only domestic hot water uses and excludes process hot water loads.

Define Energy Efficiency Measure

Secondary research was conducted to define the energy efficiency measure and its parameters. Studies of on-demand pump/controller emerging technology and equipment manufacturer studies and reports were reviewed, documented, and cataloged for comparison. Section 1.5 provides a summary of these reports. An analysis of the technologies, including their controls, characteristics, performance, and data availability and quality are detailed in the On-Demand Pump Controller Technology Comparison attachment.

The comparison included a review of five similar hot water on-demand control pump technologies from multiple manufacturers, four of which exceed both the established baseline condition and mandatory code requirements. All technologies are capable of providing hot water flow modulation through on/off demand controls, variable frequency drive (VFD) or electrically communicated motor (ECM) technology; however, there are discrete, yet discernable, differences in how each technology is controlled. The technologies can generally be grouped into two categories: those that have stand-alone VFD and temperature controls and control hot water flow to maintain a minimum return loop temperature, and those that have an integrated on/off or VFD controls that respond to return loop temperature and/or hot water use or demand.

Although there are nuanced variations in how the technologies are installed and how their control schemes are configured, this workpaper covers them as a single energy efficiency measure where hot water flow is modulated based on the return loop temperature.

Define Measurement and Verification Control Volume

After defining the baseline case and energy efficiency measure, a control volume was developed to understand the influences of heat transfer between the domestic hot water system, building environment, and interactive effects with other building systems. A representative diagram of the control volumes that includes the domestic hot water heater, recirculation loop, and pump is illustrated in Figure 4. The control volume defines the environment for how heat transfer and energy consumption is defined in the analysis and is the basis for developing ad hoc engineering analyses and building energy models.

Figure 4 – Schematic of Central Domestic Hot Water System

Develop Building Energy Models and Hot Water System Characteristics

The results of this workpaper made use of the DEER prototypical multifamily residential building energy models whose renderings are illustrated in Figure 5. Modifications to these models were necessary to describe the central domestic hot water system and define its various systems characteristics. Ad hoc engineering analyses were required to define values for unspecified parameters.

Figure 5 - DEER Prototypical Multifamily Building Model in eQUEST

Measure Analysis Software (MASControl2) was used to generate multifamily model input files compatible with eQUEST. The prototypical multifamily model domestic hot water system consisted of individual hot water heaters for each dwelling unit. These systems were removed and replaced with a centralized domestic hot water system with a recirculation loop and pump. The hot water fixture descriptions and schedules, however, were retained and used in this analysis to develop hot water demand profiles. Ad hoc engineering analyses were performed to define values for several pertinent system parameters, including piping loop heat loss coefficients, return loop minimum water flow rate, and pump horsepower. System inputs used to develop these factors and the corresponding outputs are detailed in Table 10 and included in the DHW System Characteristics attachment. The inputs were developed from data obtained from the translated eQUEST files, code and standard studies, and assumptions from industry standards, such as the American Society of Heating and Refrigeration Engineers (ASHRAE) Handbooks.

In general, the analysis indicated that the hot water recirculation loop flow and head pressure requirements were outside the operating range of traditional hot water recirculation pump curves. In cases where this occurred, the pump was upsized to the lowest available fractional horsepower size. This is consistent with our understanding of the CASE Study, where the recirculation system pumps are sized larger than flow rate requirements.

Table 10 - Domestic Hot Water System Characteristics

| System Parameters |  | Value | Sources |
| --- | --- | --- | --- |
| Building Characteristics | Gross Floor Area (ft2) | 29,000 | eQUEST building energy model |
|  | Number of Floors | 4 | eQUEST building energy model |
|  | Floor to Ceiling Height | 10 | CASE Study for multifamily buildings |
|  | Number of Units | 24 | eQUEST building energy model |
| Required Hot Water System Inputs | DEER Vintage | 2003 |  |
|  | Number of Hot Water Loops | 1 | eQUEST building energy model |
|  | Hot Water Flow Rate (GPM) | 22.00 | eQUEST building energy model |
|  | Supply Pipe Length (ft) | 334 | CASE Study for multifamily buildings |
|  | Supply Pipe Water Velocity (FPS) | 4 | ASHRAE |
|  | Hot Water Supply Pipe | Steel Pipe | ASHRAE |
|  | Hot Water Supply Temp | 135 | ASHRAE |
|  | Return Pipe Water Velocity (FPS) | 2 |  |
|  | Hot Water Return Pipe | Copper Pipe |  |
|  | Hot Water Return Temp | 105 | ASHRAE |
|  | Pipe Insulation Type | Cellular Glass | ASHRAE |
|  | Ambient Air Temp | 70 |  |
| Outputs (calculated) | UA (btu/hr-ft-F) - Supply pipe | 0.4064 | ASHRAE Handbook - HVAC Systems and Equipment |
|  | UA (btu/hr-ft-F) - Return pipe | 0.1340 | ASHRAE Handbook - HVAC Systems and Equipment |
|  | Estimated Total Pump Head (ft) | 10.9 |  |
|  | Pump Size (HP) | 1/6 |  |

A select number of building energy models were simulated to assess annual hot water energy consumption sensitivity to building age and construction, using the 11 DEER building vintages. The objective was to determine whether a single DEER vintage would be sufficient to describe the energy efficiency measure for a population of existing buildings. The analysis yielded less than a 5% variation in domestic hot water consumption across all DEER vintages, suggesting that the domestic hot water systems were not inherently sensitive to building characteristics described in the vintage models. As a result, DEER 2003 was selected as a single vintage for developing energy savings.

A sensitivity analysis was also conducted on the recirculation loop heat loss coefficients. The analysis showed that larger UA values produce higher hot water recirculation loop energy consumption and that those results are materially dependent on piping loop characteristics.

Outputs from the analysis were compared to the input references to corroborate the integrity of these assumptions. Piping heat loss coefficients for example, were developed by adjusting relevant inputs to correspond to parameter values in the ASHRAE tables. The factors were then simulated over a range of hot water flow rates and pipe insulation thermal conductivity values to estimate their mean values and as well as probability distribution (illustrated in Figure 6 and Figure 7) for both the recirculation loop supply and return piping. The mean values were then compared to the ASHRAE tables in Figure 8 for an order of magnitude comparison.

Figure 6 – Probability for Hot Water Supply Pipe UA Factor

Figure 7 – Probability for Hot Water Return Pipe UA Factor

Figure 8 – Piping Heat Loss Coefficient Tables from ASHRAE Handbook

A limited number of building energy models were then simulated to derive preliminary estimates of energy savings. These estimates were compared with the CASE study low- and high-rise multifamily building savings estimates in Figure 9 to corroborate the integrity of the building energy models. These initial estimates generated results similar to the low-rise case in Figure 9.

Figure 9 - Domestic Hot Water Energy Savings from CASE Study

After the building model’s integrity had been validated, the engineering calculations were readjusted by resetting the input factors in Table 10 back to the conditions specific for this analysis. The purpose of this analysis was to confirm that the engineering assumptions and calculations were reasonable when compared to industry standards and empirical studies.

It is notable that in Figure 9, there is a significant variance in energy savings (on a unit basis) between the low- and high-rise buildings. This is probably a result of the non-linear relationship between the hot water distribution piping length to either building floor area or number of dwelling units. That is, the hot water distribution piping length varies by building type, size, and architectural and engineering design factors and has a significant impact on the total hot water system consumption and available energy savings. The amount of heat loss in the distribution system is proportional to the piping length, piping heat loss coefficients, and difference between the indoor ambient and hot water temperatures. These factors are influenced by location of the recirculation loop, pipe material, size, insulation, and hot water demand. In addition, these factors underscore the importance of validating the assumptions—an understanding that variations from the validated assumptions may have a material impact on energy savings.

Develop Energy Savings and Demand Reduction Estimates

The building energy models described above were simulated in each of the 16 California Building Climate Zone Areas using representative location weather files. They were simulated for both the base case and measure case scenarios using eQUEST. The base case was developed by modifying the baseline case domestic hot water circulation loop properties and pump characteristics in eQUEST. They were then further modified to represent a VFD variation of the measure case described preceding sections. The recirculation loop hot water flow and minimum flow ratios were adjusted and the recirculation loop pump was changed from a standard motor class with one speed pump capacity control to a premium pump operating with a variable speed drive. The base case and measure case models were then simulated to produce estimates of energy consumption. Energy savings were then calculated as the difference in domestic hot water and pump energy consumption between these cases.

Results of the simulations can be found in the Building Energy Model Results attachment. Simulated outputs were processed to derive annual natural gas and electricity savings for whole-building, domestic hot water and pump end uses. Figure 10 illustrates the aggregate domestic hot water energy consumption for both the base case and efficiency measure case, for each of the 16 climate areas.

Figure 10 – Baseline and Measure Domestic Hot Water Consumption, by Climate Zone

Figure 11 and Figure 12 illustrate the recirculation pump (electricity) and hot water system (natural gas) savings across these same climate areas on a per dwelling unit basis, exhibiting similar trends to one another. Domestic hot water savings are inversely proportional to the system demand schedule. That is, the greatest energy savings are realized during periods of lowest system demand; although energy is saved over the entire annual load profile. Similarly, recirculation pump consumption is inversely proportional to the hot water demand schedule. Greater requirements for pump operation occur during periods of lower hot water system demand, with energy savings approximately constant over the annual load profile.

Figure 11 – Recirculation Pump Savings, by Climate Zone

Figure 12 – Domestic Hot Water System Savings, by Climate Zone

The figures above illustrate that domestic hot water system energy consumption varies by climate zone. Figure 13 on the other hand, illustrates that hot water savings in the measure case impacts the energy consumption and performance of other building end uses. Specifically, space heating consumption increases while space cooling consumption decreases, due to reduction of heat loss from the domestic hot water recirculation loop, as whole building energy consumption decreases.

Figure 13 – End Use Energy Consumption, All Fuels, All Climate Zones

In Figure 13 it can be observed that the circulation pump’s total energy consumption is small, while Figure 14 shows that the relative pump energy savings is large. This is in contrast to domestic hot water, which consumes more total energy (Figure 13) but smaller percentage of savings (Figure 14). A detailed review of the pump savings load shape shows a small variation in the amount of savings across climate zones and over the annual load profile.

Figure 14 – End Use Energy Savings, All Fuels, All Climate Zones

Develop Energy Demand Reduction Estimates

Demand energy savings were developed from an analysis of the Pump & Aux. end use electric load shapes, which were derived from simulation of building energy models. They are presented in Table 11. The measure case load shape was subtracted from the base case load shape during each of the stipulated peak demand time intervals. The table below represents that demand reduction for a 1-hour period during the 3-Weekday Period from 2:00 PM to 5:00 PM. In general, there is a small variance in the amount of demand savings that occurs by time of year, climate zone, or during the peak demand periods. The measure case produces savings for every hour of the year by reducing pumping power requirements compared to the base case recirculation pumps that run continuously with no control.

Table 11 - Energy Demand Reduction Estimates

| Climate Zone | 3-Weekday Period | Demand Savings |
| --- | --- | --- |
| 1 | Sep 16 – Sep 18 | 0.1151 |
| 2 | July 8 – July 10 | 0.1158 |
| 3 | July 8 – July 10 | 0.1161 |
| 4 | Sep 1 – Sep 3 | 0.1162 |
| 5 | Sep 8 – Sep 10 | 0.1162 |
| 6 | Sep 1 – Sep 3 | 0.1170 |
| 7 | Sep 1 – Sep 3 | 0.1173 |
| 8 | Sep 1 – Sep 3 | 0.1171 |
| 9 | Sep 1 – Sep 3 | 0.1169 |
| 10 | Sep 1 – Sep 3 | 0.1168 |
| 11 | July 8 – July 10 | 0.1159 |
| 12 | July 8 – July 10 | 0.1157 |
| 13 | July 8 – July 10 | 0.1158 |
| 14 | Aug 26 – Aug 28 | 0.1157 |
| 15 | Aug 25 – Aug 27 | 0.1172 |
| 16 | July 8 – July 10 | 0.1138 |

# Section 3. Load Shapes

Simulations of building energy models were used to develop load shapes for the base case and measure case. The load shape for net benefits estimates is the difference between these two cases. An example load shape (aggregated by month) for electric and natural gas is presented in Table 12 for California Building Climate Zone Area 11. Load shapes for the remainder of the California Building Climate Zone Areas are included in the attached Building Energy Model Results file. They were developed using demand based scaling factors and they produced identical load shapes for each of the 16 California Building Climate Zone Areas. The load shapes may be readily produced for each hour of the year and were only aggregated by month for illustration in this workpaper.

Table 12 – Electric Load Shapes

| Month | Electric Load Shape | Natural Gas Load Shape |
| --- | --- | --- |
| January | 8.2028% | 8.0745% |
| February | 7.5963% | 7.4136% |
| March | 8.4487% | 8.1872% |
| April | 8.2163% | 7.9872% |
| May | 8.5917% | 8.3963% |
| June | 8.3260% | 8.3625% |
| July | 8.6035% | 8.7872% |
| August | 8.6035% | 8.9266% |
| September | 8.3260% | 8.6529% |
| October | 8.6035% | 8.7325% |
| November | 8.1885% | 8.1952% |
| December | 8.2933% | 8.2843% |
| Total | 100% | 100% |

# Section 4. Costs

## 4.1 Base Case Cost

The base case domestic hot water recirculation system includes an uncontrolled, constant speed, fractional horsepower pump. Because this is a retrofit measure there is no base case cost and measure costs are evaluated as full costs (rather than incremental costs) according to the Ex Ante Measure Cost Study Research Plan.

## 4.2 Measure Case Cost

Implementation of the on-demand domestic hot water recirculation pump controller requires removal of the base case pump and the installation of a new recirculation pump with VFD and controllers. Table 13, which was extracted from the Variable Frequency Drive Hot Water Recirculation Pump Controller study prepared by SCG’s Engineering Analysis Center, provides a full measure cost estimate of $2,600 (per system), including materials and labor.

Table 13 - Measure Costs

| VFD Controller Cost | VFD Enabled Pump Cost | Installation Costs | Total System Costs |
| --- | --- | --- | --- |
| $ 1,800 | $ 300 | $ 500 | $ 2,600 |

## 4.3 Full and Incremental Measure Cost

Measure cost equations and values are provided in Table 14 and Table 15, respectively. The system costs are normalized by 24 dwelling units to obtain the per dwelling unit cost.

Table 14 - Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Table 15 - Full and Incremental Costs

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| REA | $2,100 + $500 = $2,600 per system or $87.50 + $20.83 = $108.33 per dwelling unit | $2,600 per system or $108.33 per dwelling unit | N/A |

# Attachments

- WPSCGREWH161128A — Technology Comparison – this file provides a summary of the various on demand pump controller technologies analyzed in development of this energy efficiency measure workpaper and is discussed in Section 1.5. This file catalogs detailed characteristics obtained from emerging technology reports, existing relevant workpapers, and manufacturer literature for each of the technologies.

- WPSCGREWH161128A — DHW System Characteristics – this file contains engineering calculations that describe the heat transfer and fluid flow characteristics for the prototypical hot water distribution system. These parameters were quality checked against standard ASHRAE values and assumptions used in the CASE study and then used as explicit inputs in the eQUEST building energy models. Included in the file are citing and sources for the various engineering formulas used.

- WPSCGREWH161128A — DEER Data – this file includes measure data extracted from the DEER READI tool and includes previous IOU workpaper data from WPSCGODE091116. It includes energy impacts from similar DEER measures and efficiency measure parameters, including EUL/RUL and NTG, discussed in Section 1.4.1 of this workpaper. Records and data fields relevant to this workpaper are filtered and/or highlighted.

- WPSCGREWH161128A — Building Energy Model Results – this file includes a summary of outputs from the building energy model simulations that underpin the energy efficiency measure savings documented in this workpaper.

# References

California Energy Commission, California Energy Maps, California Building Climate Zone Areas, Found at: http://www.energy.ca.gov/maps/renewable/building_climate_zones.html

Southern California Gas Company, Engineering Analysis Center – Applied Technologies, Project Test Report - Variable Frequency Drive Hot Water Recirculation Pump Controller, January 2014, page 31-34.

Public Interest Energy Research (PIER) Program, Multifamily Central Domestic Hot Water Distribution Systems – Final Project Report, CEC-500-2013-011, June 2013, Page 21. Found at: http://www.energy.ca.gov/2013publications/CEC-500-2013-011/CEC-500-2013-011.pdf

Public Interest Energy Research (PIER) Program, Multifamily Central Domestic Hot Water Distribution Systems – Final Project Report, CEC-500-2013-011, June 2013, Page 2. Found at: http://www.energy.ca.gov/2013publications/CEC-500-2013-011/CEC-500-2013-011.pdf

American Society of Heating, Refrigeration, and Air Conditioning Engineers, 2007 ASHRAE Handbook – HVAC Applications, Figure 24, pg. 49.20.

California Public Utilities Commission, Database of Energy Efficiency Resources (DEER) Updates, DEER2016 and Uncertain Measure Updates, Found at: http://www.cpuc.ca.gov/General.aspx?id=2017

California Utilities Statewide Codes and Standards Team, Codes and Standards Enhancement Initiative (CASE), Measure Information Template – Multifamily Central DHW and Solar Water Heating, 2013 California Building Energy Efficiency Standards, September 2011. Found at: http://www.energy.ca.gov/title24/2013standards/prerulemaking/documents/current/Reports/Residential/Water_Heating/2013_CASE_R_MF_DHW_and_Solar_Water_Heating_Oct_2011.pdf

Southern California Gas Company, On-Demand Pump Control for Central Domestic Hot Water Systems, Workpaper WPSCGODE091116, Revision 4.

Southern California Gas Company, On-Demand Pump Control for Central Domestic Hot Water Systems, Workpaper WPSCGODE091116, Revision 4.

California Utilities Statewide Codes and Standards Team, Codes and Standards Enhancement Initiative (CASE) - Multifamily Central DHW and Solar Water Heating – 2013 California Building Energy Efficiency Standards, September 2011.

Southern California Gas Company, On-Demand Pump Control for Central Domestic Hot Water Systems, Workpaper WPSCGODEO91116, Revision 4, December 2013.

California Energy Commission (CEC), 2013 Building Energy Efficiency Standards for Residential and Nonresidential Buildings – Title 24, Part 6 and Associated Administrative Regulations in Part 1, CEC-400-2012-004-CMF-REV2,  May 2012.  Found at: http://www.energy.ca.gov/title24/2013standards/

California Energy Commission (CEC), 2016 Building Energy Efficiency Standards for Residential and Nonresidential Buildings – For the 2016 Building Energy Efficiency Standards - Title 24, Part 6 and Associated Administrative Regulations in Part 1, CEC-400-2015-037-CMF,  June 2015. Found at: http://www.energy.ca.gov/title24/2016standards/

California Energy Commission (CEC), 2015 Appliance Efficiency Regulations, CEC-400-2015-021, July 2015. Found at: http://www.energy.ca.gov/appliances/

U.S. Department of Energy, Federal Register, Part III, 10 CFR Part 430 Energy Conservation Program: Energy Conservation Standards for Residential Water Heaters, Direct Heating Equipment, and Pool Heaters; Final Rule, April 16, 2010. Found at: https://www1.eere.energy.gov/buildings/appliance_standards/standards.aspx?productid=48&action=viewlive

California Utilities Statewide Codes and Standards Team, Codes and Standards Enhancement Initiative (CASE), Measure Information Template – Multifamily Central DHW and Solar Water Heating, 2013 California Building Energy Efficiency Standards, September 2011. Found at: http://www.energy.ca.gov/title24/2013standards/prerulemaking/documents/current/Reports/Residential/Water_Heating/2013_CASE_R_MF_DHW_and_Solar_Water_Heating_Oct_2011.pdf

Southern California Gas Company, On-Demand Pump Control for Central Domestic Hot Water Systems, Workpaper WPSCGODEO91116, Revision 4, December 2013.

Public Interest Energy Research (PIER) Program, Multifamily Central Domestic Hot Water Distribution Systems – Final Project Report, CEC-500-2013-011, June 2013. Found at: http://www.energy.ca.gov/2013publications/CEC-500-2013-011/CEC-500-2013-011.pdf

California Utilities Statewide Codes and Standards Team, Codes and Standards Enhancement Initiative (CASE), Measure Information Template – Multifamily Central DHW and Solar Water Heating, 2013 California Building Energy Efficiency Standards, September 2011. Found at: http://www.energy.ca.gov/title24/2013standards/prerulemaking/documents/current/Reports/Residential/Water_Heating/2013_CASE_R_MF_DHW_and_Solar_Water_Heating_Oct_2011.pdf

Public Interest Energy Research (PIER) Program, Multifamily Central Domestic Hot Water Distribution Systems – Final Project Report, CEC-500-2013-011, June 2013. Found at: http://www.energy.ca.gov/2013publications/CEC-500-2013-011/CEC-500-2013-011.pdf

California Utilities Statewide Codes and Standards Team, Codes and Standards Enhancement Initiative (CASE), Measure Information Template – Multifamily Central DHW and Solar Water Heating, 2013 California Building Energy Efficiency Standards, September 2011. Found at: http://www.energy.ca.gov/title24/2013standards/prerulemaking/documents/current/Reports/Residential/Water_Heating/2013_CASE_R_MF_DHW_and_Solar_Water_Heating_Oct_2011.pdf

Itron, Inc., Ex Ante Measure Cost Study Research Plan, Final, January 31, 2012. Found at: http://www.energydataweb.com/cpucFiles/56/WO017MeasureCostStudyResearchPlan_1.pdf

Southern California Gas Company, Engineering Analysis Center – Applied Technologies, Project Test Report - Variable Frequency Drive Hot Water Recirculation Pump Controller, January 2014, page 21.