## SummaryResults
Climate Zone | Boiler Gas Usage [therms/unit/yr] |  |  |  | Pumping Electric Usage [kWh/unit/yr] |  |  |  | Total Cost Savings [$/unit/ yr]
| Baseline | Proposed | Savings | Savings [%] | Baseline | Proposed | Savings | Savings [%]
6 | 303.5713 | 290.8912 | 12.6801 | 4.177% | 380.3244 | 379.8614 | 0.46296 | 0.1217% | 12.819
9 | 292.3844 | 278.2269 | 14.1574 | 4.842% | 379.8614 | 379.167 | 0.69445 | 0.1828% | 14.3658
16 | 521.0444 | 513.0651 | 7.9794 | 1.531% | 483.5652 | 483.3337 | 0.23148 | 0.04787% | 8.0488
[10 empty] | Climate Zone | Item | Baseline Gas Usage |  | Proposed Gas Usage |  | Gas Savings
[10 empty] | climate zone | end use | therms/ unit/yr | Percent of Demand | therms/ unit/yr | Percent of Demand | therms/ unit/yr | Percent
[10 empty] | 6 | Domestic Hot Water | 106.0623 | 33.25% | 106.0623 | 34.63% | 0
[11 empty] | Heating Hot Water | 51.2437 | 16.06% | 51.2437 | 16.73% | 0
[11 empty] | Tank Heat Loss | 5.155 | 1.616% | 4.7501 | 1.551% | 0.40489
[11 empty] | Pipe heat loss | 156.0913 | 48.93% | 143.8556 | 46.97% | 12.2357
[11 empty] | Uncategorized | 0.43452 | 0.1362% | 0.37527 | 0.1225% | 0.059253
[11 empty] | Subtotal | 318.9868 | 100% | 306.287 | 100% | 12.6998
[11 empty] | Pump heat in | -15.4156 |  | -15.3958 |  | -0.019751
[11 empty] | Total Gas Usage | 303.5713 |  | 290.8912 |  | 12.6801 | 4.177%
[10 empty] | 9 | Domestic Hot Water | 101.9442 | 33.12% | 101.9442 | 34.72% | 0
[11 empty] | Heating Hot Water | 51.4511 | 16.72% | 51.4511 | 17.52% | 0
[11 empty] | Tank Heat Loss | 5.0069 | 1.627% | 4.5526 | 1.551% | 0.45427
[11 empty] | Pipe heat loss | 148.9514 | 48.4% | 135.2936 | 46.08% | 13.6577
[11 empty] | Uncategorized | 0.42464 | 0.138% | 0.36539 | 0.1244% | 0.059253
[11 empty] | Subtotal | 307.7782 | 100% | 293.6069 | 100% | 14.1713
[11 empty] | Pump heat in | -15.3958 |  | -15.3761 |  | -0.019751
[11 empty] | Total Gas Usage | 292.3824 |  | 278.2309 |  | 14.1515 | 4.84%
[10 empty] | 16 | Domestic Hot Water | 126.1687 | 23.34% | 126.1687 | 23.69% | 0
[11 empty] | Heating Hot Water | 224.6368 | 41.55% | 224.6368 | 42.17% | 0
[11 empty] | Tank Heat Loss | 5.8956 | 1.09% | 5.629 | 1.057% | 0.26664
[11 empty] | Pipe heat loss | 182.7649 | 33.8% | 175.1016 | 32.87% | 7.6633
[11 empty] | Uncategorized | 1.1851 | 0.2192% | 1.1258 | 0.2114% | 0.059253
[11 empty] | Subtotal | 540.6511 | 100% | 532.6619 | 100% | 7.9892
[11 empty] | Pump heat in | -19.6028 |  | -19.5929 |  | -0.0098754
[11 empty] | Total Gas Usage | 521.0484 |  | 513.069 |  | 7.9794 | 1.531%
[18 empty] | Climate Zone | Boiler Gas Usage [therms/unit/yr] |  |  |  | Cost Savings [$/unit/yr]
[19 empty] | Baseline | Proposed | Savings | Savings [%]
[18 empty] | 6 | 303.5713 | 290.8912 | 12.6801 | 4.177% | 12.6801
[18 empty] | 9 | 292.3844 | 278.2269 | 14.1574 | 4.842% | 14.1574
[18 empty] | 16 | 521.0444 | 513.0651 | 7.9794 | 1.531% | 7.9794
[24 empty] | Climate Zone | HDD at 50F | Boiler Gas Usage [therms/unit/yr]
[26 empty] | Modeled | Estimated
[24 empty] | 1 | 3.11 |  | 12.1356
[24 empty] | 2 | 2.9 |  | 12.6742
[24 empty] | 3 | 2.6 |  | 13.4436
[24 empty] | 4 | 2.77 |  | 13.0076
[24 empty] | 5 | 2.75 |  | 13.0589
[24 empty] | 6 | 2.45 | 12.6801
[24 empty] | 7 | 1.96 |  | 15.0849
[24 empty] | 8 | 2.49 |  | 13.7257
[24 empty] | 9 | 2.88 | 14.1574
[24 empty] | 10 | 3.14 |  | 12.0587
[24 empty] | 11 | 3.18 |  | 11.9561
[24 empty] | 12 | 3.19 |  | 11.9305
[24 empty] | 13 | 3.02 |  | 12.3665
[24 empty] | 14 | 3.2 |  | 11.9048
[24 empty] | 15 | 3.11 |  | 12.1356
[24 empty] | 16 | 4.62 | 7.9794

## Results
Model |  | Annual Value [GJ] | gas therms/yr/bldg | gas therms/unit/yr | %totaldemand |  |  | Electricity Annual Value [GJ] | kWh/bldg/yr | kWh/unit/yr |  |  | Gas Annual Value [GJ] | therms/yr | therms/unit/yr |  |  | Annual Value [m3] | gal/yr/bldg | gal/yr/unit | gal/day |  |  | Design Size Nominal Capacity [W] | Design Size Design Water Flow Rate [m3/s] | Design Size Nominal Capacity [Btu/h] | Design Size Design Water Flow Rate [gpm] |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W] | Water Flow [gpm]
CZ6 Pre | MYWATERUSEEQUIPLOAD | 107.4 | 1272.7477 | 106.0623 | 33.25% | DHW load | MYPRIMARYPUMPELECTRICITY | 0.5 | 138.889 | 11.5741 |  | MYBOILERGAS | 384.25 | 3642.8552 | 303.5713 |  | MYWATERMETER | 866.68 | 228952.589 | 19079.3824 | 52.2723 |  | HW BOILER | 79863.93 | 0.001716 | 272495.7292 | 27.202 | SECONDARY CONST SPD PUMPPump:ConstantSpeedContinuous119562.680.002524505.26200214.610.95PRIMARY CONST SPD PUMPPump:ConstantSpeedIntermittent44836.000.001716128.8675080.480.95 | Pump:ConstantSpeed | Continuous | 119562.68 | 0.002524 | 505.26 | 200214.61 | 0.95 | 40.0104
| MYHHWCOILLOAD | 51.89 | 614.9244 | 51.2437 | 16.06% | Space heating load | MYSECONDARYPUMPELECTRICITY | 15.93 | 4425.0035 | 368.7503 | [6 empty] | MYHOTWATER | 657.45 | 173679.8814 | 14473.3235 | 39.6529 | 111.1658 | [5 empty] | PRIMARY CONST SPD PUMP | Pump:ConstantSpeed | Intermittent | 44836 | 0.001716 | 128.86 | 75080.48 | 0.95 | 27.202
| MYBOILERLOAD | 307.4 | 3642.8552 | 303.5713 |  | Boiler output (80% eff.) | Both pumps | 16.43 | 4563.8925 | 380.3244 | [6 empty] | MYCOLDWATER | 209.22 | 55270.0658 | 4605.8388 | 12.6187
| MYTANKHEATLOSSENERGY | -5.22 | 61.8598 | 5.155 | 1.616% | Tank heat loss
| MYPIPEFLUIDHEATTRANSFERENERGY | 158.06 | 1873.096 | 156.0913 | 48.93% | Pipe heat loss
| MYPRIMARYPUMPFLDHTGAINENERGY | 0.47 | 5.5698 | 0.46415 |  | Pump heat
| MYSECONDARYPUMPFLDHTGAINENERGY | 15.14 | 179.4171 | 14.9514 |  | Pump heat
| total heat in | 323.01 | 3827.8421 | 318.9868 | 99.86%
| total heat out | 322.57 | 3822.6279 | 318.5523
| uncategorized | 0.44 | 5.2142 | 0.43452 | 0.1362%
CZ6 Post | MYWATERUSEEQUIPLOAD | 107.4 | 1272.7477 | 106.0623 | 34.63% |  | MYPRIMARYPUMPELECTRICITY | 0.48 | 133.3334 | 11.1111 |  | MYBOILERGAS | 368.2 | 3490.6943 | 290.8912 |  | MYWATERMETER | 866.68 | 228952.589 | 19079.3824 | 52.2723 |  | HW BOILER | 79863.93 | 0.001716 | 272495.7292 | 27.202 | SECONDARY CONST SPD PUMP | Pump:ConstantSpeed | Continuous | 119562.68 | 0.002524 | 505.26 | 200214.61 | 0.95 | 40.0104
| MYHHWCOILLOAD | 51.89 | 614.9244 | 51.2437 | 16.73% |  | MYSECONDARYPUMPELECTRICITY | 15.93 | 4425.0035 | 368.7503 | [6 empty] | MYHOTWATER | 721.72 | 190658.2158 | 15888.1847 | 43.5293 | 122.033 | [5 empty] | PRIMARY CONST SPD PUMP | Pump:ConstantSpeed | Intermittent | 44836 | 0.001716 | 128.86 | 75080.48 | 0.95 | 27.202
| MYBOILERLOAD | 294.56 | 3490.6943 | 290.8912 |  |  | Both pumps | 16.41 | 4558.337 | 379.8614 | [6 empty] | MYCOLDWATER | 144.95 | 38291.7314 | 3190.9776 | 8.7424
| MYTANKHEATLOSSENERGY | -4.81 | 57.0011 | 4.7501 | 1.551%
| MYPIPEFLUIDHEATTRANSFERENERGY | 145.67 | 1726.2678 | 143.8556 | 46.97%
| MYPRIMARYPUMPFLDHTGAINENERGY | 0.45 | 5.3327 | 0.4444
| MYSECONDARYPUMPFLDHTGAINENERGY | 15.14 | 179.4171 | 14.9514
| total heat in | 310.15 | 3675.4442 | 306.287 | 99.88%
| total heat out | 309.77 | 3670.941 | 305.9118
| uncategorized | 0.38 | 4.5032 | 0.37527 | 0.1225%
CZ6 Diff | MYWATERUSEEQUIPLOAD | 0 | 0 | 0 |  |  | MYPRIMARYPUMPELECTRICITY | 0.02 | 5.5556 | 0.46296 | 4% | MYBOILERGAS | 16.05 | 152.1609 | 12.6801 | 4.177% | MYWATERMETER | 0 | 0 | 0 | 0 |  | HW BOILER | 0 | 0 | 0 | 0 | SECONDARY CONST SPD PUMP | Pump:ConstantSpeed | Continuous | 0 | 0 | 0 | 0 | 0 | 0
| MYHHWCOILLOAD | 0 | 0 | 0 |  |  | MYSECONDARYPUMPELECTRICITY | 0 | 0 | 0 | [6 empty] | MYHOTWATER | -64.27 | -16978.3344 | -1414.8612 | -3.8763 | -10.8672 | [5 empty] | PRIMARY CONST SPD PUMP | Pump:ConstantSpeed | Intermittent | 0 | 0 | 0 | 0 | 0 | 0
| MYBOILERLOAD | 12.84 | 152.1609 | 12.6801 |  |  | Both pumps | 0.02 | 5.5556 | 0.46296 | 0.1217% | [5 empty] | MYCOLDWATER | 64.27 | 16978.3344 | 1414.8612 | 3.8763
| MYTANKHEATLOSSENERGY | -0.41 | 4.8587 | 0.40489
| MYPIPEFLUIDHEATTRANSFERENERGY | 12.39 | 146.8282 | 12.2357
| MYPRIMARYPUMPFLDHTGAINENERGY | 0.02 | 0.23701 | 0.019751
| MYSECONDARYPUMPFLDHTGAINENERGY | 0 | 0 | 0
CZ9 Pre | MYWATERUSEEQUIPLOAD | 103.23 | 1223.331 | 101.9442 | 33.12% |  | MYPRIMARYPUMPELECTRICITY | 0.48 | 133.3334 | 11.1111 |  | MYBOILERGAS | 370.09 | 3508.6123 | 292.3844 |  | MYWATERMETER | 866.68 | 228952.589 | 19079.3824 | 52.2723 |  | HW BOILER | 79863.93 | 0.001716 | 272495.7292 | 27.202 | SECONDARY CONST SPD PUMP | Pump:ConstantSpeed | Continuous | 119562.68 | 0.002524 | 505.26 | 200214.61 | 0.95 | 40.0104
| MYHHWCOILLOAD | 52.1 | 617.413 | 51.4511 | 16.72% |  | MYSECONDARYPUMPELECTRICITY | 15.93 | 4425.0035 | 368.7503 | [6 empty] | MYHOTWATER | 650.4 | 171817.4688 | 14318.1224 | 39.2277 | 109.9738 | [5 empty] | PRIMARY CONST SPD PUMP | Pump:ConstantSpeed | Intermittent | 44836 | 0.001716 | 128.86 | 75080.48 | 0.95 | 27.202
| MYBOILERLOAD | 296.07 | 3508.5886 | 292.3824 |  |  | Both pumps | 16.41 | 4558.337 | 379.8614 | [6 empty] | MYCOLDWATER | 216.28 | 57135.1202 | 4761.26 | 13.0445
| MYTANKHEATLOSSENERGY | -5.07 | 60.0822 | 5.0069 | 1.627%
| MYPIPEFLUIDHEATTRANSFERENERGY | 150.83 | 1787.4166 | 148.9514 | 48.4%
| MYPRIMARYPUMPFLDHTGAINENERGY | 0.45 | 5.3327 | 0.4444
| MYSECONDARYPUMPFLDHTGAINENERGY | 15.14 | 179.4171 | 14.9514
| total heat in | 311.66 | 3693.3385 | 307.7782 | 99.86%
| total heat out | 311.23 | 3688.2428 | 307.3536
| uncategorized | 0.43 | 5.0957 | 0.42464 | 0.138%
CZ9 Post | MYWATERUSEEQUIPLOAD | 103.23 | 1223.331 | 101.9442 | 34.72% |  | MYPRIMARYPUMPELECTRICITY | 0.45 | 125.0001 | 10.4167 |  | MYBOILERGAS | 352.17 | 3338.723 | 278.2269 |  | MYWATERMETER | 866.68 | 228952.589 | 19079.3824 | 52.2723 |  | HW BOILER | 79863.93 | 0.001716 | 272495.7292 | 27.202 | SECONDARY CONST SPD PUMP | Pump:ConstantSpeed | Continuous | 119562.68 | 0.002524 | 505.26 | 200214.61 | 0.95 | 40.0104
| MYHHWCOILLOAD | 52.1 | 617.413 | 51.4511 | 17.52% |  | MYSECONDARYPUMPELECTRICITY | 15.93 | 4425.0035 | 368.7503 | [6 empty] | MYHOTWATER | 726.05 | 191802.0806 | 15983.5067 | 43.7904 | 122.7651 | [5 empty] | PRIMARY CONST SPD PUMP | Pump:ConstantSpeed | Intermittent | 44836 | 0.001716 | 128.86 | 75080.48 | 0.95 | 27.202
| MYBOILERLOAD | 281.74 | 3338.7704 | 278.2309 |  |  | Both pumps | 16.38 | 4550.0036 | 379.167 | [6 empty] | MYCOLDWATER | 140.63 | 37150.5084 | 3095.8757 | 8.4819
| MYTANKHEATLOSSENERGY | -4.61 | 54.631 | 4.5526 | 1.551%
| MYPIPEFLUIDHEATTRANSFERENERGY | 137 | 1623.5236 | 135.2936 | 46.08%
| MYPRIMARYPUMPFLDHTGAINENERGY | 0.43 | 5.0957 | 0.42464
| MYSECONDARYPUMPFLDHTGAINENERGY | 15.14 | 179.4171 | 14.9514
| total heat in | 297.31 | 3523.2833 | 293.6069 | 99.88%
| total heat out | 296.94 | 3518.8986 | 293.2416
| uncategorized | 0.37 | 4.3847 | 0.36539 | 0.1244%
CZ9 Diff | MYWATERUSEEQUIPLOAD | 0 | 0 | 0 |  |  | MYPRIMARYPUMPELECTRICITY | 0.03 | 8.3333 | 0.69444 |  | MYBOILERGAS | 17.92 | 169.8893 | 14.1574 | 4.842% | MYWATERMETER | 0 | 0 | 0 | 0 |  | HW BOILER | 0 | 0 | 0 | 0 | SECONDARY CONST SPD PUMP | Pump:ConstantSpeed | Continuous | 0 | 0 | 0 | 0 | 0 | 0
| MYHHWCOILLOAD | 0 | 0 | 0 |  |  | MYSECONDARYPUMPELECTRICITY | 0 | 0 | 0 | [6 empty] | MYHOTWATER | -75.65 | -19984.6118 | -1665.3843 | -4.5627 | -12.7914 | [5 empty] | PRIMARY CONST SPD PUMP | Pump:ConstantSpeed | Intermittent | 0 | 0 | 0 | 0 | 0 | 0
| MYBOILERLOAD | 14.33 | 169.8182 | 14.1515 |  |  | Both pumps | 0.03 | 8.3333 | 0.69445 | 0.1828% | [5 empty] | MYCOLDWATER | 75.65 | 19984.6118 | 1665.3843 | 4.5627
| MYTANKHEATLOSSENERGY | -0.46 | 5.4512 | 0.45427
| MYPIPEFLUIDHEATTRANSFERENERGY | 13.83 | 163.8929 | 13.6577
| MYPRIMARYPUMPFLDHTGAINENERGY | 0.02 | 0.23701 | 0.019751
| MYSECONDARYPUMPFLDHTGAINENERGY | 0 | 0 | 0
CZ16 Pre | MYWATERUSEEQUIPLOAD | 127.76 | 1514.0247 | 126.1687 | 23.34% |  | MYPRIMARYPUMPELECTRICITY | 0.85 | 236.1113 | 19.6759 |  | MYBOILERGAS | 659.52 | 6252.5332 | 521.0444 |  | MYWATERMETER | 866.68 | 228952.589 | 19079.3824 | 52.2723 |  | HW BOILER | 110191.28 | 0.002365 | 375972.6474 | 37.49 | SECONDARY CONST SPD PUMP | Pump:ConstantSpeed | Continuous | 119562.68 | 0.003174 | 635.41 | 200214.61 | 0.95 | 50.3142
| MYHHWCOILLOAD | 227.47 | 2695.6418 | 224.6368 | 41.55% |  | MYSECONDARYPUMPELECTRICITY | 20.04 | 5566.6711 | 463.8893 | [6 empty] | MYHOTWATER | 681.52 | 180038.5014 | 15003.2085 | 41.1047 | 115.2357 | [5 empty] | PRIMARY CONST SPD PUMP | Pump:ConstantSpeed | Intermittent | 44836 | 0.002365 | 177.6 | 75080.48 | 0.95 | 37.49
| MYBOILERLOAD | 527.62 | 6252.5806 | 521.0484 |  |  | Both pumps | 20.89 | 5802.7824 | 483.5652 | [6 empty] | MYCOLDWATER | 185.16 | 48914.0875 | 4076.174 | 11.1676
| MYTANKHEATLOSSENERGY | -5.97 | 70.7477 | 5.8956 | 1.09%
| MYPIPEFLUIDHEATTRANSFERENERGY | 185.07 | 2193.179 | 182.7649 | 33.8%
| MYPRIMARYPUMPFLDHTGAINENERGY | 0.81 | 9.5989 | 0.79991
| MYSECONDARYPUMPFLDHTGAINENERGY | 19.04 | 225.6342 | 18.8029
| total heat in | 547.47 | 6487.8138 | 540.6511 | 99.78%
| total heat out | 546.27 | 6473.5931 | 539.4661
| uncategorized | 1.2 | 14.2206 | 1.1851 | 0.2192%
CZ16 Post | MYWATERUSEEQUIPLOAD | 127.76 | 1514.0247 | 126.1687 | 23.69% |  | MYPRIMARYPUMPELECTRICITY | 0.84 | 233.3335 | 19.4445 |  | MYBOILERGAS | 649.42 | 6156.7809 | 513.0651 |  | MYWATERMETER | 866.68 | 228952.589 | 19079.3824 | 52.2723 |  | HW BOILER | 110191.28 | 0.002365 | 375972.6474 | 37.49 | SECONDARY CONST SPD PUMP | Pump:ConstantSpeed | Continuous | 119562.68 | 0.003174 | 635.41 | 200214.61 | 0.95 | 50.3142
| MYHHWCOILLOAD | 227.47 | 2695.6418 | 224.6368 | 42.17% |  | MYSECONDARYPUMPELECTRICITY | 20.04 | 5566.6711 | 463.8893 | [6 empty] | MYHOTWATER | 717.53 | 189551.3352 | 15795.9446 | 43.2766 | 121.3245 | [5 empty] | PRIMARY CONST SPD PUMP | Pump:ConstantSpeed | Intermittent | 44836 | 0.002365 | 177.6 | 75080.48 | 0.95 | 37.49
| MYBOILERLOAD | 519.54 | 6156.8283 | 513.069 |  |  | Both pumps | 20.88 | 5800.0046 | 483.3337 | [6 empty] | MYCOLDWATER | 149.15 | 39401.2538 | 3283.4378 | 8.9957
| MYTANKHEATLOSSENERGY | -5.7 | 67.5481 | 5.629 | 1.057%
| MYPIPEFLUIDHEATTRANSFERENERGY | 177.31 | 2101.2188 | 175.1016 | 32.87%
| MYPRIMARYPUMPFLDHTGAINENERGY | 0.8 | 9.4804 | 0.79004
| MYSECONDARYPUMPFLDHTGAINENERGY | 19.04 | 225.6342 | 18.8029
| total heat in | 539.38 | 6391.9429 | 532.6619 | 99.79%
| total heat out | 538.24 | 6378.4333 | 531.5361
| uncategorized | 1.14 | 13.5096 | 1.1258 | 0.2114%
CZ16 Diff | MYWATERUSEEQUIPLOAD | 0 | 0 | 0 |  |  | MYPRIMARYPUMPELECTRICITY | 0.01 | 2.7778 | 0.23148 | 1.176% | MYBOILERGAS | 10.1 | 95.7523 | 7.9794 | 1.531% | MYWATERMETER | 0 | 0 | 0 | 0 |  | HW BOILER | 0 | 0 | 0 | 0 | SECONDARY CONST SPD PUMP |  |  | 0 | 0 | 0 | 0 | 0 | 0
| MYHHWCOILLOAD | 0 | 0 | 0 |  |  | MYSECONDARYPUMPELECTRICITY | 0 | 0 | 0 | [6 empty] | MYHOTWATER | -36.01 | -9512.8337 | -792.7361 | -2.1719 | -6.0888 | [5 empty] | PRIMARY CONST SPD PUMP |  |  | 0 | 0 | 0 | 0 | 0 | 0
| MYBOILERLOAD | 8.08 | 95.7523 | 7.9794 |  |  | Both pumps | 0.01 | 2.7778 | 0.23148 | 0.04787% | [5 empty] | MYCOLDWATER | 36.01 | 9512.8337 | 792.7361 | 2.1719
| MYTANKHEATLOSSENERGY | -0.27 | 3.1996 | 0.26664
| MYPIPEFLUIDHEATTRANSFERENERGY | 7.76 | 91.9602 | 7.6633
| MYPRIMARYPUMPFLDHTGAINENERGY | 0.01 | 0.11851 | 0.0098754
| MYSECONDARYPUMPFLDHTGAINENERGY | 0 | 0 | 0

## Notes
System | Baseline Notes | Proposed Notes | Other Notes | CZ9 DEER MF 2003 data for calibration | Value | Notes
General | 30 timesteps |  | climate modifications | DHW [therms/yr] | 105.849 | DEER WH Calculator spreadsheet for CZ 9 MF; not including tank heat loss or standing pilot light energy
| All piping is copper w/o insulation |  | cz measure tag | Space Heat [therms/yr] | 56.4 | Space heat from DEER Tstat spreadsheet for CZ 9 multifamily
| Pump powerperflowpressure calulation method |  | climate zone file | Total [therms/yr] | 162.249
| Most componenets are autosized. |  | cz ddy data | 135F Water [gal/yr] | 13710.6564
| 95% motor efficiency for pumps |  | water main temperatures. | 135F Water [gal/dy] | 37.5634 | DEER WH Calulator spreadsheet for CZ 9 MF; assuming 135F water
| Pump Design Shaft Power per unit flow rate per unit head: 0.3 W*min/(gal*ft) for pumps |  | for OAReset, tank setpoint schedules (2)
Primary Loop | Primary Pump: intermitent constant flow rate; 15 ft of head; autosized flow rate
Outdoor piping: 10' of 2" pipe outdoors
OS:Boiler:HotWater
Nominal Thermal Efficiency = 0.80
Design Water Outlet Temperature = 150F
Minimum Part Load Ratio = 1
Sizing Factor = 1.5
Boiler flow mode: ConstantFlow
Boiler Setpoint Manager = 145F
OS:Sizing:Plant
Design Loop Exit Temperature = 150F
Design Loop Temp Diff = 20F
| assuming no pilot light. | Tank: 135F/120F (at 55F/75F ambient)
Secondary Loop Source Side | 135F tank setpoint (in the WH object and at the supply water)
5F tank setpoint differential
Secondary Pump: continuous constant flow rate; 40' head; 40 gpm
Tank volume = 150 gal; "Indirect Water Heating Recovery Time" = 0.25 hours
Tank loss is less even thought it's outside since I'm assuming the same UA for one tank.
Secondary Loop Demand Side | OS:Coil:Heating:Water (per coil)
Rated Outlet Water Temperature: 100F
Rated Inlet Air Temperature: 68F
Outdoor piping: 10' of 2" pipe outdoors
Indoor supply piping: 55' of 2"; 190' of 1.5"
Indoor return: 55' of 2"; 190' of 1.5"; 120' of 3/4" at fan coils
Only bypass pipe is past the HW coils and DHW fixtures
Water volume is at 115F (so total water flow, not hot only)
Water usage target prorated per approx. average CW temp of 65F.
70F and 20 fpm wind speed around the indoor pipes
inputed sensor and acuator node names for the HHW coils in their controller objects
130F, 30F delta T design conditions for HHW coils
Air Loops | OS:Sizing:System (per AirLoopHVAC)
Preheat Design Temperature: 44.6F to 50F
Central Heating Design Supply Air Temperature: 122F to 90F (to match the coil object)
Zone heating setpoint = 73F 24/7
Zone cooling setpoint = 75F 24/7
Constant speed supply fans, modulating HHW valves
Climate Zone 16 only | Made the following changes since load was unsatisfied:
Boiler sizing factor of 2
Autosized the secondary constant speed pump
OS:Sizing:System (per AirLoopHVAC)
Central Heating Design Supply Air Temperature: 110F (to match the coil object)
OS:Coil:Heating:Water (per coil)
Rated Outlet Air Temperature: 110F
Rated Outlet Water Temperature: 110F
Tank Volume 200 gallons
160F boiler setpoint, design temp, and exit temp

## Supporting
Conversion Factors |  |  | Water Properties |  |  | Assumed blended energy rates |  |  | OpenStudio node names for plotting |  |  | Copper pipe properties |  |  |  | Building size and pipe length calc | Heating Degree Day data from weather files
Conversion factor | 264.172 | gal/m3 | density of water | 8.2 | lbs/gal | Gas cost | 1 | $/therm | b_in | 188 | node # | https://www.engineersedge.com/properties_of_metals.htm |  |  |  | Building size 95'x71'x20' | cz6
Conversion factor | 0.13368 | ft3/gal | cp at 100F H2O | 1 | Btu/(lb*F) | Elec. Cost | 0.3 | $/kWh | b_out | 187 | node # |  | Thermal Conductivity | Density | Specific Heat | 4*95' at 1.5" for supply and return down the middle of each floor | - 126 annual (standard) cooling degree-days (10C baseline)
Conversion factor | 9.4804 | therms/GJ | [6 empty] | wh_in | 239 | node # |  | Btu / (hr-ft-F) | (lbs/in3) | (Btu/lb/F) | 71' of 2" for supply and return to the middle of the building | - 2.45 annual (standard) heating degree-days (10C baseline)
Conversion factor | 100000 | Btu/therm | [6 empty] | wh_out | 228 | node # | copper | 231 | 0.322 | 0.095 | 2*20' of 2" for up and down from the 2nd floor
Conversion factor | 277.778 | kWh/GJ | [6 empty] | wh source in | 197 | node # |  |  |  |  | So, 380' of 1.5" and 110' of 2" inside the building. Half supply, half return | - 136 annual (standard) cooling degree-days (18.3C baseline) | [6 empty] | 64.94
[9 empty] | wh source out | 216 | node # |  | Btu*in/(hr*ft^2*F) | lbs/ft^3 |  | Before and after the end uses in secondary loop (indoors): 190' of 1.5" and 55' of 2" | - 1 annual (standard) heating degree-days (18.3C baseline)
[12 empty] | copper | 2772 | 556.416
cz9
[17 empty] | - 170 annual (standard) cooling degree-days (10C baseline) | [6 empty] | 50
- 2.88 annual (standard) heating degree-days (10C baseline)
- 96 annual (standard) cooling degree-days (18.3C baseline)
- 7 annual (standard) heating degree-days (18.3C baseline)
cz16
- 454 annual (standard) cooling degree-days (10C baseline)
- 4.62 annual (standard) heating degree-days (10C baseline)
- 5 annual (standard) cooling degree-days (18.3C baseline)
- 201 annual (standard) heating degree-days (18.3C baseline)
[17 empty] | cz | hdd65 | hdd50 | Modeled (CZ 6, 9, & 16) |  | intercept | 20.1115
[17 empty] | 6 | 1 | 2.45 | 12.6801 |  | slope | -2.5646
[17 empty] | 9 | 7 | 2.88 | 14.1574
[17 empty] | 16 | 201 | 4.62 | 7.9794
[18 empty] | cz | hdd50 | hdd65 | Modeled | Estimated (remaining CZs) |  | 1.96 | 4.62
[18 empty] | 1 | 3.11 | 69 |  | 12.1356
[18 empty] | 2 | 2.9 | 63 |  | 12.6742
[18 empty] | 3 | 2.6 | 31 |  | 13.4436
[18 empty] | 4 | 2.77 | 26 |  | 13.0076
[18 empty] | 5 | 2.75 | 21 |  | 13.0589
[18 empty] | 6 | 2.45 | 1 | 12.6801
[18 empty] | 7 | 1.96 | 0 |  | 15.0849
[18 empty] | 8 | 2.49 | 2 |  | 13.7257
[18 empty] | 9 | 2.88 | 7 | 14.1574
[18 empty] | 10 | 3.14 | 11 |  | 12.0587
[18 empty] | 11 | 3.18 | 72 |  | 11.9561
[18 empty] | 12 | 3.19 | 73 |  | 11.9305
[18 empty] | 13 | 3.02 | 65 |  | 12.3665
[18 empty] | 14 | 3.2 | 99 |  | 11.9048
[18 empty] | 15 | 3.11 | 3 |  | 12.1356
[18 empty] | 16 | 4.62 | 201 | 7.9794