## Sheet1
Values to be used in WP
2015 |  |  |  |  | 2014 | [8 empty] | Metric | Combine 2014_2015 | Fluid Temp(F)
PA | First Year Gross Therm Savings |  |  |  | PA | First Year Gross Therms Savings |  |  |  | First Year Net Therms Savings |  |  |  | GRR | 0.97255
| Ex Ante Savings | Ex Post Savings | GRR | RP |  | Ex ante | Ex post | GRR | Relative Precision | Ex ante | Ex post | NRR | Relative Precision | Small Commercial Hours | 7003
[14 empty] | Large Commercial Hours | 6056
SCG | 441396 | 621752 | 141% | 31% | PGE | 370701 | 341227 | 92% |  | 247569 | 167377 | 68% |  | Industrial Hours | 6333
[14 empty] | HW Efficiency | 83.49%
Customer Type – Fluid Type | Sample Size | Ex Ante | Ex Post Savings | GRR | SCG | 905293 | 709301 | 78% |  | 543176 | 347923 | 64% |  | LPS Efficiency | 80.71%
[14 empty] | MPS Efficiency | 82.55%
[5 empty] | SDGE | 6903 | 4676 | 68% |  | 4142 | 2294 | 55% |  | HW Bare Pipe Temp(F) | 135.45 | 136.8045
Agricultural/Industrial - Steam | 5 | 124637 | 108597 | 87% | [9 empty] | LPS Bare Pipe Temp(F) | 239.6 | 241.996
Agricultural/Industrial - Hot Water | 5 | 26648 | 23033 | 86% | Statewide | 1282898 | 1055204 | 82% | 3% | 794886 | 517593 | 65% | 10% | MPS Bare Pipe Temp(F) | 291.5 | 294.415
Large Commercial - Steam | 2 | 12344 | 17876 | 145% | [9 empty] | HW Air Temp(F) | 75.15
Large Commercial - Hot Water | 9 | 53920 | 76385 | 142% | Customer Type | Sites | Observations | Ex Ante Operating Hours | Ex Post Ante Operating Hours |  |  |  |  | LowP Steam Air Temp (F) | 97.85
[14 empty] | Med P Steam Air Temp (F) | 83.6
Census Site* | 1 | 7646 | 165316 | 2162% | [9 empty] | NTG | 0.45
sum | 22 | 225195 | 391207 |  | Small Commercial* | 0 | 0 | 2425 | 0 |  |  |  |  | New Pipe Size (inch) | 4
[5 empty] | Large Commercial | 11 | 33 | 4380 | 5560
Customer Type | Sites | Observations | Ex Ante Operating Hours | Mean Ex Post Ante Operating Hours | Industrial | 20 | 60 | 7752 | 6560
Small Commercial* | 0 | 6 | 2425 | 7003
Large Commercial | 11 | 17 | 4380 | 6552
Industrial | 8 | 27 | 7752 | 6106
Fluid Type | Observations | Ex Ante Combustion | Mean Ex Post Combustion |  | Fluid Type | Observations | Ex Ante Combustion | Mean Ex Post Combustion
Hot Water | 27 | 82% | 88.1% |  | Hot Water | 36 | 82% | 77.6%
Low-Pressure Steam | 3 | 83% | 80% |  | Low-Pressure Steam | 4 | 83% | 82.9%
Medium-Pressure Steam | 20 | 83% | 83.4% |  | Medium-Pressure Steam | 53 | 83% | 83.9%
Fluid Type | Observations | Ex Ante Bare Pipe Temp | Mean Ex Post Bare Pipe Temp |  | Fluid Type | Observations | Ex Ante Bare Pipe Temp | Ex Post Bare Pipe Temp
Hot Water | 27 | 150 | 135.6 |  | Hot Water | 36 | 150 | 135.3
Low-Pressure Steam | 3 | 243 | 222.9
Medium-Pressure Steam | 20 | 328 | 270.5 |  | Low-Pressure Steam | 4 | 243 | 256.3
[5 empty] | Medium-Pressure Steam | 53 | 328 | 312.5
Fluid Type | Observations | Ex Ante Surrounding Air Temp | Mean Ex Post Surrounding Temp |  | Fluid Type | Observations | Ex Ante Surrounding Air Temp | Ex Post Surrounding Air Temp
[5 empty] | Hot Water | 36 | 75 | 77.6
Hot Water | 27 | 75 | 72.7
Low-Pressure Steam | 3 | 75 | 93.4 |  | Low-Pressure Steam | 4 | 75 | 102.3
Medium-Pressure Steam | 20 | 75 | 81.4
[5 empty] | Medium-Pressure Steam | 53 | 75 | 85.8

## Hours
2015
2015 | Site | Sector | Fluid Type | Pipe Size | Pipe Qty(ft) | Pipe Size (in) | Insulation Thickness(in) | Boiler Eff. | Proces Temp (F) | Ambient Temp (F) | Operating Hours | Evaluated Savings (MMBtu/yr) | Reported Savings (MMBtu/yr) | GRR | 2014-2015 Combined Efficiency HW | 2014-2015 Combined Efficiency LPS | 2014-2015 Combined Efficiency MPS
| 1 | LGCOM | LPS | >=1 | 50 | 10 | 1.5 | 80% | 222.9 | 93.4 | 1923 | 92 | 43 | 215% | 83.49% | 80.71% | 82.55%
|  | LGCOM | LPS | >=1 | 25 | 14 | 1.5 | 80% | 222.9 | 93.4 | 1923 | 59 | 21 | 276%
|  | LGCOM | LPS | >=1 | 847 | 3 | 1.5 | 80% | 222.9 | 93.4 | 1923 | 387 | 723 | 54%
| 2 | LGCOM | HW | >=1 | 183 | 2.5 | 2 | 97% | 125.6 | 63.4 | 8760 | 134 | 197 | 68%
|  | LGCOM | HW | <1 | 33 | 0.75 | 2 | 97% | 122.3 | 83.2 | 8760 | 5 | 6 | 85%
|  | LGCOM | HW | <1 | 549 | 0.75 | 2 | 97% | 125.6 | 63.4 | 8760 | 155 | 325 | 48%
| 4 | LGCOM | MPS | >=1 | 935 | 10 | 3 | 82% | 314.2 | 86.3 | 8760 | 16532 | 765 | 2162%
| 5 | LGCOM | HW | >=1 | 1333 | 6 | 1.5 | 85% | 153.6 | 63.4 | 2800 | 1234 | 1432 | 86%
|  | LGCOM | HW | >=1 | 119 | 6 | 1.5 | 85% | 153.6 | 83.8 | 2800 | 83 | 45 | 183%
| 6 | LGCOM | HW | >=1 | 22 | 2 | 0.5 | 85% | 165.6 | 67 | 3022 | 1 | 17 | 9%
| 8 | LGCOM | HW | >=1 | 20 | 2 | 1 | 82% | 111 | 82.9 | 4333 | 2 | 8 | 29%
|  | LGCOM | HW | >=1 | 10 | 1.5 | 1 | 82% | 111 | 82.9 | 4333 | 1 | 4 | 23%
| 9 | LGCOM | HW | >=1 | 171 | 6 | 1.5 | 86% | 145.1 | 94.5 | 8760 | 157 | 65 | 241%
|  | LGCOM | HW | >=1 | 786 | 6 | 1.5 | 86% | 114.9 | 88.4 | 8760 | 351 | 300 | 117%
| 15 | LGCOM | HW | >=1 | 169 | 1.5 | 1 | 94% | 111.6 | 81.6 | 3149 | 11 | 65 | 16%
|  | LGCOM | HW | >=1 | 42 | 2 | 1 | 94% | 111.6 | 81.6 | 3149 | 3 | 16 | 20%
| 17 | LGCOM | HW | <1 | 257 | 0.75 | 0.5 | 96% | 156.2 | 72.8 | 3873 | 34 | 31 | 111%
|  | LGCOM | HW | <1 | 257 | 0.75 | 0.5 | 96% | 145.2 | 72.8 | 3873 | 29 | 31 | 92%
|  | LGCOM | HW | >=1 | 36 | 1.25 | 1 | 96% | 165.2 | 71 | 7699 | 19 | 4 | 434%
|  | LGCOM | HW | >=1 | 36 | 1.25 | 1 | 96% | 160.2 | 71 | 7699 | 18 | 4 | 405%
| 18 | LGCOM | HW | >=1 | 233 | 4 | 1 | 80% | 146.7 | 96.9 | 8368 | 187 | 89 | 211%
|  | LGCOM | HW | >=1 | 233 | 4 | 1 | 80% | 140.4 | 96 | 8013 | 156 | 89 | 175%
| 19 | LGCOM | MPS | >=1 | 152 | 3 | 2 | 85% | 337.2 | 89.1 | 8753 | 983 | 224 | 439%
|  | LGCOM | MPS | >=1 | 152 | 2 | 2 | 85% | 214 | 89.5 | 8753 | 267 | 224 | 119%
| 3 | INDUSTRIAL | MPS | >=1 | 288 | 1.25 | 1 | 85% | 258 | 92.1 | 2914 | 148 | 753 | 20%
|  | INDUSTRIAL | MPS | >=1 | 30 | 1.25 | 1 | 85% | 258 | 92.1 | 2914 | 15 | 78 | 20%
|  | INDUSTRIAL | MPS | >=1 | 60 | 1.25 | 1 | 85% | 258 | 92.1 | 2914 | 31 | 157 | 20%
|  | INDUSTRIAL | MPS | >=1 | 60 | 1.25 | 1 | 85% | 258 | 92.1 | 2914 | 31 | 157 | 20%
|  | INDUSTRIAL | MPS | <1 | 186 | 1.25 | 1 | 85% | 146.8 | 91.3 | 2914 | 24 | 251 | 10%
| 7 | INDUSTRIAL | MPS | >=1 | 833 | 6 | 2 | 85% | 341.7 | 63 | 8760 | 10931 | 4024 | 272%
|  | INDUSTRIAL | MPS | <1 | 111 | 0.75 | 1 | 85% | 341.7 | 75 | 8760 | 230 | 150 | 153%
|  | INDUSTRIAL | MPS | >=1 | 226 | 2 | 2 | 85% | 341.7 | 75 | 8760 | 1092 | 591 | 185%
|  | INDUSTRIAL | HW | <1 | 265 | 0.75 | 1 | 85% | 138.5 | 63 | 8651 | 72 | 269 | 27%
|  | INDUSTRIAL | HW | >=1 | 184 | 2 | 1.5 | 85% | 138.5 | 75 | 8651 | 112 | 124 | 90%
|  | INDUSTRIAL | HW | >=1 | 2480 | 3 | 1.5 | 85% | 138.5 | 63 | 8651 | 2416 | 2664 | 91%
| 10 | INDUSTRIAL | MPS | >=1 | 731 | 4 | 2 | 83% | 251.6 | 88.8 | 1413 | 560 | 3855 | 15%
| 11 | INDUSTRIAL | HW | >=1 | 459 | 3 | 4 | 82% | 111.2 | 60 | 4463 | 197 | 548 | 36%
|  | INDUSTRIAL | HW | <1 | 40 | 4 | 4 | 82% | 156.4 | 87.3 | 4463 | 34 | 27 | 124%
| 12 | INDUSTRIAL | HW | >=1 | 233 | 4 | 1 | 84% | 195.2 | 88.9 | 8376 | 574 | 157 | 365%
|  | INDUSTRIAL | HW | >=1 | 233 | 4 | 1 | 84% | 173.6 | 88.9 | 8376 | 431 | 157 | 274%
| 13 | INDUSTRIAL | MPS | >=1 | 9 | 6 | 2 | 80% | 292.8 | 82.1 | 4457 | 46 | 23 | 196%
|  | INDUSTRIAL | MPS | >=1 | 9 | 4 | 2 | 80% | 292.8 | 82.1 | 4457 | 32 | 23 | 135%
|  | INDUSTRIAL | MPS | >=1 | 51 | 3 | 2 | 80% | 292.8 | 82.1 | 4457 | 141 | 132 | 106%
|  | INDUSTRIAL | MPS | >=1 | 12 | 2 | 2 | 80% | 292.8 | 82.1 | 4457 | 23 | 31 | 73%
|  | INDUSTRIAL | MPS | >=1 | 190 | 1.5 | 2 | 80% | 292.8 | 82.1 | 4457 | 294 | 494 | 60%
|  | INDUSTRIAL | MPS | >=1 | 180 | 1 | 2 | 80% | 292.8 | 82.1 | 4457 | 195 | 468 | 42%
|  | INDUSTRIAL | MPS | <1 | 6 | 0.75 | 2 | 80% | 185 | 84.4 | 2470 | 1 | 8 | 14%
| 14 | INDUSTRIAL | HW | >=1 | 150 | 2 | 1 | 85% | 138.8 | 92.7 | 8219 | 44 | 101 | 44%
| 16 | INDUSTRIAL | MPS | >=1 | 482 | 2 | 2 | 83% | 77.8 | 77.8 | - | - | 1260 | 0%
|  | INDUSTRIAL | HW | >=1 | 1895 | 2 | 1.5 | 95% | 117.9 | 77.8 | 8423 | 548 | 1280 | 43%
2014 | 1 | LGCOM | MPS | >=1 | 270 | 2 | 1.5 | 82% | 273.4 | 99.9 | 2576 | 252 | 794 | 32%
| 2 | LGCOM | MPS | >=1 | 300 | 3 | 1.5 | 81% | 317 | 84.6 | 2668 | 555 | 882 | 63%
|  | LGCOM | MPS | >=1 | 102 | 3 | 1.5 | 81% | 317 | 84.6 | 2668 | 189 | 300 | 63%
| 3 | INDUSTRIAL | MPS | >=1 | 153 | 3 | 2 | 81% | 352.5 | 77.9 | 6461 | 843 | 796 | 106%
|  | INDUSTRIAL | MPS | >=1 | 153 | 2 | 2 | 81% | 352.5 | 77.9 | 6461 | 580 | 796 | 73%
|  | INDUSTRIAL | MPS | >=1 | 153 | 1 | 2 | 81% | 352.5 | 77.9 | 6461 | 341 | 796 | 43%
| 4 | INDUSTRIAL | HW | >=1 | 1660 | 2 | 1 | 96% | 134.3 | 89.8 | 8696 | 550 | 1122 | 49%
|  | INDUSTRIAL | LPS | >=1 | 1455 | 4 | 2 | 85% | 231.8 | 106 | 8728 | 4948 | 2198 | 225%
| 5 | INDUSTRIAL | MPS | >=1 | 500 | 0.75 | 1 | 82% | 283.9 | 86.8 | 8241 | 677 | 1420 | 48%
|  | INDUSTRIAL | MPS | >=1 | 100 | 0.5 | 1 | 82% | 283.9 | 86.8 | 8241 | 111 | 284 | 39%
| 6 | INDUSTRIAL | MPS | >=1 | 280 | 3 | 2 | 80% | 340.2 | 100 | 7373 | 1599 | 732 | 218%
|  | INDUSTRIAL | MPS | <1 | 610 | 1 | 1 | 80% | 335.4 | 88 | 7206 | 1292 | 824 | 157%
| 7 | INDUSTRIAL | MPS | >=1 | 99 | 3 | 1 | 89% | 314.6 | 92 | 5679 | 325 | 515 | 63%
|  | INDUSTRIAL | MPS | >=1 | 60 | 1.5 | 1 | 89% | 314.6 | 92 | 5679 | 110 | 312 | 35%
|  | INDUSTRIAL | MPS | >=1 | 498 | 4 | 1 | 89% | 314.6 | 92 | 5679 | 2089 | 2590 | 81%
|  | INDUSTRIAL | MPS | >=1 | 1998 | 2 | 1 | 89% | 309.5 | 83.8 | 5550 | 4424 | 10390 | 43%
|  | INDUSTRIAL | MPS | >=1 | 399 | 1 | 1 | 89% | 314.6 | 92 | 5679 | 515 | 2075 | 25%
|  | INDUSTRIAL | MPS | <1 | 300 | 0.75 | 1 | 89% | 314.6 | 92 | 5679 | 307 | 1560 | 20%
|  | INDUSTRIAL | MPS | <1 | 498 | 0.5 | 1 | 89% | 314.6 | 92 | 5679 | 417 | 2590 | 16%
|  | INDUSTRIAL | MPS | >=1 | 300 | 6 | 1 | 89% | 314.6 | 92 | 5679 | 1812 | 1560 | 116%
| 8 | INDUSTRIAL | HW | >=1 | 501 | 4 | 1 | 91% | 140.3 | 81.6 | 4553 | 286 | 947 | 30%
|  | INDUSTRIAL | MPS | <1 | 252 | 0.5 | 0.5 | 84% | 299.9 | 81.6 | 3988 | 136 | 716 | 19%
|  | INDUSTRIAL | MPS | >=1 | 300 | 1.25 | 1.25 | 84% | 299.9 | 81.6 | 3988 | 348 | 1560 | 22%
|  | INDUSTRIAL | MPS | >=1 | 1002 | 2 | 2 | 84% | 299.9 | 81.6 | 3988 | 1696 | 5210 | 33%
|  | INDUSTRIAL | HW | <1 | 249 | 0.5 | 0.5 | 91% | 140.3 | 81.6 | 4553 | 26 | 261 | 10%
| 9 | INDUSTRIAL | MPS | >=1 | 21 | 2 | 1 | 74% | 328.5 | 95.9 | 4193 | 45 | 55 | 82%
|  | INDUSTRIAL | MPS | <1 | 51 | 1 | 0.75 | 74% | 328.5 | 95.9 | 4193 | 60 | 69 | 87%
|  | INDUSTRIAL | MPS | <1 | 102 | 1 | 0.75 | 74% | 328.5 | 95.9 | 4193 | 120 | 138 | 87%
|  | INDUSTRIAL | MPS | >=1 | 30 | 2 | 1 | 74% | 328.5 | 95.9 | 4193 | 65 | 78 | 82%
|  | LGCOM | HW | >=1 | 180 | 2.5 | 1 | 87% | 113.6 | 89.1 | 8577 | 46 | 69 | 67%
| 10 | LGCOM | HW | >=1 | 168 | 2.5 | 1 | 87% | 113.6 | 89.1 | 8577 | 43 | 64 | 67%
|  | LGCOM | HW | >=1 | 180 | 2.5 | 1 | 87% | 113.6 | 89.1 | 8577 | 46 | 69 | 67%
|  | LGCOM | HW | >=1 | 300 | 4 | 1 | 87% | 113.6 | 89.1 | 8577 | 118 | 115 | 103%
|  | LGCOM | HW | >=1 | 168 | 2.5 | 1 | 87% | 113.6 | 89.1 | 8577 | 43 | 64 | 67%
|  | LGCOM | HW | <1 | 120 | 0.5 | 0.75 | 87% | 113.6 | 89.1 | 8577 | 9 | 23 | 37%
|  | LGCOM | HW | <1 | 192 | 0.5 | 0.75 | 87% | 113.6 | 89.1 | 8577 | 14 | 37 | 37%
| 11 | INDUSTRIAL | MPS | >=1 | 200 | 2 | 1.5 | 83% | 233.2 | 97.7 | 8760 | 402 | 523 | 77%
|  | INDUSTRIAL | MPS | >=1 | 60 | 2 | 1.5 | 83% | 227.7 | 92.5 | 4923 | 67 | 157 | 43%
| 12 | LGCOM | HW | >=1 | 65 | 4 | 2 | 84% | 159.9 | 74.8 | 1099 | 16 | 25 | 64%
|  | LGCOM | HW | >=1 | 65 | 4 | 2 | 84% | 159.9 | 74.8 | 1099 | 16 | 25 | 64%
| 13 | INDUSTRIAL | MPS | >=1 | 300 | 2 | 1.5 | 79% | 323 | 84.2 | 6557 | 1009 | 784 | 129%
| 14 | INDUSTRIAL | HW | >=1 | 103 | 2.5 | 1 | 85% | 185.3 | 80.7 | 6574 | 121 | 36 | 341%
|  | INDUSTRIAL | HW | <1 | 27 | 1 | 1 | 85% | 185.3 | 80.7 | 6574 | 15 | 9 | 163%
| 15 | LGCOM | MPS | >=1 | 315 | 1.5 | 1 | 90% | 317.6 | 87.2 | 2825 | 297 | 139 | 214%
| 16 | INDUSTRIAL | MPS | >=1 | 15 | 3 | 2 | 82% | 348.5 | 94.1 | 4656 | 60 | 78 | 77%
|  | INDUSTRIAL | MPS | >=1 | 72 | 1.5 | 2 | 82% | 348.5 | 94.1 | 4656 | 161 | 374 | 43%
|  | INDUSTRIAL | MPS | >=1 | 12 | 6 | 2 | 82% | 348.5 | 94.1 | 4656 | 89 | 62 | 143%
|  | INDUSTRIAL | MPS | >=1 | 130 | 4 | 2 | 82% | 348.5 | 94.1 | 4656 | 663 | 676 | 98%
|  | INDUSTRIAL | MPS | >=1 | 21 | 8 | 2 | 82% | 348.5 | 94.1 | 4656 | 201 | 109 | 184%
|  | INDUSTRIAL | MPS | >=1 | 60 | 2 | 2 | 82% | 348.5 | 94.1 | 4656 | 166 | 312 | 53%
|  | INDUSTRIAL | MPS | >=1 | 102 | 2.5 | 2 | 82% | 348.5 | 94.1 | 4656 | 340 | 530 | 64%
| 17 | LGCOM | HW | >=1 | 10 | 1.5 | 1 | 80% | 193.6 | 74 | 4106 | 6 | 56 | 11%
|  | LGCOM | MPS | >=1 | 20 | 1.5 | 1 | 80% | 331.1 | 74 | 4106 | 35 | 111 | 32%
| 18 | INDUSTRIAL | MPS | >=1 | 498 | 6 | 3 | 85% | 318 | 98.5 | 8738 | 5219 | 2590 | 202%
| 19 | INDUSTRIAL | LPS | >=1 | 790 | 3 | 1 | 80% | 272.7 | 96.7 | 1582 | 588 | 1193 | 49%
| 20 | INDUSTRIAL | HW | >=1 | 1040 | 1.7692 | 1 | 68% | 141.8 | 88.1 | 4539 | 323 | 703 | 46%
|  | INDUSTRIAL | HW | <1 | 800 | 0.65625 | 1 | 68% | 141.8 | 88.1 | 4539 | 113 | 276 | 41%
| 21 | INDUSTRIAL | HW | >=1 | 2167 | 2 | 1 | 68% | 129.7 | 69.5 | 8760 | 1725 | 1560 | 111%
|  | INDUSTRIAL | HW | >=1 | 2167 | 1.5 | 1 | 68% | 148.3 | 69.5 | 8760 | 1952 | 1560 | 125%
|  | INDUSTRIAL | HW | >=1 | 2167 | 3 | 1 | 68% | 96.8 | 66.5 | 8760 | 1072 | 1560 | 69%
| 22 | INDUSTRIAL | HW | >=1 | 153 | 2 | 1 | 76% | 166.3 | 92.2 | 6892 | 117 | 103 | 113%
|  | INDUSTRIAL | MPS | >=1 | 12 | 2 | 1 | 89% | 325.7 | 110 | 7014 | 33 | 31 | 107%
| 23 | LGCOM | MPS | <1 | 201 | 1 | 1.5 | 80% | 287.8 | 87.1 | 8760 | 399 | 153 | 260%
|  | LGCOM | MPS | >=1 | 206 | 3 | 1.5 | 80% | 288.8 | 97.2 | 8760 | 997 | 304 | 328%
| 24 | INDUSTRIAL | MPS | <1 | 93 | 1 | 1.5 | 80% | 279.2 | 96.6 | 8552 | 160 | 282 | 57%
|  | INDUSTRIAL | MPS | >=1 | 100 | 2 | 1.5 | 80% | 347.7 | 79.3 | 8687 | 509 | 556 | 92%
|  | INDUSTRIAL | MPS | >=1 | 150 | 2 | 1.5 | 80% | 347.7 | 79.3 | 8687 | 764 | 834 | 92%
|  | INDUSTRIAL | MPS | >=1 | 626 | 2 | 1.5 | 80% | 347.7 | 79.3 | 8687 | 3188 | 3479 | 92%
|  | INDUSTRIAL | MPS | >=1 | 581 | 2 | 1.5 | 80% | 347.7 | 79.3 | 8687 | 2959 | 3229 | 92%
|  | INDUSTRIAL | MPS | <1 | 305 | 1 | 1.5 | 80% | 279.2 | 96.6 | 8552 | 525 | 923 | 57%
|  | INDUSTRIAL | MPS | >=1 | 24 | 2 | 1.5 | 80% | 347.7 | 79.3 | 8687 | 122 | 133 | 92%
|  | INDUSTRIAL | MPS | >=1 | 105 | 2 | 1.5 | 80% | 347.7 | 79.3 | 8687 | 535 | 583 | 92%
| 25 | LGCOM | HW | >=1 | 70 | 2 | 2 | 84% | 180 | 60.1 | 1754 | 22 | 27 | 84%
| 26 | LGCOM | HW | >=1 | 72 | 3 | 1 | 68% | 139.1 | 66.5 | 2655 | 31 | 57 | 54%
|  | LGCOM | MPS | >=1 | 600 | 1.5 | 1 | 85% | 282.1 | 67.9 | 2655 | 469 | 474 | 99%
|  | LGCOM | HW | >=1 | 18 | 4 | 1 | 68% | 139.1 | 66.5 | 2655 | 10 | 14 | 68%
|  | LGCOM | MPS | >=1 | 360 | 1.5 | 1 | 85% | 282.1 | 67.9 | 2655 | 281 | 284 | 99%
|  | LGCOM | MPS | >=1 | 416 | 1.5 | 1 | 85% | 282.1 | 67.9 | 2655 | 325 | 329 | 99%
| 27 | INDUSTRIAL | HW | <1 | 440 | 0.75 | 1 | 82% | 170.7 | 60.7 | 4234 | 119 | 587 | 20%
|  | INDUSTRIAL | HW | >=1 | 360 | 2 | 1 | 82% | 170.7 | 60.7 | 4234 | 212 | 866 | 24%
| 28 | INDUSTRIAL | HW | <1 | 82 | 0.75 | 1 | 83% | 110.6 | 69.8 | 2495 | 5 | 109 | 4%
| 29 | INDUSTRIAL | MPS | >=1 | 1011 | 4 | 2 | 79% | 323.5 | 90.1 | 3786 | 3583 | 2643 | 136%
|  | INDUSTRIAL | HW | >=1 | 990 | 4 | 2 | 95% | 149.3 | 85.9 | 3885 | 541 | 1871 | 29%
| 30 | LGCOM | HW | <1 | 385 | 0.75 | 0.5 | 68% | 150.4 | 83.1 | 7771 | 113 | 227 | 50%
|  | LGCOM | HW | >=1 | 45 | 2.5 | 1 | 68% | 150.4 | 83.1 | 7771 | 38 | 48 | 80%
|  | LGCOM | HW | <1 | 1470 | 0.75 | 0.5 | 68% | 150.4 | 83.1 | 7771 | 430 | 867 | 50%
|  | LGCOM | HW | >=1 | 81 | 2.5 | 1 | 68% | 150.4 | 83.1 | 7771 | 69 | 87 | 80%
|  | LGCOM | HW | <1 | 54 | 0.75 | 0.5 | 68% | 150.4 | 83.1 | 7771 | 16 | 32 | 50%
|  | LGCOM | HW | >=1 | 153 | 2.5 | 1 | 68% | 150.4 | 83.1 | 7771 | 130 | 164 | 80%
|  | LGCOM | LPS | >=1 | 129 | 4 | 1.5 | 80% | 343.5 | 98.8 | 8760 | 1122 | 235 | 478%
|  | LGCOM | LPS | >=1 | 132 | 1.5 | 0.75 | 80% | 343.5 | 98.8 | 8760 | 467 | 240 | 194%
| 31 | LGCOM | HW | <1 | 610 | 0.75 | 1 | 94% | 117.5 | 74.8 | 1261 | 15 | 119 | 13%
|  | LGCOM | HW | >=1 | 1045 | 4 | 1.5 | 94% | 135.3 | 75.4 | 3650 | 483 | 399 | 121%
[9 empty] | 2014 Industrial mean EFFI | 2015 Industrial Counts
0.82415