Steam Trap Survey and

Billing Analysis Report

Sponsored by

Submitted By:

360 17th Street, Suite 100

Oakland, CA 94612

(510) 834-6420

December 12, 2006

FINAL REPORT

Copyright ©2006 Southern California Gas Company. All rights reserved.

Reproduction or distribution of the whole, or any part of the contents of this document without written permission of The Gas Company is prohibited. Neither The Gas Company nor any of its employees makes any warranty, express or implied, or assumes any legal liability or responsibility for the accuracy, completeness, or usefulness of any data, information, method, product or process disclosed in this document, or represents that its use will not infringe upon any privately-owned rights, including but not limited to, patents, trademarks or copyrights.

- Table of Contents

1.0	Executive Summary	3

1.1	Steam Trap Survey Results	3

1.2	Billing Regression Analysis Results	3

2.0	Steam Trap Survey	4

2.1	Steam Trap Testing Methods	4

Temperature Readings	5

Ultrasonic Testing	5

2.2	Steam Trap Individual Test Results	6

2.3	Steam Trap Testing Summary Results	8

2.4	Steam Trap Survey Observations	8

Boilers	8

Piping & Insulation	8

Inverted Bucket Traps	8

Other Gas Equipment	8

Facility Operation	8

3.0	Billing Analysis	9

3.1	Billing Comparison	9

3.2	Billing Regression Statistical Requirements	10

3.3	Billing Regression Results	10

4.0	Appendix A: Site Survey Reports	12

# Executive Summary

Southern California Gas Company (The Gas Company) engaged kW Engineering to provide engineering support for their Express Efficiency program. During this engagement, our staff performed two work tasks. First, engineers tested steam traps at a sample of dry cleaner facilities to determine the number of failed steam traps and the percentage of failed steam traps per site. Second, our team performed billing regression analyses on a statistical sample of dry cleaners’ gas bills in an attempt to determine savings from steam trap replacements. The work was time sensitive and our staff was instructed to complete the work during November, 2006 so that results might be incorporated in a work paper presented to the CPUC at the end of November.

## Steam Trap Survey Results

kW Engineering conducted steam trap surveys at five Southern California dry cleaners in November, 2006. A total of 65 traps were tested and are summarized in this report. Of the 65 steam traps tested, 16% were blocked, 13% were leaking and 14% were blowing through (failed open) resulting in a total of 42% that were faulty. The steam distribution systems at the dry cleaners were all made up of half inch piping. Boiler system pressures ranged from 74 psi to 100 psi with an average of 82.8 psi, and annual boiler operating time ranged from 1,872 to 2,808 hours per year with an average of 2,425 hours per year.

## Billing Analysis Results

In an attempt to estimate the savings for commercial steam traps, a statistical sample of dry cleaners was selected for a billing analysis from those that had their steam traps replaced in early 2006. The analysis did not clearly show savings from billing comparisons, nor did the billing data produce valid billing regression models with the exception of one site. It is suspected that the production and operating activity at each site has such a high impact on gas usage that it was not possible to produce valid billing regression models without this data. As a result the billing comparison and regression analysis was inconclusive.

# Steam Trap Survey

## Steam Trap Testing Methods

kW Engineering, conducted steam traps surveys at 5 different dry cleaning facilities within The Gas Company’s territory. A total of 65 traps were tested as part of this report.

Commercial Dry Cleaner Site

A Fluke Model number 1100TS non-contact infrared temperature sensor was used to measure piping and steam trap temperatures. Normal use of the infrared thermometer is to measure the inlet and outlet temperatures of the steam trap. This information is used to determine whether the trap is in service and in some cases aid in determining the pressure of the system. Steam traps at all five locations were inverted buckets with a half inch pipe size. Temperature readings were taken upstream, downstream and at the trap itself.

The AccuTrak Model number VPE ultrasonic meter with contact probe was used in testing the various steam traps. This testing device uses ultrasonic sound to detect the flowing medium within the piping and through the steam traps. The ultrasonic meter translates the sound to a lower frequency which a human ear can interpret. The ultrasonic meter maintains the original sound characteristics making it possible to distinguish steam leaking or flowing in a trap from other competing background sounds.

Ultrasonic testing of each trap lasted approximately 1 to 2 minute intervals in order to determine whether the trap was operating normally or not. The traps had a distinctive on/off cycling sound if they were operating normally. The reaming traps either had a continuous clanking sound, hissing noise or were for the most part quiet. Out of 65 total traps, 9 were failed opened, 8 were leaking and 10 were blocked.

Steam trap testing was an iterative process in which data from both the temperature and ultrasonic readings were used to determine the operation of each steam trap as follows.

### Temperature Readings

- Boiler temperatures ranged between 300 oF to 320 oF.

- Most of the steam traps had normal temperature reading, close to the boiler temperature.

- If the upstream temperature was significantly lower than the boiler operating temperature the trap was potentially blocked.

- If the downstream temperature readings were relatively close to the upstream temperature readings, the trap was potentially leaking or failed open.

### Ultrasonic Testing

- If the traps had a distinctive on/off cycling, the trap was considered normal.

- If the traps had a continuous hissing or clanking sound, the trap was considered leaking.

- If the traps were completely silent or quiet, the trap was considered to be blocked.

The temperature and ultrasonic test results were compared and a combined assessment for each trap was determined.

Dry Cleaners A Steam Trap number 7, 
Armstrong 800 vertical inverted bucket steam trap

## Steam Trap Individual Test Results

Test results are shown in the tables below. Tables 1 through 5 have information gathered on the steam traps in the order in which they were tested and recorded. Trap numbers were assigned in sequence of testing. Complete test results for each site can be seen in Appendix A.

Table 1:  Dry Cleaners A Steam Trap Survey Information

Table 2:  Dry Cleaners B Cleaners Steam Trap Survey Information

Table 3:  Dry Cleaners C Cleaners Steam Trap Survey Information

Table 4:  Dry Cleaners D Steam Trap Survey Information

Table 5:  Dry Cleaners E Steam Trap Survey Information

## Steam Trap Testing Summary Results

From Table 1 through 5 it can be seen there are a total of sixty-five (65) traps listed. Of the sixty-five traps, sixty-three (63) were tested and two (2) were not in service. The quantity of failed open, leaking and blocked traps accounts for forty three percent of the steam traps. The numbers are shown in Table 6 and are expressed as percentages.

Table 6: Survey Statistics

|  | Normal | Failed Open | Leaking | Blocked | Total |
| --- | --- | --- | --- | --- | --- |
| Traps | 36 | 9 | 8 | 10 | 63 |
| Percent | 57% | 14% | 13% | 16% | 100% |

Of particular importance is the number of steam traps that are leaking or failed open. These steam traps are releasing steam to the condensate return which results in inefficient operation of the steam system and lost energy. A total of 27% of the steam traps tested were leaking or failed open.

## Steam Trap Survey Observations

The following general observations were made during the testing at the dry cleaner facilities.

### Boilers

Four out of the five dry cleaners’ boilers were rated at 9.5 hp while the other dry cleaner’s boiler was rated at 15 hp. All had an efficiency of 80% and were natural draft.

### Piping & Insulation

Four out of the five dry cleaners were built in the 1980s. Only Dry Cleaners D was built after 1990. Piping at each site was old and had little to no insulation.

### Inverted Bucket Traps

Each dry cleaning facility had a minimum of 10 inverted bucket steam traps. Most of the trap’s had a rusted appearance. At Dry Cleaners C, buckets were placed under two (2) traps to collect water leaks.

### Other Gas Equipment

Three out of five dry cleaners had both large and small dryers. Large dryers are used from 7:00 am until noon everyday.

### Facility Operation

Most of the dry cleaners are open from 7:00 am until 6:00 pm Monday through Saturday and are closed on Sundays. Most of the boilers are rated at 9.5 hp and are turned off by 2:00 pm.

# Billing Analysis

In an attempt to confirm the estimated savings for commercial steam traps, a statistical sample of dry cleaners that had their steam traps replaced in the Express Efficiency program in early 2006 were selected for billing analyses. The billing analyses used both a billing comparison and a billing regression in an attempt to determine savings from the steam trap retrofits.

## Billing Comparison

The first attempt to determine savings for the steam trap replacements involved a billing comparison. The billing comparison compared the average monthly Therm usage per day for the dry cleaners before and after the replacement of steam traps to see if there were any obvious changes in consumption. Two different baseline data sets were considered, the first using all available data up to 28 months prior to the replacement of the steam traps and second using 12 months of baseline data immediately prior to the month of installation. The installation month was not used in the billing comparison. The results of this billing comparison are shown below in Table 7.

Table 7: Billing Comparison Results

| Account ID | All Data Pre Therms/ Day | One Year Pre Therms/ Day | Post Therms/ Day | All Pre Data Savings Therms/ Day | One Year Pre Data Savings Therms/ Day |
| --- | --- | --- | --- | --- | --- |
| Account 1 | 12.9 | 14.3 | 14.9 | -1.4 | -0.6 |
| Account 2 | 35.0 | 33.6 | 30.3 | 1.3 | 3.3 |
| Account 3 | 12.2 | 11.4 | 9.6 | 0.7 | 1.8 |
| Account 4 | 28.3 | 29.9 | 30.4 | -1.7 | -0.4 |
| Account 5 | 21.3 | 21.1 | 20.1 | 0.2 | 1.0 |
| Account 6 | 12.0 | 12.3 | 13.5 | -0.4 | -1.2 |
| Account 7 | 20.7 | 20.0 | 21.4 | 0.6 | -1.3 |
| Account 8 | 27.5 | 25.3 | 28.8 | 2.2 | -3.6 |
| Account 9 | 21.2 | 22.7 | 19.9 | -1.5 | 2.8 |
| Account 10 | 13.0 | 12.6 | 13.4 | 0.4 | -0.9 |
| Average | 20.4 | 20.3 | 20.2 | 0.1 | 0.1 |

As can be seen in Table 7, the analysis did not show any obvious changes in energy consumption and some sites showed increases in energy consumption using the billing comparison. Therefore, a billing regression analysis was undertaken.

The original analysis plan was to create a billing regression analysis for each dry cleaner site based on up to two years of historical billing data. The billing regressions would then be tested for statistical validity, and if they met certain criteria to be considered valid representations of historical billing, they would be used to estimate the baseline consumption during the post installation period in order to estimate savings from steam trap replacements.

## Billing Regression Statistical Requirements

The statistical sample of dry cleaner sites was based upon an 80% confidence with 20% precision, and the sample was assumed to have a coefficient of variation of 0.5. This resulted in a maximum sample size of 11 for an infinite population. As of November, 2006, there were 434 dry cleaner sites that had their steam traps replaced in the Express Efficiency program. Using a finite population correction, the sample size dropped to 10 sites to be considered for billing regression analyses.

In order to have a minimum of six months of post installation data to determine savings from the billing regressions, only those dry cleaner sites that were installed prior to May 2006 were eligible for billing regression analysis. Ten dry cleaner sites met this criteria; enough to meet the minimum sample size selection criteria.

A billing regression model was created for each site based on a minimum of one year, and up to two years of  pre-installation billing data. The billing regression models were considered valid when a coefficient of determination (R2) value of at least 0.7 and preferably 0.8 was achieved. The billing data was reviewed to remove anomalies or outliers that may skew the results of the analysis. Weather data, billing read dates and the number of operating days in a billing period were obtained and used as independent variables in the analysis. Once a valid billing regression model was obtained for a site, a sensitivity analysis was performed to use only relevant variables in the analysis, and the statistical validity of the model was tested. Estimated savings were then determined by comparing post installation billing data to the baseline estimated billing obtained from the billing regression model.

## Billing Regression Results

Table 8 shows the results of the billing regression analyses effort.

Table 8:  Billing Regression Analysis Results

| Account ID | Best Regression R2 | Valid Model? | # Traps Replaced | If Valid, Annual Savings (Therms) | Savings per Trap |
| --- | --- | --- | --- | --- | --- |
| Account 1 | 0.31 | No | 1 | n/a | n/a |
| Account 2 | 0.56 | No | 12 | n/a | n/a |
| Account 3 | 0.45 | No | 15 | n/a | n/a |
| Account 4 | 0.75 | Yes | 12 | 754.4 | 62.9 |
| Account 5 | 0.68 | No | 4 | n/a | n/a |
| Account 6 | 0.43 | No | 13 | n/a | n/a |
| Account 7 | 0.22 | No | 13 | n/a | n/a |
| Account 8 | 0.52 | No | 2 | n/a | n/a |
| Account 9 | 0.66 | No | 7 | n/a | n/a |
| Account 10 | 0.60 | No | 11 | n/a | n/a |

The analyses found that, for all sites except one, the billing data did not produce valid billing regression models with the available data. It is suspected that the production and operating activity at each site has such a high impact on gas usage that it was not possible to produce valid billing regression models without this data.

The one site that the billing regression resulted in a valid model had a minimally acceptable R2 value of 0.75. This site used Cooling Degree Days and Heating Degree Days with a balance point of 60 oF as independent variables. This one site had annual estimated savings of 754 Therms with twelve steam traps replaced, or 63 Therms per steam trap. Given the results of the steam trap survey that found 27% of steam traps in dry cleaners to be leaking or failed open, this site would have three leaking or failed open steam traps if it was average. The savings per leaking or failed open trap for this site would be 251 Therms. This savings per site and per trap information should be considered anecdotal since it is not based upon a valid sample of facilities and actual savings could vary greatly from this number.

Since a valid sample of baseline billing regressions was not obtained, the result of the billing regression analysis was inconclusive. The billing regression analysis may be revisited in the future if historical production and operating information can be obtained from a valid sample of commercial sites. The historical data might include monthly revenue per site, or number of items processed during each month. This data may be difficult if not impossible to obtain from the dry cleaners participating in the program as they may not keep records of production levels or revenue.

# Appendix A: Site Survey Reports

The following pages show the steam trap testing survey information collected at each dry cleaner site.