Work Paper WPSDGENRHC0023

Revision 1

San Diego Gas & Electric

Energy Efficiency Engineering

Unitary Air Cooled Commercial Air Conditioning and Heat Pump Units Under 65 kBtu/h

# At-a-Glance Summary

| Applicable Measure Codes: |  |
| --- | --- |
| Measure Description: | Measure Case 1: Unitary air cooled air conditioning (AC) or heat pump (HP) unit with cooling capacity under 65 kBtu/h, meeting minimum SEER or EER requirements Measure 2 Case (To Code): Unitary air cooled air conditioning (AC) or heat pump (HP) unit with cooling capacity under 65 kBtu/h, SEER 13 |
| Base Case Description: | Base Case 1: AC or HP unit with cooling capacity under 65 kBtu/h, SEER 13 Base Case 2 (To Code): Customer existing AC or HP unit with cooling capacity under 65 kBtu/h |
| Energy Impact Common Units: | Per ton |
| Energy Savings : | Refer to Ex-Ante Database |
| Gross Measure Cost ($/unit) | Refer to Ex-Ante Database |
| Measure Incremental Cost ($/unit): | Refer to Ex-Ante Database |
| Effective Useful Life (ID): | EUL ID HVAC-airAC EUL ID HVAC-airHP |
| Measure Application Type: | Measure 1: ROB, NEW Measure 2 (To Code): RET |
| Net-to-Gross Ratios (ID): | NonRes-sAll-mHVAC-DX-up |
| Important Comments: | Adopted SCE workpaper WPSCEHC12.3 and updated per the 2013 Title 24 Code. |

# Document Revision History

| Revision # | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 10/18/12 | Charles Harmstead/SDGE | Adopted from SCE work paper SCE13HC012, Rev 0 dated May 30, 2012 and revised on 5/16/12 to Rev 1 with scaling factors and heat pumps added. This revision included the following changes: Created SDGE workpaper number Modified Core Measures Summary Table for SDGE IOU climate zone-all measure options. Updated Costing and NTG Summary Table for all measure options Removed reference to Solution codes Revised Delivery Mechanism wording to replace Distributor with Contractor This is a third party and contractor program Added attachment 11/6/12- “Packaged, Split, Packaged Heat Pump, & Split Heat Pump” providing Energy and Demand Savings developed from DEER 2011 for SEER 14, SEER 15, SEER 16, SEER 17 air Conditioning units and heat pumps |
| 1 | 08/29/2014 | Martin Vu/RMS Energy Consulting, LLC | Adopted SCE workpaper WPSCEHC12.3 and updated per the 2013 Title 24 Code. |

# Section 1. General Measure & Baseline Data

### 1.1a Measure Description

Measure Description: Air cooled air conditioning or heat pump units with cooling capacities < 65 kBtuh, for use in non-residential buildings, meeting the minimum efficiency requirements listed in Table 2.

Base Case Description: Air cooled air conditioning units with cooling capacities < 65 kBtu/h, for use in non-residential buildings, meeting the federal minimum efficiency standard of 13 SEER.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| AC-71098 | <55kBtu/hr 14 SEER (11.6 EER/12 EER) Package/Split System Air Conditioner DX Equipment |
| AC-98037 | 55-64kBtu/hr 14 SEER (11.6 EER/12 EER) Package/Split System Air Conditioner DX Equipment |
| AC-87165 | <55kBtu/hr 15 SEER (12 EER/12.5 EER) Package/Split System Air Conditioner DX Equipment |
| AC-85741 | 55-64kBtu/hr 15 SEER (12 EER/12.5 EER) Package/Split System Air Conditioner DX Equipment |
| AC-79354 | <55kBtu/hr 16 SEER (12.4 EER/13 EER) Package/Split System Air Conditioner DX Equipment |
| AC-93613 | 55-64kBtu/hr 16 SEER (12.4 EER/13 EER) Package/Split System Air Conditioner DX Equipment |
| AC-98011 | <55kBtu/hr 17 SEER (13 EER/13.5 EER) Package/Split System Air Conditioner DX Equipment |
| AC-16981 | 55-64kBtu/hr 17 SEER (13 EER/13.5 EER) Package/Split System Air Conditioner DX Equipment |
| AC-96253 | <55kBtu/hr 18 SEER (14 EER/14 EER) Package/Split System Air Conditioner DX Equipment |
| AC-74823 | 55-64kBtu/hr 18 SEER (14 EER/14 EER) Package/Split System Air Conditioner DX Equipment |
| AC-40394 | <55kBtu/hr 14 SEER (11.6 EER/12 EER) Heat Pump |
| AC-19661 | 55-64kBtu/hr 14 SEER (11.6 EER/12 EER) Heat Pump |
| AC-38463 | <55kBtu/hr 14.5 SEER (12 EER/12.5 EER) Heat Pump |
| AC-59802 | 55-64kBtu/hr 14.5 SEER (12 EER/12.5 EER) Heat Pump |
| AC-68505 | <55kBtu/hr 15 SEER (12 EER/12.5 EER) Heat Pump |
| AC-30431 | 55-64kBtu/hr 15 SEER (12 EER/12.5 EER) Heat Pump |
| AC-89113 | <55kBtu/hr 16 SEER (12.4 EER/13 EER) Heat Pump |
| AC-32647 | 55-64kBtu/hr 16 SEER (12.4 EER/13 EER) Heat Pump |
| AC-10277 | <55kBtu/hr 17 SEER (13 EER/13.5 EER) Heat Pump |
| AC-46126 | 55-64kBtu/hr 17 SEER (13 EER/13.5 EER) Heat Pump |
| AC-59791 | <55kBtu/hr 18 SEER (14 EER/14 EER) Heat Pump |
| AC-16146 | 55-64kBtu/hr 18 SEER (14 EER/14 EER) Heat Pump |
| AC-80742 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment |
| AC-14070 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment |
| AC-99735 | <55kBtu/hr To Code Savings Portion Heat Pump |
| AC-35797 | 55-64kBtu/hr To Code Savings Portion Heat Pump |

## 1.1b Technical Description

A unitary system is an air conditioning system that cools one or a few spaces, in contrast to a centralized system where a chiller serves most or all of the building. Unitary systems use direct expansion, are usually factory designed, and are available as packaged or split systems for commercial use. A split system consists of an indoor unit (fan, cooling coil, heating elements, filter) connected by refrigerant piping to an outdoor unit (fan, compressor, condenser, expansion valve). A packaged system incorporates all the equipment into a single unit that is typically mounted on the roof. Heat pumps allow the refrigeration cycle to run in reverse and can therefore provide heating or cooling to the conditioned space.

### 1.1c Delivery and Incentive Mechanism

The delivery method is Upstream Programs – Up-Stream Incentive. Incentives are provided to the HVAC equipment distributor, who provides site installation information for each unit.

The install type for the Upstream Prescriptive rebate is Replace-On Burnout (ROB) and New Construction (NEW). Additionally, an early retirement measure will also be offered through the HVAC optimization program as Retrofit (RET). In this delivery approach, units identified through the HVAC optimization program as still functional, but needing replacement, will be retired prematurely. The program will provide incentives to the contractor for this to occur.

### 1.1d Measure Requirements

For early retirement offerings, identified as “To Code Savings Portion,” within this work paper:

- The HVAC Early Retirement will utilize the CPUC’s Early Retirement (ER) Savings methodology, but only claim the portion of savings that remain after the Replace on Burnout (ROB) savings is claimed by Upstream Program.

- Initial leads for the program will be generated from participants in the Quality Maintenance (QM) and Quality Renovation (QR) Programs. Maintenance records and analyses performed for the QM and QR program will be collected to help verify unit operation. Additional information on existing EER and operating efficiency may be collected on some applications to help document the existing baseline.

- Program requirement including pre-inspection and verification are in place to ensure that equipment is Early Retirement (ER, previously RET) and ROB or New Construction (NEW). The program will require pre-inspections on 75% of installations for the first 3 months, but target a 100% inspection rate. Pre-inspections will inspect nameplate information such as manufacturing year, visual verification of unit operation, or perform verification readings including: amperage, supply air temperature, outdoor air temperature, and mixed air temperature. After 3 months, the program will adjust the inspection percentage based on the pass-fail rates. Two rebates will be paid for Early Retirement Installation, but savings will only be claimed once.

- Certain evidence must be provided to participate in this program, including:

  - Pre-inspection data to evaluate that the units are still operating

  - Customer statement that the existing equipment is still in proper working condition and will continue to operate at least one year

- The evidence below will be asked to be provided by the contractor or customer, but because it may not always be available, will not be a requirement for program participation:

  - Make, model and serial number of existing equipment

  - Records of ongoing equipment maintenance and performance

  - Existing equipment installation dates and invoices

- The above evidence, any other evidence, and the sampling rate of this evidence, will be used to demonstrate the preponderance of evidence of program-induced early retirement through ongoing EM&V coordination. Other evidence may include emails, notes, and customer statements that help demonstrate evidence of how the early retirement program accelerated the early retirement of the existing unit and if any additional drivers other than energy efficiency helped influence the decision for early retirement.

Efficiency Requirements

The minimum tier efficiency requirements are listed in Table 2. Tier 1 and 2 specifications are derived from the Tier 1 and 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 3, 4, and 5 have been added to promote higher efficiency units offered by the HVAC industry.

Table 2 Minimum Efficiency Requirements

|  | Program Tier | Minimum SEER | Minimum EER |
| --- | --- | --- | --- |
| Packaged Air Conditioner | Min. Title 24 | 13.0 | 10.8 |
|  | Tier 1 | 14.0 | 11.6 |
|  |  | 14.5 | 12.0 |
|  | Tier 2 | 15.0 | 12.0 |
|  | Tier 3 | 16.0 | 12.4 |
|  | Tier 4 | 17.0 | 13.0 |
|  | Tier 5 | 18.0 | 14.0 |
| Split System Air Conditioner | Min. Title 24 | 13.0 | 10.8 |
|  | Tier 1 | 14.0 | 12.0 |
|  |  | 14.5 | 12.0 |
|  | Tier 2 | 15.0 | 12.5 |
|  | Tier 3 | 16.0 | 13.0 |
|  | Tier 4 | 17.0 | 13.5 |
|  | Tier 5 | 18.0 | 14.0 |
| Packaged Air Cooled Heat Pump | Min. Title 24 | 13.0 | 10.8 |
|  | Tier 1 | 14.0 | 11.6 |
|  |  | 14.5 | 12.0 |
|  | Tier 2 | 15.0 | 12.0 |
|  | Tier 3 | 16.0 | 12.4 |
|  | Tier 4 | 17.0 | 13.0 |
|  | Tier 5 | 18.0 | 14.0 |
| Split System Air Cooled Heat Pump | Min. Title 24 | 13.0 | 10.8 |
|  | Tier 1 | 14.0 | 12.0 |
|  |  | 14.5 | 12.0 |
|  | Tier 2 | 15.0 | 12.5 |
|  | Tier 3 | 16.0 | 13.0 |
|  | Tier 4 | 17.0 | 13.5 |
|  | Tier 5 | 18.0 | 14.0 |

In order to qualify for the program, units must meet either the SEER or EER requirement; units are not required to meet both specifications.

Eligibility Requirements

- All unitary DX equipment is eligible. Central systems and DHW systems are not eligible.

- Replacement must be like for like: HP for HP; AC-only for AC-only.

- Specifically under the Early Retirement program applicability, only contractors actively participating in the HVAC Optimization Program are allowed to participate in this Program.  Part of the application process will include verification procedures for ensuring that equipment is installed and operational.

- Retrofitted HVAC equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR contractor must provide a load calculation verifying that the new unit is sized correctly for the load.

- All non-residential building types and vintages are eligible for the upstream rebate.

### 1.2  DEER Differences Analysis

The Database for Energy Efficient Resources (DEER) Version 2014 includes measure for split and packaged commercial AC units <55 kBtu/h and 55-64 kBtu/h up to 14 SEER, but not 15, 16, 17, or 18 SEER. DEER also contains 14 and 15 SEER packaged heat pumps and 14.5 and 15 SEER split heat pumps <55 kBtu/h or 55-64 kBtu/h, but it does not contain 15, 16, 17, or 18 SEER heat pumps. These DEER measures were scaled to estimate savings for 15, 16, 17 and 18 SEER savings.

Table 3 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | Yes |
| Scaled DEER Measure | Yes |
| DEER Building Prototypes Used | No |
| Deviation from DEER | Scaling factors are developed to determine savings for measures not in DEER. |
| DEER Version | DEER 2014 v2.0.1 |
| DEER Run ID and Measure Name (Sample) | NE-HVAC-airAC-Pkg-lt55kBtuh-14p0seer NE-HVAC-airHP-Pkg-lt55kBtuh-14p0seer-8p0hspf |

READi Technology Fields

To support the development of the ED ex ante tables, select fields from the ex ante database will be identified in the workpaper. For a full set of values associated with the measures in the workpaper refer the Excel calculation template.

Table 4 READi Tech IDs

| READi Field Name | Values included in this workpaper |
| --- | --- |
| Measue Case UseCategory | HVAC |
| Measure Case UseSubCats | Space Cooling, Space Heating and Cooling |
| Measure Case TechGroups | dX AC Equipment, dx HP Equipment |
| Measure Case TechTypes | SEER Rated Split System AC, SEER Rated Split System HP |
| Base Case TechGroups | dX AC Equipment, dx HP Equipment |
| Base Case TechTypes | SEER Rated Split System AC, SEER Rated Split System HP |

## 1.3  Code Analysis

### Code of Federal Regulations (10 CFR 430.32(c)):

Per Federal Register technical amendment to the Code of Federal Regulations [393], the SEER 13 standard will apply to conventional [single phase] central air conditioners manufactured on or after January 23, 2006, and before January 1, 2015:

### EISA 2007 (42 USC 6313 & 42 USC 17001):

On December 19, 2007, federal code 42 USC 17001 known as the ‘Energy Independence and Security Act of 2007’ [427] was enacted which in part modified 42 USC 6313 as follows:

``(D) For equipment manufactured on or after the later of January 1, 2008, or the date that is 180 days after the date of enactment of the Energy Independence and Security Act of 2007—

[NOTE: As 42 USC 17001 was enacted as Public Law No: 110-140 Dec 19, 2007, adding 180 days means paragraph (D) became effective on June 16, 2008.]

``(i) the minimum seasonal energy efficiency ratio of air-cooled 3-phase electric central air conditioners and central air conditioning heat pumps less than 65,000 Btu per hour (cooling capacity), split systems, shall be 13.0;

``(ii) the minimum seasonal energy efficiency ratio of air-cooled 3-phase electric central air conditioners and central air conditioning heat pumps less than 65,000 Btu per hour (cooling capacity), single package, shall be 13.0;

``(iii) the minimum heating seasonal performance factor of air-cooled 3-phase electric central air conditioning heat pumps less than 65,000 Btu per hour (cooling capacity), split systems, shall be 7.7; and

``(iv) the minimum heating seasonal performance factor of air-cooled 3-phase electric central air conditioning heat pumps less than 65,000 Btu per hour (cooling capacity), single package, shall be 7.7.'';

### California Title 20 2014:

Appliance Efficiency Regulations [422] under California Code of Regulations Title 20, Section 1605.1 (c) (1) states “The EER, SEER, COP, HSPF, and SCOP, as applicable, of all central air conditioners, including computer room air conditioners, shall be not less than the applicable values shown in Tables C-2, C-3, C-4, C-5, and C-6.”

### California Title 24 2013:

Title 24 [355] does not address the measures in this work paper; it provides requirements for unitary AC and HP units ≥ 65k Btu/h

Table 5 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Code of Federal Regulations | 10 CFR 430.32 Conventional [single phase] central air conditioners | January 23, 2006 |
| EISA 2007 | Air-cooled 3-phase electric central air conditioners and central air conditioning heat pumps less than 65,000 Btu per hour, single package | June 16, 2008 |
| Title 20 (2014) | Central Air Conditioners Other than Water-Source Heat Pumps Below 240,000 Btu/hr | January 23, 2006 |

## 1.4  Measure Effective Useful Life

Refer to the Ex-Ante Database for the EUL values.

Table 6 EUL Value/Methodology

| EUL ID | Market | Enduse | Measure |
| --- | --- | --- | --- |
| HVAC-airAC HVAC-airHP | Non-Residential | HVAC – Split/Package | Air Conditioners / Heat Pumps (split and unitary) |

## 1.5  Net-to-Gross Ratios for Different Program Strategies

Refer to the Ex-Ante Database for the NTG values.

Table 7 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID |
| --- | --- | --- | --- | --- |
| NonRes-sAll-mHVAC-DX-up | All package and split system AC & HP replacements | Com | Com | PreRebUp |

## 1.6  Time-of-Use Adjustment Factor

As directed by the CPUC in decision 06-06-063 dated June 29, 2006, time-of-use (TOU) adjustment factors are to be applied for residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only.   Since this is an A/C measure, the TOU adjustment factor is 100.  Additionally, if a measure is assigned a DEER08 load shape, i.e. the load shape starts with “DEER:” the TOU assigned to that measure should also be zero.

Table 8 TOU Summary Table

| Measure | % |
| --- | --- |
| All package and split system AC & HP replacements | 100 |

# Section 2. Energy Savings & Demand Reduction Calculations

## 2.1  Energy Savings & Demand Reduction Calculations

DEER 2014 contains the following measures that are relevant to this work paper:

- SEER 14 Commercial AC, for size ranges <55 kBtu/h and 55-64 kBtu/h, packaged and split

- SEER 14 (packaged only), 14.5 (split only), 15 (packaged and split) Commercial Heat Pump, for size ranges <55 kBtu/h and 55-64 kBtu/h

  - Note: Some of the DEER heat pump savings are negative for certain climate zones.

- SEER 14, 15, 16, 17, 18 Residential AC, split only

- SEER 14, 15, 16 Residential HP

If a measure was available from DEER, the DEER savings were used. The following measures were not available, so their savings were calculated by scaling existing DEER measures:

- SEER 15, 16, 17, 18 Commercial AC, for size ranges <55 kBtu/h and 55-64 kBtu/h

- SEER 16, 17, 18 Commercial Heat Pump, for size ranges <55 kBtu/h and 55-64 kBtu/h

Scaling Factors

The DEER residential AC measures are used to scale the commercial measures. It is assumed that the ratio of savings between a SEER 15 and SEER 14 residential AC unit is the same as it is for commercial AC units. This assumption is extended (i.e. ratios of 16 to 14 SEER, 17 to 14 SEER, and 18 to 14 SEER are the same for residential and commercial) in order to develop estimates for all measures in this work paper.

Example: SEER 15 commercial AC unit, Assembly building type, climate zone 6, < 55k BTU/h:

SEER 14 Residential Split AC kWh Savings Above Code (average of SFM, MFM, DMO) = 13.53

SEER 15 Residential Split AC kWh Savings Above Code (average of SFM, MFM, DMO) = 29.70

Scaling Factor = 29.70 / 13.53 = 2.19458

SEER 14 Commercial AC kWh Savings Above Code (average of split and packaged) = 286

SEER 15 Commercial AC Scaled DEER kWh Savings Above Code

= 14 SEER Commercial AC kWh Savings * Scaling Factor

= 286 * 2.19458

= 627.65

Table 9 shows sample scaling factors for climate zone 6. Note that since only up to SEER 16 residential HP measures were available in DEER, the 17 and 18 SEER commercial HP measures used the AC scaling factors.

Table 9 Sample Scaling Factors

| System | SEER | kWh/ton savings | kW/ton savings | Therms/ton savings | kWh Scaling Factor | kW Scaling Factor | Therms Scaling Factor | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| AC | 14 | 13.53 | 0.00630 | -0.274 | 1.00 | 1.00 | 1.00 | No scaling; in DEER already. |
| AC | 15 | 29.70 | 0.01361 | -0.500 | 2.19 | 2.16 | 1.82 | Scales off of SEER 14 AC. |
| AC | 16 | 20.97 | 0.00850 | -0.290 | 1.55 | 1.35 | 1.06 | Scales off of SEER 14 AC. |
| AC | 17 | 41.00 | 0.01913 | -0.552 | 3.03 | 3.04 | 2.01 | Scales off of SEER 14 AC. |
| AC | 18 | 47.93 | 0.02577 | -0.485 | 3.54 | 4.09 | 1.77 | Scales off of SEER 14 AC. |
| HP | 14 | 48.30 | 0.00536 | 0.00 | 1.00 | 1.00 | 1.00 | No scaling; in DEER already. |
| HP | 14.5 | N/A | N/A | N/A | 1.00 | 1.00 | 1.00 | No scaling; in DEER already. |
| HP | 15 | 93.07 | 0.02179 | 0.011 | 1.00 | 1.00 | 1.00 | No scaling; in DEER already. |
| HP | 16 | 118.87 | 0.01250 | 0.015 | 1.28 | 0.57 | 1.31 | Scales off of SEER 15 HP. |
| HP | 17 | N/A | N/A | N/A | 3.03 | 3.04 | 2.01 | Same as SEER 17 AC factor. |
| HP | 18 | N/A | N/A | N/A | 3.54 | 4.09 | 1.77 | Same as SEER 18 AC factor. |

All measure savings are listed in the ex-ante database.

Discussion of Scaling Factors

The scaling approach assumes that residential split AC units scale similarly to commercial units. It also assumes that the EER values for residential split AC units are the same as for commercial units.

Data from the AHRI and from the 2010-2012 SCE and PG&E Program show that the EER values for SEER 16 and 17 three phase commercial package units (99% of the units submitted under this measure) are much higher than the EER values modeled in the residential HVAC measures. The average EER of SEER 14, 15, 16, and 17 three phase package AC units from AHRI and the 2010-2012 SCE and PG&E Program are compared to the average EER for DEER residential split AC measures in Table 10.

Table 10 Average EER Values of Three Phase Packaged Commercial AC Units

| SEER | Average EER for 3 Phase Package AC <65kBtuh in AHRI database | Average EER for 3 Phase Package and Split AC <65kBtuh in 2010-2012 PG&E and SCE Upstream HVAC Program | Average EER for DEER Residential Split AC Measures |
| --- | --- | --- | --- |
| 14-14.99 | 12.02 | 11.93 | 12.15 |
| 15-15.99 | 12.52 | 12.73 | 12.72 |
| 16-16.99 | 13.07 | 13.83 | 11.61 |
| 17+ | 13.23 | 12.66 | 12.28 |

The EER values for the DEER residential measures are significantly lower than values found in both the program data and the AHRI database for SEER 16 and 17 measures. Because the residential scaling factor is used, the SEER 16 and 17 AC units may actually have lower savings and less demand reduction than SEER 15 units.

In addition to higher SEER residential units having lower EERs, residential savings load shapes are different from commercial load shapes. Commercial building are highly dependent on internal loads and operate on three phase power, while residential systems are much more dependent on the building shell than on internal loads and operate on single phase power.  Furthermore, residential buildings have far fewer annual run time hours, which leads to less total savings, and are often unoccupied during peak hours. This fundamental difference in the operation of the air conditioning systems makes it unlikely that the scaling ratio of residential savings can accurately describe the scaling ratio for commercial savings.

Ultimately these higher SEER units should be modeled in eQUEST and added to the DEER database.  This will allow programs to accurately claim savings for higher SEER units, and enable programs to effectively promote higher SEER commercial AC units. Until these units are modeled, scaling factors must be used to estimate savings.  The residential scaling factors derived above do not accurately represent savings for commercial units. In place of the residential scaling factor, it is recommended that a scaling factor is derived by taking the ratio of commercial unit’s seasonal and full load kW/ton ratings as outlined below.

EER Energy Efficiency Ratio and SEER, the Seasonal Energy Efficiency Ratio, are expressed in units of Btu/Watt-hour. This can be converted into kW/ton using the following equation:

kW/ton = 12/(Btuh/watt)

Therefore EER or SEER could be expressed in terms of kW/ton. The table below shows the equivalent kW/ton values for SEER ratings. As the equipment is less than 65 kBtu/hr, SEER is used rather than EER.

Table 11 Equivalent kW/ton Values for SEER Ratings

| SEER | kW/ton |
| --- | --- |
| 13 | 0.923 |
| 14 | 0.857 |
| 15 | 0.800 |
| 16 | 0.750 |
| 17 | 0.706 |
| 18 | 0.667 |

The difference in kW/ton per SEER is lowered as SEER values get higher. This can be seen in Figure 1.

Figure 1. EER vs Delta kW/ton over SEER 13 Baseline

As defined by AHRI 210-240 SEER is “The total heat removed from the conditioned space during the annual cooling season, expressed in Btu’s, divided by the total electrical energy consumed by the air conditioner or heat pump during the same season, expressed in watt-hours” [435].  Therefore, SEER represents the average kW/ton of an AC or HP unit over the course of an entire cooling season, or the average annual kW/ton.

Using SEER values the predicted energy savings between a SEER 14 AC unit and a SEER 13 AC unit would be the difference in kW/ton multiplied by the Annual Cooling Hours.

SEER 14 predicted savings	= (12/13 SEER – 12/14 SEER) * Annual Cooling Hours

= (0.923 - 0.857) * Annual Cooling Hours

= (0.066) * Annual Cooling Hours

The predicted savings between a SEER 15 AC unit and a SEER 13 AC unit would be as follows:

SEER 15 predicted savings	= (12/13 SEER – 12/15 SEER) * Annual Cooling Hours

= (0.923 - 0.800) * Annual Cooling Hours

= (0.123) * Annual Cooling Hours

Therefore the ratio of predicted saving between a SEER 15 and 14 AC would be 0.123/0.066 = 1.86.

This ratio of predicted savings could be applied to the 14 SEER savings in DEER to estimate savings for SEER 15, 16, 17 and 18 equipment. For example:

Estimated SEER 15 savings	= SEER 14 Savings (from DEER) * (Difference in average annual kW/ton between a SEER 15 and 13 AC unit/ Difference in average annual kW/ton between a SEER 15 and 13 AC unit)

= SEER 14 Savings (from DEER) * (0.123/0.066)

= SEER 14 Savings (from DEER) * 1.86

This same scaling factor can be derived for SEER 16, 17, and 18 AC units to scale energy savings. The recommended scaling factors for energy savings are shown in Table 12.

Table 12 Recommended Energy Scaling Factor for SEER 15, 16, 17, and 18 Commercial AC Units

| SEER | kW/ton | Difference in kW/ton over SEER 13 unit | Energy Scaling Factor |
| --- | --- | --- | --- |
| 13 | 0.923 | 0 | 0 |
| 14 | 0.857 | 0.066 | 1 |
| 15 | 0.800 | 0.123 | 1.86 |
| 16 | 0.750 | 0.173 | 2.62 |
| 17 | 0.706 | 0.217 | 3.29 |
| 18 | 0.667 | .256 | 3.88 |

The same methodology can be applied to the average EER values to predict demand reduction.  The AHRI condition for testing EER for unitary AC units represents the btuh/Wh of a unit operating at an outdoor dry bulb temperate of 95 degrees. This rating system was developed to estimate the average btuh/Wh of a unit during peak loading conditions. As with SEER, EER can also be expressed in terms of kW/ton. Using the average EER values from AHRI, the EER and kW/ton of 14, 15, 16, 17+ SEER equipment can be derived. These values can then be used to determine the scaling factor for demand reduction. The recommended demand scaling factors for Three Phase Commercial AC units are shown in Table 13.

Table 13 Recommended Demand Scaling Factor for SEER 14 to 17+ Three Phase Package Commercial AC Units

| SEER | EER used in DEER 2011 for Commercial 3 Phase Package AC <65kBtuh | Average EER for 3 Phase Package AC <65kBtuh in AHRI database | Average kW/ton for 3 Phase Package AC <65kBtuh in AHRI database | Difference in kW/ton (Compared to SEER 13 Unit) | Demand Scaling Factor |
| --- | --- | --- | --- | --- | --- |
| 13-13.99 | 11.04 | 11.16 | 1.075 | 0 |  |
| 14-14.99 | 12.04 | 12.02 | 0.998 | 0.077 | 1.000 |
| 15-15.99 |  | 12.52 | 0.959 | 0.116 | 1.508 |
| 16-16.99 |  | 13.07 | 0.918 | 0.157 | 2.041 |
| 17+ |  | 13.23 | 0.907 | 0.168 | 2.185 |

This delta kW/ton scaling method enables the use of SEER and EER rating that are reflective of the equipment in the program and can more accurately represent the savings of commercial measures until DEER include the higher SEER rated measures for commercial AC units.

To Code Savings Portion Measures

The “To Code Savings Portion” measures in this work paper are savings from retrofitting customer existing equipment (various SEER values) to SEER 13 code-compliant equipment. The savings are taken directly from DEER as the Above Customer Existing savings for SEER 13 AC or HP units. These RET savings are attributed to the early retirement mechanism, while savings from any of the ROB/NEW measures for SEER 14 or higher equipment are attributed to the Upstream HVAC program.

## 2.2  Gross Savings Installation Adjustment

For all the savings discussed above, there is an installation rate applied to values associated with the installation GSIA ID in Table 14. The GSIA ID is identified in the ex-ante implementation tables for all programs and measures. The installation rate (IR) is applied to the gross savings calculations using the values associated with the IDs below.

Table 14 Gross Savings Installation Adjustment (GSIA) IDs

| GSIA_ID | Description | Sector | BldgType | UseCategory | TechType |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Non-Res | Any | HVAC | SEER Rated Split System AC, SEER Rated Split System HP |

Spillage Rate

Spillage rate will also be applied to measures however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available. Therefore, the closest load shape chosen for this measure is the DEER:HVAC_Split-Package_AC and DEER: HVAC_Split-Package_HP load shapes. See Table 15 for a list of all Building Types and Load Shapes. See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 15 Building Types and Load Shapes

| Building Type | Load Shape |
| --- | --- |
| Any | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

DEER 2008 provided costs for several AC units but not HP units, so DEER 2005 was used for HP cost; see Table 16. These costs are per Cooling Ton.

Table 16 DEER Cost Data

| Cost Case Description | DEER Cost Case ID | Material Cost | Labor Cost |
| --- | --- | --- | --- |
| 13 SEER (11.09 EER) Package Air Conditioner - Single Phase | airAC-Pkg-lt65kBtuh 1phs-13p0seer | $950.10 | $357.73 |
| 13 SEER (11.09 EER) Three Phase Package A/C – Three Phase | airAC-Pkg-lt65kBtuh 3phs-13p0seer | $980.70 | $357.73 |
| 14 SEER(12.15 EER) Package Air Conditioner | airAC-Pkg-lt65kBtuh 1phs-14p0seer | $1,063.20 | $357.73 |
| 9.7 SEER Package Air Conditioner | airAC-Pkg-lt65kBtuh3phs-9p7seer | $645.60 | $357.73 |
| 13 SEER (7.7 HPSF) Three Phase Package HP | D03-113 | $959.29 | $459.88 |
| 12 SEER (7.4 HSPF) Three Phase Package HP | D03-112 | $906.94 | $459.88 |
| 9.7 SEER (6.6 HSPF) HP (varies by vintage) | D03-112, D03-113 | $802.25 | $459.88 |

The material costs for the two SEER 13.0 units were averaged to determine a base case material cost for SEER 13:

SEER 13 AC Cost = ($950.10 + $980.70) / 2 = $965.40

## 4.2 Gross Measure Cost

DEER only provides cost data for up to SEER 14 units for ACs and up to SEER 13 units for HPs. For higher SEER units, the difference in costs for lower units are scaled to predict higher SEER costs. For example, for the SEER 15 unit, the difference between the SEER 13 and 14 units is used to extrapolate the SEER 15 price:

SEER 15 AC Cost = $1063.20 + ($1063.20 - $965.40) = $1161.00

The same methodology is used to calculate measure costs for the rest of the measures; see Table 17

For ROB, GMC is represented by the equation below:

GMC = Measure Equipment Cost – Base Case Equipment Cost

For RET, GMC is represented by the equation below:

GMC = Measure Equipment Cost + Measure Labor Cost

For all RET measures contained within this work paper, the costs shown are derived per the methodology above. The only difference, however, is that the values reported are the RET minus ROB costs, i.e. 1st baseline costs minus 2nd baseline costs, which will prevent the double counting of 2nd baseline costs with the Upstream HVAC program. The ROB costs will be reported in the upstream HVAC program, and the RET minus ROB costs will be reported for the early retirement mechanism.

Table 17 Cost Table

| Measure | Base Case Cost | Base Labor Cost | Measure Cost | Measure Labor Cost | GMC | IMC |
| --- | --- | --- | --- | --- | --- | --- |
| 14 SEER AC | $965.40 | $357.73 | $1,063.20 | $357.73 | $97.80 | $97.80 |
| 15 SEER AC | $965.40 | $357.73 | $1,161.00 | $357.73 | $195.60 | $195.60 |
| 16 SEER AC | $965.40 | $357.73 | $1,258.80 | $357.73 | $293.40 | $293.40 |
| 17 SEER AC | $965.40 | $357.73 | $1,356.60 | $357.73 | $391.20 | $391.20 |
| 18 SEER AC | $965.40 | $357.73 | $1,454.40 | $357.73 | $489.00 | $489.00 |
| 14 SEER HP | $959.29 | $459.88 | $1,011.64 | $459.88 | $52.35 | $52.35 |
| 14.5 SEER HP | $959.29 | $459.88 | $1,037.82 | $459.88 | $78.53 | $78.53 |
| 15 SEER HP | $959.29 | $459.88 | $1,063.99 | $459.88 | $104.70 | $104.70 |
| 16 SEER HP | $959.29 | $459.88 | $1,116.34 | $459.88 | $157.05 | $157.05 |
| 17 SEER HP | $959.29 | $459.88 | $1,168.69 | $459.88 | $209.40 | $209.40 |
| 18 SEER HP | $959.29 | $459.88 | $1,221.04 | $459.88 | $261.75 | $261.75 |
| To Code AC Portion | $645.60 | $357.73 | $965.40 | $357.73 | $1,323.13 | $0.00 |
| To Code HP Portion | $802.25 | $459.88 | $959.29 | $459.88 | $1,419.17 | $0.00 |

## 4.3 Incremental Measure Cost

For ROB, the Gross Measure Cost and Incremental Measure Cost are the same; see Table 17.

For the RET measures, as per the comment in Section 4.3.1 about double counting the costs, the Incremental measure cost is equal to zero. Please refer to ex-ante database for all cost calculations.

# Attachments

1.

2.

# References