Work Paper WPSDGENRLG0025

Revision 0

San Diego Gas & Electric

Energy Efficiency Engineering

Linear Fluorescent Dimming Ballasts

### Core Measure Summary Table

| General Measure Information |  |  |  |  |  |  |  | PT |  | 1st Baseline Period |  |  |  | 2nd Baseline Period |  |  |  | TOU |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Measure RunID | Solution Code | CZ | Building Type | Load Shape | EUL | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | Gross Unit Annual Electricity Savings (kWh/unit) | User Entered kW Savings per unit (kW/unit) | Gas Savings (Therms) | 1st Baseline Useful Life | kWh Saving per unit (kWh/unit) | kW Savings per unit (kW/unit) | Gas Savings (Therms) | 2nd Baseline Useful Life | % TOU |
| Dimming Ballasts – 20% Tuning | To be exported by MMDB |  | 06 | Education - Primary School | DayLt & Controls | 8.0 | Ballast | RET | No | 29.52 | 0.00020 | -0.094 | 2.7 | 29.52 | 0.00020 | -0.094 | 5.3 | 0.00 |
| Dimming Ballasts – 20% Tuning | To be exported by MMDB |  | 08 | Education - Primary School | DayLt & Controls | 8.0 | Ballast | RET | No | 29.82 | 0.00805 | -0.085 | 2.7 | 29.82 | 0.00805 | -0.085 | 5.3 | 0.00 |
| Dimming Ballasts – 20% Tuning | To be exported by MMDB |  | 09 | Education - Primary School | DayLt & Controls | 8.0 | Ballast | RET | No | 29.88 | 0.00020 | -0.083 | 2.7 | 29.88 | 0.00020 | -0.083 | 5.3 | 0.00 |
| Dimming Ballasts – 20% Tuning | To be exported by MMDB |  | 10 | Education - Primary School | DayLt & Controls | 8.0 | Ballast | RET | No | 28.75 | 0.00020 | -0.103 | 2.7 | 28.75 | 0.00020 | -0.103 | 5.3 | 0.00 |
| Dimming Ballasts – 20% Tuning | To be exported by MMDB |  | 13 | Education - Primary School | DayLt & Controls | 8.0 | Ballast | RET | No | 28.38 | 0.00020 | -0.167 | 2.7 | 28.38 | 0.00020 | -0.167 | 5.3 | 0.00 |
| Dimming Ballasts – 20% Tuning | To be exported by MMDB |  | 14 | Education - Primary School | DayLt & Controls | 8.0 | Ballast | RET | No | 27.52 | 0.00020 | -0.207 | 2.7 | 27.52 | 0.00020 | -0.207 | 5.3 | 0.00 |
| Dimming Ballasts – 20% Tuning | To be exported by MMDB |  | 15 | Education - Primary School | DayLt & Controls | 8.0 | Ballast | RET | No | 30.46 | 0.00020 | -0.036 | 2.7 | 30.46 | 0.00020 | -0.036 | 5.3 | 0.00 |
| Dimming Ballasts – 20% Tuning | To be exported by MMDB |  | 16 | Education - Primary School | DayLt & Controls | 8.0 | Ballast | RET | No | 24.42 | 0.00020 | -0.447 | 2.7 | 24.42 | 0.00020 | -0.447 | 5.3 | 0.00 |

Note: For the complete list of Measures, refer to Attachment 5 “Dimmable Ballast Worksheet.xlsx” for San Diego Climate zones and SDGE Workpaper WPSDGENRLG0999 NonRes Master Lighting Lookup Table

### Costing and NTG Summary Table

| General Measure Information |  |  |  | PT |  | NTG |  |  | IR | 1st Baseline Period | 2nd Baseline Period | IMC | DIM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Solution Code | CZ | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | NTG Non-Res. | NTG Res. | NTG Multi Family | NTG Non-Res. | Gross Measure Cost per unit | Gross Measure Cost per unit | Incremental Measure Cost per unit | Delivery & Incentive Method |
| Dimming Ballasts – 20% Tuning |  | 06 | Ballast | RET | No | 0.60 | N/A | N/A | 0.950 | $61.02 | $41.77 | $41.77 | Financial Support / Down-Stream Incentive - Deemed |
| Dimming Ballasts – 20% Tuning |  | 08 | Ballast | RET | No | 0.60 | N/A | N/A | 0.950 | $65.65 | $44.94 | $44.94 | Financial Support / Down-Stream Incentive - Deemed |
| Dimming Ballasts – 20% Tuning |  | 09 | Ballast | RET | No | 0.60 | N/A | N/A | 0.950 | $67.54 | $46.23 | $46.23 | Financial Support / Down-Stream Incentive - Deemed |
| Dimming Ballasts – 20% Tuning |  | 10 | Ballast | RET | No | 0.60 | N/A | N/A | 0.950 | $63.41 | $43.40 | $43.40 | Financial Support / Down-Stream Incentive - Deemed |
| Dimming Ballasts – 20% Tuning |  | 13 | Ballast | RET | No | 0.60 | N/A | N/A | 0.950 | $62.71 | $42.92 | $42.92 | Financial Support / Down-Stream Incentive - Deemed |
| Dimming Ballasts – 20% Tuning |  | 14 | Ballast | RET | No | 0.60 | N/A | N/A | 0.950 | $61.65 | $42.20 | $42.20 | Financial Support / Down-Stream Incentive - Deemed |
| Dimming Ballasts – 20% Tuning |  | 15 | Ballast | RET | No | 0.60 | N/A | N/A | 0.950 | $65.65 | $44.94 | $44.94 | Financial Support / Down-Stream Incentive - Deemed |
| Dimming Ballasts – 20% Tuning |  | 16 | Ballast | RET | No | 0.60 | N/A | N/A | 0.950 | $69.23 | $47.39 | $47.39 | Financial Support / Down-Stream Incentive - Deemed |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet and SDGE Workpaper WPSDGENRLG0999 NonRes Master Lighting Lookup Table

# Document Revision History

| Revision # | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 10/19/2012 | Charles Harmstead/SDGE | Adopted from Work Paper SCE13LG031 Revision 0, Linear Fluorescent Dimming Ballasts Dated April 11, 2012 by Jared Kruzek/AESC original work paper for 2013 PC. Revised Work paper number. Calculated whole building savings for each measure using DEER 2011 LF lighting interactive effects. See Attachment 5 |

# Section 1. General Measure & Baseline Data

## 1.1  Measure & Delivery Description

### 1.1a Measure Description

This work paper documents the energy savings associated with retrofitting T8 and T5 linear fluorescent fixtures with dimming ballasts and various control strategies. These measures save energy and reduce electric demand by controlling the operating hours and power output of linear fluorescent fixtures.

The baseline for these measures will be set as T8 and T5 linear fluorescent fixtures with non-dimming ballasts and without automatic controls.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
|  | Dimming Ballasts - 20% Tuning |
|  | Dimming Ballasts - 20% Tuning + Daylight Harvesting |
|  | Dimming Ballasts - 20% Tuning + Occupancy Sensor |
|  | Dimming Ballasts - 20% Tuning + Occupancy Sensor + Daylight Harvesting with Side Lighting Photo Controls |

The definition of each control strategy is as follows:

Dimming Ballasts: Controllable ballasts that allow the light level and power level of a lamp to be modulated based on area needs.

Tuning: Either a permanent or time-varying reduction in light output to avoid over-illumination which can be achieved by:

- A factory preset reduction in output level

- A field set permanent reduction in output level

- Photo controls for luminance maintenance

Occupancy sensors (vacancy sensors): Sensors are vacancy sensors complying with Title-24 section 119 [A]. Assume individual vacancy sensors are located over each workstation, which control all the lighting over that workstation.  If the sensor controlled only a portion of the lighting, savings would have to be de-rated accordingly.

Daylight Harvesting and Daylight Harvesting with Side Lighting Photo Controls: Daylight harvesting uses photocells to sense natural sunlight in an area and to then shut down the area lights if enough daylight is present. Savings value applies to entire day lit area, not just to primary side lit daylight area.  Savings estimate was based on Side lighting Photo controls Field Study.

### 1.1b Delivery and Incentive Mechanism

The delivery methods that are available for these measures are:

- Financial Support  / Down-Stream Incentive – Deemed

- Partnerships / Down-Stream Incentive – Deemed

- Financial Support / Direct Install

- Partnership / Direct Install

- Midstream Programs / Mid-Stream Incentive

The program/install type for the above measures is:

- Retrofit (RET)

- Replace on Burn-out (ROB)

### 1.1c Measure Requirements

- The existing fixtures must be T8 or T5 linear fluorescent fixtures with non-dimming ballasts. Existing T12 fixtures do not qualify.

- Existing controls must be bi-level switching with no other controls.

- The building type must fall into one of the categories below. This work paper only addresses these building types as these are typical buildings types where dimming ballasts are implemented and have been effective in saving energy.

  - Education – Primary: Elementary schools and religions education facilities

  - Education – Secondary: Middle schools, junior high and high schools

  - Education – Relocatable: Mobile classroom

  - Education – Community College: Community colleges, career or vocational training, adult education buildings used for classroom instruction

  - Education – University: College and university buildings used for classroom instruction

  - Office – Large: Government office, bank, city hall, social service, collectively over 100,000 square feet.

  - Office – Small: Daycare or preschool, church, contractor or sales office, collectively under 100,000 square feet

  - Retail – Multistory Large: Department stores

  - Retail – Single-story Large: Big box retail stores, dealerships or showrooms, rental centers

  - Retail – Small: Stores located in strip malls, studio, gallery

  - Miscellaneous Commercial

## 1.2  DEER Differences Analysis

The Database for Energy Efficient Resources (DEER) 2011 v4.0 [49] contains energy savings for occupancy sensors but not for dimming ballasts or daylight harvesting. Since this measure is for dimming ballasts and control strategies in combination with dimming ballasts, the DEER measures are not applicable.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | Yes |
| Deviation from DEER | DEER does not contain this type of measure. |
| DEER Version | N/A |
| DEER Run ID and Measure Name | N/A |

## 1.3  Code Analysis

Effective July 14th, 2012, multiple T12 lamp types will be impacted by the new US Department of Energy standards set for general service fluorescent lamps. Accordingly, T12 fixtures are being phased out as an eligible baseline lighting technology for the purpose of calculating energy savings for lighting retrofit projects [B]. In accordance with the requirement, all T12 fixtures are not eligible as the Base Case for this measure.

Additionally, Title 24 Section 119 lists requirements for Occupancy Sensors, Section 119(d), and for daylighting controls, Section 119(f) [A]. These requirements, however, do not affect the savings calculations for a second baseline since according to Section 149(b)1 of Title 24, “Replacement of parts of an existing luminaire, including installing a new ballast or new lamps, without replacing the entire luminaire is not an alteration subject to the requirements of Section 149(b)1” [C]. Since the existing luminaires are not being replaced as part of this measure, Title 24 code is not triggered for savings calculations purposes.

Table 3 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| US DOE Standards (2009) | DOE 10 CFR Part 30 | July 14, 2012 |
| Title 24 | Section 119(d),(f) | January 1, 2010 |

## 1.4  Measure Effective Useful Life

DEER11 documentation provides EUL and RUL information to be used for the 13-14 program cycle on www.deeresources.com. The DEER documentation “Summary of EUL-RUL Analysis for the April 2008 Update to DEER” provides the RUL value as a flat 1/3 of the EUL value.

To obtain the EUL value the DEER11 documentation, EUL_Summary_10-1-08.xls [213], was consulted. The EUL was taken from the Daylighting-controls and Occupancy Sensors measures for non-residential indoor lighting in the table which both give an EUL of 8 years. Table 4 below identifies the value/methodology used for the measures in this work paper.

This workpaper references DEER EUL_IDs ILtg-OccSens and GlazDaylt-Dayltg.

Table 4 DEER08 EUL Value/Methodology

| Market | End-use | Measure | EUL (Years) | RUL (Years) | DEER EUL_ID |
| --- | --- | --- | --- | --- | --- |
| Non-Residential | Indoor Lighting | Dimming Ballasts – 20% Tuning | 8 | 2.7 | ILtg-OccSens GlazDaylt-Dayltg |
| Non-Residential | Indoor Lighting | Dimming Ballasts - 20% Tuning + Daylight Harvesting | 8 | 2.7 | ILtg-OccSens GlazDaylt-Dayltg |
| Non-Residential | Indoor Lighting | Dimming Ballasts - 20% Tuning + Occupancy Sensor | 8 | 2.7 | ILtg-OccSens GlazDaylt-Dayltg |
| Non-Residential | Indoor Lighting | Dimming Ballasts - 20% Tuning + Occupancy Sensor + Daylight Harvesting with Side Lighting Photo Controls | 8 | 2.7 | ILtg-OccSens GlazDaylt-Dayltg |

## 1.5  Net-to-Gross Ratios for Different Program Strategies

The NTG values were obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 4 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [132]. The relevant NTGRs for these measures are shown in Table 55 below.

Table 5 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| NonRes-sAll-mLtgCtrl | Lighting controls | Com | Any | PreRebDown | 0.60 |
| NonRes-sAll-mLtgCtrl | Lighting controls | Ind | Any | PreRebDown | 0.60 |
| NonRes-sAll-mLtgCtrl | Lighting controls | Ag | Any | PreRebDown | 0.60 |
| NonRes-sAll-mLtgCtrl-htr | Lighting controls | Com | Any | DirInstall | 0.89 |
| NonRes-sAll-mLtgCtrl-htr | Lighting controls | Ind | Any | DirInstall | 0.89 |
| NonRes-sAll-mLtgCtrl-htr | Lighting controls | Ag | Any | DirInstall | 0.89 |
| All-Default<=2yrs | All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years | All | Any | All | 0.70 |

The installation rate (IR) is identified in the calculation attachment. This value is obtained from a spreadsheet created by the DEER team titled “GrossSavingsAdjustments.xlsx”. The installation rate varies by end use, sector, technology, application, and delivery method.

## Spillage rate will also be applied to measures however the values will not be tracked in the work papers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

## 1.6  Time-of-Use Adjustment Factor

As directed by the CPUC in decision 06-06-063 dated June 29, 2006, time-of-use (TOU) adjustment factors are to be applied for residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only.   Since this is not an A/C measure, the TOU adjustment factor is 0.  Additionally, if a measure is assigned a DEER08 load shape, i.e. the load shape starts with “DEER:” the TOU assigned to that measure should also be zero.

Table 6  TOU Summary Table

| Measure | % |
| --- | --- |
| Dimming Ballasts – 20% Tuning | 0 |
| Dimming Ballasts - 20% Tuning + Daylight Harvesting | 0 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor | 0 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor + Daylight Harvesting with Side Lighting Photo Controls | 0 |

# Section 2. Energy Savings & Demand Reduction Calculations

These measures save energy and reduce peak demand by reducing the power output of the fixtures with dimming ballasts and daylight harvesting. Additional savings are achieved by reducing operating hours of fixtures with occupancy sensors.

Tuning is a process where the power level of the circuit is reduced by a given percentage, in this case 20%. This is done when the light level from a fixture(s) is greater than required for a given area and can be reduced by reducing the power draw of the ballast. The 20% tuning for this paper is assumed to be a permanent change to the output level either done at the factory or in the field when the ballasts are being installed. Savings are achieved from tuning since the power draws (i.e. the kW) of each ballast is reduced by a given percentage, in this case 20%.

Four measures were evaluated in this work paper. The first measure involves the installation of dimming ballasts with 20% tuning. 20% tuning reduces the maximum power output to 80% of the ballast’s capability. The second measure combines the 20% ballast tuning with daylight harvesting (DH). Additional savings are achieved from reducing the light levels based on available daylight. The third measure combines the 20% ballast tuning with occupancy sensors (OS). Occupancy sensors provide further savings by reducing the operating hours of the fixtures. The final measure combines all three control strategies, 20% tuning, daylight harvesting, and occupancy sensors. To account for interactive effects of the modifications, savings are calculated based on the assumption that the 20% tuning will be implemented first, followed by daylight harvesting, and lastly occupancy sensors.

The Dimmable Ballast Tool in the SCE IDSM Online Application Tool (OAT) v2.8 was used to quantify the energy and demand savings, defined in terms of kWh/ballast and kW/ballast respectively, for these measures [D]. The Dimmable Ballast Tool Guide details how this tool works and the calculation methodology used [E]. This tool is a preferred calculation tool for the Statewide Customized Offering, and allows with the user to identify a baseline fixture and then calculate savings based on the proposed measure: dimming ballast with 20% tuning, dimming ballast with 20% tuning and daylight harvesting, dimming ballast with 20% tuning and occupancy sensors, or dimming ballast with 20% tuning, daylighting harvesting and occupancy sensors. For each of the four measures, the tool was run for the following building and area types:

Table 7  Building and Area Types

| Building Type | Description | Area Types |
| --- | --- | --- |
| Primary School | Elementary schools and religions education facilities | Auditorium Classroom Lecture Office |
| Secondary School | Middle schools, junior high and high schools | Auditorium Classroom Lecture Office |
| Relocatable Classroom | Mobile classroom | Auditorium Classroom Lecture Office |
| Community College | Community colleges, career or vocational training, adult education buildings used for classroom instruction | Auditorium Classroom Lecture Office |
| University | College and university buildings used for classroom instruction | Auditorium Classroom Lecture Office |
| Large Office | Government office, bank, city hall, social service, collectively over 100,000 square feet. | Conference Corridors Office |
| Small Office | Daycare or preschool, church, contractor or sales office, collectively under 100,000 square feet | Conference Corridors Office |
| Large Retail | Department stores and big box retail stores, dealerships or showrooms, rental centers | Multistory Retail Sales Multistory Retail Showroom Single-story Retail Sales Single-story Retail Showroom |
| Small Retail | Stores located in strip malls, studio, gallery | Retail Sales Retail Showroom |
| Miscellaneous Commercial | Average of small office and small retail | Small Office- Office Small Retail - Showroom Small Retail - Dining |

The building types were limited to educational, office, retail and miscellaneous commercial as these are the targeted building types for the Dimming Ballast Tool.  The area types for each building type were selected as a representative sample so that average energy and demand savings could be calculated for each building type. Because occupancy sensor savings vary by area type, a variety of area types were needed in order to calculate a meaningful average savings. The savings associated with 20% tuning and 20% tuning with daylight harvesting are not affected by room type. The energy and demands savings from each building type were then averaged in order to find an overall average savings for each measure.

Climate zone, area square footage, number of fixtures and type of fixture were held constant for all runs. The climate zone was set to ‘SCE Weighted’ since these measures are for all SCE climate zones. The area square footage and number and type of fixture were chosen so that the savings would be representative of one (1) ballast. The area was set to 75 ft2 for one (1) 4ft 2-lamp T8 fixture. The tool does not have an option for T5 fixtures. However, the selected fixture and area results in 0.79 watts/ft2.  This efficiency is reasonable as it falls between what can be expected of T5 and T8 fixtures. In this way, the calculations take into account both types of fixtures and find a reasonable average savings.

The tool does not have an explicit miscellaneous commercial building type so it was created using the average of a small office and small retail building types. The CPUC defines miscellaneous commercial as the average of small office, small retail, and sit-down restaurant. In order to calculate savings for miscellaneous commercial, the Tool results for a building type of ‘small office’ with an area type of ‘office’ was averaged with the results from a building type of ‘small retail’ with two area types, ‘showroom’ and ‘dining’.

The Dimmable Ballast Tool produces results in terms of kWh/year and kW peak demand for the base and measure cases.  Because the tool was run for one fixture, which includes only one ballast, results are presented in specific energy (kWh/ballast) and specific demand (kW/ballast). An average baseline and measure case specific energy and specific power was calculated for each measure and broken out by building type.

Specific energy savings (kWh/ballast) for each building type were calculated as the difference between the building type average base case specific energy and the building type average measure case specific energy.  Specific power savings were calculated as the difference between the building type base case specific power and the building type measure case specific power. This was done for each of the four measures and for all building types. The tables below show the energy and demand savings for each measure by building type for the First Baseline.

Table 7 20% Tuning Energy and Demand Savings

| 20% Tuning |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Baseline |  | Proposed |  | Savings |  |
|  | kW | kWh | kW | kWh | kW | kWh |
| Primary School | 0.06000 | 126.3 | 0.05000 | 101.0 | 0.01000 | 25.3 |
| Secondary School | 0.06000 | 134.5 | 0.05000 | 107.6 | 0.01000 | 26.9 |
| Relocatable Classroom | 0.06000 | 146.3 | 0.05000 | 117.1 | 0.01000 | 29.2 |
| Community College | 0.06000 | 142.8 | 0.05000 | 114.2 | 0.01000 | 28.6 |
| University | 0.06000 | 138.6 | 0.05000 | 110.9 | 0.01000 | 27.7 |
| Large Office | 0.06000 | 155.8 | 0.05000 | 124.6 | 0.01000 | 31.2 |
| Small Office | 0.06000 | 152.8 | 0.05000 | 122.2 | 0.01000 | 30.6 |
| Retail | 0.06000 | 251.9 | 0.05000 | 201.5 | 0.01000 | 50.4 |
| Small Retail | 0.06000 | 199.4 | 0.05000 | 159.5 | 0.01000 | 39.9 |
| Misc Commercial | 0.06000 | 212.4 | 0.05000 | 169.9 | 0.01000 | 42.5 |

Table 8 20% Tuning + DH Energy and Demand Savings

| 20% Tuning + DH |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Baseline |  | Proposed |  | Savings |  |
|  | kW | kWh | kW | kWh | kW | kWh |
| Primary School | 0.06000 | 126.3 | 0.03000 | 83.0 | 0.03000 | 43.3 |
| Secondary School | 0.06000 | 134.5 | 0.03000 | 89.6 | 0.03000 | 44.9 |
| Relocatable Classroom | 0.06000 | 146.3 | 0.03000 | 117.1 | 0.03000 | 47.2 |
| Community College | 0.06000 | 142.8 | 0.03000 | 96.2 | 0.03000 | 46.6 |
| University | 0.06000 | 138.6 | 0.03000 | 92.9 | 0.03000 | 45.7 |
| Large Office | 0.06000 | 155.8 | 0.04000 | 110.4 | 0.02000 | 45.4 |
| Small Office | 0.06000 | 152.8 | 0.03000 | 105.4 | 0.03000 | 47.4 |
| Retail | 0.06000 | 251.9 | 0.04000 | 190.6 | 0.02000 | 61.3 |
| Small Retail | 0.06000 | 199.4 | 0.04000 | 148.6 | 0.02000 | 50.8 |
| Misc Commercial | 0.06000 | 212.4 | 0.02333 | 157.0 | 0.03667 | 55.4 |

Table 9 20% Tuning + OS Energy and Demand Savings

| 20% Tuning + OS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Baseline |  | Proposed |  | Savings |  |
|  | kW | kWh | kW | kWh | kW | kWh |
| Primary School | 0.06000 | 126.3 | 0.05000 | 74.1 | 0.01000 | 52.2 |
| Secondary School | 0.06000 | 134.5 | 0.05000 | 78.9 | 0.01000 | 55.6 |
| Relocatable Classroom | 0.06000 | 146.3 | 0.05000 | 85.8 | 0.01000 | 60.5 |
| Community College | 0.06000 | 142.8 | 0.05000 | 83.8 | 0.01000 | 59.0 |
| University | 0.06000 | 138.6 | 0.05000 | 81.3 | 0.01000 | 57.3 |
| Large Office | 0.06000 | 155.8 | 0.05000 | 93.5 | 0.01000 | 62.3 |
| Small Office | 0.06000 | 152.8 | 0.05000 | 91.7 | 0.01000 | 61.1 |
| Retail | 0.06000 | 251.9 | 0.05000 | 171.3 | 0.01000 | 80.6 |
| Small Retail | 0.06000 | 199.4 | 0.05000 | 135.6 | 0.01000 | 63.8 |
| Misc Commercial | 0.06000 | 212.4 | 0.05000 | 135.9 | 0.01000 | 76.5 |

Table 10 20% Tuning + DH + OS Energy and Demand Savings

| 20% Tuning + DH + OS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Baseline |  | Proposed |  | Savings |  |
|  | kW | kWh | kW | kWh | kW | kWh |
| Primary School | 0.06000 | 126.3 | 0.02000 | 43.8 | 0.04000 | 82.5 |
| Secondary School | 0.06000 | 134.5 | 0.02000 | 63.4 | 0.04000 | 71.1 |
| Relocatable Classroom | 0.06000 | 146.3 | 0.02000 | 55.5 | 0.04000 | 90.8 |
| Community College | 0.06000 | 142.8 | 0.02000 | 53.5 | 0.04000 | 89.3 |
| University | 0.06000 | 138.6 | 0.02000 | 51.0 | 0.04000 | 87.6 |
| Large Office | 0.06000 | 155.8 | 0.02000 | 64.4 | 0.04000 | 91.4 |
| Small Office | 0.06000 | 152.8 | 0.02000 | 64.5 | 0.04000 | 88.3 |
| Retail | 0.06000 | 251.9 | 0.04000 | 160.3 | 0.02000 | 91.6 |
| Small Retail | 0.06000 | 199.4 | 0.04000 | 124.6 | 0.02000 | 74.8 |
| Misc Commercial | 0.06000 | 212.4 | 0.03333 | 119.6 | 0.02667 | 92.8 |

Since this is a retrofit measure, a second baseline is established using minimum efficiencies required by code or standard industry practice. However, there is no required code that is triggered for these measures and therefore, the second baseline is the same as the first. Thus, the savings for the second baseline period are identical to those listed above. Savings with interactive effects for SDGE climate zones are provided in Attachment 5,  “Dimmable Ballast Worksheet.xlsx”

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for these measures is the ‘DayLt & Controls’ load shape.  See Table 11 for a list of all Building Types and Load Shapes.

Table 11 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Education – Primary School | K-thru_12_School | DayLt & Controls |
| Education – Secondary School | K-thru_12_School | DayLt & Controls |
| Education – Relocatable Classroom | School | DayLt & Controls |
| Education – Community College | College_University | DayLt & Controls |
| Education – University | College_University | DayLt & Controls |
| Misc- Commercial | Misc._Commercial | DayLt & Controls |
| Office – Large | Large_Office | DayLt & Controls |
| Office – Small | Small_Office | DayLt & Controls |
| Retail – Multistory Large | Large_Retail_Store | DayLt & Controls |
| Retail – Single-story Large | Large_Retail_Store | DayLt & Controls |
| Retail -Small | Small_Retail_Store | DayLt & Controls |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

The dimming ballast is the only equipment in the four measure cases that constitutes a retrofit. For this reason, only a base case cost was calculated for the ballast. The occupancy sensors and daylighting controls are add-on features and as such, the base case cost is assumed to be zero. For the ballast base case cost, no information was available in the DEER database or in RSMeans. In order to establish a base equipment cost, an average cost per non-dimmable ballast was found from various online sources for an assortment of ballast types and manufacturers [F]. The average base case cost is $22.13. It is assumed that the labor cost to install non-dimmable and dimmable ballasts is the same. The basis for this assumption is that tuning is generally done at the factory based on customer specifications in which case there is no additional labor cost for the customer. Therefore, labor cost is not included in the base case cost, as it would be canceled out in calculations for gross measure cost. The table below shows the base case cost for each measure. Since only the ballast contributes to the base case cost, the cost is the same for all measures.

Table 12 Base Case Costs

| Measure name | Base Case Cost |
| --- | --- |
| Dimming Ballasts – 20% Tuning | $22.13 |
| Dimming Ballasts - 20% Tuning + Daylight Harvesting | $22.13 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor | $22.13 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor + Daylight Harvesting with Side Lighting Photo Controls | $22.13 |

## 4.2 Gross Measure Cost

A gross measure cost was found for the dimming ballasts, daylighting controls, and occupancy sensors. In order to calculate a measure cost for dimming ballasts, several online sources were consulted and averaged since no information was available in the DEER database or in RSMeans [G]. The average cost for a dimming ballast is $70.14. For occupancy sensors, the DEER Database was consulted. The cost per sensor is $47.15 for material and $44.12 for labor, which gives a measure cost of $91.27 per sensor [49]. According to DEER, each sensor controls three fixtures.  Typically, one ballast serves one fixture. Therefore, the cost per ballast is $30.42. Since the DEER database did not have cost information available for daylighting controls, 2012 RSMeans was consulted [H]. The total cost per sensor is $131.00 for material and $79.00 for labor, which gives a total measure cost of $210.00 per sensor. RSMeans does not give an estimate of how many fixtures each sensor controls. The 2013-2014 Title 24 Codes and Standards Enhancement (CASE) study on Controllable Lighting [I] includes a cost analysis on daylighting controls. The study assumes the typical number of fixtures served by daylighting controls sensors for three spaces: office, open office and reception.  For an office, the study assumes that five (5) sensors are required for five (5) fixtures. For an open office, the study assumes that two (2) sensors are required for sixteen (16)  fixtures. For a reception area, the study assumes that one (1) sensor is required for four (4) fixtures. To be conservative, the GMC for daylighting controls assumes one (1) sensor serves eight (8) fixtures, similar to the CASE study’s assumption for open offices.  Therefore, the cost per ballast for each daylight harvesting sensor is $26.25. Table 13 shows the measure case cost per measure. The cost varies for each measure depending on the included equipment.

Table 13 Measure Case Costs

| Measure Name | Measure Case Cost |
| --- | --- |
| Dimming Ballasts – 20% Tuning | $70.14 |
| Dimming Ballasts - 20% Tuning + Daylight Harvesting | $96.39 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor | $100.56 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor + Daylight Harvesting with Side Lighting Photo Controls | $126.81 |

The gross measure cost for RET depends on the baseline period. For the first baseline period, the gross measure cost is the same as the measure cost. The gross measure costs for the first baseline period are listed in Table 14.

Table 14 1st Baseline Period Gross Measure Costs

| Measure Name | Gross Measure Cost |
| --- | --- |
| Dimming Ballasts – 20% Tuning | $70.14 |
| Dimming Ballasts - 20% Tuning + Daylight Harvesting | $96.39 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor | $100.56 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor + Daylight Harvesting with Side Lighting Photo Controls | $126.81 |

The gross measure cost for ROB and the RET Second Baseline period is the difference between the measure cost and base case cost. Table 15 lists the ROB and RET Second Baseline period gross measure costs for each measure.

Table 15 2nd Baseline Period Gross Measure Costs

| Measure Name | Gross Measure Cost |
| --- | --- |
| Dimming Ballasts – 20% Tuning | $48.01 |
| Dimming Ballasts - 20% Tuning + Daylight Harvesting | $74.26 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor | $78.43 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor + Daylight Harvesting with Side Lighting Photo Controls | $104.68 |

## 4.3 Incremental Measure Cost

For ROB and RET measures, the incremental measure cost is the same as the gross measure cost from the RET Second Baseline period. Table 16 lists the incremental measure cost.

Table 16 Incremental Measure Costs

| Measure Name | Incremental Cost |
| --- | --- |
| Dimming Ballasts – 20% Tuning | $48.01 |
| Dimming Ballasts - 20% Tuning + Daylight Harvesting | $74.26 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor | $78.43 |
| Dimming Ballasts - 20% Tuning + Occupancy Sensor + Daylight Harvesting with Side Lighting Photo Controls | $104.68 |

# Attachments

1.

2.

3.

4.

5.

# References

[49]

[132]

- 2008 Building Energy Efficiency Standards. Section 119, Page 69-70. http://www.energy.ca.gov/2008publications/CEC-400-2008-001/CEC-400-2008-001-CMF.PDF.

- 2012 Statewide Customized Offering Procedures Manual For Business –  Customized 1.0 Policy http://asset.sce.com/Documents/Business%20-%20Energy%20Management%20Solutions/120215_Customized1_0Policy.pdf

- 2008 Building Energy Efficiency Standards. Section 149, Page 129. http://www.energy.ca.gov/2008publications/CEC-400-2008-001/CEC-400-2008-001-CMF.PDF.

- SCE Online Application Tool: https://www.sceonlineapp.com/

- Attachment 4. Dimmable Ballast Tool Guide. 2010.

- Base case cost PDFs

- Measure case cost

- 2012 RSMeans Electrical Cost Data. 35th Annual Edition.

- 2011 California Building Energy Efficiency Standards: Requirements for Controllable Lighting. http://www.energy.ca.gov/title24/2013standards/prerulemaking/documents/2011-04-04_workshop/review/Nonres_Controllable_Lighting.pdf