Work Paper WPSDGENRLG0026

High Performance Linear

Fluorescent Fixtures

Revision # 0

San Diego Gas & Electric Company

Energy Efficiency Engineering

High Performance Linear Fluorescent Fixtures

Measure Codes Lxx1 - Lxx32

# At-a-Glance Summary

| Applicable Measure Codes: | Lxx1-Lxx32 |
| --- | --- |
| Measure Description: | Install new T5 or T8 linear fluorescent fixture with advanced optical design and T5 ballast or high-efficiency T8 ballast. |
| Energy Impact Common Units: | Fixture |
| Base Case Description: | T8 fixture with Premium T8 ballast; 3-lamp 2x4 or 2-lamp 2x2 |
| Base Case Energy Consumption: | 0.083 kW or 0.054 kW |
| Measure Energy Consumption: | Various. Refer to At-A-Glance Measure List Source: PG&E Calculations. |
| Energy Savings (Base Case – Measure) | Various. Refer to At-A-Glance Measure List. Source: PG&E Calculations. |
| Costs Common Units: | $ per fixture. |
| Base Case Equipment Cost ($/fixture): | Various. Refer to At-A-Glance Measure List. Source: PG&E Upstream Survey of Electrical Distributors. |
| Measure Equipment Cost ($/fixture): | Various. Refer to At-A-Glance Measure List. Source: PG&E Upstream Survey of Electrical Distributors. |
| Gross Measure Cost ($/fixture) | Various. Refer to At-A-Glance Measure List. Source: PG&E Upstream Survey of Electrical Distributors. |
| Measure Incremental Cost ($/fixture): | Various. Refer to At-A-Glance Measure List. Source: PG&E Upstream Survey of Electrical Distributors. |
| Effective Useful Life (years): | Varies by building type, 15 years max is shown for linear fluorescents Source: DEER 2011 |
| Program Type: | ROB/NC. |
| Net-to-Gross Ratios: | Commercial: 0.70 Source: DEER2011 v4.01, NTGR_ID=All-Default<=2yrs |
| Important Comments: |  |

- At-A-Glance Measure List

|  |  |  |  |  |  |  |  | 1st Baseline |  |  |  |  |  |  |  | 2nd Baseline |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Code | Version Source | Measure Description | Measure Application Type | Building Type | Building Vintage | Climate Zone | Unit Definition | KW Peak Electric Demand Reduction | KWh Electric Savings | THM Gas Savings | (EUL) LIFE CYCLE | Base Case Cost ($/unit) | Measure Cost ($/unit) | Labor Cost ($/unit) | IMC Incremental Measure Cost ($/unit) | KW Peak Electric Demand Reduction | KWh Electric Savings | THM Gas Savings | LIFE CYCLE | Base Case Cost ($/unit) | Measure Cost ($/unit) | Labor Cost ($/unit) | IMC Incremental Measure Cost ($/unit) | GRR_ kW | GRR_ kWh | GRR_ therm | NTG | Implementation Method [DI, DD, I] | ISR |
| Lxx1 | N/A | 2x4 high performance 2L T8 fixture with RLO NEMA Premium ballast | ROB | OfL | AV | All | Fixture | 0.033 | 104 | -0.58 | 15 | $69.00 | $150.00 | $0.00 | $81.00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
| Lxx2 | N/A | 2x2 high performance 2L T8 fixture with RLO NEMA Premium ballast | ROB | OfL | AV | All | Fixture | 0.025 | 80 | -0.45 | 15 | $59.00 | $126.00 | $0.00 | $67.00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
| Lxx3 | N/A | 2x4 high performance 2L T8 kit with RLO NEMA Premium ballast | ROB | OfL | AV | All | Fixture | 0.033 | 104 | -0.58 | 15 | $69.00 | $108.00 | $0.00 | $39.00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
| Lxx4 | N/A | 2x2 high performance 2L T8 kit with RLO NEMA Premium ballast | ROB | OfL | AV | All | Fixture | 0.025 | 80 | -0.45 | 15 | $59.00 | $96.00 | $0.00 | $37.00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
| Lxx5 | N/A | 2x4 high performance 2L T8 fixture with NLO NEMA Premium ballast | ROB | OfL | AV | All | Fixture | 0.027 | 86 | -0.48 | 15 | $69.00 | $150.00 | $0.00 | $81.00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
| Lxx6 | N/A | 2x2 high performance 2L T8 fixture with NLO NEMA Premium ballast | ROB | OfL | AV | All | Fixture | 0.021 | 68 | -0.38 | 15 | $59.00 | $126.00 | $0.00 | $67.00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
| Lxx7 | N/A | 2x4 high performance 2L T5 fixture with NLO Ballast | ROB | OfL | AV | All | Fixture | 0.023 | 74 | -0.42 | 15 | $69.00 | $180.00 | $0.00 | $111.00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
| Lxx8 | N/A | 2x2 high performance 2L T5 fixture with NLO Ballast | ROB | OfL | AV | All | Fixture | 0.020 | 64 | -0.36 | 15 | $59.00 | $150.00 | $0.00 | $91.00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet

# Work Paper Approvals

| Peter Ford Manager, Customer Programs Engineering | Date |
| --- | --- |

# Document Revision History

| Revision # | Date | Section by Section Description of Revisions | Author (Company) |
| --- | --- | --- | --- |
| Revision 0 | 06/06/2012 | Original work paper | Greg Barker and Joey Lande (Energy Solutions) |
| Revision 0 | 10/24/12 | Developed from PGE workpaper PGECOLTG160 High Performance Linear Fluorescent Fixtures Rev1. Original workpaper authored by Greg Barker and Joey Lande (Energy Solutions).dated 6/6/2012 Added new SDGE Workpaper number, added Table designating Baseline, Measure Case and Saved wattages- in Attachments “High Performance Linear Fluorescent Fixtures”. Added reference to SDGE Lighting table WPSDGENRLG0999 that contains product code savings for multiple SDGE climate zones and building types (Master Lighting Lookup table). | Charles Harmstead , SDGE. |

# Table of Contents

At-a-Glance Summary	ii

At-A-Glance Measure List	iii

Work Paper Approvals	iv

Document Revision History	v

Table of Contents	vi

List of Tables	vii

Section 1. General Measure & Baseline Data	1

1.1 Product Measure Description & Background	1

1.3 Transaction Types	3

1.4 Product Base Case and Measure Case Data	3

1.4.1 DEER Base Case and Measure Case Information	3

1.4.2 Codes & Standards Requirements Base Case and Measure Information	4

1.4.3 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information	5

1.4.4 Assumptions and Calculations from other sources—Base and Measure Cases	5

Section 2. Calculation Methods	7

2.1 Electric Energy Savings Estimation Methodologies	9

2.2. Demand Reduction Estimation Methodologies	10

2.3. Gas Energy Savings Estimation Methodologies	10

Section 3. Load Shapes	11

3.1 Base Case Load Shapes	11

3.2 Measure Load Shapes	11

Section 4. Base Case & Measure Costs	12

4.1 Base Case(s) Costs	12

4.2 Measure Case Costs 	12

4.3 Incremental & Full Measure Costs	13

4.3.1 Gross Measure Cost	13

4.3.2	Incremental Measure Costs	13

Attachments ……………………………………………………………………………………..13

References:	15

# List of Tables

Table 1 Net-to-Gross Ratios	4

Table 6 Building Types and Load Shapes	11

Table 7 Building Types and Load Shapes	12

# Section 1. General Measure & Baseline Data

## 1.1 Product Measure Description & Background

Catalog Description

Install new T5 or T8 linear fluorescent fixture with advanced optical design and T5 ballast or high-efficiency T8 ballast.  All non-emergency T8 ballasts in the fixture must be NEMA Premium ballasts listed by the National Electrical Manufacturers’ Association (NEMA) or High Performance T8 (HPT8) ballasts listed by the Consortium for Energy Efficiency.  Fixture may be used for new construction or for replacement of existing fixtures, either on a 1-for-1 fixture replacement or fixture redesign.  Fixture may be either 2’ x 4’ or 2’ x 2’.  Ballast Factor may be Normal Light Output (NLO, 0.85 < BF ≤ 0.95); Reduced Lighting Output (RLO, BF ≤ 0.85); High Light Output (HLO, 0.96 < BF ≤ 1.1); or Very High Light Output (VHLO, 1.1 < BF).

Requirements:

- New fixtures or new retrofit kits only

- Only certain combinations of lamp number and ballast factor are eligible

- Fixture efficiency must exceed 80%

| Product Code | Description |
| --- | --- |
| Lxx1 | 2x4 high performance 2L T8 fixture with RLO NEMA Premium ballast |
| Lxx2 | 2x2 high performance 2L T8 fixture with RLO NEMA Premium ballast |
| Lxx3 | 2x4 high performance 2L T8 kit with RLO NEMA Premium ballast |
| Lxx4 | 2x2 high performance 2L T8 kit with RLO NEMA Premium ballast |
| Lxx5 | 2x4 high performance 2L T8 fixture with NLO NEMA Premium ballast |
| Lxx6 | 2x2 high performance 2L T8 fixture with NLO NEMA Premium ballast |
| Lxx7 | 2x4 high performance 2L T5 fixture with NLO Ballast |
| Lxx8 | 2x2 high performance 2L T5 fixture with NLO Ballast |
| Lxx9 | 2x4 high performance 2L T8 kit with NLO NEMA Premium ballast |
| Lxx10 | 2x2 high performance 2L T8 kit with NLO NEMA Premium ballast |
| Lxx11 | 2x4 high performance 2L T5 kit with NLO Ballast |
| Lxx12 | 2x2 high performance 2L T5 kit with NLO Ballast |
| Lxx13 | 2x4 high performance 2L T8 fixture with HLO NEMA Premium ballast |
| Lxx14 | 2x2 high performance 2L T8 fixture with HLO NEMA Premium ballast |
| Lxx15 | 2x4 high performance 2L T5 fixture with HLO Ballast |
| Lxx16 | 2x2 high performance 2L T5 fixture with HLO Ballast |
| Lxx17 | 2x4 high performance 2L T8 kit with HLO NEMA Premium ballast |
| Lxx18 | 2x2 high performance 2L T8 kit with HLO NEMA Premium ballast |
| Lxx19 | 2x4 high performance 2L T5 kit with HLO Ballast |
| Lxx20 | 2x2 high performance 2L T5 kit with HLO Ballast |
| Lxx21 | 2x4 high performance 1L T8 fixture with NLO NEMA Premium ballast |
| Lxx22 | 2x2 high performance 1L T8 fixture with NLO NEMA Premium ballast |
| Lxx23 | 2x4 high performance 1L T8 kit with NLO NEMA Premium ballast |
| Lxx24 | 2x2 high performance 1L T8 kit with NLO NEMA Premium ballast |
| Lxx25 | 2x4 high performance 1L T8 fixture with HLO NEMA Premium ballast |
| Lxx26 | 2x2 high performance 1L T8 fixture with HLO NEMA Premium ballast |
| Lxx27 | 2x4 high performance 1L T8 kit with HLO NEMA Premium ballast |
| Lxx28 | 2x2 high performance 1L T8 kit with HLO NEMA Premium ballast |
| Lxx29 | 2x4 high performance 1L T8 fixture with VHLO NEMA Premium ballast |
| Lxx30 | 2x2 high performance 1L T8 fixture with VHLO NEMA Premium ballast |
| Lxx31 | 2x4 high performance 1L T8 kit with VHLO NEMA Premium ballast |
| Lxx32 | 2x2 high performance 1L T8 kit with VHLO NEMA Premium ballast |

Program Restrictions and Guidelines

For non-residential customers, the delivery channel for these measures will be Downstream Deemed Programs.

Terms and Conditions:

The customer must be a non-residential SDG&E electric customer.

T8 measures are based on the savings provided by utilizing a one-lamp or two-lamp fixture instead of the industry-standard three-lamp fixture. Additional savings are realized if a RLO ballast is used instead of the standard, base-case NLO ballast. Savings are reduced if a HLO or VHLO ballast is used.

T5 measures are based on the savings provided by utilizing a two-lamp T5 fixture instead of the industry-standard three-lamp T8 fixture.  Additional savings are realized if a NLO ballast is used instead of a HLO ballast.  VHLO T5 ballasts are excluded due to insufficient savings relative to the base case.

These rebates cannot be combined with rebates from other catalog measures or other programs claiming lighting savings.

Market Applicability:

2x4 and 2x2 recessed fixtures are standard commercial luminaires often used in offices, retail, education, and elsewhere for general illumination needs. This measure applies to the non-residential market.

Type of Transaction:

This measure is applicable in replace on burnout (ROB) and new construction (NC) transactions, in downstream channels. The rebate incentivizes the choice of lower-wattage fluorescent equipment over the base case industry standard equipment.

1.2 Product Technical Description

This workpaper contains measures for both T8 and T5 linear fluorescent two-foot-by-two-foot (2x2) and two-foot-by-four-foot (2x4) fixtures.  The eight T5 measures are all for two-lamp fixtures, and vary by ballast factor, fixture size, and new fixture versus kit.  The twenty-four T8 measures vary by ballast factor, lamp quantity, fixture size, and new fixture versus kit.

Advanced optical design fixtures are those fixtures where improved design allows a single- or dual-lamp profile fixture to replace a three-lamp fixture that predominates in recessed applications.  Advanced optical design fixtures are manufactured with either a louver or a lens.  The eligible louvered fixtures have two-cell profiles: e.g. 2 x 6 = 12 cells for a 2x4 fixture.  The eligible lensed fixtures have a non-planar lens that allows higher light transmission and improved reflectivity. These measures will only be applicable to fixtures rated at or above 80% fixture efficiency according to IES luminaire testing procedures.

This measure describes savings attributable to:

- Using RLO versions of the premium ballasts, which provide 6 to 18 watts savings compared to the NLO generic ballasts.

- Using fewer lamps per fixture than the industry standard; either:

  - Using 2 four-foot lamps in a 2x4 recessed fixture, instead of the standard three-lamp design, and utilizing higher-performance optics to compensate for the lamp reduction

  - Using 2 two-foot lamps in a 2x2 recessed fixture, instead of the standard two-four-foot-U-bend-lamp design, and utilizing higher-performance optics to compensate for the lamp reduction

Improvements in linear fluorescent fixture design allow lighting of commercial interior spaces with fixtures that have fewer lamps.  These improvements include:

- More widespread use of the full variety of ballast factors, beyond just NLO for T8 and HLO for T5

- Improved materials, such as highly reflective optical materials and highly transmissive lenses that still protect against glare

- Improved design, such as non-planar lenses to reduce lens reflection, and computer-aided optics

- Preference for shallow-cell, rather than deep-cell, louvers as glass Visual Display Terminals (VDTs) are no longer present in office environments

These improvements also build on each other, as each lamp removed from the fixture improves efficiency for the remaining lamps by removing an optical obstacle and reducing heat.

This workpaper describes the improvements in recessed linear fluorescent fixtures, defines a high-performance standard for those fixtures, and calculates the energy savings associated with their selection in place of the existing industry standard recessed fixture options.

## 1.3 Transaction Types

The DEER Measure Cost Data Users Guide, version 2.01, defines the terms as follows:

- Replace on Burnout (ROB) – replacing a technology at the end of its useful life.

- New Construction (NC) – installing a technology in a new construction or major renovation project.

For these measures, in non-residential markets, ROB and NC are the dominant transaction types.

## 1.4 Product Base Case and Measure Case Data

## 1.4.1 DEER Base Case and Measure Case Information

The 2011 DEER v4.01 data provided by Energy Division includes: coincidence peak factors, hours of operations, and interactive effect values for different building types and climate zones of non-CFL interior lighting, which was used to develop measure savings.

Therms Savings Assumption (ΔTh)

Gas Savings (ΔTh): Interactive Effects only DEER 4.01 and Impact IDs

| Building type | Bldg Vintage | Climate Zone | Interactive Only? | Gas Savings Therms | DEER units | DEER Version | Impact IDs |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Varies – all Non-Res types | AV | All | Yes | Varies | Therms/kWh | 2011 4.01- | N/A |

Net-to-Gross Assumption:

Net to Gross Value:

Table 1 below summarizes all applicable Net-to-Gross ratios for programs that may be used by this measure, based on DEER2011 v4.01.  This measure is being newly introduced for the 2013-14 program cycle, so the relevant NTGR is the default for new technology in program for 2 or fewer years.Error: Reference source not found

Table 1 Net-to-Gross Ratios

|  |  | DEER Spreadsheet |  |
| --- | --- | --- | --- |
| Program Approach | NTG | NTGR_ID, Description | Cell Number |
| Commercial | 0.7 | NTG ID: All-Default<=2yrs, All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years | T66 |

The NTG Ratios in Table 1 are appropriate for the measures because:

- The technology is new to the program this year.

- The default NTGR is appropriate for all Delivery channels

- The default NTGR is appropriate for all Markets

## 1.4.2 Codes & Standards Requirements Base Case and Measure Information

Title 20: These measures do not currently fall under Title 20 of the California Energy Regulations.  Many fluorescent lamps and ballasts are regulated by the federal government, which preempts California from setting its own standards. However, the Pacific Gas and Electric Company (PG&E) Codes and Standards Enhancement (CASE) Initiative project has examined standard options for linear fluorescent fixtures, based on a minimum ballast efficiency factors (BEF) and other metrics, but no standard is active in current proceedings.

Title 24: These measures do not fall under Title 24 of the California Energy Regulations.

Federal Standards: Two recent Federal Regulations affect these measures, both coming into effect in the next 19 months. Fluorescent fixtures themselves are not regulated by the federal government.  However, there are federal standards for fluorescent ballasts and fluorescent lamps. The ballast standards, originally established through the National Appliance and Energy Conservation Amendments of 1988, were subsequently updated by the DOE in 2000 and in a recent rulemaking begun in 2008.  The published final rule will go into effect in 2014. As a result, the base-case ballast considered for this workpaper is the Electronic Premium ballast, designated “Elec-Prem” in PG&E’s Appendix B Table of Standard Lighting Wattages.

The new Federal Standard on General Service Fluorescent lamps goes into effect in July, 2012. Increased minimum performance standards for lamps do not directly affect fixture energy consumption, but does affect the assumed light output of the fixtures in this workpaper, affecting both base case and measure case fixtures.

## 1.4.3 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

1.4.3.1 Study #1

Market potential estimates are from the 2008 CASE Report on linear fluorescent fixtures, preliminary version.   Page 14 of this report states:

“Based on 2005 ballast sales from the U.S. Census Bureau (2006), 83 million fluorescent ballasts are shipped each year nationwide and 72% are shipped to fixture manufacturers.  Of the total ballasts shipped, 5 million of these (7%) are intended for use in the residential sector, not including imports (which are likely significant). We estimate that California represents 9.06% of this market, based on the percentage of national commercial floor area in the Pacific West census region (EIA, 2003) and the portion of the Pacific West population that resides in California (Census Bureau, 2002). For California’s share of residential fixture sales, we chose 10.9% based on population only.  Assuming a 25-year life for most four-foot fluorescent fixtures, we derived existing stock estimates for commercial and residential fixtures, as shown in Table 7. By these assumptions we estimate that there are 5.1 million linear fluorescent fixtures sold each year in the California commercial building sector, excluding T5 fixtures, along with another 0.4 million fixtures sold in the residential market.”

The total number of linear fluorescent fixtures sold in PG&E territory for the commercial building sector can be calculated from this California statewide sales estimate of 5.1 million fixtures, by applying PG&E’s share of statewide electricity sales. According to the California Energy Commission’s (CEC’s) 2006 numbers, PG&E sold 31.8% of the kWh in California.   The resultant estimate of fluorescent fixtures sales sold annual in PG&E territory is 1.6 million fixtures.

The annual savings potential in PG&E territory from converting all 1.6 million fixtures to premium ballasts, using the assumptions in the CASE Report of 4.8 watts of savings per fixture and 78% coincident diversity factor, was estimated at 6 peak megawatts (MW) and 19.4 gigawatt hours per year (GWh/yr).  This is the savings generally captured in the recent Federal ballast rulemaking.

The more modest savings, from reducing the number of lamps in 10% of the recessed fixture market, is still 1.3 peak MW and 4.1 GWh/yr. This study likely overestimates the savings potential based on the slowdown in sales due to the economic downturn of the last 4 years, as documented in NEMA’s manufacturing index and elsewhere.

## 1.4.4 Assumptions and Calculations from other sources—Base and Measure Cases

Energy Savings Assumption (ΔW):

- Base case and measure wattages shown below are from the PG&E 2012 Appendix B Table of Standard Lighting Wattages, where available.Error: Reference source not found

- The base case wattages are 83 Watts for 2x4 fixtures, from fixture code F43ILL, and 54 Watts for 2x2 fixtures, from fixture code F42ILL.

- Certain measure case wattages do not appear in PG&E’s Table of Standard Lighting Wattages.  The Table only lists T5 ballasts with HLO ballast factors; no Premium ballasts for F17T8s; no HLO and VHLO ballast factors for 1L F32T8s; and no Premium ballasts for HLO ballast factor F32T8s. A wattage tables prepared for PG&E by Stan Walerczyk in 2006 and manufacturer datasheets have been used for these measure case wattages.,

| Building type | Bldg Vintage | Climate Zone | Electric Savings Watts | Savings units | Reference |
| --- | --- | --- | --- | --- | --- |
| Varies – all Non-Res types | AV | All | Varies | Watts | Appendix B, Stan Walerczyk data; Manufacturer data & PG&E calculations |

Base Case Costs and Measure Case Costs:

- Estimated fixture costs are based on an extensive survey of distributors from 2010, and updated quotes provided by contractors, fixture manufacturers, and sales reps in 2012.,  While the costs shown incorporate the best information available, vendors described significant differences in mark-up practices.  It can be assumed that equipment costs may vary greatly, influenced primarily by the sales channel.

|  |  |  | Costs ($) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Building type | Bldg Vintage | Climate Zone | Base Case | Measure Case | IMC | Reference |
| Varies – all Non-Res types | AV | All | Varies | Varies | Varies | PG&E distributor survey, PG&E calculations |

Effective Useful Life:

- The EUL is calculated based on lamp life and different hours of operation by building type. DEER 2011 has a lamp life of 70,000 hours for linear fluorescents and a max EUL of 15 years.

| Building type | Bldg Vintage | Climate Zone | EUL (yrs) | DEER Version | Impact IDs |
| --- | --- | --- | --- | --- | --- |
| Varies – all Non-Res types | AV | All | Max 15 | DEER 2011 | N/A |

- In-service factor/first year installation rate:  The in-service rate is assumed to be one.

| Building type | Bldg Vintage | Climate Zone | In service rate |
| --- | --- | --- | --- |
| Varies – all Non-Res types | AV | All | 1 |

1.4.5 Time-of-Use Adjustment Factor

We are required by CPUC decision 06-06-063 dated June 29, 2006 to apply time-of-use (TOU) adjustment factors on residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only. Since this is not an A/C measure, the TOU adjustment factor is 0.

1.5 Summary of Inputs for Savings Calculations

The following sections provide the inputs for calculation:

| Input Variable | Variations | Base Case Average Value | Measure Case Average Value | Reference Section |
| --- | --- | --- | --- | --- |
| Electric Savings | All climate zones, AV, All non-res building types | N/A | Varies | Section 1.4.4 |
| Gas Savings | All climate zones, AV, All non-res building types | N/A | Varies | Section 1.4.1 |
| Hours of operation | All climate zones, AV, All non-res building types | Varies | Varies | Section 1.4.1 |
| Full Cost | N/A | N/A | N/A | N/A |
| Incremental Cost | ROB, NC | N/A | Varies | Section 1.4.4 |
| EUL | ROB, NC | Varies | Varies | Section 1.4.4 |
| NTG | N/A | Com – 0.70 | Com – 0.70 | Section 1.4.1 |
| ISR | Applies | 1 | 1 | Section 1.4.4 |
| TOU Factor | A/C projects only | N/A | N/A | Section 1.4.5 |

# See Attachments (High Performance Linear Fluorescent Fixtures) for Base Case, Measure Case and Saved wattages. Master Lighting Lookup Table WPSDGENRLG0999 lists savings by building type and climate zone.

# Section 2. Calculation Methods

| Install / Program Type | Measure Life Basis | First Baseline Period -- Energy Savings Baseline | Second Baseline Period -- Energy Savings Baseline |
| --- | --- | --- | --- |
| NEW | EUL – DEER 2008 | N/A | N/A |
| ROB | EUL – DEER 2008 | N/A | N/A |

The following table lists the descriptions of the base case and measure case for each measure code.

| Measure Code | Base Case Description | Measure Case Description |
| --- | --- | --- |
| Lxx1 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 2L T8 fixture with RLO NEMA Premium ballast |
| Lxx2 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 2L T8 fixture with RLO NEMA Premium ballast |
| Lxx3 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 2L T8 kit with RLO NEMA Premium ballast |
| Lxx4 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 2L T8 kit with RLO NEMA Premium ballast |
| Lxx5 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 2L T8 fixture with NLO NEMA Premium ballast |
| Lxx6 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 2L T8 fixture with NLO NEMA Premium ballast |
| Lxx7 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 2L T5 fixture with NLO Ballast |
| Lxx8 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 2L T5 fixture with NLO Ballast |
| Lxx9 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 2L T8 kit with NLO NEMA Premium ballast |
| Lxx10 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 2L T8 kit with NLO NEMA Premium ballast |
| Lxx11 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 2L T5 kit with NLO Ballast |
| Lxx12 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 2L T5 kit with NLO Ballast |
| Lxx13 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 2L T8 fixture with HLO NEMA Premium ballast |
| Lxx14 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 2L T8 fixture with HLO NEMA Premium ballast |
| Lxx15 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 2L T5 fixture with HLO Ballast |
| Lxx16 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 2L T5 fixture with HLO Ballast |
| Lxx17 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 2L T8 kit with HLO NEMA Premium ballast |
| Lxx18 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 2L T8 kit with HLO NEMA Premium ballast |
| Lxx19 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 2L T5 kit with HLO Ballast |
| Lxx20 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 2L T5 kit with HLO Ballast |
| Lxx21 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 1L T8 fixture with NLO NEMA Premium ballast |
| Lxx22 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 1L T8 fixture with NLO NEMA Premium ballast |
| Lxx23 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 1L T8 kit with NLO NEMA Premium ballast |
| Lxx24 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 1L T8 kit with NLO NEMA Premium ballast |
| Lxx25 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 1L T8 fixture with HLO NEMA Premium ballast |
| Lxx26 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 1L T8 fixture with HLO NEMA Premium ballast |
| Lxx27 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 1L T8 kit with HLO NEMA Premium ballast |
| Lxx28 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 1L T8 kit with HLO NEMA Premium ballast |
| Lxx29 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 1L T8 fixture with VHLO NEMA Premium ballast |
| Lxx30 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 1L T8 fixture with VHLO NEMA Premium ballast |
| Lxx31 | 2x4 standard 3L F32T8 recessed fluorescent fixture | 2x4 high performance 1L T8 kit with VHLO NEMA Premium ballast |
| Lxx32 | 2x2 standard 2L F32T8/U-bend recessed fluorescent fixture | 2x2 high performance 1L T8 kit with VHLO NEMA Premium ballast |

## 2.1 Electric Energy Savings Estimation Methodologies

- This measure includes HVAC interactive effects savings.

- This measure is not an Early Retirement measure.

∆Watts/fixture: The demand difference (watts per fixture) is simply the difference between the electric demand of the base fixture and the electric demand of the energy efficient fixture.

∆Watts/fixture = Base Case Watts/fixture - Measure Case Watts/fixture

Where:

Base Case Watts/fixture is either 83 or 54 W, representing two-lamp or three-lamp F32T8 fixtures

Example:

∆Watts/fixture = 83 W – 48 W = 35 ∆Watts/fixture

Annual Electric Savings:

Annual Energy Savings [kWh/fixture] = (∆Watts/fixture) x (Annual Hours of Operation) x (Energy Interactive Effects) / (1,000 Watts / kW)

Example for Asm building type:

Annual Energy Savings = 35 ∆Watts/fixture x 2,610 hours x 1.05 kWh/kWh / 1,000 Watts/kW 
= 96 kWh

The measures in this workpaper address two distinct base case product classes: 2x4 recessed fluorescent fixtures and 2x2 recessed fluorescent fixtures.  Based on market data and sales histories gathered from manufacturers and distributors, each of those classes has a lamp configuration that defines the industry’s standard practice.

The 3-lamp F32T8 NLO ballast factor configuration is the industry standard for 2x4 recessed fixtures, dominating both louvered (including parabolic) and lensed variations that size.  This workpaper presents 16 measures as possible lower-wattage replacements for that industry standard, varying by lamp diameter, number of lamps, ballast factor, and retrofit kit or full fixture options.  The energy savings and equipment costs vary across the 16 measures, but the base case is the same for all: 83 watts.  This workpaper offers a full range of options for 2x4 recessed fluorescent applications, and the selection of the appropriate fixture will depend on the illumination requirements of the space and the choice of the customer, contractor, or lighting designer.

Likewise, the 2-lamp F31T8/U-bend, NLO ballast factor configuration is the industry standard for 2x2 recessed fixtures, dominating both louvered (including parabolic) and lensed variations that size.  Again, this workpaper presents another 16 measures as possible lower-wattage replacements for that industry standard, again varying by lamp diameter, number of lamps, ballast factor, and retrofit kit or full fixture options.  The energy savings and equipment costs vary across the 16 measures, but the base case is the same for all: 54 watts.  This workpaper offers a full range of options for 2x2 recessed fluorescent applications, and the selection of the appropriate fixture will depend on the illumination requirements of the space and the choice of the customer, contractor, or lighting designer.

The light output of the measure case fixtures will be typically lower than the overall light output of the base case fixtures, but may offer improvements in distribution and uniformity.  Fixtures with lower photopic output may be appropriate in some applications as per-lamp lumen output has increased, some visual tasks have become less demanding—particularly in offices, and occupants are taking advantage of a broader range of color temperatures in fluorescent lighting.

## 2.2. Demand Reduction Estimation Methodologies

- This measure includes HVAC interactive effects savings.

- This measure is not an Early Retirement measure.

∆Watts/fixture: The demand difference (watts per fixture) is simply the difference between the electric demand of the base fixture and the electric demand of the energy efficient fixture.

∆Watts/fixture = Base Watts/fixture - Energy Efficient Watts/fixture

Where:

Base Case Watts/fixture is either 83 or 54 W, representing two-lamp or three-lamp F32T8 fixtures

Demand Reduction:

Demand Reduction [kW/fixture] = (∆Watts/fixture) x (Lighting Coincident Demand) x (Demand Interactive Effects) / (1,000 Watts/kW)

Example for Asm building type:

Demand Reduction = 35 ∆Watts/fixture x 0.53 x 1.16 kW/kW / 1,000 Watts/kW 
= 0.0215 kW

## 2.3. Gas Energy Savings Estimation Methodologies

- Gas estimates are entirely those estimating increased gas use through calculated interactive effects.

- This measure is not an Early Retirement measure.

∆Watts/fixture: The demand difference (watts per fixture) is simply the difference between the electric demand of the base fixture and the electric demand of the energy efficient fixture.

∆Watts/fixture = Base Watts/fixture - Energy Efficient Watts/fixture

Where:

Base Case Watts/fixture is either 83 or 54 W, representing two-lamp or three-lamp F32T8 fixtures

Annual Gas Savings:

Annual Gas Savings [∆Therms/fixture] = (∆Watts/fixture) x (Annual Hours of Operation) x (Gas Interactive Effects) / 1,000 Watts/kW

Example for Asm building type:

Annual Gas Savings = 35 ∆Watts/fixture x 2,610 hours x -0.0090 Therms/kWh / 1,000 Watts/kW 
= -0.822 Therms

# Section 3. Load Shapes

Load Shapes are an important part of the life-cycle cost analysis of any energy efficiency program portfolio. The net benefits associated with a measure are based on the amount of energy saved and the avoided cost per unit of energy saved. For electricity, the avoided cost varies hourly over an entire year. Thus, the net benefits calculation for a measure requires both the total annual energy savings (kWh) of the measure and the distribution of that savings over the year. The distribution of savings over the year is represented by the measure’s load shape. The measure’s load shape indicates what fraction of annual energy savings occurs in each time period of the year. An hourly load shape indicates what fraction of annual savings occurs for each hour of the year. A Time-of-Use (TOU) load shape indicates what fraction occurs within five or six broad time-of-use periods, typically defined by a specific utility rate tariff. Formally, a load shape is a set of fractions summing to unity, one fraction for each hour or for each TOU period. Multiplying the measure load shape with the hourly avoided cost stream determines the average avoided cost per kWh for use in the life cycle cost analysis that determines a measure’s Total Resource Cost (TRC) benefit.

## 3.1 Base Case Load Shapes

The closest load shape chosen for this measure is the DEER:Indoor_Non-CFL_Ltg load shape.

Table 2 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Varies – all Non-Res types | NON_RES | DEER:Indoor_Non-CFL_Ltg |

## 3.2 Measure Load Shapes

The measure load shape for this measure is determined based on the applicable residential, commercial, or multifamily market sector and the lighting end-use.

The closest load shape chosen for this measure is the DEER:Indoor_Non-CFL_Ltg load shape.

Table 3 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Varies – all Non-Res types | NON_RES | DEER:Indoor_Non-CFL_Ltg |

# Section 4. Base Case & Measure Costs

| Install/Program Type | Measure Life Basis | First Baseline Period Gross Measure Cost (RUL) | Second Baseline Period Gross Measure Cost (EUL – RUL) |
| --- | --- | --- | --- |
| NEW | EUL | Calculated as Incremental Measure Cost | N/A |
| ROB | EUL | Calculated as Incremental Measure Cost | N/A |

The incremental measure cost (IMC)  is calculated as the difference of the energy efficient material and labor cost minus the base material and labor cost. It is assumed that the labor cost for the energy efficient unit and the base unit is the same so the IMC is calculated as the difference of the cost of the material for the measure and base case.

## 4.1 Base Case(s) Costs

The following Transaction types are appropriate to these measures. The Base Case Costs are:

| Measure Code | Transaction | Baseline | Equipment Cost |
| --- | --- | --- | --- |
| All 2x4 measure codes | ROB/NC | 3L 2x4 F32T8 recessed fluorescent | $69.00 |
| All 2x2 measure codes | ROB/NC | 2L 2x2 F32T8/U-bend recessed fluorescent | $59.00 |

All costs are noted as $ per fixture

Base case fixture costs are based on an extensive survey of distributors from 2010, and updated quotes provided by contractors, fixture manufacturers, and sales reps in 2012.Error: Reference source not found

## 4.2 Measure Case Costs

The transaction types appropriate to these measures are ROB and NC.. The Measure Case Costs are shown in section 4.3, the Incremental Measure Cost table.

Measure case fixture costs are based on an extensive survey of distributors from 2010, and updated quotes provided by contractors, fixture manufacturers, and sales reps in 2012.Error: Reference source not found

## 4.3 Incremental & Full Measure Costs

| Install/Program Type | Gross Measure Cost (RUL Period/First Baseline) | Gross Measure Cost (EUL-RUL Period/ Second Baseline) | Incremental Measure Cost |
| --- | --- | --- | --- |
| NEW | Measure Equipment Cost – Base Case Equipment Cost | N/A | Measure Equipment Cost – Base Case Equipment Cost |
| ROB | Measure Equipment Cost – Base Case Equipment Cost | N/A | Measure Equipment Cost – Base Case Equipment Cost |

# 4.3.1 Gross Measure Cost

Gross measure cost calculation does not apply to this work paper.

# Incremental Measure Costs

Incremental Measure Cost is the premium cost to install an energy efficient measure over a standard efficiency measure or code baseline measure. The labor costs for the base case and measure case fixtures are assumed to be the same, so the incremental measure cost is just the difference in equipment costs.

IMC = Measure Equipment Cost – Base Case Equipment Cost

IMC for the first measure = $150 per fixture - $69 per fixture = $81 per fixture

Summary Table for Section 4

| Measure ID | Transaction Type | Base Case Total Cost | Measure Case Total Cost | Incremental Measure Cost |
| --- | --- | --- | --- | --- |
| Lxx1 | ROB/NC | $69.00 | $150.00 | $81.00 |
| Lxx2 | ROB/NC | $59.00 | $126.00 | $67.00 |
| Lxx3 | ROB/NC | $69.00 | $108.00 | $39.00 |
| Lxx4 | ROB/NC | $59.00 | $96.00 | $37.00 |
| Lxx5 | ROB/NC | $69.00 | $150.00 | $81.00 |
| Lxx6 | ROB/NC | $59.00 | $126.00 | $67.00 |
| Lxx7 | ROB/NC | $69.00 | $180.00 | $111.00 |
| Lxx8 | ROB/NC | $59.00 | $150.00 | $91.00 |
| Lxx9 | ROB/NC | $69.00 | $108.00 | $39.00 |
| Lxx10 | ROB/NC | $59.00 | $96.00 | $37.00 |
| Lxx11 | ROB/NC | $69.00 | $144.00 | $75.00 |
| Lxx12 | ROB/NC | $59.00 | $120.00 | $61.00 |
| Lxx13 | ROB/NC | $69.00 | $150.00 | $81.00 |
| Lxx14 | ROB/NC | $59.00 | $126.00 | $67.00 |
| Lxx15 | ROB/NC | $69.00 | $180.00 | $111.00 |
| Lxx16 | ROB/NC | $59.00 | $150.00 | $91.00 |
| Lxx17 | ROB/NC | $69.00 | $108.00 | $39.00 |
| Lxx18 | ROB/NC | $59.00 | $96.00 | $37.00 |
| Lxx19 | ROB/NC | $69.00 | $144.00 | $75.00 |
| Lxx20 | ROB/NC | $59.00 | $120.00 | $61.00 |
| Lxx21 | ROB/NC | $69.00 | $150.00 | $81.00 |
| Lxx22 | ROB/NC | $59.00 | $126.00 | $67.00 |
| Lxx23 | ROB/NC | $69.00 | $108.00 | $39.00 |
| Lxx24 | ROB/NC | $59.00 | $96.00 | $37.00 |
| Lxx25 | ROB/NC | $69.00 | $150.00 | $81.00 |
| Lxx26 | ROB/NC | $59.00 | $126.00 | $67.00 |
| Lxx27 | ROB/NC | $69.00 | $108.00 | $39.00 |
| Lxx28 | ROB/NC | $59.00 | $96.00 | $37.00 |
| Lxx29 | ROB/NC | $69.00 | $150.00 | $81.00 |
| Lxx30 | ROB/NC | $59.00 | $126.00 | $67.00 |
| Lxx31 | ROB/NC | $69.00 | $108.00 | $39.00 |
| Lxx32 | ROB/NC | $59.00 | $96.00 | $37.00 |

Attachments:

# High Performance Linear Fluorescent Fixtures savings

# Master Lighting Lookup Table

# References:

Database for Energy-Efficient Resources 2011, Version 4.01; from DEER2011_NTGR_2012-05-16.xls

NEMA’s Premium list is maintained at http://www.nema.org/Policy/Energy/Efficiency/Documents/nema_premium_electronic_ballast_program.pdf

CEE’s HPT8 ballast list is maintained at http://www.cee1.org/com/com-lt/com-lt-main.php3

“LighitngHVACInteractiveEffects_26Jan2012.xls,” posted to www.deeresources.com on May 23, 2012.

PG&E 2012. Unified Manual Appendix B Table of Standard Lighting Wattages. Accessed at: http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf

Eilert, P. Fernstrom, G. and E. Elliott, 2008. Codes and Standards Enhancement Initiative.  For PY2008: Title 20 Standards Development.  Analysis of Standards Options for Linear Fluorescent Fixtures, Preliminary CASE Report.  May 14 2008.

California Energy Commission website; accessed at: http://www.energy.ca.gov/maps/maps-pdf/UTILITY_SERVICE_AREAS_DETAIL.PDF

Walerczyk, S., 2009.  25-32W F32T8 Lamp and Electronic Ballast Wattage Table.

Sylvania et al; manufacturer specification data. Accessed at:

http://www.lithonia.com/RT5/pdf/Osram.134.10.pdf; http://www.advance.philips.com/documents/uploads/literature/Section 1.pdf; http://www.unvlt.com/literature/flyers/t5_he.pdf

PG&E, 2009.   2009 PG&E Upstream Survey of Electrical Distributors.  Conducted by Michael Faria, Trade Professional Consultant to PG&E Customer Energy Efficiency with assistance from Energy Solutions, Inc.

First Light Lighting Systems, 2010. Fluorescent Lamp Lighting Catalogue. Accessed at: http://www.firstlightsystems.com/flca/pdf_files/flhay51_4.pdf