Work Paper WPSDGENRLG0027

LED Refrigeration Case Lighting with Occupancy Sensors

Revision # 0

San Diego Gas & Electric Company

Energy Efficiency Engineering

LED Refrigeration Case Lighting with Occupancy Sensors

Measure Codes L-RXX

# November 9, 2012

# At-a-Glance Summary

| Applicable Measure Codes: | L-RXX |
| --- | --- |
| Measure Description: | LED light bars replacing single or multiple lamp fluorescent profiles in refrigerated display cases; with or without occupancy sensors; Tiers 1 through 4 |
| Energy Impact Common Units: | Per linear foot |
| Base Case Description: | Linear fluorescent lighting in refrigerated cases: <=5 foot T8 Normal Output; or > 5 foot T12 High Output |
| Base Case Energy Consumption: | Variable, per existing lamp configuration and per linear foot Source: SDG&E calculations |
| Measure Energy Consumption: Source: PG&E calculations | Variable, per-linear foot and controls Source: SDG&E calculations |
| Energy Savings (Base Case – Measure) | Variable, per existing lamp configuration, per-linear foot and controls Source: SG&E calculations |
| Costs Common Units: | $ per unit |
| Base Case Equipment Cost ($/unit): | Variable, per linear foot Source: PG&E calculations |
| Measure Equipment Cost ($/unit): | Variable, per-linear foot Source: PG&E calculations |
| Measure Incremental Cost ($/unit): | Variable, per-linear foot Source: PG&E calculations |
| Effective Useful Life (years): | Varies by building type Source: 2011 DEER |
| Program Type: | Replace on burnout (ROB) / New Construction (NC) / Direct Install (DI) |
| Net-to-Gross Ratios: | 0.70, Source: 2011 DEER, NTGR_ID= All-Default<=2yrs |

At A Glance measure List

|  |  |  |  |  |  |  |  | 1st Baseline |  |  |  |  |  |  |  | 2nd Baseline |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Code | Version Source | Measure Description | Measure Application Type | Building Type | Building Vintage | Climate Zone | Unit Definition | KW Peak Electric Demand Reduction | KWh Electric Savings | THM Gas Savings | (EUL) LIFE CYCLE | Base Case Cost ($/unit) | Measure Cost ($/unit) | Labor Cost ($/unit) | IMC Incremental Measure Cost ($/unit) | KW Peak Electric Demand Reduction | KWh Electric Savings | THM Gas Savings | LIFE CYCLE | Base Case Cost ($/unit) | Measure Cost ($/unit) | Labor Cost ($/unit) | IMC Incremental Measure Cost ($/unit) | GRR_ kW | GRR_ kWh | GRR_ therm | NTG | Implementation Method [DI, DD, I] | ISR |
| L-RXX | N/A | Linear foot of Tier 1 LED Lightbar, <= 5-foot unit, with occupancy sensor control replacing single lamp profile | ROB | Gro | EX | IOU | Linear Foot | 0.008 | 41 | 0 | 16 | $3.14 | $28.50 | $0.00 | $25.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
|  | N/A | Linear foot of Tier 1 LED Lightbar, <= 5-foot unit, no occupancy sensor control replacing single lamp profile | ROB | Gro | EX | IOU | Linear Foot | 0.008 | 39 | 0 | 16 | $3.14 | $24.84 | $0.00 | $21.70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
|  | N/A | Linear foot of Tier 1 LED Lightbar, > 5-foot unit, with occupancy sensor control replacing single lamp profile | ROB | Gro | EX | IOU | Linear Foot | 0.025 | 124 | 0 | 16 | $7.01 | $28.50 | $0.00 | $21.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
|  | N/A | Linear foot of Tier 1 LED Lightbar, > 5-foot unit, no occupancy sensor control replacing single lamp profile | ROB | Gro | EX | IOU | Linear Foot | 0.025 | 121 | 0 | 16 | $7.01 | $24.84 | $0.00 | $17.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |
|  | N/A | Linear foot of Tier 2 LED Lightbar, <= 5-foot unit, with occupancy sensor control replacing single lamp profile | ROB | Gro | EX | IOU | Linear Foot | 0.005 | 30 | 0 | 16 | $3.14 | $28.50 | $0.00 | $25.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.70 | I, DI | 1 |

Note: For the complete list of Measure and savings, refer to the attached calculation spreadsheet

# Work Paper Approvals

| Pete Ford Manager, Customer Programs Engineering | Date |
| --- | --- |

# Document Revision History

| Revision # | Date | Section by Section Description of Revisions | Author (Company) |
| --- | --- | --- | --- |
| Revision 0 | 11/9/12 | Adopted from PGE work paper PGECOLTG174 LED Refrigeration Case Lighting with Occ Sensors, Revision 0 Dated 8/29/12 by Alina Zohrabian (PGE). Revised At A Glance Measure List savings. Added “refrigerated case lighting.xls” savings calculations in “Attachments”. Revised example energy savings calculation, page 12 to more fully explain savings calculations for occupancy sensor savings. Deleted reference to 17.1%occupancy savings factor in favor of more extensive calculations. Updated GRO annual hours to 4907. Deleted reference to PGE Measure Codes | Charles Harmstead (SDGE) |

# Table of Contents

At-a-Glance Summary	ii

Work Paper Approvals	iv

Document Revision History	v

Table of Contents	vi

List of Tables	vii

Section 1. General Measure & Baseline Data	1

1.1 Product Measure Description & Background	1

1.3 Transaction Types	5

1.4 Product Base Case and Measure Case Data	5

1.4.1 DEER Base Case and Measure Case Information	5

1.4.2 Codes & Standards Requirements Base Case and Measure Information	6

1.4.3 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information	7

1.4.4 Assumptions and Calculations from other sources—Base and Measure Cases	7

Section 2. Calculation Methods	10

2.0.1 Compressor Savings	10

2.1 Electric Energy Savings Estimation Methodologies	11

2.2. Demand Reduction Estimation Methodologies	12

2.3. Gas Energy Savings Estimation Methodologies	13

Section 3. Load Shapes	13

3.1 Base Case Load Shapes	13

3.2 Measure Load Shapes	13

Section 4. Base Case & Measure Costs	14

4.1 Base Case(s) Costs	14

4.2 Measure Case Costs	15

4.3 Incremental & Full Measure Costs	15

4.3.1 Full Measure Cost	15

4.3.2	Incremental Measure Costs	16

Attachments: …………………………………………………………………………………….17

References:	18

# List of Tables

Table 1 Net-to-Gross Ratios	6

Table 2 Building Types and Load Shapes	13

Table 3 Building Types and Load Shapes	14

# Section 1. General Measure & Baseline Data

## 1.1 Product Measure Description & Background

Catalog Description

Light emitting diodes (LEDs) are emerging as a viable replacement for incandescent and fluorescent lighting technologies in certain applications. One such application is refrigerated cases for perishable goods. Refrigerated cases are found in most grocery stores and convenience stores, as well as some other specialty stores.  Illumination in refrigerated cases is typically provided by fluorescent sources, but while fluorescent light sources are efficient, they are optimized to operate in ambient air temperatures of 60ºF to 80ºF.

Performance of LED light sources improves in cold temperature applications. Many of the LED components available specify that they are suitable for use in low temperature settings.  The brightness, long life and high efficacy of LEDs make them a suitable energy efficient replacement for fluorescent lighting in refrigerated cases.  Demonstration projects have shown that customer response to LED case lighting is positive, and even when there has been a reduction in light levels with new case LEDs, store staff have viewed the lighting technology change favorably. There are also indications that refrigerated case LEDs may have a positive impact on product sales. LEDs save energy, perform well in the cold environment and provide consistent luminance.  The energy savings results from reduced lighting load and reduced refrigeration load due to reduced heat gain from the lighting equipment.

This work paper details the energy and demand savings of new measures related to LED lighting in refrigerated cases.

| Measure Code | Measure Description |
| --- | --- |
| LB02 | Linear foot of Tier 1 LED Lightbar, <= 5-foot unit, with occupancy sensor control replacing single lamp profile |
| LB03 | Linear foot of Tier 1 LED Lightbar, <= 5-foot unit, no occupancy sensor control replacing single lamp profile |
| LB04 | Linear foot of Tier 1 LED Lightbar, > 5-foot unit, with occupancy sensor control replacing single lamp profile |
| LB05 | Linear foot of Tier 1 LED Lightbar, > 5-foot unit, no occupancy sensor control replacing single lamp profile |
| LB06 | Linear foot of Tier 2 LED Lightbar, <= 5-foot unit, with occupancy sensor control replacing single lamp profile |
| LB07 | Linear foot of Tier 2 LED Lightbar, <= 5-foot unit, no occupancy sensor control replacing single lamp profile |
| LB08 | Linear foot of Tier 2 LED Lightbar, > 5-foot unit, with occupancy sensor control replacing single lamp profile |
| LB09 | Linear foot of Tier 2 LED Lightbar, > 5-foot unit, no occupancy sensor control replacing single lamp profile |
| LB10 | Linear foot of Tier 3 LED Lightbar, <= 5-foot unit, with occupancy sensor control replacing single lamp profile |
| LB11 | Linear foot of Tier 3 LED Lightbar, <= 5-foot unit, no occupancy sensor control replacing single lamp profile |
| LB12 | Linear foot of Tier 3 LED Lightbar, > 5-foot unit, with occupancy sensor control replacing single lamp profile |
| LB13 | Linear foot of Tier 3 LED Lightbar, > 5-foot unit, no occupancy sensor control replacing single lamp profile |
| Lxx13 | Linear foot of Tier 1 LED Lightbar, <= 5-foot unit, with occupancy sensor control replacing multiple lamp profile |
| Lxx14 | Linear foot of Tier 1 LED Lightbar, <= 5-foot unit, no occupancy sensor control replacing multiple lamp profile |
| Lxx15 | Linear foot of Tier 1 LED Lightbar, > 5-foot unit, with occupancy sensor control replacing multiple lamp profile |
| Lxx16 | Linear foot of Tier 1 LED Lightbar, > 5-foot unit, no occupancy sensor control replacing multiple lamp profile |
| Lxx17 | Linear foot of Tier 2 LED Lightbar, <= 5-foot unit, with occupancy sensor control replacing multiple lamp profile |
| Lxx18 | Linear foot of Tier 2 LED Lightbar, <= 5-foot unit, no occupancy sensor control replacing multiple lamp profile |
| Lxx19 | Linear foot of Tier 2 LED Lightbar, > 5-foot unit, with occupancy sensor control replacing multiple lamp profile |
| Lxx20 | Linear foot of Tier 2 LED Lightbar, > 5-foot unit, no occupancy sensor control replacing multiple lamp profile |
| Lxx21 | Linear foot of Tier 3 LED Lightbar, <= 5-foot unit, with occupancy sensor control replacing multiple lamp profile |
| Lxx22 | Linear foot of Tier 3 LED Lightbar, <= 5-foot unit, no occupancy sensor control replacing multiple lamp profile |
| Lxx23 | Linear foot of Tier 3 LED Lightbar, > 5-foot unit, with occupancy sensor control replacing multiple lamp profile |
| Lxx24 | Linear foot of Tier 3 LED Lightbar, > 5-foot unit, no occupancy sensor control replacing multiple lamp profile |
| Lxx25 | Linear foot of Tier 4 LED Lightbar, <= 5-foot unit, with occupancy sensor control replacing multiple lamp profile |
| Lxx26 | Linear foot of Tier 4 LED Lightbar, <= 5-foot unit, no occupancy sensor control replacing multiple lamp profile |
| Lxx27 | Linear foot of Tier 4 LED Lightbar, > 5-foot unit, with occupancy sensor control replacing multiple lamp profile |
| Lxx28 | Linear foot of Tier 4 LED Lightbar, > 5-foot unit, no occupancy sensor control replacing multiple lamp profile |

The twenty eight new measures (4 tiers) are designed to offer customers with additional opportunities to reduce lighting and refrigeration costs. Customers can choose the appropriate wattage and light output for the LED case lighting to replace their linear fluorescent lamps.  Additional savings opportunity is available to customers who further reduce kWh usage with occupancy sensors, or with the removal of multiple lamp profiles.

The wattage limits of the tiers are designed to incentivize the sale of the most efficacious lightbars available, while also considering that certain applications require a higher wattage lightbar to provide adequate light levels.

| Product Description | Wattage | Basecase lamp length | Occupancy Control | Basecase lamp profile |
| --- | --- | --- | --- | --- |
| Linear Foot of Tier 1 LED Lightbar | <=2 watts/foot | <=5 or >5 foot lamp | With/without occupancy sensor | Replacing single or multiple lamp profile |
| Linear foot of Tier 2 LED Lightbar | >2 watts/foot <=4 watts/foot | <=5 or >5 foot lamp | With/without occupancy sensor | Replacing single or multiple lamp profile |
| Linear foot of Tier 3 LED Lightbar | >4 watts/foot <=6 watts/foot | <=5 or >5 foot lamp | With/without occupancy sensor | Replacing single or multiple lamp profile |
| Linear foot of Tier 4 LED Lightbar | >6 watts/foot <=9 watts/foot | <=5 or >5 foot lamp | With/without occupancy sensor | Replacing multiple lamp profile |

Within each tier there is an option for claiming credit for lamp removal, for refrigerated cases where fluorescent lamps currently exist side-by-side, referred to here as multiple lamp profile. The fourth tier, for highest-wattage LED lightbars, applies to the highest output horizontal lightbars, which are installed as a replacement for multiple lamp, high output canopy fixtures. This tier of LED lightbar only qualifies for incentives when replacing multiple lamp profile fluorescents, as a single lamp profile basecase would provide little or no savings. This tier gives customers an option to replace multiple fluorescent lamps with a single lightbar, while qualifying for a higher incentive and increasing energy savings.

An analysis of PG&E- and Design Lights Consortium (DLC)-qualified LED products was conducted to survey the distribution of lightbars across different wattage ranges. PG&E will continue to use the DLC listing requirements for luminous efficacy (lm/W) and light distribution for these products. Determination of which of the 4 tiers, if any, a DLC-listed product qualifies for will be based on the wattage of the product.  The wattage requirement for the highest savings tier, Tier 1, is restrictive enough to mean that most products at the writing of this workpaper will not qualify, and this was done intentionally to prolong the useful life of these measures before new savings assumptions are needed, given the improvement trends in LED light output and efficacy

A special methodology applies to the calculation of qualifying per-foot wattage for a vertical lightbar. This allows manufacturers to claim center-mounted and end-mounted lightbars as part of the same measure code. Most manufacturers produce a center lightbar that illuminates in two directions from a center mullion and an end lightbar that illuminates only one direction, to replace the fluorescent lamp mounted up against the side of a refrigerated case. These two products are typically sold as part of the same product family. A few manufacturers install identical units for centers and ends. Rather than assign products in the same family to different tiers, the center/end lightbar combination will be qualified for a specific tier based on the average of their wattages weighted by the relative prevalence of center and end units. The prevalence data is taken from more than 3 years of historical data from PG&E’s ERCO program, and it was determined that there are on average 2.19 center bars for every end bar; in other words the average case has two end bars and 4.38 center bars.  The qualification wattage of a vertical lightbar combination will be calculated with this formula:

Qualifying Wattage/foot = [(Center Bar Watts/foot) x 2.19 + (End Bar Watts/foot)] / (1 + 2.19)

Additional savings potential are included for LED fixtures equipped with occupancy sensors.  Occupancy sensors bring the LED lightbar to full light output when occupancy is detected near the refrigerated case, and allow the LED to drop to a lower power output or turn off during vacant periods.  Case studies have shown that occupancy sensors will enable the LED to operate at low power output for 34% of operating hours.,

Definitions:

Refrigerated display cases come in a variety of shapes and sizes. This work paper is designed to include all LED refrigerated case lightbars regardless of the orientation of the lighting product and whether the case is open or closed.

Vertical Reach-In Display Cases: “Vertical Cases” cases are either low-temp (i.e. freezers) or medium temp (i.e. refrigerators) and generally hold frozen and other perishable food products. Some reach-in cases are also “walk-in” for stocking purposes, but still have a vertical door closed door facing the customer. The lights illuminating the food products are found on the bars separating two doors, called mullions, and at each end of a set of doors.

Horizontal, Open Case: “Horizontal Cases” are commonly referred to as “multi-deck” cases and are often found in grocery stores to display meats, dairy products, beverages, produce and baked goods. The lights illuminating the food products are found in three basic places:

- “Canopy” lights are down-lights located at the top of the case that can potentially illuminate all levels of a multi-deck case

- “Shelf” lights are found under multi-level shelves

- “Nose” lights, also referred to as “rail” lights, are up-lights located at the bottom of the case closest to the consumer

Program Restrictions and Guidelines

This program is for new construction and replace on burnout, for non-residential customers.  The delivery channel for these measures will be Midstream/Upstream Programs. This measure is also available for direct install applications. This program has no climate zone or building restrictions.

Horizontal and Vertical Case Lighting must be on the Design Lights Consortium qualified product list and be listed with the Department of Energy Lighting Facts Program. The DLC specifications for horizontal and vertical refrigerated case lighting are shown here:

In addition to the above requirements, products that are installed with an occupancy sensor must be capable of dimming to at least 40% less than full power output. Only hardwired passive infrared detectors are eligible.

Terms and Conditions:

The customer must be a non-residential PG&E electric customer. Incentives are available in two channels: for the Midstream / Upstream channel products must be sold by a Qualified Participant; for the 3rd Party channel these measures could be delivered by a direct install program. All participants must sign a participation agreement and must be pre-enrolled prior to applying for incentives.

Horizontal and Vertical Case Lighting must be on the Design Lights Consortium qualified product list and be listed with the Department of Energy Lighting Facts Program.

LED lightbar savings are based on the replacement of existing single or multiple lamp fluorescent with a new LED lightbar, with a wattage below the maximum value of one of four tiers.  Additional savings are realized if the LED lightbar is installed with an occupancy sensor and dimmable driver.

Measure lengths are in whole feet only, and actual LED lightbar lengths are often slightly shorter than the length of fluorescent lamp being replaced.  The measure quantity, in linear feet, is determined by the original fluorescent lamp length, and the LED lightbar may be as much as 2 inches longer or 10 inches shorter than the original fluorescent lamp.

These rebates cannot be combined with rebates from other catalog measures or other programs claiming lighting savings.

Market Applicability:

These measures are primarily applicable to the grocery store sector, provided that the customer meets the terms and conditions above.  In some cases, these measures may also be applicable to the small business, retail, hospitality, and hospital sectors that have lighted refrigerated cases.

Type of Transaction:

This measure is applicable in replace on burnout (ROB) and new construction (NC) transactions in Upstream/Midstream channels, and in direct install (DI) transactions in 3rd Party channels. The rebate incentivizes the choice of lower-wattage fluorescent equipment over the base case industry standard equipment.

1.2 Product Technical Description

The measure case products are LEDs arranged in a linear, narrow “lightbar” that are installed in a vertical or horizontal refrigerated case and classified by wattage as Tier 1, Tier 2, Tier 3 or Tier 4. The unit for these measures is “linear foot.”  A distinction is drawn between LED fixtures 5 feet and less and longer than 5 feet due to a difference in base case lamp types; T8 and T12HO respectively. A linear foot of LED will replace a linear foot of fluorescent lighting, in a single or multiple lamp profile.

The base case products for these measures are fluorescent lamps and ballasts.  Surveys of grocery stores and correspondence with vendors and manufacturers has shown that there are very few, if any, T8 lamps installed in refrigerated cases that are longer than 5 feet.  Conversely, market surveys have shown that lamps 5 feet and shorter are predominantly T8.  For the energy savings and cost calculations in this workpaper, all 6 foot lamps are assumed to be T12HO, and all lamps 5 feet and shorter are assumed to be T8.

Each vertical and horizontal product can be installed with or without an occupancy sensor. Any lightbars controlled by a sensor are eligible for a higher incentive amount, and customers may apply for controlled and uncontrolled measures as part of the same installation. As mentioned above, products that are sold with a motion sensor must be capable of dimming by at least 40% power (dimming to 60% or less of full output power) to qualify for the higher “with occupancy sensor” rebates.

## 1.3 Transaction Types

The DEER Measure Cost Data Users Guide, version 2.01, defines the terms as follows:

- Replace on Burnout (ROB) – replacing a technology at the end of its useful life.

- New Construction (NC) – installing a technology in a new construction or major renovation project.

- Direct Install (DI)

For these measures, in non-residential markets, ROB is the dominant transaction types.

## 1.4 Product Base Case and Measure Case Data

## 1.4.1 DEER Base Case and Measure Case Information

The Database for Energy Efficiency Resources (DEER) provides California energy savings for many technologies.  These measures are not found in DEER and therefore, DEER difference analysis is not applicable.

Therms Savings Assumption (ΔTh)

Gas Savings (ΔTh): The Interactive Effects are from DEER 2011

| Building type | Bldg Vintage | Climate Zone | Interactive Only? | Gas Savings Therms | DEER units | DEER Version | Impact IDs |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Varies – all Non-Res types | AV | All | Yes | Varies | Therms/kWh | 2011 v4.01 | N/A |

Net-to-Gross Assumption:

Net to Gross Value:

Table 1 below summarizes all applicable Net-to-Gross ratios for programs that may be used by this measure, based on DEER2011 v4.01.  This measure is being newly introduced for the 2013-14 program cycle, so the relevant NTGR is the default for new technology in program for 2 or fewer years, NTGR_ID: All-Default<=2yrs.

Table 1 Net-to-Gross Ratios

|  |  | DEER Spreadsheet |  |
| --- | --- | --- | --- |
| Program Approach | NTG | NTGR_ID, Description | Cell Number |
| Commercial Midstream | 0.7 | All-Default<=2yrs, All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years | T66 |
| Commercial Direct Install | 0.7 | All-Default<=2yrs, All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years | T66 |

The NTG Ratios in Table 1 are appropriate for the measures because:

- The technology is new to the program this year.

- The default NTGR is appropriate for all Delivery channels

- The default NTGR is appropriate for all Markets

Hours of Operation:

Annual hours of operation are based on the “GRO” building type hours of 4910 from DEER 2011 v.4.01.

## 1.4.2 Codes & Standards Requirements Base Case and Measure Information

Title 20: These measures do not fall under Title 24 of the California Energy Regulations.

Title 24: These measures do not fall under Title 24 of the California Energy Regulations.

Federal Standards: The Energy Policy Act of 2005 (EPAct 2005) required the Department of Energy to develop energy efficiency standards for many types of commercial refrigeration equipment, including display cases.  However, the regulatory language does not cover specific technologies, but rather energy performance of the display case as a whole.  In addition, EPAct 2005 covers “General Service” fluorescent lamps (GSFLs), and a GSFL standard takes effect July 2012, but non-general applications are excluded. Fluorescent lamps specifically designed for cold temperature installations are specifically excluded from regulation.

## 1.4.3 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

LED Refrigerated Case lighting technology has been closely tracked in California Emerging Technology studies. PG&E has conducted a series of three ET studies, and SCE and SMUD have conducted studies: Application Assessment Reports #0723, #0722, #0608 (Ref #3) and #0606 (Ref # 5). These studies have all studied reach-in cases (i.e. with glass doors), and all but one have focused on low-temperature rather than medium-temperature cases (i.e. freezers instead of refrigerators).  Even with these limitations, the ET studies provide reliable information on lighting performance, the contribution of refrigeration savings and occupancy sensing savings, and customer satisfaction.

PG&E’s Emerging Technologies group has established that nearly half of supermarket electric costs are spent on refrigeration, and that lighting accounts for about 15% of the total energy consumed by commercial refrigerators.  The ET group’s demonstration projects show that LED refrigerated case lighting can lower lighting energy usage, and produce refrigeration savings as well.

Another gauge of the market potential in LED refrigerated case lighting is the continuing success of the PG&E’s ERCO midstream program, and the vendor and customer feedback in day-to-day Program operations.  To date, the PG&E offerings for refrigerated case LED lighting have focused entirely on vertical cases.  Vendors and customers have relayed that while vertical cases are a good application, additional potential can be found in horizontal case lighting, where multiple lamp profiles are common, particularly for canopy lighting.  Current ERCO participants indicate support for the expanded measures in this workpaper.

LED lighting is a rapidly advancing technology. It is anticipated that on-going improvements to LED technology, power supplies, and installation methods will lead to continuing price reductions and increases in energy savings.

## 1.4.4 Assumptions and Calculations from other sources—Base and Measure Cases

Energy Savings Assumption (ΔW):

- Base case wattages shown below are based on averages from the PG&E 2012 Appendix B Table of Standard Lighting Wattages. All lightbars 5 feet and shorter are calculated with a base case of T8 lamps and normal ballast factor, standard efficiency ballasts.  6 foot fixtures are calculated with a base case of T12 lamps. Base case wattages are an average of Appendix B listings for T12HO lamp/ballast combinations for that length.

- Measure case wattages are based on the maximum allowable per-foot wattages for Tiers 1 through 4.   Wattages for product qualification are taken from the Design Lights Consortium lists. Measure lengths are in whole feet only, and actual LED lightbar lengths are often slightly shorter than the length of fluorescent lamp being replaced.  The measure quantity, in linear feet, is determined by the original fluorescent lamp length, and the LED lightbar may be as much as 2 inches longer or 10 inches shorter than the original fluorescent lamp.

- The methodology for calculating the annual electrical energy savings from both lighting and refrigeration, in kWh/year, is explained in section 2.1.

- SCE’s emerging technology demonstration showed that with occupancy sensing in aisles with refrigerated display case lights, measured demand reduction is generally only 5-10% during peak periods as a result of high customer traffic.Error: Reference source not found Therefore, no additional peak demand reduction is claimed for this measure.

- Because Grocery (GRO) is the dominant building type for these measures, the default Com building type will use the Operating hours and interactive effects assumptions from the GRO building type.  Any Upstream savings calculated using the Com default building type will be based on GRO operating hours.

| Building type | Bldg Vintage | Climate Zone | Electric Savings Watts | Savings units | Reference |
| --- | --- | --- | --- | --- | --- |
| Varies – all Non-Res types | AV | All | Varies | Watts | Appendix B, Manufacturer & Vendor Data, ET Case Studies and PG&E calculations |

Base Case Costs and Measure Case Costs:

- Estimated fixture costs are based on an extensive survey of vendors from 2011.  While the costs shown incorporate the best information available, vendors described significant differences in mark-up practices.  It can be assumed that equipment costs may vary greatly, influenced by the sales channel and the manufacturer.

|  |  |  | Costs ($) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Building type | Bldg Vintage | Climate Zone | Base Case | Measure Case | IMC | Reference |
| Varies – all Non-Res types | AV | All | Varies | Varies | Varies | PG&E calculations |

Effective Useful Life:

EUL varies across building types based on the different hours of operation. READI tool has a EUL of 16 years for Display case Lighting LED’s. (EUL_ID= GrocDisp-FixtLtg-LED).  Since READI tool shows an EUL of 16 years for this grocery measure, the LED lifetime in hours is calculated as 16 times the GRO annual operating hours, 16*4907 = 78,519 hours. This value is used to calculate the EUL for the different building types.

| Building type | Bldg Vintage | Climate Zone | EUL (yrs) | DEER Version | Impact IDs |
| --- | --- | --- | --- | --- | --- |
| Varies – all Non-Res types | AV | All | 16 | DEER 2011 | N/A |

- In-service factor/first year installation rate: The ISR is assumed to be one for these measures.

| Building type | Bldg Vintage | Climate Zone | In service rate |
| --- | --- | --- | --- |
| Varies – all Non-Res types | AV | All | 1 |

1.4.5 Time-of-Use Adjustment Factor

We are required by CPUC decision 06-06-063 dated June 29, 2006 to apply time-of-use (TOU) adjustment factors on residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only. Since this is not an A/C measure, the TOU adjustment factor is 0.

1.5 Summary of Inputs for Savings Calculations

The following sections provide the inputs for calculation:

| Input Variable | Variations | Base Case Average Value | Measure Case Average Value | Reference Section |
| --- | --- | --- | --- | --- |
| Electric Savings | All climate zones, AV, All non-res building types | N/A | Varies | Section 1.4.4 |
| Gas Savings | All climate zones, AV, All non-res building types | N/A | Varies | Section 1.4.1 |
| Hours of operation | All climate zones, AV, All non-res building types | Varies | Varies | Section 1.4.1 |
| Full Cost | N/A | N/A | N/A | N/A |
| Incremental Cost | ROB, NC | N/A | Varies | Section 1.4.4 |
| EUL | ROB, NC | 16 | 16 | Section 1.4.4 |
| NTG | N/A | Com – 0.70 | Com – 0.70 | Section 1.4.1 |
| ISR | 1 |  |  | Section 1.4.4 |
| TOU Factor | A/C projects only | N/A | N/A | Section 1.4.5 |

# Section 2. Calculation Methods

### 2.0.1 Compressor Savings

Any heat contributed by lighting to a refrigerated case must be removed to maintain desired temperatures. Removing fluorescent lamps in favor of more efficient LEDs will reduce the heat load in the case, and thus reduce energy consumption by the difference in lighting fixture wattage plus an additional refrigeration factor.

The three PG&E ET studies have established several assumptions for calculating the refrigeration savings:

- Most, but not all, of the electrical energy from case lighting is dissipated inside the case.  Generally the fluorescent ballast or LED power supply is outside the refrigerated compartment and does not contribute heat to the case.  The percentage of lighting energy introduced to the case varies between 86% and 90% of the lighting wattage. The exact percentage used in each study varies by the precise model number and nominal wattage of each luminaire, so this assumption is presented as an average rather than calculated for each specific product.

- Most, but not all, of the electrical energy introduced into the refrigerated case is dissipated as heat (rather than light) energy. Based on data from the Handbook of the Illuminating Engineering Society, 79% of the electrical energy is dissipated as heat.

- Less than 1 Watt of energy is required to remove 1 Watt of heat from the refrigerated case by running the refrigerant compressor motor.  This relationship is expressed as the compressor coefficient of performance (COP).  COPs for refrigerated cases in the ET studies vary between 1.4 (for freezers) and 2.5 (for refrigerators).

Refrigeration energy consumption can be calculated by combining these three assumptions:

Refrigeration Energy = Lighting Energy x % Lighting inside case x % lighting as heat / COP

This equation can be rewritten to express refrigeration energy as a percentage of lighting energy

% Refrigeration Energy = % Lighting inside case x % lighting as heat / Compressor COP

Using typical numbers from the ET studies yields the following:

% Refrigeration Energy = 90% x 79% / 1.9 = 37.4%

Total Energy = Lighting Energy x 137.4%

Similar assumptions are used for Refrigeration savings in all three ET reports. For this workpaper, the assumptions from each ET report were weighted to account for the correct proportion of medium-temperature and low-temperature cases.  For each measure in this workpaper, refrigeration wattage is calculated as an additional 37.4% of the case lighting wattage, representing an average of the ET study results weighted by case temperature.

## 2.1 Electric Energy Savings Estimation Methodologies

- This measure includes HVAC interactive effects savings.

- This measure is not an Early Retirement measure.

Field surveys and feedback solicited from vendors has shown that horizontal refrigerated cases are often equipped with fixtures that have a multiple lamp profile, particularly in the canopy area of the fixture.  Shelf and nose fixtures normally use a single lamp profile, though multiple-lamp profile configurations do exist in nose lighting.   Vertical refrigerated cases are normally illuminated with fluorescent fixtures using a single lamp profile.  While fixtures 5 feet and shorter use both T12 and T8 lamps and ballasts, 6 foot fixtures overwhelmingly use T12HO equipment—no other lamp types have been documented.

The light output of the measure case fixtures will be typically lower than the overall light output of the base case fixtures, but typically offer improvements in distribution and uniformity.  Measure case light output will also vary based on the lamp profile of the existing fluorescent fixture.  In instances of a multiple lamp profile fixture, vendors may install multiple LED lightbars in an attempt to match the output of the existing fixture.  One alternative is to install a single LED lightbar as a replacement for a multiple lamp base case.  This is commonly referred to as “de-lamping”, although somewhat inaccurately in technical terms because the lighting technology type has changed, and the LED product is not technically a lamp.

When de-lamping occurs, the vendor may install a higher wattage, higher output lightbar than used for single-lamp replacement. Therefore the fourth, highest-wattage tier of LED lightbars is only applicable in cases of de-lamping. Products from Tiers 1 through 3 may be used in conjunction with de-lamping if customers’ needs for illumination are met.

When occupancy sensors are installed in addition to a qualifying lightbar, energy consumption of the light bars is reduced during the time period the occupancy sensors indicate no activity.  Additional reductions in energy consumption are based upon  a minimum 50% wattage reduction in low-power mode, and on the results of four case studies that establish the percentage of operating hours spent in low-power operation during vacant periods at 34%.  No demand savings are claimed for occupancy sensors.

∆Watts/linear foot: The demand difference (watts per linear foot) is the difference between the electric demand of the base fixture in watts/foot and the electric demand of the energy efficient fixture in watts/foot, all multiplied by the compressor savings factor of 137.4%.

∆Watts/foot = (Base Case Watts/foot - Measure Case Watts/foot) x Compressor Savings Factor

Where:

Base Case watts/foot varies between 7.6 W and 36.3 W, representing the watts per foot of a fluorescent system that is either T8 or T12, and either single-lamp profile or multiple-lamp profile.  For this workpaper, every multiple lamp profile configuration is treated conservatively as 2-lamp profile, even though field surveys have shown that 3-lamp profile system do exist.

Measure Case watts/foot is the maximum wattage that defines the appropriate tier—either 2 W, 4 W, 6 W or 9 W—increased by the 37.4% refrigeration savings factor.  The examples below are for a Tier 3 LED.

Examples:

∆Watts/foot = (7.6 W – 6 W) x 137.4% = 2.2 ∆Watts/foot

∆Watts/foot (multiple lamp profile) = ((2 lamps x 7.6 W) – 6 W) x 137.4% = 20.9 ∆Watts/foot

Annual Electric Savings:

Annual Electric Savings= ((∆Watts/foot) x (DEER 2011 Annual Hours of Operation)/ (1,000 Watts / kW)

No Interactive effects are claimed, since heat generated by case lighting is removed by refrigeration system to the outside (external refrigeration condensers)

Example for GRO building type:

Annual Electric Savings = ((2.2 ∆Watts/foot x (4,907 Annual Hours of Operation) / 1000 Watts/kW) = 10.0kWh

Annual Electric Savings with Occupancy Sensors:

Annual Energy Savings [kWh/foot] = [(Base Case Watts/foot x DEER Annual Hours of Operation) – (Measure Case Watts/foot) x (DEER Annual Hours of Operation) x (1-34%) – (Measure Case Watts/foot) x.5 x (DEER Annual Hours of Operation) x 34%] x (Compressor Savings Factor)] / (1,000 Watts / kW)

For the Direct Install program instead of the “GRO” building type hours of operation the “COM” building type hours of operation are used since COM represents smaller customers participating in Direct Install Program

## 2.2. Demand Reduction Estimation Methodologies

- This measure includes refrigeration system interactive effects savings, but no HVAAC interactive effects.

- This measure is not an Early Retirement measure.

∆Watts/foot: The demand difference (watts per foot) is simply the difference between the base fixture’s watts/foot and the electric demand of the energy efficient fixture in watts/foot, all multiplied by the compressor savings factor of 137.4%.

∆Watts/foot = (Base Case Watts/foot - Measure Case Watts/foot) x Compressor Savings Factor

Where:

Base Case watts/foot varies between 7.6 W and 36.3 W, representing the watts per foot of a fluorescent system that is either T8 or T12, and either single-lamp profile or multiple-lamp profile.  For this workpaper, every multiple lamp profile configuration is treated conservatively as 2-lamp profile; even though field surveys have shown that 3-lamp profile system do exist.

Demand Reduction:

Demand Reduction [kW/foot] = (∆Watts/foot) x (DEER 2011 Lighting Coincident Demand) x / (1,000 Watts/kW)

Example for GRO building type:

∆Watts/foot = (7.6 W – 6 W) x 137.4% = 2.2 ∆Watts/foot

Demand Reduction [kW/foot] = (2.2 ∆Watts/foot) x 0.69 x / (1,000 Watts/kW

= 1.51 kW

For the Upstream/Midstream program instead of the “GRO” building type Coincident demand factor and interactive effects, the “COM” building type Coincident demand factor and interactive effects are used since for this building type more closely represents the smaller customer applications

## 2.3. Gas Energy Savings Estimation Methodologies

- There is no therm interactive effect for this measure. Therefore there is no negative therm savings associated with this measure.

- This measure is not an Early Retirement measure.

# Section 3. Load Shapes

Load Shapes are an important part of the life-cycle cost analysis of any energy efficiency program portfolio. The net benefits associated with a measure are based on the amount of energy saved and the avoided cost per unit of energy saved. For electricity, the avoided cost varies hourly over an entire year. Thus, the net benefits calculation for a measure requires both the total annual energy savings (kWh) of the measure and the distribution of that savings over the year. The distribution of savings over the year is represented by the measure’s load shape. The measure’s load shape indicates what fraction of annual energy savings occurs in each time period of the year. An hourly load shape indicates what fraction of annual savings occurs for each hour of the year. A Time-of-Use (TOU) load shape indicates what fraction occurs within five or six broad time-of-use periods, typically defined by a specific utility rate tariff. Formally, a load shape is a set of fractions summing to unity, one fraction for each hour or for each TOU period. Multiplying the measure load shape with the hourly avoided cost stream determines the average avoided cost per kWh for use in the life cycle cost analysis that determines a measure’s Total Resource Cost (TRC) benefit.

## 3.1 Base Case Load Shapes

The closest load shape chosen for this measure is the DEER:Indoor_Non-CFL_Ltg load shape. See Table 3 for a list of all Building Types and Load Shapes.

Table 2 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Varies – all Non-Res types | NON_RES | DEER:Indoor_Non-CFL_Ltg |

## 3.2 Measure Load Shapes

The measure load shape for this measure is determined based on the applicable commercial, market sector and the lighting end-use.

The closest load shape chosen for this measure is the DEER:Indoor_Non-CFL_Ltg load shape. See Table 3 for a list of all Building Types and Load Shapes.

Table 3 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Varies – all Non-Res types | NON_RES | DEER:Indoor_Non-CFL_Ltg |

# Section 4. Base Case & Measure Costs

Data on both basecase and measure fixture costs are derived from product pricing provided by vendors via personal communications and online price listings where available.  In refrigerated case lighting as in other lighting applications, new generation LEDs are more expensive than older fluorescent equipment.  DEER cost data is not available for this application and has not been used in this workpaper. These measures are dominantly ROB so the cost is calculated as the incremental measure cost. The labor to replace a base case and measure case is assumed to be the same so the cost is calculated as the difference of the cost of material for the base and measure case. For the direct install the labor is added and Full measure cost is calculated instead of the incremental cost.

## 4.1 Base Case(s) Costs

The following Transaction types are appropriate to these measures. The Base Case Costs are:

| Measure Code | Transaction | Baseline | Equipment Cost |
| --- | --- | --- | --- |
| LB02, LB03, LB06, LB07, LB10, LB11 | ROB/NC/DI | Linear Foot of T8 Fluorescent Case Lamp with ballast, single lamp profile | $3.14 |
| LB04, LB05, LB08, LB09, LB12, LB13 | ROB/NC/DI | Linear Foot of T12HO Fluorescent Case Lamp with ballast, single lamp profile | $7.01 |
| Lxx13, Lxx14, Lxx17, Lxx18, Lxx21, Lxx22, Lxx25, Lxx26 | ROB/NC/DI | Linear Foot of T8 Fluorescent Case Lamp with ballast, multiple lamp profile | $6.28 |
| Lxx15, Lxx16, Lxx19, Lxx20, Lxx23, Lxx24, Lxx27, Lxx28 | ROB/NC/DI | Linear Foot of T12HO Fluorescent Case Lamp with ballast, multiple lamp profile | $14.03 |

All costs are noted as $ per linear foot

Base case linear foot costs are based on an extensive survey of distributors from 2010, and updated quotes provided by contractors, fixture manufacturers, and sales reps in 2012.

## 4.2 Measure Case Costs

The following Transaction types are appropriate to these measures. The Measure Case Costs are:

| Measure Code | Transaction | Measure Case | Measure Equipment Cost |
| --- | --- | --- | --- |
| LB02, LB04, LB06, LB08, LB10, LB12, | ROB/NC | Linear foot of LED Lightbar, with occupancy sensor control replacing single lamp profile | $28.50 |
| LB03, LB05, LB07, LB09, LB11, LB13 | ROB/NC | Linear foot of LED Lightbar, no occupancy sensor control replacing single lamp profile | $24.84 |
| Lxx13, Lxx15, Lxx17, Lxx19, Lxx21, Lxx23, Lxx25, Lxx27 | ROB/NC | Linear foot of Lightbar, with occupancy sensor control replacing multiple lamp profile | $31.16 |
| Lxx14, Lxx16, Lxx18, Lxx20, Lxx22, Lxx24, Lxx26, Lxx28 | ROB/NC | Linear foot of LED Lightbar,no occupancy sensor control replacing multiple lamp profile | $27.50 |

All costs are noted as $ per linear foot

Measure case linear foot costs are based on an extensive survey of distributors from 2010, and updated quotes provided by contractors, fixture manufacturers, and sales reps in 2012Error: Reference source not found.

## 4.3 Incremental & Full Measure Costs

# 4.3.1 Full Measure Cost

This is used for the direct install measures. This is calculated as the sum of the material and labor cost for the measure case. The labor cost is taken from DEER 2008, and assumed to be the same install cost for LED Lightbars as for Linear Fluorescents.

| Measure Code | Transaction Type | Labor Cost | Measure Equipment Total Cost | Full Measure Cost |
| --- | --- | --- | --- | --- |
| LB02, LB04, LB06, B08, LB10, LB12 | DI | $2.42 | $28.50 | $30.92 |
| LB03, LB05, LB07, LB09, LB11, LB13 | DI | $2.42 | $24.84 | $27.26 |
| Lxx13, Lxx15, Lxx17, Lxx19, Lxx21, Lxx23, Lxx25, Lxx27 | DI | $2.42 | $31.16 | $33.58 |
| Lxx14, Lxx16, Lxx18, Lxx20, Lxx22, Lxx24, Lxx26, Lxx28 | DI | $2.42 | $27.50 | $29.92 |

# Incremental Measure Costs

Incremental Measure Cost is the premium cost to install an energy efficient measure over a standard efficiency measure or code baseline measure. While IMC has a straight forward definition depending on the install type, the equation does vary.

For Upstream/Midstream measures with transaction type NC or ROB, the Incremental Measure Cost (IMC) is represented by the equation below:

IMC = (Measure Equipment Cost + Measure Labor Cost) –

(Base Case Equipment Cost + Base Case Labor Cost)

*Note: The measure case labor and base case labor are assumed to be the same value reducing the equation to the following:

IMC = Measure Equipment Cost – Base Case Equipment Cost

IMC for the first measure = $28.50 per linear foot- $3.14 per linear foot = $25.36 per linear foot

Summary Table for Section 4

| Measure ID | Transaction Type | Base Case Total Cost | Measure Eqpt Cost | Incremental Measure Cost |
| --- | --- | --- | --- | --- |
| LB02, LB06, LB10 | ROB/NC | $3.14 | $28.50 | $25.36 |
| LB03, LB07, LB11, | ROB/NC | $3.14 | $24.84 | $21.70 |
| LB04, LB08, LB12 | ROB/NC | $7.01 | $28.50 | $21.49 |
| LB05, LB09, LB13 | ROB/NC | $7.01 | $24.84 | $17.83 |
| Lxx13, Lxx17, Lxx21, Lxx25 | ROB/NC | $6.28 | $31.16 | $24.88 |
| Lxx14, Lxx18, Lxx22, Lxx26 | ROB/NC | $6.28 | $27.50 | $21.22 |
| Lxx15, Lxx19, Lxx23, Lxx27 | ROB/NC | $14.03 | $31.16 | $17.13 |
| Lxx16, Lxx20, Lxx24, Lxx28 | ROB/NC | $14.03 | $27.50 | $13.47 |

# Attachment:

# LED Refrigeration Case Lighting with Occupancy Sensors Energy and Demand Savings Calculations

# References:

Demonstration Assessment of Light-Emitting Diode (LED) Freezer Case Lighting. U.S. DOE Solid State Lighting Technology Demonstration GATEWAY Program.  October, 2009. http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/gateway_freezer-case.pdf

Fricke, Brian A., and Bryan R. Becker. Doored Display Cases – They Save Energy, Don’t Lose Sales.” American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc. September, 2010. Posted to www.ashrae.org

Theobald, Marc A., “Application Assessment Report #0608, LED Supermarket Case Lighting.” LED Supermarket ET Study Final.doc. PG&E and EMCOR Energy Services. January 2007. p. 7-1. http://www.etcc-ca.com/images/stories/pdf/ETCC_Report_204.pdf

Bisbee, Dave. “Customer Advanced Technologies Program Technology Evaluation Report: LED Freezer Case Lighting Systems.” Energy Efficiency, Customer Research & Development.  Sacramento Municipal Utility District. July 25, 2008 http://www.etcc-ca.com/images/ET07SMUD1003%20(LED%20Freezer%20Case%20Lighting).pdf

LED Lighting for Low Temperature Reach-in Refrigerated Display Cases. ET 06.06 Report. Design & Engineering Services, Customer Service Business Unit, Southern California Edison.  December 17, 2009.  http://www.etcc-ca.com/images/stories/et_06.06_-_led_display_case_lighting.pdf

DEER2011_NTGR_2012-05-16.xls, accessed at http://www.deeresources.com/DEER2011/download/DEER2011_NTGR_2012-05-16.xls

U.S. Department of Energy. Energy Conservation Program: Energy Conservation Standards and Test Procedures for General Service Fluorescent Lamps and Incandescent Reflector Lamps. Federal Register. Vol. 74, No. 133. Docket Number EE-2006-STD-0131. July 14, 2009.

Application Assessment Report #0723. LED Lighting in Reach-In Freezer Cases:Retail Sector. PG&E Emerging Technologies Program, 2008. http://www.etcc-ca.com/images/stories/ledfreezercasestudy1.pdf

Application Assessment Report #0722. LED Refrigerated Case Lighting, Costco, Northern California. PG&E Emerging Technologies Program. http://www.etcc-ca.com/images/stories/pdf/ETCC_Report_469.pdf

Statewide Customized Offering Manual.  Appendix B: Table of Standard Fixture Wattages.  January 1, 2012. <http://www.pge.com/mybusiness/energysavingsrebates/rebatesincentives/ief/>

? “Refrigerated Case LED Calculations_2012610” developed by Greg Barker and Joey Lande, Energy Solutions, under contract to PG&E.  Delivered 6/11/2012. Tabs – “Sensors”

Personal Communications.  Greg Barker, Nate Dewart and Joey Lande. Outreach with PG&E ERCO Program Participants. 2010-2012.

Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008), accessed at http://www.deeresources.com/deer0911planning/downloads/DEER2008_Costs_ValuesAndDocumentation_080530Rev1.zip