Work Paper WPSDGENRPH0001

Revision 1

San Diego Gas & Electric

Energy Efficiency Engineering

Process Boilers (Including Direct Contact Water Heaters)

### Core Measure Summary Table

| General Measure Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PT |  | 1st Baseline Period |  |  |  | 2nd Baseline Period |  |  |  | TOU |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | PreDesc | StdDesc | Measure RunID | Solution Code | CZ | Building Type | UseCategory | UseSubCategory | TechGroup | TechType | PreTechGroup | PreTechType | StdTechGroup | StdTechType | Load Shape | EUL_ID | EUL | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | Gross Unit Annual Electricity Savings (kWh/unit) | User Entered kW Savings per unit (kW/unit) | Gas Savings (Therms) | 1st Baseline Useful Life | Gross Unit Annual Electricity Savings (kWh/unit) | User Entered kW Savings per unit (kW/unit) | Gas Savings (Therms) | 2nd Baseline Useful Life | % Eligible for TOU AC Adjustment |
| Process Boiler (Steam) |  | Process Boiler (80% Efficiency) | N/A | G-E2 | 07 | Industrial | ProcHeat | SteamDist | SteamHtg_eq | Boiler_Et |  |  | SteamHtg_eq | Boiler_Et | 35-OTI-OtherIndustrial-PROC_OTH | PrcHt-Blr | 20.0 | Mbtuh | ROB | No | 0.00 | 0.00 | 0.48 | 20.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| Process Boiler (Water) Tier 1 non-condensing |  | Process Boiler (80% Efficiency) | N/A | G-E1 | 07 | Industrial | SHW | Heating | SteamHtg_eq | Boiler_Et |  |  | SteamHtg_eq | Boiler_Et | 35-OTI-OtherIndustrial-PROC_OTH | PrcHt-Blr | 20.0 | Mbtuh | ROB | No | 0.00 | 0.00 | 0.86 | 20.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| Process Boiler (Water) Tier 2 condensing |  | Process Boiler (80% Efficiency) | N/A | G-E1 | 07 | Industrial | SHW | Heating | SteamHtg_eq | Boiler_Et |  |  | SteamHtg_eq | Boiler_Et | 35-OTI-OtherIndustrial-PROC_OTH | PrcHt-Blr | 29.0 | Mbtuh | ROB | No | 0.00 | 0.00 | 2.01 | 29.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet []

### Costing and NTG Summary Table

| General Measure Information |  |  |  | PT |  | NTG |  |  | IR | 1st Baseline Period | 2nd Baseline Period | IMC | DIM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Solution Code | CZ | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | NTG Non-Res. | NTG Res. | NTG Multi Family | Installation Rate | Gross Measure Cost per unit | Gross Measure Cost per unit | Incremental Measure Cost per unit | Delivery & Incentive Method |
| Process Boiler (Steam) | G-E2 | 7 | Mbtuh | ROB | No | 0.60 |  |  | 1.00 | $4.35 | $0.00 | $4.35 | Financial Support / Down-Stream Incentive - Deemed |
| Process Boiler (Water) Tier 1 non-condensing | G-E1 | 7 | Mbtuh | ROB | No | 0.60 |  |  | 1.00 | $2.16 | $0.00 | $2.16 | Financial Support / Down-Stream Incentive - Deemed |
| Process Boiler (Water) Tier 2 condensing | G-E1 | 7 | Mbtuh | ROB | No | 0.70 |  |  | 1.00 | $12.17 | $0.00 | $12.17 | Financial Support / Down-Stream Incentive - Deemed |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet [A]

# Document Revision History

| Revision # | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 06/15/2012 | Kelvin Valenzuela / SDGE | Adopted WPSCGNRPH120206A_Rev4_Process Boilers-May22.docx, updated May 18, 2012. |
| 1 | 06/19/2014 | Judelson Enriquez / RMS Energy Consulting, LLC | 1. Updated to new workpaper format and adopted revisions made in WPSCGNRPH120206A_Rev5_ProcessBoilers_05302014.docx, updated May 28, 2014, which provides savings per CZ. 2. Added measure table in Section 1, EUL ID Summary table, TOU language, GSIA language and ID table, and load shape table. 3. Generated calculation spreadsheet based on IOU statewide Calculation Template output. Added Mark M.’s additional columns and removed CZ cost factor. |

# Section 1. General Measure & Baseline Data

## 1.1  Measure & Delivery Description

### 1.1a Measure Description

This work paper documents the rationale for the process boiler measure as listed in SDG&E’s Energy Efficiency Business Rebates Natural Gas Catalog [].

- Measure Description

- Process boilers are pressure vessels that transfer heat to water for manufacturing.  Manufacturing involves the mechanical or chemical transformation of materials or substances into a new product that is neither a structure nor any other fixed improvement.

- In most boilers, a heat exchanger separates the combustion products from the water.  Boilers can be configured as an integrated packaged boiler, or, in some cases, the boiler (which may resemble an instantaneous water heater) may be connected to a separate tank that contains an internal heat exchanger.  Energy efficient units may have one or more of the following features:  high-efficiency/low NOx burners, power burners, water tubes, relatively large heat exchange surfaces, and flue exhaust heat recovery systems.

- Another type of process heating arrangement is the direct contact water heater.  In direct contact water heaters, the combustion products directly contact the water and heat from the flame comes into direct contact with small droplets of cold water that run through a stainless steel heat exchange media.  Droplets composed from this process come into direct contact with rising heat from the flame and as a result the water is heated directly.

- The 2008 Process Boilers Workpaper includes a more detailed technology description in its Appendix A [].

Table 1 Measure Summary Table

| Product Code | Measure name | Unit Definition |
| --- | --- | --- |
| G-E1 | Process Boiler (Steam) | MBtuh |
| G-E2 | Process Boiler (Water) | MBtuh |

### 1.1b Delivery and Incentive Mechanism

The delivery method for the measure(s) in this workpaper is:

- Down-Stream Incentive – Deemed

Process boilers with rated input >2,000 MBtuh may participate in the Energy Efficiency Calculated Incentive Program (EECIP).

The measure install types are:

- Replace on Burnout (ROB) or New Construction (NEW)

### 1.1c Measure Requirements

- Terms & Conditions

Measure eligibility requirements for the measures addressed in this work paper are established in the San Diego Gas & Electric Energy Efficiency Business Rebates Product Catalog [B].

- Only process boilers (i.e., units not primarily used for domestic hot water or space heating use) qualify.

- This rebate is available to end-use customers in NAICS codes 11, 21, 31-33, and 8123.

- The rebate applies to gas-for-gas equipment replacements on burnout or for new installations in existing buildings.

- The rebate does not apply to New Construction.

- The manufacturer’s name and equipment model number must be provided.

- A flue gas analysis (FGA) measured under full load conditions is required to document combustion efficiency under full load conditions after the installation is complete.  If necessary, customers must provide proof of unit efficiency (e.g., manufacturer’s equipment specification sheet).

- Market Applicability

- These measures are applicable to any small or medium process boiler application.

- The primary application for this measure is the industrial sector (NAICS 31-33), but process boilers are not limited to the industrial sector.  For example, process boilers are used in the following sectors:  agricultural sector (NAICS 11), oil & gas extraction (NAICS 21), and drycleaning/laundry services (NAICS 8123).

- Boilers used primarily for domestic hot water or space heating end uses do not qualify.

- Qualifying Efficiency

- Test methods for measuring boiler efficiencies are referenced in the California Titles 20 and 24 standards [H,I].

- Minimum qualifying combustion efficiency (CE) for process boilers:

  - 85% for Tier 1 hot water boilers (non-condensing)

  - 90% for Tier 2 hot water boilers (condensing)

  - 83% for steam boilers

- Direct contact water heaters are included under the Tier 2 condensing hot water boiler category.

- Tier 2 condensing hot water boilers require the return water temperature to be significantly lower than 100 °F to achieve these high efficiencies.  In addition, Tier 2 condensing hot water boilers often require flue modifications to handle the condensate.  These modifications increase installation costs and may be eligible for a higher rebate amount.

## 1.2  DEER Differences Analysis

- Measure Efficiency

  - The 2014 Database for Energy-Efficient Resources (DEER) [] does not cover high efficiency process boilers.

  - The “Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008)” [] has incomplete efficiency data for process boilers that mimics the data for space heating boilers, including the inappropriate use of annual fuel utilization efficiency for boilers with rated input less than 300 MBtu/hr.

  - Tier 1 hot water boiler – the qualifying CE is set to 85% to match medium and large space heating hot water boilers.

  - Tier 2 hot water boiler – the qualifying CE is set to 90% to be consistent across all types of boilers and water heaters (90% efficiency can only be achieved with condensing boilers).

  - Steam boiler – the qualifying CE is set to 83% to match medium and large space heating steam boilers.  Also, 83% CE is used due to the limited availability of medium and large steam boilers with CE above 83% in the CEC Energy Efficiency Appliance Database [].

- Baseline Efficiency

- The “2011 Database for Energy-Efficient Resources (DEER) for Use in the California IOU 2013-14 Energy Efficiency Planning” [] does not include process boilers.

- Hot water boiler – the Titles 20 and 24 standard value of 80% CE for gas packaged boilers is used in this workpaper.

- Steam boiler – the Titles 20 and 24 standard value of 80% CE for gas packaged boilers is used in this workpaper.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | No |
| Deviation from DEER | DEER 2014 does not contain these measures. |
| DEER Version | N/A |
| DEER Run ID and Measure Name (Sample) | N/A |

## 1.3  Code Analysis

The 2014 California Title 20 Appliance Efficiency Regulations [] include standards for both federally regulated appliances and nonfederally-regulated appliances that are sold or offered for sale in California; however, Title 20 does not govern the measures found in this workpaper.

The 2013 California Title 24 Building Energy Efficiency Standards [] include standards to improve the energy efficiency of newly constructed building and additions and alterations to existing buildings for residential and nonresidential buildings; however, Title 24 does not govern the measures found in this workpaper.

Federal DOE or EPA Energy Regulations do not govern the measures found in this workpaper.

Table 3 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 20 (2014) | N/A | N/A |
| Title 24 (2013) | N/A | N/A |
| Federal Standards | N/A | N/A |

## 1.4  Measure Effective Useful Life

## DEER and the CPUC ED Workpaper Disposition for Lighting Retrofits documentation provide EUL and RUL information to be used on www.deeresources.com.

## To obtain the EUL value, the updated CPUC ED EUL table documentation issued on February 5, 2014, “DEER2014-EUL-table-update_2014-02-05.xlsx”, was consulted. The table below identifies the value/methodology used for the measures in this work paper.

Table 4 DEER EUL Value/Methodology

| Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- |
| Non-Residential | ProcHeat | High Efficiency Boiler | 20 | 6.67 |

Table 5 identifies the EUL IDs used in this workpaper.

Table 5 EUL ID Summary

| EUL_ID | Description | Sector |
| --- | --- | --- |
| PrcHt-Blr | High Efficiency Boiler | Com |

## 1.5  Net-to-Gross Ratios for Different Program Strategies

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” [] on the DEER website as required by Version 4 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual. The relevant NTGR for this measure is shown in Table 6 below.

- Measures for process heating is covered by the “Ind-Default>2yrs” EUL ID, while the Tier 2 condensing process hot water boiler measure belong under the “All-Default <= 2yrs” EUL ID.

Table 6 Net-to-Gross Ratio Summary Table

| NTGR_ID | Description* | Sector | BldgType | ProgDelivID |
| --- | --- | --- | --- | --- |
| Ind-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Ind | Any | All |
| All-Default<=2yrs | All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years | All | Any | All |

## 1.6  Time-of-Use Adjustment Factor

As directed by the CPUC in decision 06-06-063 dated June 29, 2006, time-of-use (TOU) adjustment factors are to be applied for residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only.   Since this is not an A/C measure, the TOU adjustment factor is zero.  Additionally, if a measure is assigned a DEER08 load shape, i.e. the load shape starts with “DEER:” the TOU assigned to that measure should also be zero.

Table 7 TOU Summary Table

| Measure | % |
| --- | --- |
| Commercial Boiler | 0 |

*Note:  Check Section 3 if a measure appears to require a non-zero percentage but is assigned zero. If the load shape is a DEER08 load shape, a TOU of zero is correct.

# Section 2. Energy Savings & Demand Reduction Calculations

## 2.1 Electric Energy Savings Estimation Methodologies

## There are no electric energy savings associated with this measure.

## 2.2 Demand Reduction Estimation Methodologies

## There are no anticipated demand reductions associated with this measure.

## 2.3 Gas Energy Savings Estimation Methodologies

    - The annual gas energy savings are calculated from the annual operating time, load factor, rated input, and the efficiency ratio of the baseline unit and the new high-efficiency unit.  The energy savings is calculated for process hot water boilers (including direct contact water heaters) and process steam boilers.  The data and calculations for annual operating time, load factor, and rated input are included in an Excel file embedded as Attachment #4 [].

    - Annual Operating Time

- The annual operating time represents the number of hours that gas equipment is expected to be in operation or available for operation at any input rating (zero load, part load, or full load).  Hours when the equipment is shut down are not included.

- For determining the annual operating time, the following steps were followed:

  - In 2006, a SoCalGas MAS query was conducted to identify gas customers with North American Industry Classification System (NAICS) categories 31, 32, or 33.  The query identified gas customers that had only process hot water boilers or only process hot water boilers in combination with gas space heating.  A similar query was run for steam boilers.

  - The results were divided into four categories:

    - ≤2 MMBtu/hr input with process hot water output

    - 2-10 MMBtu/hr input with process hot water output

    - ≤2 MMBtu/hr input with process steam output

    - 2-10 MMBtu/hr input with process steam output

  - The monthly scheduled operating time for each process boiler was calculated using data entered in the MAS database.  This data was typically entered in multiple fields in the form of hrs/day, days/week, and weeks/yr.

  - The annual operating time is 12 times the average monthly scheduled operating time.

  - The resulting annual operating times are listed in Table 8 below.

    - Load Factor

- The load factor for hot water and steam boilers are based on an analysis of the SoCalGas MAS database records and energy use data.  The load factor is the average load percentage during the scheduled operating hours (i.e., the actual gas consumption divided by maximum possible gas consumption by the process boiler).

- For determining load factors, the following steps were followed:

  - The SoCalGas MAS database was searched for customers meeting the following criteria:

    - North American Industry Classification System (NAICS) categories 31, 32, or 33.

    - Customers with process hot water boilers only, or process hot water boilers in combination with gas space heating boilers with rated input ≤10 MMBtu/hr.

    - Customers with process steam boilers only, or process steam boilers only in combination with gas space heating boilers with rated input ≤10 MMBtu/hr.

  - The results were divided into four categories:

    - ≤2 MMBtu/hr rated input, process hot water output

    - 2-10 MMBtu/hr rated input, process hot water output.

    - ≤2 MMBtu/hr rated input, process steam output

    - 2-10 MMBtu/hr rated input, process steam output

  - The monthly scheduled operating time for each process boiler was calculated using data entered in the MAS database. This data was typically entered in multiple fields in the form of hrs/day, days/week, and weeks/yr.

  - The maximum possible gas usage for the five-month period of May through September at a customer site was calculated by multiplying the nameplate boiler rated input by the scheduled operating hours.  It was assumed that during this time period, all of the gas consumption occurred due to process boiler use.  If the customer had more than one process boiler, all boilers were included in the calculation of maximum gas use.  If the customer had space heating boilers, they were not included in the calculation, since space heating boilers were assumed to not operate during the relatively warm five-month time period.

  - Actual gas usage for each customer was determined by examining the customer monthly billing records for 2004 (May-September).

  - Load factors were calculated by dividing the actual gas use by the maximum possible gas use.

  - To eliminate suspect records, customer sites with load factors greater than 100% or less than 10% were eliminated from the analysis.

  - After screening suspect records, 490 customer sites remained.  These 490 customer sites were used to compute weighted average load factors for each of the four categories (steam and hot water, ≤ 2 MMBtu/hr and 2-10 MMBtu/hr).  The resulting load factors are listed in Table 8 below.

- The baseline load factors for direct contact water heaters were set equal to the load factors for process hot water boilers (direct contact water heaters are assumed to be a replacement option for process hot water boilers).

Table 8 Average Load Factors and Operating Hours by Equipment Type

| Equipment Type | Process Hot Water Boiler |  | Process Steam Boiler |  |
| --- | --- | --- | --- | --- |
| Rated Input (MMBtu/hr) | ≤ 2 | 2 – 10 | ≤ 2 | 2 – 10 |
| Number of Customers Analyzed | 86 | 30 | 218 | 156 |
| Scheduled Annual Operating Time | 4,305 | 5,545 | 3,479 | 4,711 |
| Average Load Factor | 29.7% | 24.4% | 30.1% | 32.0% |

    - Rated Input

- To determine average equipment rated input, the SoCalGas MAS database was searched for customers meeting the following criteria:

  - North American Industry Classification System (NAICS) categories 31, 32, 33

  - Customers with process hot water boilers only, or process hot water boilers only in combination with gas space heating boilers with rated input ≤10 MMBtu/hr.

  - Customers with process steam boilers only, or process steam boilers only in combination with gas space heating boilers with rated input ≤10 MMBtu/hr.

- The results were divided into four categories:

  - ≤2 MMBtu/hr input, process hot water output

  - 2-10 MMBtu/hr input, process hot water output

  - ≤2 MMBtu/hr input, process steam output

  - 2-10 MMBtu/hr input, process steam output

- The monthly scheduled operating time for each process boiler was calculated using data entered in the MAS database.  This data was typically entered in multiple fields in the form of hrs/day, days/week, and weeks/yr.

- The maximum possible gas usage for the five-month period of May through September at a customer site was calculated by multiplying the nameplate boiler rated input by the scheduled operating hours.  It was assumed that during this time period, all of the gas consumption occurred due to process boiler use.  If the customer had more than one process boiler, all boilers were included in the calculation of maximum gas use.  If the customer had space heating boilers, they were not included in the calculation, since space heating boilers were assumed to not operate during the relatively warm five-month time period.

- Actual gas usage for each customer was determined by examining the customer monthly billing records for 2004 (May-September).

- Load factors were calculated by dividing the actual gas use by the maximum possible gas use.

- To eliminate suspect records, customer sites with load factors greater than 100% or less than 10% were eliminated from the analysis.

- After screening suspect records, 490 customers remained.  A weighted average of the equipment rated input for each of the four categories was computed, yielding the values shown in Table 9 below.

- The baseline rated inputs for direct contact water heaters were set equal to the baseline rated inputs for process hot water boilers (direct contact water heaters are assumed to be a replacement option for process hot water boilers).

Table 9 Average Rated Inputs by Equipment Type

| Equipment Type | Process Hot Water Boiler |  | Process Steam Boiler |  |
| --- | --- | --- | --- | --- |
| Rated Input (MMBtu/hr) | ≤ 2 | 2 – 10 | ≤ 2 | 2 – 10 |
| Number of Customers Analyzed | 86 | 30 | 218 | 156 |
| Average Rated Input (MBtu/hr) | 1,273 | 3,920 | 1,257 | 5,310 |

    - Equipment Efficiency

- Boiler Combustion Efficiencies.  Table 10 shows the range of process boiler combustion efficiencies found in the CEC Appliance Database [].  Only 25 medium steam boilers were listed with combustion efficiency at 83%, and none were higher.  Only 14 large steam boilers were listed with combustion efficiency at 83%, and none were higher.

- Figure 1 shows the distribution of combustion efficiency for non-condensing hot water boilers with rated input ≤2 MMBtu/hr.

- Figure 2 shows the distribution of combustion efficiency for non-condensing hot water boilers with rated input 2-10 MMBtu/hr.

- Figure 3 shows the distribution of combustion efficiency for condensing hot water boilers with rated input ≤2 MMBtu/hr.

- Figure 4 shows the distribution of combustion efficiency for condensing hot water boilers with rated input 2-10 MMBtu/hr.

- Figure 5 shows the distribution of combustion efficiency for steam boilers with rated input ≤2 MMBtu/hr.

- Figure 6 shows the distribution of combustion efficiency for steam boilers with rated input 2-10 MMBtu/hr.

Table 10 Boiler Efficiency Ranges from California Energy Commission Appliance Efficiency Database

| Equipment Type | Rated Input (MBtu/hr) | Efficiency Units | Minimum Efficiency | Maximum Efficiency |
| --- | --- | --- | --- | --- |
| Heating Products, Hot Water Boilers, Non-condensing | 300 – 2,000 | CE | 80.0% | 87.0% |
|  | 2,031 – 9,500 | CE | 80.0% | 87.0% |
| Heating Products, Hot Water Boilers, Condensing | 300 – 2,000 | CE | 85.3% | 98.3% |
|  | 2,160 – 5,443 | CE | 85.8% | 96.9% |
| Heating Products, Steam Boilers | 300 – 2,000 | CE | 80.0% | 86.0% |
|  | 2,049 – 10,000 | CE | 80.0% | 83.0% |

Figure 1 CEC Efficiency Data (Hot Water Boilers ≤2 MMBtu/hr, Non-condensing)

- Figure 2 CEC Efficiency Data (Hot Water Boilers 2-10 MMBtu/hr, Non-condensing)

- Figure 3 CEC Efficiency Data (Hot Water Boilers ≤2 MMBtu/hr, Condensing)

- Figure 4 CEC Efficiency Data (Hot Water Boilers 2-10 MMBtu/hr, Condensing)

- Figure 5 CEC Efficiency Data (Steam Boilers ≤2 MMBtu/hr)

- Figure 6 CEC Efficiency Data (Steam Boilers 2-10 MMBtu/hr)

- Baseline and Measure Efficiencies. Table 11 lists the efficiency units and efficiency values recommended for space heating boilers.

  - The minimum baseline efficiencies match the California Titles 20 and 24 standards for packaged and non-packaged space heater boilers in the same size range.

  - The qualifying measure efficiency for Tier 1 hot water is similar to the Tier 1 value for large space heating hot water boilers.

  - The qualifying measure efficiency for Tier 2 hot water matches the Tier 2 value for large space heating hot water boilers.

  - The qualifying measure efficiency for steam matches the value for large space heating steam boilers, and it is the highest practical qualifying efficiency given the lack of availability of any higher efficiency boilers in the CEC Appliance Database [L].

Table 11 Baseline and Qualifying Measure Efficiencies for Process Boilers

| Equipment Type | Rated Input (MBtu/hr) | Efficiency Units | Baseline Efficiency | Qualifying Efficiency |
| --- | --- | --- | --- | --- |
| Hot Water, Tier 1 (non-condensing) | 300-10,000 | CE | 80% | 85% |
| Hot Water, Tier 2 (condensing) | 300-10,000 | CE | 80% | 90% |
| Steam | 300-10,000 | CE | 80% | 83% |

    - Annual Energy Savings

- For calculating energy savings, the following assumptions are used:

  - The high-efficiency boiler has the same rated input (measured in MBtu/hr) as the boiler being replaced.

  - Both boilers deliver the same amount of hot water or steam on an annual basis (i.e., customer demand for hot water or steam does not change).

  - The average combustion efficiency of hot water and steam boilers for calculating energy savings is assumed to be equal to the average combustion efficiency of the high efficiency boilers in the CEC Appliance Database [L] that qualify:

    - Tier 1 hot water boilers with rated input ≤2 MMBtu/hr range from 85% to 87%, with an average of 85.6%.

    - Tier 1 hot water boilers with rated input >2 MMBtu/hr range from 85% to 87%, with an average of 85.5%.

    - Tier 2 hot water boilers with rated input ≤2 MMBtu/hr range from 90% to 98.3%, with an average of 94.4%.

    - Tier 2 hot water boilers with rated input >2 MMBtu/hr range from 90% to 96.9%, with an average of 93.4%.

    - Steam boilers with rated input ≤2 MMBtu/hr range from 83% to 86%, with an average of 83.2%.

    - Steam boilers with rated input >2 MMBtu/hr range were all 83%, with an average of 83%.

- With these assumptions, the energy saved by a new high-efficiency boiler is calculated as follows:

- ∆Q = t X LF X (R/100) X (1- Eb/Em)	Eqn-1

- Where

  - ∆Q – Energy Saved (therms/yr).  Savings which results from installing the high-efficiency equipment.

  - t – Scheduled Annual Operating Time (hrs/yr).  The scheduled operating time represents the time that gas equipment is expected to be in operation or available for operation at any rated input (zero load, part load, or full load).  Hours when the equipment is shut down are not included.

  - LF – Load Factor.  The load factor is the average load during the scheduled operating time, and is calculated by dividing the actual gas consumption by the maximum possible gas consumption during the scheduled operating time.  For non-modulating equipment (e.g., most storage water heaters), the load factor represents the fraction of time that the boiler is operating at its nameplate rated input.  For modulating equipment (e.g., most boilers), the load factor can be interpreted in one of two ways:  1) the equivalent fraction of the operating time that the gas equipment operates at its nameplate rated input, or 2) the average input (as a fraction of its nameplate rated input) during the operating time.  For a given time interval, a modulating gas system may operate at both part load and full load.

  - R – Rated Input (MBtuh).  The rated input is the maximum firing rate, which is generally equivalent to the nameplate rating.  The baseline and high-efficiency boilers are assumed to have the same rated input.

  - Eb – Baseline Efficiency (%).  Efficiency of the baseline boiler being replaced (also called the reference efficiency).

  - Em – Measure Efficiency (%).  Efficiency of the new high-efficiency boiler.

- The estimated energy savings for all three categories are shown in Table 12.  The data and calculations are included in an Excel file embedded as Attachment #5 [].

Table 12 Annual Energy Savings by Equipment Type

| Equipment Type | Tier 1 Hot Water Boiler |  | Tier 2 Hot Water Boiler |  | Steam Boiler |  |
| --- | --- | --- | --- | --- | --- | --- |
| Rated Input (MMBtu/hr) | ≤ 2 | 2 – 10 | ≤ 2 | 2 – 10 | ≤ 2 | 2 – 10 |
| Scheduled Annual Operating Time | 4,305 | 5,545 | 4,305 | 5,545 | 3,479 | 4,711 |
| Average Load Factor | 28.0% | 23.0% | 25.3% | 21.0% | 29.0% | 30.8% |
| Average Rated Input | 1,273 | 3,920 | 1,273 | 3,920 | 1,257 | 5,310 |
| Average Base Efficiency | 80% | 80% | 80% | 80% | 80% | 80% |
| Qualifying Measure Efficiency | 85% | 85% | 90% | 90% | 83% | 83% |
| Average Measure Efficiency | 85.6% | 85.5% | 94.4% | 93.4% | 83.2% | 83.0% |
| Annual Energy Savings (therms/yr/unit) | 1,065 | 3,412 | 2,483 | 7,609 | 506 | 2,893 |
| Annual Energy Savings (therms/yr/MBtuh) | 0.836 | 0.870 | 1.950 | 1.941 | 0.403 | 0.545 |
| Annual Energy Savings (therms/yr/MBtuh) | 0.85 |  | 1.95 |  | 0.47 |  |

- The estimated gas savings for SoCal territory were then used to calculate the savings for all 16 weather climate zones in California. From the basic principle of thermodynamics, the energy used by a boiler to raise the temperature of water is calculated by (Q = MC.∆T).  Assuming no changes on the boiler operating condition, the Mass flow rate and Specific heat of water for the 16 weather zones should be the same. However, the water temperature difference will vary for the 16 weather zones, since the ground source water temp for these zones averages from (51 to 75°F). Therefore, the previous energy balance equation can be simplified in the following correlation formula:

- ∆Q zones (1-16) = ∆Qzone-9(SoCal) x (TSoCal - TMixed temp. zones (1-16)) / (TSoCal - TMixed temp. zone9)	Eqn-2

- Where:

  - ∆Q = Energy Saved (therms/yr).  Savings which results from installing the high-efficiency measure equipment for each boiler category and weather zone.

  - T = Supply & Return Temperatures of the hot water leaving and entering the boiler, respectively.

  - Subscript zones (1-16) = California weather zones 1 thru 16, measure (new high-efficiency) equipment.

  - Subscript zone-9(SoCal) =  SoCal savings, used as baseline (reference) equipment

  - Subscript Mixed temperature = The mixed water temp entering the boiler will include the following:

    - Return water and makeup water (for HW boiler)

    - Return water, makeup water and the condensate from the flue gas water vapor (for condensing boiler)

    - Steam condensate return, makeup water and steam preheating the feedwater at the deareator (for steam boiler).

  - Mixed Temperature was included in equ.2 for the proposed measure (zones 1-16) and baseline (standard, zone-9).

  - The Supply temperature for three boiler categories used in the calculations, and shown in Table 13, were based on Commercial & Industrial sets of data used in other SCG documents, such as the Pipe Insulation workpaper.

Table 13 Fluid Temperature Specification and Assumptions

| Working Fluid | Rated Input (MMBtu/hr) | Fluid Temperature (F) |  |
| --- | --- | --- | --- |
|  |  | Specification | Used in Analysis |
| Hot Water Boiler | Any | 120-200 | 150 |
| Condensing Boiler | Any | 160-200 | 180 |
| Small Steam Boiler | ≤ 2 | 200-250 | 241 |
| Large Steam Boiler | 2 – 10 | 250-500 | 328 |

- The estimated energy savings of the three boiler categories in the California’s 16 weather zones are shown in the Measure Summary Table.  The data and calculations are included in the Excel file of Attachment #5 [M].

    - For all the savings discussed above, there is an installation rate applied to values associated with the installation GSIA ID in Table 14. The GSIA ID is identified in the ex-ante implementation tables for all programs and measures. The installation rate (IR) is applied to the gross savings calculations using the values associated with the IDs below.

Table 14 Gross Savings Installation Adjustment (GSIA) IDs

| GSIA_ID | Description | Sector | BldgType | UseCategory | TechType |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA | Any | Any | Any | Any |

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available. Therefore, for the sake of the E3 calculation, the closest load shape chosen for this measure is the 35-OTI-OtherIndustrial-PROC_OTH load shape. See Table 15 for a list of all Building Types and Load Shapes. See the KEMA report for a more thorough discussion regarding the load shapes for this measure.

Table 15 Building Types and Load Shapes

| Building Type | Load Shape |
| --- | --- |
| Assembly | 35-OTI-OtherIndustrial-PROC_OTH |
| Education - Primary School | 35-OTI-OtherIndustrial-PROC_OTH |
| Education - Secondary School | 35-OTI-OtherIndustrial-PROC_OTH |
| Education - Community College | 35-OTI-OtherIndustrial-PROC_OTH |
| Education - University | 35-OTI-OtherIndustrial-PROC_OTH |
| Grocery | 35-OTI-OtherIndustrial-PROC_OTH |
| Food Store | 35-OTI-OtherIndustrial-PROC_OTH |
| Health/Medical - Hospital | 35-OTI-OtherIndustrial-PROC_OTH |
| Health/Medical - Nursing Home | 35-OTI-OtherIndustrial-PROC_OTH |
| Health/Medical - Clinic | 35-OTI-OtherIndustrial-PROC_OTH |
| Lodging - Hotel | 35-OTI-OtherIndustrial-PROC_OTH |
| Lodging - Guest Rooms | 35-OTI-OtherIndustrial-PROC_OTH |
| Lodging - Motel | 35-OTI-OtherIndustrial-PROC_OTH |
| Manufacturing - Bio/Tech | 35-OTI-OtherIndustrial-PROC_OTH |
| Manufacturing - Light Industrial | 35-OTI-OtherIndustrial-PROC_OTH |
| Misc - Commercial | 35-OTI-OtherIndustrial-PROC_OTH |
| Office - Large | 35-OTI-OtherIndustrial-PROC_OTH |
| Office - Small | 35-OTI-OtherIndustrial-PROC_OTH |
| Restaurant - Fast-Food | 35-OTI-OtherIndustrial-PROC_OTH |
| Restaurant - Sit-Down | 35-OTI-OtherIndustrial-PROC_OTH |
| Retail - Multistory Large | 35-OTI-OtherIndustrial-PROC_OTH |
| Retail - Single-Story Large | 35-OTI-OtherIndustrial-PROC_OTH |
| Retail - Small | 35-OTI-OtherIndustrial-PROC_OTH |
| Storage - Conditioned | 35-OTI-OtherIndustrial-PROC_OTH |
| Storage - Unconditioned | 35-OTI-OtherIndustrial-PROC_OTH |
| Transportation - Communication - Utilities | 35-OTI-OtherIndustrial-PROC_OTH |
| Warehouse - Refrigerated | 35-OTI-OtherIndustrial-PROC_OTH |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

- When the customer is replacing equipment on burnout (ROB) or buying new equipment (NEW), the customer must buy a new boiler to continue operating, so the base case cost is that of a baseline (standard) boiler.

- The base case costs are shown in Table 16 below.

  - The upper section of the table lists the 2008 DEER cost data taken from the “2011 Database for Energy-Efficient Resources (DEER) for Use in the California IOU 2013-14 Energy Efficiency Planning” [].  The average base case costs are the average of the measure cost for boilers with medium rated input (between 300 and 2,500 MBtu/hr) and with large rated input (over 2,500 MBtu/hr).  In addition, the equipment efficiency ranges used for the DEER cost data do not match the equipment efficiency ranges used in this workpaper.

    - The 2008 DEER base thermal efficiency for medium rated input is 75%.

    - The 2008 DEER base combustion efficiency for large rated input is 75%.

  - The middle section of the table lists the results of a survey of equipment vendors that sell process hot water and steam boilers in California.  The vendor calls produced data for the categories of boiler type, rated input, and efficiency used in this workpaper.  The base measure costs shown in Table 16 represent an arithmetic average of the equipment cost per MBtu/hr in each category.

  - The lower section of the table lists the average of the DEER cost data and the survey data.  The data and calculations are included in an Excel file embedded as Attachment #7 [].

## 4.2 Gross Measure Cost

- The gross measure costs include the cost of the equipment, excluding installation and start-up costs.  For the purposes of determining incremental measure costs, the installation and start-up costs are assumed to be the same for the base case and measure equipment.

- The gross measure costs are shown in Table 16 below.

  - The upper section of the table lists the 2008 DEER cost data taken from the “2011 Database for Energy-Efficient Resources (DEER) for Use in the California IOU 2013-14 Energy Efficiency Planning” [N].  The average gross measure costs are the average of the measure cost for boilers with medium rated input (between 300 and 2,500 MBtu/hr) and with large rated input (over 2,500 MBtu/hr).  In addition, the equipment efficiency ranges used for the DEER cost data do not match the equipment efficiency ranges used in this workpaper.

    - The 2008 DEER measure thermal efficiency for medium rated input is 85%.

    - The 2008 DEER measure combustion efficiency for large rated input is 85%.

  - The middle section of the table lists the results of a survey of equipment vendors that sell hot water and steam space heating boilers in California.  The gross measure costs shown in Table 16 represent an arithmetic average of the equipment cost per MBtu/hr in each category.

  - The lower section of the table lists the average of the DEER cost data and the survey data.  The cost data and calculations are included in an Excel file embedded as Attachment #7 [O].

## 4.3 Incremental Measure Cost

- The incremental measure cost (IMC) is the difference between the average base case cost and the average gross measure cost.

- The incremental measure costs are shown in Table 16 below.

Table 16 Gross and Incremental Measure Cost by Equipment Type

| Equipment Type | Process Hot Water Boiler, Tier 1 | Process Hot Water Boiler, Tier 2 | Process Steam Boiler |
| --- | --- | --- | --- |
| Rated Input (MMBtu/hr) | ≥ 300 | ≥ 300 | ≥ 300 |
| 2008 DEER Cost Data |  |  |  |
| Average Base Cost ($/MBtuh) | $9.33 | N/A | N/A |
| Average Gross Measure Cost ($/MBtuh) | $10.72 | N/A | N/A |
| Average Incremental Measure Cost ($/MBtuh) | $1.39 | N/A | N/A |
| 2012 Vendor Survey Data |  |  |  |
| Average Base Cost ($/MBtuh) | $12.22 | $12.22 | $14.89 |
| Average Gross Measure Cost ($/MBtuh) | $15.17 | $22.95 | $19.24 |
| Average Incremental Measure Cost ($/MBtuh) | $2.95 | $10.73 | $4.35 |
| Average of DEER and 2012 Vendor Survey Data |  |  |  |
| Base Case ($/MBtuh) | $10.78 | $10.78 | $14.89 |
| Average Gross Measure Cost ($/MBtuh) | $12.94 | $22.95 | $19.24 |
| Average Incremental Measure Cost ($/MBtuh) | $2.17 | $12.17 | $4.35 |

# Attachments

# References

[] Attachment #1 – Calculation Template v2.2.xlsm.

[] SDG&E’s Energy Efficiency Business Rebates Natural Gas Catalog. http://www.sdge.com/rebates-finder/earn-rebates-your-improvements

[] Attachment #2 - Space Heating Boilers Workpaper, Revision A, EEA Report No. B-REP-06-599-01A, March 20, 2006.

[] Database for Energy Efficiency Resources, 2014. http://www.deeresources.com/

[] Attachment #3 - “Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008)_Original.xls”, http://www.deeresources.com/index

[] California Energy Commission Appliance Efficiency Database (Accessed March 7, 2012 at http://www.appliances.energy.ca.gov/AdvancedSearch.aspx).

[] DEER Database for Energy-Efficient Resources, Version 2011 4.00, For Use in the California IOU 2013-14 Energy Efficiency Planning (Accessed Mar. 7, 2012 at http://www.deeresources.com/).

[] The 2014 Appliance Efficiency Regulations – Title 20: http://www.energy.ca.gov/2014publications/CEC-400-2014-009/CEC-400-2014-009-CMF.pdf

[] The 2013 Building Energy Efficiency Standards for Residential and Nonresidential Buildings – Title 24, Part 6: http://www.energy.ca.gov/2012publications/CEC-400-2012-004/CEC-400-2012-004-CMF-REV2.pdf

[] DEER2011 Update Net-To-Gross table  (05/16/2012) http://www.deeresources.com/files/DEER2011/download/DEER2011_NTGR_2012-05-16.xls

[] Attachment #4 – Average Input and Load Factor Calculations

[] California Energy Commission Appliance Efficiency Database (Accessed March 7, 2012 at http://www.appliances.energy.ca.gov/AdvancedSearch.aspx).

[] Attachment #5 – Process Boiler Annual Gas Savings Data and Calculations

Attachment #6 - Technology and Measure Cost Data/Effective and Remaining Useful Life (EUL/RUL) Values,  http://www.deeresources.com/index. (EUL_Summary_10-1-08.xls)

[] Attachment #7 – Process Boiler Cost Data and Calculations