Workpaper WPSDGENRWH0014

Tank Insulation

Revision 0

San Diego Gas & Electric Company

Energy Efficiency Engineering

Tank Insulation

Measure Codes G-I1, G-I2, G-I3, G-I4

# At-A-Glance Summary

| Applicable Measure Codes: | G-I4 | G-I3 | G-I2 | G-I1 |
| --- | --- | --- | --- | --- |
| Measure Description: | This measure provides incentives for installing 2” thick insulation on a bare tank (120º-170ºF) | This measure provides incentives for installing 1” thick insulation on a bare tank (120º-170ºF) | This measure provides incentives for installing 2” thick insulation on a bare tank (170º-200ºF) | This measure provides incentives for installing 1” thick insulation on a bare tank (170º-200ºF) |
| Energy Impact Common Units: | sq. ft. of insulation | sq. ft. of insulation | sq. ft. of insulation | sq. ft. of insulation |
| Base Case Description: | Bare uninsulated tank | Bare uninsulated tank | Bare uninsulated tank | Bare uninsulated tank |
| Base Case Energy Consumption: | Source: PG&E calculations 15.21 therms/yr.ft2 | Source: PG&E calculations 15.21 therms/yr.ft2 | Source: PG&E calculations 26.90 therms/yr.ft2 | Source: PG&E calculations 26.90 therms/yr.ft2 |
| Measure Energy Consumption: | Source: PG&E calculations 1.02 therms/yr.ft2 | Source: PG&E calculations 1.79 therms/yr.ft2 | Source: PG&E calculations 1.70 therms/yr.ft2 | Source: PG&E calculations 3.02 therms/yr.ft2 |
| Energy Savings (Base Case – Measure) | Source: PG&E calculations 14.18 therms/yr.ft2 | Source: PG&E calculations 13.41 therms/yr.ft2 | Source: PG&E calculations 25.19 therms/yr.ft2 | Source: PG&E calculations 23.88 therms/yr.ft2 |
| Costs Common Units: | sq. ft. of insulation | sq. ft. of insulation | sq. ft. of insulation | sq. ft. of insulation |
| Base Case Equipment Cost ($/unit): | Source: N/A 0. | Source: N/A 0. | Source: N/A 0. | Source: N/A 0. |
| Measure Equipment Cost ($/unit): | Source: MEANS Mechanical Cost 2007Error: Reference source not found and McMaster Carr catalogError: Reference source not found $7.87 | Source: MEANS Mechanical Cost 2007Error: Reference source not found and McMaster Carr catalogError: Reference source not found $8.94 | Source: MEANS Mechanical Cost 2007Error: Reference source not found and McMaster Carr catalogError: Reference source not found $7.87 | Source: MEANS Mechanical Cost 2007Error: Reference source not found and McMaster Carr catalogError: Reference source not found $8.94 |
| Measure Incremental Cost ($/unit): | Equal to Measure Equipment Cost above | Equal to Measure Equipment Cost above | Equal to Measure Equipment Cost above | Equal to Measure Equipment Cost above |
| Effective Useful Life (years): | Source: CALMACError: Reference source not found 15 years | Source: CALMACError: Reference source not found 15 years | Source: CALMACError: Reference source not found 15 years | Source: CALMACError: Reference source not found 15 years |
| Program Type: | Replace on Burnout (ROB) | Replace on Burnout (ROB) | Replace on Burnout (ROB) | Replace on Burnout (ROB) |
| Net-to-Gross Ratios: | 0.60 Source: DEER 2011, NTGR_ID: Ind-Default>2yrs | 0.60 Source: DEER 2011, NTGR_ID: Ind-Default>2yrs | 0.60 Source: DEER 2011, NTGR_ID: Ind-Default>2yrs | 0.60 Source: DEER 2011, NTGR_ID: Ind-Default>2yrs |

# At-A-Glance Measure List

|  |  |  |  |  |  |  |  | 1st Baseline |  |  |  |  |  |  |  | 2nd Baseline |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Code | Version Source | Measure Description | Measure Application Type | Building Type | Building Vintage | Climate Zone | Unit Definition | KW Peak Electric Demand Reduction | KWh Electric Savings | THM Gas Savings | (EUL) LIFE CYCLE | Base Case Cost ($/unit) | Measure Cost ($/unit) | Labor Cost ($/unit) | IMC Incremental Measure Cost ($/unit) | KW Peak Electric Demand Reduction | KWh Electric Savings | THM Gas Savings | LIFE CYCLE | Base Case Cost ($/unit) | Measure Cost ($/unit) | Labor Cost ($/unit) | IMC Incremental Measure Cost ($/unit) | GRR_ kW | GRR_ kWh | GRR_ therm | NTG | Implementation Method [DI, DD, I] | ISR |
| G-I4 | N/A | 2” thick tank insulation – liquid or solution temperature 120–170ºF | ROB | ANY | ANY | IOU | Area-ft2 | 0 | 0 | 14.18 | 15 | 0 | 2.73 | 6.21 | 8.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.6 | I | 1 |
| G-I3 | N/A | 1” thick tank insulation – liquid or solution temperature 120–170ºF | ROB | ANY | ANY | IOU | Area-ft2 | 0 | 0 | 13.41 | 15 | 0 | 1.94 | 5.93 | 7.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.6 | I | 1 |
| G-I2 | N/A | 2” thick tank insulation – liquid or solution temperature 170-200ºF | ROB | ANY | ANY | IOU | Area-ft2 | 0 | 0 | 25.19 | 15 | 0 | 2.73 | 6.21 | 8.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.6 | I | 1 |
| G-I1 | N/A | 1” thick tank insulation – liquid or solution temperature 170–200ºF | ROB | ANY | ANY | IOU | Area-ft2 | 0 | 0 | 23.88 | 15 | 0 | 1.94 | 5.93 | 7.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.6 | I | 1 |

# Work Paper Approvals

| Peter Ford Manager, Energy Efficiency Engineering | Date |
| --- | --- |
| Charles Harmstead Supervisor, Energy efficiency Engineering | Date |

# Document Revision History

Revision # 		Date 		         Description		         Author (Company)

| Revision 0 | 10/8/13 | Adopted PGECOPRO103 R4.doc dated August 29, 2012 | Charles Harmstead |
| --- | --- | --- | --- |

# Table of Contents

At-A-Glance Summary	i

At-A-Glance Measure List	ii

Work Paper Approvals	iii

Document Revision History	iv

Table of Contents	v

List of Tables	vi

List of Figures	vi

Section 1. General Measure & Baseline Data	7

1.1 Measure Description & Background	7

1.2 DEER Differences Analysis	7

1.3 Codes & Standards Requirements Analysis	8

1.4 EM&V, Market Potential, and Other Studies	8

1.5 Base Cases for Savings Estimates: Existing & Above Code	8

1.6 Base Cases & Measure Effective Useful Lives	8

1.7 Net-to-Gross Ratios for Different Program Strategies	8

Section 2. Calculation Methods	8

2.1 Electric Energy Savings Estimation Methodologies	8

2.2. Demand Reduction Estimation Methodologies	8

2.3. Gas Energy Savings Estimation Methodologies	9

Section 3. Load Shapes	11

3.1 Base Case Load Shapes	11

3.2 Measure Load Shapes	11

Section 4. Base Case & Measure Costs	12

4.1 Base Case(s) Costs	12

4.2 Measure Costs	12

4.3 Incremental & Full Measure Costs	13

Index	14

References	15

# List of Tables

Table 1:  DEER USE and TECHNOLOGY TABLE	8

Table 2 - Net-to-Gross Ratios	8

Table 3 – Insulation Conductivity	10

Table 4 - Energy Savings Calculations	11

Table 5 – Measure materials costs	12

Table 6 – Measure labor costs	12

Table 7 – Measure total costs	13

# List of Figures

Figure 1 – Hot water boiler efficiencies from the CEC listing	10

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

Catalog Description

Requirements:

- One or two inch diameter of fiberglass or foam insulation must be added to existing bare liquid, solution storage or transfer tanks.

- The tanks must be coupled to gas-fired commercial or industrial equipment that transfers heat to the contained liquid or solution.

- Tanks with pre-existing insulation do not qualify for a rebate.  This rebate cannot be used for the replacement of old or damaged insulation.

- California Building Energy Efficiency Standards (Title 24), Section 123 establishes requirements for tank insulation in the design and installation of space-conditioning and service water heating systems and equipment.  Any tank requiring insulation per these standards does not qualify for a rebate.  Details are available at www.energy.ca.gov/title24.

- Tanks insulated to prevent burns do not qualify for rebate.  Insulation for exposed hot-water tanks within 7 feet of the floor that are not otherwise guarded in such manner as to prevent contact do not qualify for rebate.

Application Process:

- The insulation thickness and tank solution temperature will determine the rebate amount.

- Must include manufacturer’s name, insulation material type and the material k-value rating.

Program Restrictions and Guidelines

Terms and Conditions

See Catalog Description above.

Market Applicability

This measure applies to most commercial and industrial facilities, including, but not limited to, offices, restaurants, retail, schools, colleges, hotels, motels, and recreational facilities.

Technical Description

Owing to first cost sensitivity and/or a low level of awareness, many commercial and industrial customers – particularly smaller, hard to reach businesses – install tanks and piping systems with no insulation. These measures address cost-effective energy efficiency opportunities in the tank insulation area.

Installing insulation on a bare surface greatly reduces heat losses to ambient air, achieving significant energy savings at a relatively low cost.

## 1.2 DEER Differences Analysis

The DEER database does not contain any measure for tank surface insulation.

Table 1:  DEER USE and TECHNOLOGY TABLE

## 1.3 Codes & Standards Requirements Analysis

This measure is not governed by either state or federal codes and standards.

## 1.4 EM&V, Market Potential, and Other Studies

There are no EM&V studies identified that address commercial and industrial tank insulation.

## 1.5 Base Cases for Savings Estimates: Existing & Above Code

The base case is a tank with no insulation.

## 1.6 Base Cases & Measure Effective Useful Lives

DEER 2011 doesn’t contain an EUL for this measure.  The document “CADMAC Protocol and Procedures for the Verification of Costs, Benefits, and Shareholder Earnings, Appendix F - Effective Useful Life Values for Major Energy Efficiency Measures” shows an EUL of 15 years for tank insulation measures.

## 1.7 Net-to-Gross Ratios for Different Program Strategies

Table 2 below summarizes all applicable Net-to-Gross ratios for programs that may be used by this measure.  The NTGR for this measure is a default value taken from DEER 2011 equaling 0.60.  This NTGR represents the default for existing industrial measures with no evaluated NTGR that have had the same delivery mechanism for more than two years.

Table 2 - Net-to-Gross Ratios

|  |  |  | DEER Spreadsheet |  |
| --- | --- | --- | --- | --- |
| Program Approach | NTG | NTGR_ID | File name | Cell Number |
| ROB | 0.60 | Ind-Default>2yrs | DEER2011_NTGR_2012-05-16.xls | U57 |

# Section 2. Calculation Methods

## 2.1 Electric Energy Savings Estimation Methodologies

There are no electric energy savings associated with these gas measures.

## 2.2. Demand Reduction Estimation Methodologies

There is no demand reduction associated with these gas measures.

## 2.3. Gas Energy Savings Estimation Methodologies

The savings from this method result from reduced heat losses on the tank surface, resulting in reduced heating load on the connected gas-fired equipment. The savings were calculated as the difference in heat losses between the uninsulated tank surface (base case) and the insulated surface (measure). Average boiler efficiency (calculated from the CEC boiler listing)Error: Reference source not found was then factored in to translate the reduced heat losses from the tank into reduced gas consumption of the boiler.

### Methodology

The annual energy saved by pipe insulation can be calculated as follows:

ΔQ=t∗(Qb−Qi)100,000∗Eb

Where:

Q = annual energy savings (in therms)

t = annual operating time, in hours

Qb = Heat Loss from Bare Tank (Btu/hr/ft2)

Qi = Heat Loss from Insulated Tank (Btu/hr/ft2)

Eb = Efficiency (%) of the boiler being used to generate the hot water or steam in the pipe

100,000 = conversion factor (1 therm = 100,000 Btu)

### Heat loss calculations

The heat loss calculations were performed using industry-accepted software from the North American Insulation Manufacturers Association (NAIMA). The NAIMA 3E Plus v4 software uses the calculation methodology from the most recent version of the ASTM C 680 Standard. The main inputs used in the software were:

- Base case: bare surface (to stay consistent with catalog Terms and Conditions)

- Base tank material: steel – emissivity: 0.8
Steel is the most common material for hot water tanks

- Insulation material: Fiber glass-type insulation (cellular glass BLOCK, Gr1, C552-03). The temperature-dependent thermal conductivity of the fiber glass used by 3E Plus software is shown in Table 3 – Table 3. Foam insulation (the other acceptable type of material in this measure) has similar R-values to fiber glass and provides similar savings to fiberglass, since the savings are driven primarily by the heat losses from the base case (uninsulated tank).

- Operating hours: 8,760 hours / yr 
(assuming continuous tank operation)

- Process temperature (temperature inside the tank): 145ºF for H13 and H114, 185ºF for H18 and H115. 
Temperatures were chosen as the midpoints of the temperature ranges for each measure. 145ºF = (120 ºF +170 ºF)/2, 185 ºF = (170 ºF +200 ºF)/2

- Ambient temperature: 75ºF – typical indoor ambient temperature

Table 3 – Insulation Conductivity

### Boiler efficiency

To convert reduced heat losses from the tank into energy savings of the boiler, boiler efficiency needs to be taken into account. To determine representative boiler efficiencies, data from the California Energy Commission (CEC) was examined. The CEC lists several hundred steam and hot water boilers. The average efficiency of the boilers in this listing was calculated for steam boilers and hot water boilers, both for small and large boilers listings. We obtained an average efficiency value of 82.5% for hot water boilers and used this value to compute the energy input for hot water and steam generation.

The figures below show the distribution of combustion efficiencies based on the CEC listing data.

Figure 1 – Hot water boiler efficiencies from the CEC listing

### Results

Table 4 below presents the inputs and the results of the energy savings calculations for this measure.

Table 4 - Energy Savings Calculations

G-I4                G-I3                  G-I2             G-I1

# Section 3. Load Shapes

Load Shapes are an important part of the life-cycle cost analysis of any energy efficiency program portfolio.  The net benefits associated with a measure are based on the amount of energy saved and the avoided cost per unit of energy saved.  For electricity, the avoided cost varies hourly over an entire year.  Thus, the net benefits calculation for a measure requires both the total annual energy savings (kWh) of the measure and the distribution of that savings over the year.  The distribution of savings over the year is represented by the measure’s load shape.  The measure’s load shape indicates what fraction of annual energy savings occurs in each time period of the year.  An hourly load shape indicates what fraction of annual savings occurs for each hour of the year.  A Time-of-Use (TOU) load shape indicates what fraction occurs within five or six broad time-of-use periods, typically defined by a specific utility rate tariff.  Formally, a load shape is a set of fractions summing to unity, one fraction for each hour or for each TOU period.  Multiplying the measure load shape with the hourly avoided cost stream determines the average avoided cost per kWh for use in the life cycle cost analysis that determines a measure’s Total Resource Cost (TRC) benefit.

## 3.1 Base Case Load Shapes

Load shapes are not applicable to gas measures, because the price of gas is not dependent on time-of-use.

## 3.2 Measure Load Shapes

Load shapes are not applicable to gas measures, because the price of gas is not dependent on time-of-use.

# Section 4. Base Case & Measure Costs

## 4.1 Base Case(s) Costs

There are no base case costs associated with these measures. The base case is existing tanks with no insulation.

## 4.2 Measure Costs

Typical material costs for this measure were estimated using the McMaster-Carr website. The cost data below was updated to match the McMaster-Carr data as of June 2012.  Different insulation materials meeting the measures requirements were priced for 1 inch and 2 inch thicknesses, and a simple average of these costs was used.

Typical installation labor costs were calculated using MEANS and assuming a 25% overhead and profit (O&P).  Labor cost data for this measure is not available in the 2011 version of RS MEANS, so the 2007 data is still used.

Table 5 – Measure materials costsError: Reference source not found

Material cost

Material

McMaster Item

#

1 in thickness

rigid fiberglass w aluminium jacket

1.65

9350K1

rigid polystyrene foam

1.53

9255K1

Fiberglass

0.72

9160K4

Aluminium insulation jacketing

1.91

Fiberglass + alu jacket - total cost

2.63

2 in thickness

Rigid fiberglass w aluminium jacket

2.52

9350K3

rigid polystyrene foam

2.92

9255K3

Fiberglass

0.83

9346K38

Aluminium insulation jacketing

1.91

Fiberglass + alu jacket - total cost

2.74

average cost ($ / ft

2

)- 1 in

1.94

average cost ($ / ft

2

)- 2 in

2.73

Material Cost

($ / ft

2

)

Table 6 – Measure labor costsError: Reference source not found

Table 7 – Measure total costs

Cost summary

1 inch

2 inches

H13 H18

H114 - H115

Material costs ($ / ft

2

)

$1.94

$2.73

Labor costs ($ / ft

2

)

$5.93

$6.21

Total Cost ($ / ft

2

)

$7.87

$8.94

G-I1, G-I3                                                                              G-I4,G-2

## 4.3 Incremental & Full Measure Costs

Incremental costs are equal to measure costs since the base costs are zero. Full measure costs are equal to measure costs.

# Index

3E Plus v4 software	9

ASTM C 680 Standard	9

Boiler efficiency	10

California Energy Commission	See CEC

CEC	10

cellular glass	9

DEER	7

Effective Useful Life	See EUL, See EUL

EUL	8

heat losses	7, 9

Load Shapes	11

Process temperature	10

# References

? CADMAC Protocol and Procedures for the Verification of Costs, Benefits, and Shareholder Earnings, Appendix F - Effective Useful Life Values for Major Energy Efficiency Measures – pg 18, measure 151 – water heating, insulation, boiler / storage tank

DEER2011_NTGR_2012-05-16.xls from  DEER Database for Energy-Efficient Resources; Version 2011 4.01 found at :http://www.deeresources.com/index.php?option=com_content&view=article&id=68&Itemid=60

Under: DEER2011 Update Documentation linked at: DEER2011 Update Net-To-Gross table

Cells: (U57)

3E Plus® v4 Insulation Thickness Computer Program - http://www.pipeinsulation.org/

ASTM C 680 Standard Practices for Determination of Heat Gain or Loss and the Surface Temperature of Insulation Piping on Equipment Systems by the Use of a Computer System – www.astm.org

CEC Appliances database: http://www.appliances.energy.ca.gov/

McMaster-Carr catalog, items #9350K1, 9255K1, 9160K4, 9350K3, 9255K3, 9346K38

www.mcmaster.com , retrieved June 2012

MEANS 2007 Mechanical data, items # 23-07-16.10-2420, 23-07-16.10-2440

# Attachments