Work Paper WPSDGEREHC1065

Revision 1

San Diego Gas & Electric

Residential HVAC Quality Maintenance and Motor Retrofit

### Core Measure Summary Table

| General Measure Information |  |  |  |  |  |  |  | PT |  | 1st Baseline Period |  |  |  | 2nd Baseline Period |  |  |  | TOU |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Measure RunID | Solution Code | CZ | Building Type | Load Shape | EUL | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | Gross Unit Annual Electricity Savings (kWh/unit) | User Entered kW Savings per unit (kW/unit) | Gas Savings (Therms) | 1st Baseline Useful Life | kWh Saving per unit (kWh/unit) | kW Savings per unit (kW/unit) | Gas Savings (Therms) | 2nd Baseline Useful Life | % TOU |
| HVAC Quality Maintenance |  | n/a | 06 | Residential Single Family | DEER:HVAC_Eff_AC | 5.0 | Ton | RET | No | 12.24 | 0.01 | -0.02 | 5.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| HVAC Quality Maintenance |  | n/a | 07 | Residential Single Family | DEER:HVAC_Eff_AC | 5.0 | Ton | RET | No | 14.20 | 0.02 | -0.01 | 5.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| HVAC Quality Maintenance |  | n/a | 08 | Residential Single Family | DEER:HVAC_Eff_AC | 5.0 | Ton | RET | No | 20.33 | 0.04 | -0.01 | 5.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| HVAC Quality Maintenance |  | n/a | 10 | Residential Single Family | DEER:HVAC_Eff_AC | 5.0 | Ton | RET | No | 23.34 | 0.04 | -0.01 | 5.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| HVAC Quality Maintenance |  | n/a | 14 | Residential Single Family | DEER:HVAC_Eff_AC | 5.0 | Ton | RET | No | 38.91 | 0.05 | 0.00 | 5.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| HVAC Quality Maintenance |  | n/a | 15 | Residential Single Family | DEER:HVAC_Eff_AC | 5.0 | Ton | RET | No | 41.18 | 0.04 | 0.00 | 5.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet

### Costing and NTG Summary Table

| General Measure Information |  |  |  | PT |  | NTG |  |  | IR | 1st Baseline Period | 2nd Baseline Period | IMC | DIM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Solution Code | CZ | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | NTG Non-Res. | NTG Res. | NTG Multi Family | Installation Rate | Gross Measure Cost per unit | Gross Measure Cost per unit | Incremental Measure Cost per unit | Delivery & Incentive Method |
| HVAC Quality Maintenance | n/a | 6 | Ton | RET | No |  | 0.70 |  | 1.00 | $103.79 | $0.00 | $5.68 | Financial Support / Down-Stream Incentive - Deemed |
| HVAC Quality Maintenance | n/a | 7 | Ton | RET | No |  | 0.70 |  | 1.00 | $124.21 | $0.00 | $8.44 | Financial Support / Down-Stream Incentive - Deemed |
| HVAC Quality Maintenance | n/a | 8 | Ton | RET | No |  | 0.70 |  | 1.00 | $109.74 | $0.00 | $6.56 | Financial Support / Down-Stream Incentive - Deemed |
| HVAC Quality Maintenance | n/a | 10 | Ton | RET | No |  | 0.70 |  | 1.00 | $93.38 | $0.00 | $5.50 | Financial Support / Down-Stream Incentive - Deemed |
| HVAC Quality Maintenance | n/a | 14 | Ton | RET | No |  | 0.70 |  | 1.00 | $75.32 | $0.00 | $4.53 | Financial Support / Down-Stream Incentive - Deemed |
| HVAC Quality Maintenance | n/a | 15 | Ton | RET | No |  | 0.70 |  | 1.00 | $72.72 | $0.00 | $4.43 | Financial Support / Down-Stream Incentive - Deemed |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet

# Document Revision History

| Revision # | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 06/26/2012 | Peter Ford (SDGE) | Adopted PECI Workpaper SDGEREHC002_0 by Janice Peterson, PECI, dated 29 January 2012. Updated NTG to DEER 2011, converted to SDG&E numbering and changed minor formatting. Embedded savings & measures files for reference |
| 0.1 | 01/23/2014 | Phillip Hasley/Hasley Consulting | -Updated workpaper to be in compliance with CPUC ED Disposition dated May 2, 2013 -Broke out Duct Sealing measure as a separate measure from Quality Maintenance -Changed EUL to 5 years -Changed NTG to 0.70 -Updated savings values to conform to ED Disposition approved values -Removed Restore and Improve Duct System Insulation treatment per ED Disposition -Updated workpaper to new Template |

Document History Reminders

# Section 1. General Measure & Baseline Data

## 1.1  Measure & Delivery Description

### 1.1a Measure Description

This work paper details the Residential HVAC Quality Maintenance (QM) and Motor Retrofit measure for packaged and split system HVAC units.  The work paper includes the QM measure which consists of multiple treatments related to HVAC unit optimization, duct testing and sealing (DTS) and the installation of a brushless direct current (BDC) motor with selectable speed control designed to directly replace a permanent split capacitor (PSC) motor in a residential direct drive blower fan application.  The measures in this work paper apply only to residential single family building types with central air conditioning (direct expansion) and gas heat.

This work paper includes the following possible measures and treatments:

- HVAC Quality Maintenance

  - Possible Treatments:

- Refurbish degraded ducts

- Condenser coil cleaning

- Evaporator coil cleaning

- New Air Filter to Match the Blower

- TXV attachment and insulation correction

- Refrigerant system test and charge adjustment

- HVAC Duct Test and Seal

  - Possible Treatments:

- Refurbish degraded ducts

- Duct Seal

- HVAC Brushless Direct Current Blower Motor Replacing Standard Eff Motor

Measure A contains several possible treatments related to the performance of the HVAC equipment and air distribution.  Savings are determined by expected value analysis for this group.  Measure B includes refurbishing and sealing ducts.  Measure C is a motor retrofit that is likely to be installed in only a small percentage of homes.  Savings for the motor retrofit are analyzed separately, assuming that measures A and B have already been applied.

The level of maintenance by technicians on a typical air conditioner unit is minimal with service being performed at an unacceptable level. This may eventually lead to unit failure and/or poor performance, forcing premature equipment replacement. In response to this problem, Air Conditioner Contractors of America (ACCA) developed Standard 4 for “Maintenance of Residential HVAC Systems” [1]. For the measures contained in this work paper, an assessment and report is required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop treatment recommendations.

Proper maintenance of the unit enables an air conditioner to operate at or near its optimal efficiency. The Quality Maintenance measure consists of several treatments designed to increase the unit’s ability to deliver heating and cooling efficiently and to provide increased thermal comfort.  The blower fan retrofit also increases energy efficiency by lowering the amount of electrical energy needed to deliver heating and cooling to the home.

The measure names are listed below in Table 1

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
|  | HVAC Quality Maintenance |
|  | HVAC Duct Test and Seal |
|  | HVAC Brushless Direct Current Blower Motor replacing Standard Eff Motor |

### 1.1b Delivery and Incentive Mechanism

The delivery method for all measures is Financial Support – Downstream Incentive – Deemed. The program type for all measures is RET.

### 1.1c Measure Requirements

Measures are to be applied to residential single family homes in SDG&E’s climate zones 6, 7, 8, 10, 14, and 15 that use central air-cooled direct expansion cooling and gas heating. The participant must have electricity distributed by San Diego Gas and Electric (SDG&E) to the installation service address. Additionally, the following pre-requisites must be met before the Quality Maintenance measure can be implemented:

HVAC Quality Maintenance Requirements:

- Unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to airflow are completed and before refrigerant charge is tested and/or adjusted.

- Unit must be drawing power

- Unit must have a condenser over ambient temperature (COAT) of at least 3 degrees

- Customer must agree to QM Service Agreement

The 350 cfm/ton airflow requirement ensures that the refrigerant system can be properly diagnosed and charged. If the system is not delivering 350 cfm/ton upon initial inspection, an assessment should be made to determine if the system will be able to deliver 350 cfm/ton by implementing some or all of the QM treatments related to airflow. If it is determined that the supply fan and duct system in place do not have the capability to deliver 350 cfm/ton after the airflow treatments have been performed, refrigerant charge cannot be properly diagnosed, rendering the QM process incomplete and the savings in this work paper invalid.

If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per 2008 Title 24 Section 152(b) 1D [2], or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2008 Title 24 Section 152(b) 1D.

The motor replacement measure is to be applied after quality maintenance and duct sealing have been completed and is optional. The motor replacement measure applies to units with shaded pole or permanent split capacitor motors currently installed. As stated previously, the replacement blower motor is to be a brushless direct current motor with selectable speed control designed to replace a PSC motor in a residential direct drive fan application.

## 1.2  DEER Differences Analysis

The Residential QM measure is not included in the Database for Energy Efficient Resources (DEER).[3]  The DEER database contains some of the QM treatments as standalone measures with the assumption that all other features of the prototype held constant at an energy efficient baseline.  HVAC systems and the dwelling being served need to be treated holistically which is what ACCA Standard 4 supports.  The DEER standalone measures are refrigerant charge and adjustment, refrigerant charge with duct sealing, and commercial condenser coil cleaning.

Table 2 DEER QM Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | Yes |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | No |
| Deviation from DEER | CPUC ED deemed assumptions for non-DEER components |
| DEER Version | 2011 |
| DEER Run ID and Measure Name (Sample) | Res-RefrigCharge-wtd; Res-CondCoilClng |

Two measures are in DEER for the duct sealing measure. The two measures are, one for high initial duct leakage (measure ID Res-DuctSeal-HighToLow-wtd) and one for medium initial duct leakage (measure ID Res-DuctSeal-MedToLow-wtd).  Per the CPUC ED disposition, energy savings values for the duct sealing measure are taken directly from DEER.  The CPUC ED disposition energy savings values are the weighted average of those provided in the two measures.  Additionally, CPUC ED staff assigned the following incidence factors:

High initial leakage:	0.14

Medium initial leakage:	0.39

CPUC ED staff also assigned an installation rate of 0.75 for this measure.

Table 3 DEER Duct Sealing Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | Yes |
| Scaled DEER Measure | Yes |
| DEER Building Prototypes Used | No |
| Deviation from DEER | CPUC ED multipliers on incidence and installation rate |
| DEER Version | 2011 |
| DEER Run ID and Measure Name (Sample) | Res-DuctSeal-HighToLow-wtd; Residential: Duct Sealing (Total Leakage Reduced from High (40/35%) to Low (15/12%) |

The motor retrofit treatments are not included in the Database for Energy Efficient Resources (DEER).[3]  The deemed savings analysis for the motor retrofit measure used in this work paper uses DEER single family prototype file for DOE2 (eQUEST) batch runs.  Modifications were made to the input assumptions in the eQUEST simulation model to assess the impact of treatments for quality maintenance and duct sealing on an air conditioner unit.  The eQUEST methodology for the motor retrofit measures uses the results from the eQUEST QM measures, which separates the evaporator blower motor usage and run time hours.

### Energy Simulation with eQUEST

eQUEST [5, G] is a DOE2 based simulation software package used to produce estimates of energy use of prototype residential building models.  DEER single family prototypes [6] were used as the basis for all eQUEST simulations.

To reach an overall measure energy savings EV within a single climate zone using only eQUEST would require simulation runs for each treatment in each of the baselines as well as for each possible combination of treatments within the measure.  This quickly adds up to hundreds of runs even without considering multiple permutations of each treatment.  In order to reduce the number of runs and maintain a proper analysis of interaction complexity, a Design of Experiments (DoEx) process was used to specify a reduced number of runs that can be handled by using the batch process capability of eQUEST.  To model all possible combinations of parameters for either the base case or QM case would require 112,500 simulation runs. With DoEx this number was reduced to 68 runs needed for a statistically valid result when comparing to the results from running the eQUEST simulation.

Table 4 DEER Motor Replacement Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | Yes |
| Deviation from DEER | DEER does not contain this type of measure package. |
| DEER Version | N/A |
| DEER Run ID and Measure Name (Sample) | N/A |

## 1.3  Code Analysis

The measures contained in this work paper are generally not governed by either state or federal codes and standards.

However, in the event that ducts are found to be so badly damaged that some or all of the ductwork must be replaced, the total length of the replaced ducts shall be less than 40 linear feet in total per 2008 Title 24 Section 152(b) 1D, or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2008 Title 24 Section 152(b) 1D. [2]

Title 24 does not deal with quality maintenance issues. The program requires the HVAC contractor to be license by the California State Licensing Board (CSLB) and the HVAC technicians to be EPA certified. Under state mechanical code, changes, alterations, or repairs of a minor nature not affecting structural features, egress, sanitation, safety, or accessibility as determined by the enforcing agency are exempt from the requirement to obtain a mechanical permit.

Regarding the motor replacement measure, the mechanical code states that the replacement of any component part or assembly of an appliance that does not alter its original approval and complies with other applicable requirements of the mechanical code is exempt from the requirement to obtain a mechanical permit. In the event that a replacement motor requires a different voltage or number of phases than the original motor, the installation is to include disconnects not present on the original equipment, or the installation will alter the electrical system in any other way an electrical permit must be obtained pursuant to Title 24, Part 3 California Electrical Code.

Regarding 1.8.4 Permits, Fees, Applications, and Inspections, a written construction permit shall be obtained from the enforcing agency prior to the erection, construction, reconstruction, installation, relocation, or alteration of any mechanical system.

Exceptions:

- Work exempt from permits as specified in Chapter 1, Administration, Division II, Sections 112.2 through 112.2.3 of this code.

- Changes, alterations, or repairs of a minor nature not affecting structural features, egress, sanitation, safety, or accessibility as determined by the enforcing agency.

Table 5 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2008) | Title 24, Part 3 California Electrical Code | 2008 |
| Title 20 (2010) | None | N/A |

## 1.4  Measure Effective Useful Life

DEER08 documentation provides EUL and RUL information to be used for the 13-14 program cycle on www.deeresources.com. The DEER documentation “Summary of EUL-RUL Analysis for the April 2008 Update to DEER” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

Per the CPUC ED disposition dated May 2, 2013, The EUL shall be 5 years, which is the RUL of package equipment being treated. This value comes from DEER EUL ID HV-ResRCx. Although individual measures included in Quality Maintenance and Duct Sealing in DEER have EUL values different than the disposition EUL value, the EUL value of 5 years from the disposition has been used because the measures are part of a larger Quality Maintenance program.

Table 6 below identifies the value/methodology used for the measures in this work paper.

Table 6 DEER08 EUL Value/Methodology

| Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- |
| Residential | HVAC | HVAC Quality Maintenance | 5 | 1.7 |
| Residential | HVAC | HVAC Test and Seal Ductwork | 5 | 1.7 |
| Residential | HVAC | HVAC Brushless Direct Current Blower Motor Replacing Standard Eff Motor | 5 | 1.7 |

## 1.5  Net-to-Gross Ratios for Different Program Strategies

Per the CPUC ED disposition dated May 2, 2013, the NTG value is 0.70, which is the DEER value for all other residential measures with moderate market share and no convincing strategies to discourage free ridership. This NTG value was obtained from the “Updated DEER NTGR Values - 053008.xls” on the DEER website. The relevant NTGR for this measure is shown in Table 7 below.

Table 7 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| DEER 2008 | New Measures not Otherwise Addressed; Single Family Or Multfamily Markets with Moderate Market Share (>=5%) | RES | SFam | Financial Support – Downstream Incentive Deemed | 0.7 |

*Denotes that the column is taken from the DEER NTG Table.

## 1.6  Time-of-Use Adjustment Factor

As directed by the CPUC in decision 06-06-063 dated June 29, 2006, time-of-use (TOU) adjustment factors are to be applied for residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only.  The specific TOU adjustment factors are inherent in the avoided-cost calculation performed in the E3 calculator.

Since the load shape used for all measures is a new DEER load shape, i.e. the load shape starts with the prefix “DEER:”, the TOU for purposes of the E3 calculator should remain 0% as shown in Table 8.

Table 8  TOU Summary Table

| Measure | % |
| --- | --- |
| HVAC Quality Maintenance | 0 |
| HVAC Duct Test and Seal | 0 |
| HVAC Brushless Permanent Magnet Blower Motor Replacing Standard Eff Motor | 0 |

# Section 2. Energy Savings & Demand Reduction Calculations

Estimated savings were revised by CPUC ED Disposition dated May 2, 2013. The Disposition revised the calculation process for the Quality Maintenance and Duct Test and Seal measures to use DEER database values as a basis for savings for the measures instead of eQUEST simulation models. Per the Disposition’s directive, the estimated savings for the HVAC Duct Test and Seal measure were broken out of the HVAC Quality Maintenance measure. The Disposition also revised the Blower Motor Replacement savings based on ED staff research. The Disposition savings values can be found in attachments “20132014-ResidentialHVACMaintenance-SavingsValues-April2013-v1-2-rev-SDGE-01-24-14.xlsx” and “20132014ResBlowerRaplacementDisposition-v1-2.xlsx.”

## 2.1 HVAC Quality Maintenance

The ED disposition revised the HVAC Quality Maintenance measure energy savings by providing a single set of values based on those provided in the 2011 DEER database.  The Disposition savings values include the following steps:

- Start with energy savings values from the 2011 DEER database for commercial RCA efforts.

- Separate those values into task components of charge adjustment, condenser and evaporator coil cleaning and air flow adjustment.

- Provide adjustments to the various components to account for proper application of DEER assumptions and installation rates that represent best estimates of the current state of programs in obtaining DEER values.

DEER savings estimates used as a starting point in this portion of the disposition are based on 2011 DEER ID Res-RefrigCharge-wtd. These values were developed by weighting the four individual refrigerant charge measures (high overcharge, typical overcharge, high undercharge, typical undercharge) for the “existing” building vintage. Where building weights did not include populations for a particular IOU and climate zone, statewide weightings for the climate zone were used. These provide savings estimates for all residential building types across all IOUs and climate zones.

ED staff estimated that non-charge related services may account for an additional 25% savings on top of refrigerant charge adjustment (RCA).  Based on this assessment, published DEER benefits are segregated into charge adjustment and non-charge adjustment remedies as follows:

Gross Charge Adjustment Savings = DEER values 	 	           (1)

Gross Non-Charge Adjustment Savings = DEER values * 0.25  		(2)

The DEER values used in Equation 1 are weighted values that accrue only for charge adjustments greater that 10% of unit nominal charge.  The DEER savings values are a simple weighting of original savings estimates based on low and high charge adjustments whose minimum charge adjustment threshold is ±10%.  Current programs do not include charge level as a savings accrual requirement.  The ED Disposition addresses this by applying a multiplier to charge-related DEER values from Equation 1 to account for the number of systems that will receive a charge adjustment in the program, but are below the threshold needed to generate significant energy savings.

Figure 1 provides the distribution of units from which DEER impacts are evaluated based on the charge adjustment for each unit.  Based on the data collected, 45% of all serviced units had charge adjustments less than 10%.  No significant energy savings related to charge adjustment occurs for those units.  From this, when the level of charge adjustment is ignored, the charge adjustment savings (based on values in the 2011 DEER) must be reduced by the number of units for which no significant savings are expected. In consideration of values from Figure 9 as well as the possibility that some refrigerant charge adjustments may result in increased energy use, ED staff assigned an incidence fraction of 0.40 to savings values for RCA.

Figure 1 - Unit Distribution by Charge Adjustment Level

In addition to the expected incidence occurrence for refrigerant charge adjustments, a standard installation rate of 0.568 was applied to all refrigerant charge measures. This is the statewide value included in READI for residential refrigerant charge measures. For statewide Quality Maintenance programs, the installation rate is included in the calculation of the overall savings for each Quality Maintenance claim. This is necessary since installation rate values for each treatment within the Quality Maintenance program vary and must be included in the savings calculation. Then, since the claimed savings for the Quality Maintenance program will include installation rate adjustments for each of the contributing measures, the claimed installation rate for Quality Maintenance claims shall be 1.

There is no known evidence as to the relative impact from the three measures – condenser coil cleaning, evaporator coil cleaning and air flow adjustment - that generate non-charge adjustment savings.  It is generally recognized that typical efficiency improvements associated with condenser coil cleaning is much larger than the other two.  Given a paucity of direct measurements of field conditions, ED used the following apportioning of non-charge adjustment savings among the three possible measures:

Condenser Coil Cleaning:	50% of the total

Evaporator Coil Cleaning:	25% of the total

Air Flow Adjustment:	25% of the total.

In addition to the fractions described above, ED staff also assigned the following incidence fractions to the gross savings results:

Condenser Coil Cleaning:	0.80

Evaporator Coil Cleaning:	0.60

Air Flow Adjustment:	0.60

The approved energy savings values for RCA and related measures are included in the embedded workbook “20132014-ResidentialHVACMaintenance-SavingsValues-April2013-v1-2-rev-SDGE-01-24-14.xlsx” in the following tabs:

Refrigerant Charge Adjustment:	DEER2011-RefrigCharge-Wtd

Condenser Coil Cleaning:	ResCondCoilCleaning

Evaporator Coil Cleaning:	ResEvapCoilCleaning

Air Flow Adjustment:	ResAirFlowAdjust

## 2.2 HVAC Duct Test and Seal

The ED disposition revised the HVAC Duct Test and Seal (DTS) measure energy savings based on values provided in the 2011 DEER database.  There are two measures in DEER, one for high initial duct leakage (measure ID Res-DuctSeal-HighToLow-wtd) and medium initial duct leakage (measure ID Res-DuctSeal-MedToLow-wtd). The ED Disposition savings values are the weighted average of those provided in the two measures.  Additionally, ED staff assigned the following incidence factors:

High initial leakage:	0.14

Medium initial leakage:	0.39

The statewide installation rate for DTS measures from the 2006-2008 evaluations is 0.463. This essentially means that more than half the installations have no benefit, even if, on those installations, some amount of duct sealing was performed that did not result in requisite reduction in duct leakage. In consideration of partial benefits as well as the likelihood that utilities have instituted improvements to installation and verification, ED staff believe that the installation rate should be increased by 50%, according to the following equation:

IRadj = 0.463 + 0.50 * ( 1 – 0.463 ) = 0.73

Given the lack of precision in the analysis of installation rates, ED staff used an installation rate of 0.75 for DTS measures.

## 2.3 HVAC Brushless Direct Current Blower Motor Replacing Standard Efficiency Motor

The quality maintenance measure energy savings (including duct sealing) were originally calculated using eQUEST building simulation models. The brushless direct current blower motor retrofit was then modeled as an iterative retrofit to the quality maintenance measure. The quality maintenance measure energy savings were revised in the CPUC ED Disposition dated May 2, 2013 to be based on values from the DEER database and duct sealing was broken out as a separate measure. However, the brushless direct current blower motor retrofit still uses eQUEST savings calculations with adjustments by the ED Disposition. Therefore, the iterative eQUEST brushless direct current blower motor retrofit calculations are used as a basis for the savings for this measure.

The eQUEST calculation methodology for quality maintenance is discussed below. These savings calculations are only used as a basis for the brushless direct current blower motor retrofit measure. Since the quality maintenance measure consisted of multiple treatments having interactive effects an analysis method that takes all of the treatment and interaction effects into account was required. The steps taken to achieve this are listed below.

.

- Estimation methods were developed that would allow simulation of the quality maintenance improvements.

- Seven factors that significantly impact energy usage in homes were selected for the purpose of building multivariate regressions to predict electric energy usage, electric peak demand, and gas energy usage for one and two story homes in each of the climate zones. Some of the factors also have the ability to be adjusted to accomplish the estimation methods developed in step 1.

- The highest and lowest likely values of each factor were determined as well as a midpoint value. A design of experiment approach was used to select 68 unique combinations of the 7 factors for one and two story homes in each climate zone.

- Each of the 7 factors was translated into eQUEST [G] inputs, and the 68 runs defined in step 2 were run using eQUEST’s batch processing capability for one and two story homes in each climate zone.

- The kWh, kW, and therm annual use results from the 68 runs were used to develop regressions.  Regression statistics were calculated to ensure the ability of the regressions to predict the responses.

- For each of the 7 factors, probability distributions were developed for the range of values in the base case and after quality maintenance has been performed.

- The probability distributions of the 7 factors were used in the regression equations to determine the probability distribution of kWh, kW, and therms in the base case and QM case for one and two story homes in each climate zone. The expected value (EV), or weighted average of the kWh, kW, and therms for the QM case was subtracted from the EV of the base case to determine the EV of the savings for one and two story homes in each climate zone.

- The EV savings calculated in step 8 were normalized by cooling capacity in tons. The one and two story savings for each climate zone were then weighted by the percentage of one and two story homes in the climate zone.

- Additional eQuest runs were made with randomly generated values of the 7 factors. The results of these runs were compared to the regression predictions using the same randomly generated values for the 7 factors to test the ability of the regressions to predict energy usage for values of the 7 factors that were not included in the 68 runs used to create the regressions.

Table 9 lists each of the possible treatments in the quality maintenance measure and a short description of the estimation method used to represent the effect of the treatment.

Table 9  Estimation Methods for QM Measure Treatments

| Treatment | Estimation Method |
| --- | --- |
| Refurbish Ducts | Airflow improvement, EER, and Cooling Capacity Improvement |
| Restore and Improve Duct Insulation | Duct heat transfer coefficient reduction (R-Value improvement) |
| Duct Seal | Duct leakage reduction |
| Clean Evaporator Coil and Blower | Airflow improvement and evaporator heat transfer improvement resulting in EER and cooling capacity improvement |
| New Air Filter to Match the Blower | Airflow improvement, EER improvement, and cooling capacity improvement |
| Clean Condenser Coil | Condenser heat transfer improvement resulting in Cooling Capacity improvement and EER improvement |
| Thermal Expansion Valve (TXV) Bulb Insulation and Attachment Correction or Replacement | EER and Cooling Capacity Improvement |
| Refrigerant Charge Correction | EER and Cooling Capacity Improvement |

Seven factors were selected that would significantly affect home energy usage, would adequately represent the possible range of homes in each climate zone and would allow for adjustment to represent the estimation methods in Table 6. Distributions of the possible values of each of the 7 factors were then developed using various sources and methods.

Table 10 lists the factors and a short description of the source of each factor’s distribution of possible values. A more detailed description of the factors, the methods used for translation to eQUEST inputs to reflect the estimation methods in Table 7, and the development of the base case and quality maintenance case distributions for each factor can be found in “Expected Values Analysis.docx.”

Table 10  Factors Affecting Energy Usage and Methods of Estimating Distribution of Factors

| Type | Unit | Method/Source for Estimating Distributions |
| --- | --- | --- |
| Refrigeration Impact Factor (RIF) | % energy impact | Robert Mowris data set [12] analysis. RIF is the factor representing the % energy impact resulting from airflow and refrigeration corrections in a sample of 56 residential units. RIF accounts for both airflow and refrigeration corrections and interaction effects between the two. |
| Duct Leakage | % of Airflow | Data set from Verified field studies [13], over 6,500 data points |
| Duct UA | Btu/(hr ° F) | DEER prototypes for area [4]; code and assumed levels of degradation for U-values |
| Tstat offset | ° F | RASS data transformed to 24 hr average setpoint [14] |
| Nominal SEER | Btu/(Watt-hr) | DEER values weighted by vintage [16] |
| AFUE | % Efficiency | Average Value provided by SDG&E from program data, assumed distribution |
| Shell UA | Btu/(hr ° F) | Wall/window/roof areas from prototype model; U-values from DEER [15] – change for each climate zone and vintage; includes infiltration |

In order to determine the expected savings that would result from upgrading a blower motor to a brushless direct current motor after quality maintenance has been performed, 7 quality maintenance factors resulting in the expected QM kWh, kW, and therms for the one and two story homes in each climate zone were derived from the expected value analysis. DEER single family home prototypes were then modified to reflect the expected value of the factors and the prototypes were simulated in eQUEST. Conversion of factors to eQUEST inputs followed the same methodologies that were used for QM. The process of converting the factors to eQUEST inputs and performing the baseline and retrofit case runs is detailed in “Blower Motor Retrofit.docx”.

With the 7 factors defined, the next step was to determine the impact that the full range of those seven factors could have on energy consumption and demand. In order to represent the full range of possibilities a design of experiment approach was used to select combinations of the highest and lowest values for each factor that are likely to be encountered in the population of homes. By using the highest and lowest level of each factor the full possible effect of the factor is represented in the response.

Starting with DEER single family home prototypes developed in eQUEST, 68 runs with the selected combinations of high and low factors were run for both one and two story homes in each of the SDG&E climate zones.

Originally the intention was to use the prototypes representing the QM case as the base case for the blower motor upgrade, however it was discovered that the motor power (expressed in Watts/cfm at 1” of water column) used in the DEER prototypes is far lower than the power for motors typically found in residential HVAC units. The DEER assumption for blower motor power is 0.365 W/cfm at 1” of water column. [3] A PIER report, “Characteristics and Opportunities for New California Homes” [18], determined the average blower motor power for 45 HVAC systems with PSC motors to be 0.65 W/cfm. Two other studies conducted by Pigg at the Wisconsin Energy Center [17] found that PSC motors in residential supply fan applications use 0.517 to 0.528 W/cfm and that electronically commutated motors use 0.320 to 0.341 W/cfm. Based on these studies it was determined that the QM case would be used to represent the system after the motor retrofit was performed with a blower motor power of 0.365 W/cfm at 1” of water column, and a blower motor power of 0.65 W/cfm at 1” of water column would be modeled to represent the base case for the blower motor retrofit. None of the 7 factors were changed from the base case to the retrofit case, just the motor power.

Electric energy, peak demand, and gas energy savings were then calculated by subtracting the retrofit case kWh, kW, and therms from the base case.

The ED Disposition revised the supply air blower motor replacement measure energy savings as described below.  Base savings values for the supply air blower motor replacement were taken from previous IOU Quality Maintenance workpaper supporting documents.  Savings are for single family air conditioning systems with gas heat only.  Other residential building types or HVAC systems are not covered.  Savings are by climate zone alone and are the same across all IOUs.  The ED Disposition adjusted savings values as described below.

- Energy Division claims that the efficiency difference between PSC and BPM motors falls to zero as the motor rated capacity reaches 1 horsepower (hp).  Efficiency differences provided in the workpapers are acceptable for motors with capacities of ½ hp or less.

- The supply air blower motor capacity by unit nominal cooling capacity assumed by Energy Division is provided in Table 11.

Table 11 - Assumed Supply Air Blowr Motor Horsepower

| Capacity | hp |
| --- | --- |
| ≥ 3.5 tons | 1/2 |
| 4 tons | 3/4 |
| 5 tons | 1 |

- Energy Division assumes the efficiency differences between PSC and BPM ¾ hp motors is assumed to produce half the savings claimed in workpapers.  The PSC and BPM 1 hp motors are assumed to operate at the same efficiency.

- The distribution of nominal cooling capacities for residential cooling systems was estimated from the database of units in the 2006-2008 evaluation of air conditioner replacement programs.  Other program evaluation data were examined for RCA and DTS, but much of it was for multi-family sites not covered by the QM programs.  From the 2006-2008 data, the distribution of units by nominal cooling capacity is provided in Table 12

Table 12 - Distribution of Cooling Equipment by Nomincal Cooling Capacity

| Capacity | hp |
| --- | --- |
| ≥ 3.5 tons | 50.9% |
| 4 tons | 30.3% |
| 5 tons | 18.8% |

- Based on the distribution of units provided in Table 11, and the assumed efficiency declines noted in Item 3, Energy Division believes that workpaper UES values should be reduced by 33.9%.  This assumes that there are only ½ the benefit for 30.3% of the motors replaced (4 ton units) and no benefit for 18.8% of the motors replaced (5 ton units).

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the DEER:HVAC_Eff_AC load shape.  See Table 12 for a list of all Building Types and Load Shapes.  See the KEMA report [19] for a more thorough discussion regarding the load shapes for this measure.

Table 13 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Residential Single Family | RES | DEER:HVAC_Eff_AC |

# Section 4. Base Case & Measure Costs

The measure costs for Quality Maintenance are based on DEER 2008 and DEER 2005 [6].  The DEER 2008 and DEER 2005 indicate a value for Refrigerant Charge and Adjustment (RCA), Duct Test and Seal (DTS), and Condenser Coil Cleaning.  It is assumed the cost for evaporator coil cleaning will be identical to condenser coil cleaning.

### Refrigerant Charge Adjustment

For Refrigerant Charge Adjustment (RCA), the DEER 2008 provides cost data for both “typical charge adjustment” (units with a pre-charge condition 80% to 120% of full charge) and “high charge adjustment” (units with a pre-charge condition less than 80% of full charge and greater than 120% of full charge).  The units are in a “per ton cooling” basis.  Since the impact savings from the EV results in single value for each CZ, the measure costs are weighted based on SDG&E’s 2010 RCA participant data [7] to come up with a single value. It is assumed that the distribution is typical for California.   Because the impact savings are “per system” with one system per dwelling, it’s necessary to convert the weighted costs value to a “per household” basis.  The measure cost for RCA was calculated using the following equation:

Where,

Material Cost ($) = DEER 2008 material cost for refrigerant varying by charge levels.

Labor Cost ($) = DEER 2008 installation labor cost.

Tons Cooling per household = 3.27 tons, DEER 2008 average tonnage for single family

homes weighted by climate zone and vintage.

Distribution Percentage (%) = Percentage based on 2010 PG&E RCA field data.

Table 14: DEER Costs for Refrigerant Charge Measure

| Cost Case Description | Material Cost/ton | Labor Cost /ton | Installed Cost/ton | Distribution Percent | Measure Cost at 3.27 tons/household |
| --- | --- | --- | --- | --- | --- |
| Increase Refrigerant Charge - Typical (< 20% rated charge) | $11.55 | $36.82 | $48.37 | 55.50% | $87.79 |
| Increase Refrigerant Charge - High (>= 20% rated charge) | $19.93 | $36.82 | $56.75 | 10.72% | $19.89 |
| Decrease Refrigerant Charge - Typical (< 20% rated charge) | $5.58 | $36.82 | $42.40 | 29.47% | $40.86 |
| Decrease Refrigerant Charge - High (>= 20% rated charge) | $10.04 | $36.82 | $46.86 | 2.05% | $3.14 |
|  |  |  | Total Costs |  | $151.75 |

The Residential HVAC QM program will require that all units be brought to the specified level of refrigerant charge.  The refrigerant charge and adjustment cost is adjusted based on the number of units needing charge using the 2010 PG&E RCA field data. Table 7 shows that 65% of units are equal to or over the ±10 percent charge limit.[7] Using the total weighted cost from Table 13 above and multiplied by 65%, the new determined cost for refrigerant charge and adjustment was found to be $100.15.

Table 15 2010 PG&E RCA Program distribution on percentage charge

| 2010 PG&E RCA program distribution |  |
| --- | --- |
| Percent Charge | Distribution Count |
| 150.00% | 16 |
| 140.00% | 177 |
| 120.00% | 8 |
| 119.99% | 628 |
| 110.00% | 2257 |
| 100.10% | 0 |
| 100.00% | 221 |
| 99.90% | 3218 |
| 90.00% | 2127 |
| 80.99% | 88 |
| 80.00% | 880 |
| 60.00% | 84 |
| 50.00% | 34 |
| 40.00% | 51 |
| Total Units | 9789 |
| Units< ±10% charge | 3439 |
| % don't need adjustment | 35% |
| % need adjustment | 65% |

The measure costs for Condenser Coil Cleaning treatment is based on DEER 2005, which lists the cost at $114.15 per household.  Since there are no cost data for Evaporator coil cleaning, it’s assumed the cost will be the same as the condenser coil cleaning at $114.15 per household.

Table 16 summarizes the overall total cost of $328.45 for the Quality Maintenance measure.

Table 16 Total cost for QM Treatments

| Measure | Household costs (weighted) | Normalizing Unit |
| --- | --- | --- |
| RCA | $100.15 | Household |
| Condenser coil cleaning | $114.15 | Household |
| Evaporator coil cleaning | $114.15 | Household |
| Total: | $328.45 | Household |

Table 17 Total cost for QM Treatments per Ton

| CZ | Tons | Materials/ton | Labor/ton | Total/ton |
| --- | --- | --- | --- | --- |
| 6 | 3.35 | $6.52 | $91.52 | $98.05 |
| 7 | 2.59 | $8.44 | $118.38 | $126.82 |
| 8 | 3.12 | $7.01 | $98.27 | $105.27 |
| 10 | 3.59 | $6.09 | $85.40 | $91.49 |
| 14 | 4.24 | $5.16 | $72.31 | $77.47 |
| 15 | 4.62 | $4.73 | $66.36 | $71.09 |

### Duct Sealing

For Duct Test & Seal (DTS), the DEER 2008 indicate values for sealing high and low leakage duct systems for single family homes.  The measure cost for this treatment was based on Summit Blue Consulting’s cost analysis of $129 per ton.  The costs do not vary between low and high leakage duct systems.  The measure cost for DTS was calculated to be $422.01 per household ($129/ton x 3.27 tons/household).  However, it is assumed that SDG&E’s QM program will not perform diagnostic testing on customer’s duct system, only duct sealing will be completed by participating contractors/technicians.  Based on Mike Yim [8] of Summit Blue Consulting, one hour of labor is estimated for the duct diagnostic testing. By eliminating the test, the total cost will be reduced by $70.34 ($422.01 ÷ 6 hours). The total Duct Seal Cost then comes to $351.68.

Table 18 Total cost for Duct Seal Treatments

| Measure | Household costs (weighted) | Normalizing Unit |
| --- | --- | --- |
| Duct Seal | $351.68 | Household |

Table 19 Total cost for QM Treatments per Ton

| CZ | Tons | Materials/ton | Labor/ton | Total/ton |
| --- | --- | --- | --- | --- |
| 6 | 3.35 | $13.24 | $91.73 | $104.98 |
| 7 | 2.59 | $17.13 | $118.65 | $135.78 |
| 8 | 3.12 | $14.22 | $98.50 | $112.72 |
| 10 | 3.59 | $12.36 | $85.60 | $97.96 |
| 14 | 4.24 | $10.46 | $72.48 | $82.94 |
| 15 | 4.62 | $9.60 | $66.52 | $76.12 |

### Blower Motor

The estimated equipment measure cost for the motor retrofit was derived from HVAC distributor, KG power systems website, [10] and 2011 RS Means [11] for labor cost.  The total charges for the brushless permanent magnet (BPM) Blower motor retrofit measure was calculated to be $312.18. According to RS Means, 1.501 man hours are needed at $75.50 per hour for installation, the material cost for the motor was set at $198.85 per motor, which was derived from the EFI [9] distributor data sheet.

Table 20 Total Cost for Motor Retrofit

| Cost Case Description | Material Cost | Installation Man Hours - Retrofit | Installation Labor Cost Per hour - Retrofit | Measure Cost |
| --- | --- | --- | --- | --- |
| Blower Motor Retrofit | $198.85 | 1.501 | $75.50 | $312.18 |

Table 21 Motor Retrofit Cost per Ton

| CZ | Tons | Materials/ton | Labor/ton | Total/ton |
| --- | --- | --- | --- | --- |
| 6 | 3.35 | $59.36 | $22.54 | $81.90 |
| 7 | 2.59 | $76.80 | $29.16 | $105.96 |
| 8 | 3.12 | $63.73 | $24.20 | $87.93 |
| 10 | 3.59 | $55.39 | $21.03 | $76.42 |
| 14 | 4.24 | $46.90 | $17.81 | $64.71 |
| 15 | 4.62 | $43.04 | $16.34 | $59.38 |

## 4.3 Incremental Measure Cost

The Incremental measure cost (IMC)[7] for this measure is the same as the equipment measure cost.

# Glossary of Terms and Acronyms

The following definitions are used throughout this work paper.

- ANSI/AHRI Standard 210/240-2008 – The purpose of this standard is to establish, for Unitary Air-Conditioners and Air-Source Unitary Heat Pumps: definitions, classifications, test requirements, rating requirements, minimum data requirements for published ratings, operating requirements, marking and nameplate, and conformance conditions.  This standard is intended for the guidance of the industry, including manufacturers, engineers, installers, contractors, and users.

- Air Conditioning Contractors of America, Standard 4 (ACCA 4) – The ANSI/ACCA Standard 4 Maintenance of Residential HVAC Systems-2008.  The purpose of this standard is to establish minimum inspection requirements in the maintenance of HVAC equipment found in one-family and two-family dwellings of three stories or less.

- Base case cost - The cost for base case equipment/treatment per common unit.

- CPUC Energy Division (ED) - The California Public Utilities Commission (CPUC) regulates privately owned electric communications, electric, natural gas, water, railroad, rail transit, and passenger transportation companies.  The CPUC's Energy Division develops and administers energy policy and programs “to serve the public interest”, advise the Commission, and ensure compliance with the Commission decisions and statutory mandates.

- Decision Programming Language (DPL) – The software package DPL is a decision support software tool used to perform calculations and generate graphics illustrating the inputs and results.  http://www.syncopation.com/?gclid=CJXd6Nfp1qoCFVMZQgodwHBO7w

- Design of Experiments (DoEx) – A software tool used for statistical process, resulting in a statistically valid regression model which accounts for the full range of treatment interactions for this quality maintenance work paper.  See “Design of Experiment.docx”for statistical process.http://www.statease.com/dx8descr.html

- eQUEST (DOE2) – Software to perform detailed comparative analysis of building designs and technologies by applying sophisticated building energy use simulation techniques. SCE requires that eQUEST version 3.64 or newer shall be used for this work.

http://doe2.com/eQUEST/

- Databases for Energy Efficient Resources (DEER) - The DEER provides estimates of the energy-savings potential for a variety of technologies of measures in residential and nonresidential applications.  http://www.deeresources.com/

- DEER Single Family Prototype - The DEER Single Family Prototype describes a single site configuration, including one or multiple building shells served by one or more HVAC system types.  Prototype characteristics correspond to eQUEST building “creation wizard” inputs, where the characteristics were developed specifically for DEER analysis.    http://www.doe2.com/download/DEER/MAStool/

- Expected Value Analysis (EV) – Using the DPL software, the measure package value is determined by probability based analysis to make an expert projection of what the likely states for parameters might be with a reasonable estimation of their probability.  The “expected value” is a weighted value based on multiple parameters.

- HVAC - The heating, ventilation and air conditioning system(s) in a home used for heating, cooling, and maintaining the home at a controlled temperature, surrounded by fresh air, at a humidity level that is safe and comfortable for the building and its contents.

- Incremental Measure Cost (IMC) - The value of the incremental cost of the measure (measure equipment cost less base equipment cost) per common unit.

- Labor cost – The cost of labor to perform the work of specific measures/treatments.

- Measure Case Cost – The cost for measure case equipment/treatment per common unit.

- SDG&E– San Diego Gas and Electric.

- Implementer - A QM Implementer is a company that provides documented verification of work performed by licensed HVAC contractors performing a specified type of work or service. In the context of the Program, the service which the QM Implementer is to follow a program performance specification, market, recruit, and train licensed HVAC contractors and their technicians to offer the comprehensive quality maintenance service to the customers.

- Regression Fit Model – Regression is a term for all methods that fit a mathematical model to observed data in order to quantify the relationship between independent and dependent variables.  The fitted model is then used to describe the relationship between the two groups of variables and to predict new values of the dependent variable.

- Quality Maintenance (QM) – ACCA Standard 4 defines what must be done to implement Quality Maintenance on residential HVAC systems.  Using multiple treatments/measures the HVAC system and its elements are maintained on a regular interval to provide the intended thermal comfort and energy efficiency.

- Work Paper (WP) - A document developed by the utility that documents the product description, savings methodology, measure costs, effective useful life, and net-to-gross ratios.

# Attachments

# References

1. ACCA, “Maintenance of Residential HVAC Systems” - ANSI/ACCA Standard 4, 2008. https://www.acca.org/industry/ansi-standards

2.Title 24 2008 Building Energy Efficiency Standards for Residential and Nonresidential Buildings,

3. Itron, Inc. “2008 Database for Energy Efficiency Resources”, Version 2008.2.05, December 2008. http://www.deeresources.com/

4. Database for Energy Efficiency Resources (DEER) Single Family Prototype Input File. http://www.doe2.com/download/DEER/MAStool/

5. eQUEST – Building Energy Use and Cost Analysis Software, developed by James J. Hirsch & Associates (JJH), version 3.64 was the latest release. http://www.doe2.com/

6. DEER Single Family Prototypes with adjusted inputs.  Adapted from 2004-2005 Database for Energy Efficiency Resources (DEER) Update Study, Final Report, prepared for Southern California Edison by Itron, Inc. with support from J. J. Hirsch and Associates, December 2005.

7. Measure Costs Analysis spreadsheet, January 2013.

8. Mike Yim, Summit Blue Consulting, e-mail message on duct seal cost, July 25, 2011.

9. Energy Federation Incorporated (EFI). New High Efficiency Concept 3 motor Specification Sheet. http://www.efi.org/wholesale/pdfs/concept_3.pdf

10. KC power systems. “5464 U.S. Motors/Emerson RESCUE Condenser Motor (1/6-1/3 HP, 208-230 Volts, 825 RPM), price at $116.20.  (assessed on July 26, 2011)  http://store.kgpowersystems.com/5464-U.S.-Motors-Emerson-RESCUE-Condenser-Fan-Motor-1-6---1-3-HP-208-230-Volts-825-RPM.aspx

11. RS Means Company. “2011 Building Construction Cost Data – 69th Annual Edition”.  Motors Applications Category, page 554.  2011

12. Mowris’ dataset of field measurements for 56 residential units 2004 and derivation of RIF,

13. MDSS_PGE_duct leak_Distribution_Analysis, June 2011

14. Tstat probability_v4, June 2011

15. DEER SFRes Properties- Capacity-SEER, November2011

16. Vintage Distribution of Home Type, November 2011

17. Pigg, Scott, Central Air Conditioning in Wisconsin: A Compilation of Recent Field Research, ECW Report Number 241-1, May 2008.

18. Results are summarized in “Table 14 – Mean System Airflow…” of the PIER report Efficiency Characteristics and Opportunities for New California Homes by Proctor, Chitwood and Wilcox for the CEC.

19. KEMA, The Cadmus Group, and Summit Blue Consulting. “Evaluation Measurement and Verification of the California Public Utilities Commission HVAC High Impact Measures and Specialized Commercial Contract Group Programs.” CPUC. February 10, 2010.   http://www.cpuc.ca.gov/PUC/energy/Energy+Efficiency/EM+and+V/

Bracketed letters refer to the Glossary and bracketed numbers refer to the References and Endnotes

p. 1-212, Mowris, Robert J., Anne Blankenship and Ean Jones, Robert Mowris & Associates, “Field Measurements of Air Conditioners with and without TXVs”, 2004 ACEEE Summer Study Proceedings.