## Calculations Summary
Project Summary & Calculation worksheet for Heat Recovery in Single-Stage and Dual-Stage Economizers
Blue indicates inputs, Green indicates reference, Black indicates calculated
| Project Name | Project 1 | Project 2 | Project 3 | Project 4 | Project 5 | Project 6 | Project 7 | Project 8 | Project 9 | Project 10
| Parameter / Calculation | Value1 | Value2 | Value3 | Value4 | Value5 | Value6 | Value7 | Value8 | Value9 | Value10 | Units | Source
Reference Values
A | Density of Liquid Water = | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | lbm/gallon | Reference
B | Specific Heat of Liquid Water = | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | BTU/lbm-F | Reference
C | Stack Exhaust Specific Heat = | 0.2624 | 0.2612 | 0.2647 | 0.2625 | 0.2612 | 0.2612 | 0.2625 | 0.2612 | 0.2612 | 0.2612 | Btu/lb/°F | @ stack temp
D | Stack Exhaust Density = | 0.046 | 0.0481 | 0.0465 | 0.0455 | 0.0481 | 0.045 | 0.0455 | 0.0455 | 0.0426 | 0.0455 | Lb/ft^3 | @ stack temp
E | Steam Enthalpy = | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | Btu/lb | (1150-180) @212°F sat.
F | kBTU to therm | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | kBTU/therm | Reference
G | Steam Boiler HP | 600 | 600 | 1000 | 500 | 700 | 700 | 500 | 1200 | 50 | 500 | BHP | Specification
H | 1 Boiler HP | 33475 | 33475 | 33475 | 33475 | 33475 | 33475 | 33475 | 33475 | 33475 | 33475 | Btuh | Constant
I | Boiler combustion efficiency = | n/a | n/a | n/a | n/a | n/a | n/a | 82% | 84.4% | n/a | n/a | % | Reference
I | (or) Boiler thermal efficiency = | 82% | 82% | 80.8% | 80% | 80% | 80.4% | 80% | n/a | 80% | 84.3% | % | Reference
Baseline Calculation
J | Boiler Connected Load = | 20085 | 20085 | 33475 | 16737.5 | 23432.5 | 23432.5 | 16737.5 | 40170 | 1673.75 | 16737.5 | kBtu/hr | =G*H
K | Boiler Rated Input Capacity = | 24493.9024 | 24493.9024 | 41429.4554 | 20921.875 | 29290.625 | 29144.9005 | 20921.875 | 47594.7867 | 2092.1875 | 19854.6856 | kBtu/hr | =J/I
L | Operating Hours = | 4000 | 4000 | 4000 | 7488 | 6024 | 3825 | 5252 | 8760 | 4000 | 7488 | hr/yr | Reference
M | Load of Maximum Output = | 100% | 50% | 100% | 100% | 100% | 50% | 100% | 69% | 100% | 100% | % | Specification
Flow Rate Calculation
N | Flue Exhaust Flow Rate = | 4792 | 2382 | 8320 | 8268 | 6305 | 7000 | 8268 | 6450 | 438.3333 | 5658 | SCFM | Specification
O | Steam Flow Rate = | 20706.1856 | 10353.0928 | 34510.3093 | 17255.1546 | 24157.2165 | 12078.6082 | 17255.1546 | 28574.5361 | 1725.5155 | 17255.1546 | Lbm/hr | =J*1000*M/E
P | Natural gas consumption = | 24493902.439 | 12246951.2195 | 41429455.4455 | 20921875 | 29290625 | 14572450.2488 | 20921875 | 32840402.8436 | 2092187.5 | 19854685.6465 | Btu/lb | =O*E/I
Q | Feedwater Flow Rate = | 41.9 | 21 | 68 | 32.7083 | 50.3 | 30.2 | 32.7083 | 3.5 | 3.5 | 32.7083 | gallons/min | Spec
Stage 1
R | Exhaust Flow Rate = | 13225.92 | 6874.452 | 23212.8 | 22571.64 | 18196.23 | 18900 | 22571.64 | 17608.5 | 1120.38 | 15446.34 | lbm/hr | =N*D*60
S | Inlet stack temperature = | 407 | 372 | 490 | 410 | 374 | 404 | 404 | 371 | 480 | 375 | °F | Specification
T | Outlet stack temperature = | 270 | 272 | 200 | 331 | 250 | 304 | 330 | 265 | 350 | 274 | °F | Assumed (trial & error)
U | Feedwater Flow Rate = | 20966.76 | 10508.4 | 34027.2 | 16367.25 | 25170.12 | 15112.08 | 16367.25 | 1751.4 | 1751.4 | 16367.25 | lbm/hr | =Q*A*60
V | Feedwater Inlet Temperature = | 227 | 227 | 240 | 227 | 227 | 373 | 214 | 225 | 240 | 226 | °F | Spec
W | Feedwater Outlet Temperature = | 250 | 244 | 292 | 256 | 254 | 398 | 240 | 270 | 262 | 255 | °F | Spec
X | Sensible heat load = | 475455.9529 | 179560.6862 | 1781884.1664 | 468079.3845 | 589354.0542 | 493668 | 438454.107 | 487530.0612 | 38043.6233 | 407492.9848 | Btu/hr | =R*C*(S-T)
Y | Economizer Fuel savings = | 579824.3328 | 218976.4466 | 2205302.1861 | 585099.2306 | 736692.5678 | 614014.9254 | 548067.6338 | 577642.2526 | 47554.5291 | 483384.3236 | Btu/hr | =X/I
Z | Proposed gas consumption = | 23914078.1062 | 12027974.7729 | 39224153.2594 | 20336775.7694 | 28553932.4322 | 13958435.3234 | 20373807.3662 | 32262760.591 | 2044632.9709 | 19371301.3229 | Btu/hr | =P-Y
AA | Annual NG Therm Savings = | 23192.9733 | 8759.0579 | 88212.0874 | 43812.2304 | 44378.3603 | 23486.0709 | 28784.5121 | 50601.4613 | 1902.1812 | 36195.8182 | therms/yr | =Y*L/10^5
AB | Stage-1 efficiency = | 83.99% | 83.49% | 85.34% | 82.3% | 82.06% | 83.94% | 82.15% | 85.91% | 81.86% | 86.4% | % | =O*E/Z
AC | Stage-1 efficiency improvement = | 1.988% | 1.493% | 4.543% | 2.302% | 2.064% | 3.537% | 2.152% | 1.511% | 1.861% | 2.104% | % | =AB-I
AD | Stage-1 Econo. energy savings = | 0.94689 | 0.3576 | 2.1292 | 2.0941 | 1.5151 | 0.80584 | 1.3758 | 1.0632 | 0.90918 | 1.823 | therms/kBtuh | =AA/K
| Stage 2 | [7 empty] | n/a | n/a | n/a
AE | Inlet stack temperature = | 270 | 272 | 200 | 331 | 250 | 304 | 330 |  |  |  | °F | =T
AF | Outlet stack temperature = | 176 | 156 | 170 | 232 | 157 | 201 | 201 |  |  |  | °F | Spec
AG | Sensible heat load = | 326225.2524 | 208290.396 | 184332.8448 | 586580.4945 | 442015.5407 | 508478.04 | 764332.1595 |  |  |  | Btu/hr | =R*C*(AE-AF)
AH | Water vapor flow @ inlet = | 1454.8512 | 756.1897 | 2553.408 | 2482.8804 | 2001.5853 | 2079 | 2482.8804 |  |  |  | Lbm/hr | =R*11% (total vapor)
AI | Water vapor flow @ outlet = | 347.8417 | 219.9825 | 1053.8611 | 2302.3073 | 818.8303 | 1833.3 | 2189.4491 |  |  |  | Lbm/hr | =R*3% to 6% (exiting)
AJ | Condensed Water = | 1107.0095 | 536.2073 | 1499.5469 | 180.5731 | 1182.755 | 245.7 | 293.4313 |  |  |  | Lbm/hr | =AH-AI
AK | Latent heat load = | 1073799.2189 | 520121.0383 | 1454560.4736 | 175155.9264 | 1147272.3015 | 238329 | 284628.3804 |  |  |  | Btu/hr | =AJ*E
AL | Stage-2, Sensible+Latent heat Load = | 1400024.4712 | 728411.4344 | 1638893.3184 | 761736.4209 | 1589287.8422 | 746807.04 | 1048960.5399 |  |  |  | Btu/hr | =AG+AK
Dual-Stages
AM | Total Recovered heat = | 1875480.4241 | 907972.1206 | 3420777.4848 | 1229815.8054 | 2178641.8964 | 1240475.04 | 1487414.6469 |  |  |  | Btu/hr | =X+AL
AN | Economizer Fuel savings = | 2287171.2489 | 1107283.0739 | 4233635.501 | 1537269.7567 | 2723302.3705 | 1542879.403 | 1859268.3086 |  |  |  | Btu/hr | =AM/I
AO | Proposed gas consumption = | 22206731.1901 | 11139668.1456 | 37195819.9446 | 19384605.2432 | 26567322.6295 | 13029570.8458 | 19062606.6914 |  |  |  | Btu/hr | =P-AN
AP | Annual NG Therm Savings = | 91486.85 | 44291.323 | 169345.42 | 115110.7594 | 164051.7348 | 59015.1372 | 97648.7716 |  |  |  | therms/yr | =AN*L/10^5
AQ | Dual-Stage efficiency = | 90.45% | 90.15% | 90% | 86.34% | 88.2% | 89.92% | 87.8% |  |  |  | % | =O*E/AO
AR | Final efficiency improvement = | 8.446% | 8.151% | 9.197% | 6.344% | 8.2% | 9.52% | 7.803% |  |  |  | % | =AQ-I
AS | Dual-Stage Econo. energy savings = | 3.7351 | 1.8083 | 4.0876 | 5.5019 | 5.6008 | 2.0249 | 4.6673 |  |  |  | therms/kBtuh | =AP/K
Adjusted savings based on PG&E’s Process Boiler workpaper PGECOPRO101, Revision 5, 2017
| Capacity Factor, PG&E workpaper | 41.9% | 41.9% | 41.9% | 41.9% | 41.9% | 41.9% | 41.9% | 41.9% | 41.9% | 41.9% | % | PG&E’s Process Boiler workpaper PGECOPRO101, Revision 5, 2017
| Boiler Operation, Continuous | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | hrs | PG&E’s Process Boiler workpaper PGECOPRO101, Revision 5, 2017
Single-Stage:
| average efficiency improvement | 2.355%
| Adjusted energy savings (Stage-1) | 0.86887 | 0.65628 | 1.9538 | 1.0265 | 0.92316 | 1.5466 | 0.96151 | 0.64561 | 0.83428 | 0.89361 | therms/kBtuh
| average adjusted savings | 1.031
Dual-Stage:
| average efficiency improvement | 8.237%
| Adjusted energy savings (Dual-Stages) | 3.4274 | 3.3186 | 3.7508 | 2.6969 | 3.4126 | 3.8861 | 3.2618 | n/a | n/a | n/a | therms/kBtuh
| average adjusted savings | 3.3935
Adjusted savings based on the 2017 SMALL/MEDIUM COMMERCIAL SECTOR_ESPI IMPACT EVALUATION, March 1st, 2019
-10
-20
| Capacity Factor, ESPI study | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | % | TABLE 5-22: CAPACITY FACTOR COMPARISON FOR THE PG&E SAMPLE
| Boiler Operation, ESPI study | 7640 | 7640 | 7640 | 7640 | 7640 | 7640 | 7640 | 7640 | 7640 | 7640 | hrs | TABLE 5-19: ANNUAL OPERATING HOURS COMPARISON FOR THE PG&E SAMPLE
Single-Stage:
| average efficiency improvement | 2.355%
| Adjusted energy savings (Stage-1) | 0.72342 | 0.54642 | 1.6267 | 0.85464 | 0.76862 | 1.2877 | 0.80055 | 0.53753 | 0.69462 | 0.74402 | therms/kBtuh
| average adjusted savings | 0.85842
Dual-Stage:
| average efficiency improvement | 8.237%
| Adjusted energy savings (Dual-Stages) | 2.8536 | 2.763 | 3.1229 | 2.2454 | 2.8413 | 3.2356 | 2.7158 | n/a | n/a | n/a | therms/kBtuh
| average adjusted savings | 2.8254

## Cost Data
Cost estimates provided by vendors and projects completed by SoCalGas C&I team
Project name | Boiler size (BHP) | Quantity | MBH output | MBH input | Econo. Type | Baseline TE eff | Equp. Cost | $/BHP | $/MBH in | parts/mat. | Labor | Total | Ave cost ($/BHP) | Ave cost ($/MBtuh) | $/Mbtuh input cap
Project 10 | 500 | 2 | 33475 | 41843.75 | Single-Stage | 80% | 32900 | 32.9 | 0.78626 | 7200 | 30000 | 70100 | 70.1 | 2.0941 | 1.6753
Project 8 | 1200 | 1 | 40170 | 48750 | Single-Stage | 82.4% | 23031.8 | 19.1932 | 0.47245 | 10000 | 40000 | 73031.8 | 60.8598 | 1.8181 | 1.4981
Project 5 | 700 | 1 | 23432.5 | 28069.5975 | Dual-Stage | 83.48% | 98084.15 | 140.1202 | 3.4943 | 2720 | 33049.14 | 133853.29 | 191.219 | 5.7123 | 4.7686
Project 6 | 700 | 1 | 23432.5 | 29134.0296 | Dual-Stage | 80.43% | 80875 | 115.5357 | 2.776 | 0 | 0 | 80875 | 115.5357 | 3.4514 | 2.776
Project 11 | 400 | 1 | 13390 | 15959.4756 | Dual-Stage | 83.9% | 50503.31 | 126.2583 | 3.1645 | 0 | 0 | 50503.31 | 126.2583 | 3.7717 | 3.1645
Project 12 | 800 | 1 | 26780 | 31505.8824 | Dual-Stage | 85% | 59804.6216 | 74.7558 | 1.8982 | 0 | 84605.6732 | 144410.2948 | 180.5129 | 5.3925 | 4.5836
Project 7 | 500 | 1 | 16737.5 | 20141.3959 | Dual-Stage | 83.1% | 69432 | 138.864 | 3.4472 | 5900 | 23600 | 98932 | 197.864 | 5.9108 | 4.9119
Project 4 | 500 | 1 | 16737.5 | 20141.3959 | Dual-Stage | 83.1% | 48711.1 | 97.4222 | 2.4185 | 15646.87 | 7761 | 72118.97 | 144.2379 | 4.3088 | 3.5806
Project 13 | 900 | 1 | 30127.5 | 36473.9709 | Dual-Stage | 82.6% | 130750.81 | 145.2787 | 3.5848 | 0 | 0 | 130750.81 | 145.2787 | 4.3399 | 3.5848
Project 1 | 600 | 1 | 20085 | 24493.9024 | Single-Stage | 82% | 24000 | 40 | 0.97984 |  | 30000 | 54000 | 90 | 2.6886 | 2.2046
Project 14 | 600 | 1 | 20085 | 24493.9024 | Dual-Stage | 82% | 88000 | 146.6667 | 3.5927 |  | 40000 | 128000 | 213.3333 | 6.3729 | 5.2258
Average cost-1 |  |  | 31243.3333 | 38362.5508 | Single-Stage | 81.47% | 26643.9333 | 30.6977 | 0.74618 |  | 1.0465 | 65710.6 | 73.6533 | 2.2002 | 1.7927
Average cost-2 |  |  | 21340.3125 | 25739.9563 | Dual-Stage | 82.95% | 78270.124 | 123.1127 | 3.047 |  | 1.0274 | 104930.4593 | 164.28 | 4.9075 | 4.0745
Note on H7: Bashar, Raad: 84.4% CE converted to TE
Note on I7: Bashar, Raad: GMC EECIP Measures - Post-Installation. Economizer (6.4% of "Subtotal") = $ 23,031.80
Note on I14: Bashar, Raad: Supply and Install Condensing Stack Gas Economizer on Johnston 750HP Boiler PRICE TO INCLUDE: Stainless Steel High Efficiency Condensing Economizer and Piping Piping Materials Circ Loop Valves Circ Loop Bypass Piping Piping Insulation and Cover Economizer Support Structure Modifications Stainless Steel Discharge Stack Piping DA Tank Supply and FeedWater Supply Modifications Labor to Install Mechanical Systems Labor to Install Electronic Systems Freight Sales Tax TURN KEY PRICE ......................$137,610.72

## Detailed Analysis_Ex.2
Dual-Stage Economizer Estimate
Boiler Specs |  |  |  | Non-Cond. (Feedwater) Economizer |  |  |  |  | Savings:
Superior Steam Boiler 1000HP |  | 33475 | KBtu/hr | Inlet stack temperature |  | 490 |  |  | Feedwater Sensible Heat |  | 1787032.0359 | Btu/hr
Rated Steam Capacity |  | 34510.3093 | lb/hour | Outlet stack temperature | - | 200 | (assumed) |  | Makeup Water Sensible Heat | + | 184865.383 | Btu/hr
Boiler Rated Input Capacity |  | 41429.4554 | KBtu/hr | ∆T | = | 290 |  |  | Makeup Water Latent Heat | + | 1458708.698 | Btu/hr
Boiler thermal efficiency |  | 80.8% |  | Stack flow | x | 23279 | Lb/hr |  | Total Recovered heat | = | 3430606.1169 | Btu/hr
Flue Gas Stack Flow Rate |  | 8320 | SCFM | Stack exhaust spec.heat | x | 0.26471 | Btu/lb/°F |  | Boiler Efficiency | ÷ | 80.8%
| = | 23279 | lb/hour | Sensible heat load | = | 1787032.0359 | Btu/hr |  | Total Fuel Savings |  | 4245799.6497 | Btu/hr
Flue gas stack temperature |  | 490 | °F | [5 empty] | Hours per year | x | 4000 | hrs
Feed Water Flow |  | 34510.3093 | lb/hour | Boiler feedwater | ÷ | 34510.3093 | Lb/hr |  | Conversion factor | ÷ | 100000 | Btu/Therms
Make-Up Water Flow |  | 68 | GPM | Feedwater spec.heat | ÷ | 1 | Btu/lb/°F |  | Annual NG Therm Savings | = | 169831.986 | Therms
| = | 34027.2 | lb/hour | Inlet feedwater temperature | + | 240 |  |  |  |  | 95105.9122
|  |  |  | Outlet feedwater temperature | = | 291.7826
Load Factor | = | 100% | [6 empty] | New efficiency
Average Steam Load | = | 34510.3093 | lb/hr |  |  |  |  | 1). | Feedwater Sensible Heat |  | 1787032.0359 | Btu/hr
|  |  |  | Condensing Economizer (sensible load) |  |  |  |  | Steam Flow Rate |  | 34510.3093 | Lb/hr
Average Feedwater Rate |  | 34510.3093 | lb/hour | Inlet stack temperature |  | 200 |  |  | Saturated Steam Enthalpy | x | 970 | Btu/lb
Condensate Return % |  | 0% |  | Outlet stack temperature | - | 170 | bulk-temp |  | Existing Boiler efficiency | ÷ | 80.8%
Average Make Up Water Rate |  | 34510.3093 | lb/hour | ∆T | = | 30 |  |  | Proposed natural gas cons. | = | 41429455.4455 | Btu/hr
Average Stack Flow Rate |  | 23279 | lb/hour | Stack flow | x | 23279 | Lb/hr |  | Feedwater (Stage-1) fuel savings | = | 2211673.3118 | Btu/hr
Average Stack Temperature |  | 490 | °F | Stack exhaust spec.heat | x | 0.26471 | Btu/lb/°F |  | Stage-1 natural gas load | = | 39217782.1338 | Btu/hr
|  |  |  | Sensible heat load | = | 184865.383 | btu/hr
Hours per year |  | 4000 | hrs | [5 empty] | Stage-1 efficiency | = | 85.36% | efficiency
|  |  |  | Condensing Economizer (latent load) |  |  |  |  | Stage-1 efficiency improvement | = | 4.557%
|  |  |  | Inlet stack temperature |  | 200 |  |  | Stage-1 Econo. energy savings | = | 2.1354 | therms/Mbtuh input capacity
Vendor provided info from a project: |  |  |  | Outlet stack temperature |  | 170 | bulk-temp
|  |  |  | Dew Point |  | 135
|  |  |  | Water vapor by weight @ inlet |  | 11% | @ 200°F | 2). | Steam Flow Rate |  | 34510.3093 | Lb/hr
|  |  |  | Water vapor by weight @ outlet |  | 4.54% | @ 170°F |  | Saturated Steam Enthalpy | x | 970 | Btu/lb
|  |  |  | Water vapor flow @ inlet | = | 2560.69 | lb/hr @ 200°F |  | Existing Boiler efficiency | ÷ | 80.8%
|  |  |  | Water vapor flow @ outlet | - | 1056.8666 | lb/hr @ 170°F |  | Natural Gas Load | = | 41429455.4455 | Btu/hr
|  |  |  | Condensed Water | = | 1503.8234 | Lb/hr |  | Economizer fuel savings | - | 4245799.6497 | Btu/hr
|  |  |  | Water Latent Heat | x | 970 | Btu/lb |  | Proposed natural gas cons. | = | 37183655.7959 | Btu/hr
|  |  |  | Latent heat load | = | 1458708.698 | Btu/hr
[9 empty] | Final (dual-stage) efficiency | = | 90.03% | efficiency
|  |  |  | Sensible heat load | = | 184865.383
|  |  |  | Latent heat load | + | 1458708.698 |  |  | Efficiency improvement | = | 9.226%
|  |  |  | Condensing Recovered heat | = | 1643574.081 | Btu/hr |  | Dual-Stage Econo. energy savings | = | 4.0993 | therms/Mbtuh input capacity
|  |  |  | DA makeup water | ÷ | 34027.2 | Lb/hr
|  |  |  | Feedwater spec.heat | ÷ | 1 | Btu/lb/°F
|  |  |  | Inlet makeup water temperature | + | 70
|  |  |  | Outlet makeup water temperature | = | 118.3018 |  |  |  | Average Capacity Factor = | 40% | based on the 2017 SMALL/MEDIUM COMMERCIAL SECTOR_ESPI IMPACT EVALUATION, March 1st, 2019
[10 empty] | Boiler hours of operation = | 7640 | based on the 2017 SMALL/MEDIUM COMMERCIAL SECTOR_ESPI IMPACT EVALUATION, March 1st, 2020
Heat Recovered, MBTU/Hr |  | 1788.4 | 1645.6
|  | 274 | 104 | [6 empty] | Stage-1 adjusted savings = | 1.6314 | therms/Mbtuh input capacity
|  | 95.95% | 99.48% | [6 empty] | Dual-Stage adjusted savings | 3.1319 | therms/Mbtuh input capacity
3353
|  | 41.509 | 41.4975
166036
92980.16
Fuel Cost per 100,000 BTU (USD): |  | 0.56
Exhaust Entering Temp, °F (°C) |  | 490 | 254
Exhaust Flow Rate, SCFM |  | 8320
0.748
0.617
Exhaust Density, kg/m^3 (lb/ft^3) |  | 0.68774 | 0.042936
Exhaust Flow Rate, lb/hr |  | 21433.4556
23279
Liquid Flow Rate, GPM (lb/hr) |  | 68 | 34027.2
1.097
1.122
Specific Heat, kJ/kgK (Btu/lb.F) |  | 1.1085 | 0.2388
Specific Heat, Btu/lb.F |  | 0.26471 | @ 490deg.F

## Detailed Analysis_Ex.3
Dual-Stage Economizer Estimate
Boiler Specs |  |  |  | Non-Cond. (Feedwater) Economizer |  |  |  |  | Savings:
Cleaver Brooks boiler -CBEX Elite-700-600 |  | 20085 | KBtu/hr | Inlet stack temperature |  | 407 |  |  | Feedwater Sensible Heat |  | 475978.9852 | Btu/hr
Steam Rated Flow Rate |  | 20706.1856 | lb/hour | Outlet stack temperature | - | 270 | (assumed) |  | Makeup Water Sensible Heat | + | 326584.1212 | Btu/hr
Boiler thermal efficiency |  | 82% |  | ∆T | = | 137 |  |  | Makeup Water Latent Heat | + | 1074811.7088 | Btu/hr
Boiler Rated Input Capacity |  | 24493.9024 | KBtu/hr | Stack flow | x | 13238.3908 | Lb/hr |  | Total Recovered heat | = | 1877374.8152 | Btu/hr
Flue Gas Stack temperature |  | 407 | °F | Stack exhaust spec.heat | x | 0.26244 | Btu/lb/°F |  | Boiler Efficiency | ÷ | 82%
Flue Gas Stack Flow Rate |  | 13238.3908 | lb/hour | Sensible heat load | = | 475978.9852 | Btu/hr |  | Total Fuel Savings |  | 2289481.4819 | Btu/hr
Feed Water Flow |  | 41.9 | gpm | [5 empty] | Hours per year | x | 4000 | hrs
| = | 20966.76 | lb/hour | Boiler feedwater | ÷ | 20966.76 | Lb/hr |  | Conversion factor | ÷ | 100000 | Btu/Therms
|  |  |  | Feedwater spec.heat | ÷ | 1 | Btu/lb/°F |  | Annual NG Therm Savings | = | 91579.2593 | Therms
Load Factor | = | 100% |  | Inlet feedwater temperature | + | 227
Average Steam Load | = | 20706.1856 | lb/hr | Outlet feedwater temperature | = | 249.7016 |  |  | New efficiency
[8 empty] | 1). | Stage-1 (Non-Condensing)
Average Feedwater Rate |  | 20966.76 | lb/hour | [5 empty] | Steam Flow Rate |  | 20706.1856 | Lb/hr
Condensate Return % |  | 0% |  | Condensing Economizer (sensible load) |  |  |  |  | Steam Enthalpy | x | 970 | Btu/lb
Average Make Up Water Rate |  | 20966.76 | lb/hour | Inlet stack temperature |  | 270 |  |  | Existing Boiler efficiency | ÷ | 82%
Average Stack Flow Rate |  | 13238.3908 | lb/hour | Outlet stack temperature | - | 176 | bulk-temp |  | Proposed natural gas cons. | = | 24493902.439 | Btu/hr
Average Stack Temperature |  | 407 | °F | ∆T | = | 94 |  |  | Feedwater Sensible Heat |  | 475978.9852 | Btu/hr
|  |  |  | Stack flow | x | 13238.3908 | Lb/hr |  | Feedwater (Stage-1) fuel savings | = | 580462.177 | Btu/hr
Hours per year |  | 4000 | hrs | Stack exhaust spec.heat | x | 0.26244 | Btu/lb/°F |  | Stage-1 natural gas load | = | 23913440.262 | Btu/hr
|  |  |  | Sensible heat load | = | 326584.1212 | btu/hr
[9 empty] | Stage-1 efficiency | = | 83.99% | efficiency
|  |  |  | Condensing Economizer (latent load) |  |  |  |  | Stage-1 efficiency improvement | = | 1.99%
|  |  |  | Inlet stack temperature |  | 270 |  |  | Stage-1 Econo. energy savings | = | 0.94793 | therms/Mbtuh input capacity
Exhaust Entering Temp, °F (°C) |  | 407 | 208 | Outlet stack temperature |  | 176 | bulk-temp
Exhaust Flow Rate, SCFM |  | 4792 |  | Dew Point |  | 135
|  |  |  | Water vapor by weight @ inlet |  | 11% | @ 270°F | 2). | Dual-Stage (Total)
|  | 0.748 |  | Water vapor by weight @ outlet |  | 2.63% | @ 176°F |  | Steam Flow Rate |  | 20706.1856 | lb/hr
|  | 0.617 |  | Water vapor flow @ inlet | = | 1456.223 | lb/hr @ 270°F |  | Steam Enthalpy | x | 970 | btu/lb
Exhaust Density, kg/m^3 (lb/ft^3) |  | 0.73752 | 0.046043 | Water vapor flow @ outlet | - | 348.1697 | lb/hr @ 176°F |  | Existing Boiler efficiency | ÷ | 82%
|  |  |  | Condensed Water | = | 1108.0533 | lb/hr |  | Natural Gas Load | = | 24493902.439 | Btu/hr
Exhaust Flow Rate, lb/hr |  | 13238.3908 |  | Water Latent Heat | x | 970 | btu/lb |  | Economizer fuel savings | - | 2289481.4819 | Btu/hr
|  |  |  | Latent heat load | = | 1074811.7088 | btu/hr |  | Proposed natural gas cons. | = | 22204420.9571 | Btu/hr
Liquid Flow Rate, GPM (lb/hr) |  | 41.9 | 20966.76 | Sensible heat load | = | 326584.1212 |  |  | Final (dual-stage) efficiency | = | 90.45% | efficiency
|  |  |  | Latent heat load | + | 1074811.7088
|  |  |  | Condensing Recovered heat | = | 1401395.83 | btu/hr |  | Dual-Stage efficiency improvement | = | 8.455%
|  | 1.097 | [6 empty] | Dual-Stage Econo. energy savings | = | 3.7389 | therms/Mbtuh input capacity
|  | 1.122 |  | DA makeup water | ÷ | 20966.76 | lb/hr
Specific Heat, kJ/kgK (Btu/lb.F) |  | 1.099 | 0.2388 | Feedwater spec.heat | ÷ | 1 | btu/lb/°F
Specific Heat, Btu/lb.F |  | 0.26244 | @ 407deg.F | Inlet makeup water temperature | + | 50 |  |  | Disclaimer:
|  |  |  | Outlet makeup water temperature | = | 116.8389
Up to 85% based boiler efficiency
Non Condensing (CRE or CCE, boiler size depending)
Up to 90% base boiler efficiency
Condensing (C2X or C1X, two stage vs single stage)
The boiler has a base efficiency of roughly 82%.
[10 empty] | Average Capacity Factor = | 40% | based on the 2017 SMALL/MEDIUM COMMERCIAL SECTOR_ESPI IMPACT EVALUATION, March 1st, 2019
[10 empty] | Boiler hours of operation = | 7640 | based on the 2017 SMALL/MEDIUM COMMERCIAL SECTOR_ESPI IMPACT EVALUATION, March 1st, 2020
[10 empty] | Stage-1 adjusted savings = | 0.72422 | therms/Mbtuh rated input capacity
[10 empty] | Dual-Stage adjusted savings = | 2.8565 | therms/Mbtuh rated input capacity