## SCE 2018 draft workpaper models
|  | Offset | 0 | 1 | 2 | 3 | 4 | 5 | 6
|  | WLT/WMT | WLT | WLT | WLT | WLT | WMT | WMT | WMT | Compare column A | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 5
| CZ | Motor | PSC_Baseline | ECM_PSC | ECM_SPM | SPM | ECM_PSC | ECM_SPM | SPM | Compare column B | 1 | 2 | 3 | 4 | 5 | 6 | 2 | 3 | 4 | 5 | 6 | 3 | 4 | 5 | 6 | 4 | 5 | 6 | 5 | 6 | 6
| 1 |  | SWCR004-01 WLT PSC_CZ1/SWCR004-01 WLT PSC_CZ1_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ1/SWCR004-01 WLT ECM_PSC_CZ1.inp | SWCR004-01 WLT ECM_SPM_CZ1/SWCR004-01 WLT ECM_SPM_CZ1.inp | SWCR004-01 WLT SPM_CZ1/SWCR004-01 WLT SPM_CZ1.inp | SWCR004-01 WMT ECM_PSC_CZ1/SWCR004-01 WMT ECM_PSC_CZ1.inp | SWCR004-01 WMT ECM_SPM_CZ1/SWCR004-01 WMT ECM_SPM_CZ1.inp | SWCR004-01 WMT SPM_CZ1/SWCR004-01 WMT SPM_CZ1.inp | diff -u20 | diff -u20 "SWCR004-01 WLT PSC_CZ1/SWCR004-01 WLT PSC_CZ1_Baseline.inp" "SWCR004-01 WLT ECM_PSC_CZ1/SWCR004-01 WLT ECM_PSC_CZ1.inp" | diff -u20 "SWCR004-01 WLT PSC_CZ1/SWCR004-01 WLT PSC_CZ1_Baseline.inp" "SWCR004-01 WLT ECM_SPM_CZ1/SWCR004-01 WLT ECM_SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT PSC_CZ1/SWCR004-01 WLT PSC_CZ1_Baseline.inp" "SWCR004-01 WLT SPM_CZ1/SWCR004-01 WLT SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT PSC_CZ1/SWCR004-01 WLT PSC_CZ1_Baseline.inp" "SWCR004-01 WMT ECM_PSC_CZ1/SWCR004-01 WMT ECM_PSC_CZ1.inp" | diff -u20 "SWCR004-01 WLT PSC_CZ1/SWCR004-01 WLT PSC_CZ1_Baseline.inp" "SWCR004-01 WMT ECM_SPM_CZ1/SWCR004-01 WMT ECM_SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT PSC_CZ1/SWCR004-01 WLT PSC_CZ1_Baseline.inp" "SWCR004-01 WMT SPM_CZ1/SWCR004-01 WMT SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT ECM_PSC_CZ1/SWCR004-01 WLT ECM_PSC_CZ1.inp" "SWCR004-01 WLT ECM_SPM_CZ1/SWCR004-01 WLT ECM_SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT ECM_PSC_CZ1/SWCR004-01 WLT ECM_PSC_CZ1.inp" "SWCR004-01 WLT SPM_CZ1/SWCR004-01 WLT SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT ECM_PSC_CZ1/SWCR004-01 WLT ECM_PSC_CZ1.inp" "SWCR004-01 WMT ECM_PSC_CZ1/SWCR004-01 WMT ECM_PSC_CZ1.inp" | diff -u20 "SWCR004-01 WLT ECM_PSC_CZ1/SWCR004-01 WLT ECM_PSC_CZ1.inp" "SWCR004-01 WMT ECM_SPM_CZ1/SWCR004-01 WMT ECM_SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT ECM_PSC_CZ1/SWCR004-01 WLT ECM_PSC_CZ1.inp" "SWCR004-01 WMT SPM_CZ1/SWCR004-01 WMT SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT ECM_SPM_CZ1/SWCR004-01 WLT ECM_SPM_CZ1.inp" "SWCR004-01 WLT SPM_CZ1/SWCR004-01 WLT SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT ECM_SPM_CZ1/SWCR004-01 WLT ECM_SPM_CZ1.inp" "SWCR004-01 WMT ECM_PSC_CZ1/SWCR004-01 WMT ECM_PSC_CZ1.inp" | diff -u20 "SWCR004-01 WLT ECM_SPM_CZ1/SWCR004-01 WLT ECM_SPM_CZ1.inp" "SWCR004-01 WMT ECM_SPM_CZ1/SWCR004-01 WMT ECM_SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT ECM_SPM_CZ1/SWCR004-01 WLT ECM_SPM_CZ1.inp" "SWCR004-01 WMT SPM_CZ1/SWCR004-01 WMT SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT SPM_CZ1/SWCR004-01 WLT SPM_CZ1.inp" "SWCR004-01 WMT ECM_PSC_CZ1/SWCR004-01 WMT ECM_PSC_CZ1.inp" | diff -u20 "SWCR004-01 WLT SPM_CZ1/SWCR004-01 WLT SPM_CZ1.inp" "SWCR004-01 WMT ECM_SPM_CZ1/SWCR004-01 WMT ECM_SPM_CZ1.inp" | diff -u20 "SWCR004-01 WLT SPM_CZ1/SWCR004-01 WLT SPM_CZ1.inp" "SWCR004-01 WMT SPM_CZ1/SWCR004-01 WMT SPM_CZ1.inp" | diff -u20 "SWCR004-01 WMT ECM_PSC_CZ1/SWCR004-01 WMT ECM_PSC_CZ1.inp" "SWCR004-01 WMT ECM_SPM_CZ1/SWCR004-01 WMT ECM_SPM_CZ1.inp" | diff -u20 "SWCR004-01 WMT ECM_PSC_CZ1/SWCR004-01 WMT ECM_PSC_CZ1.inp" "SWCR004-01 WMT SPM_CZ1/SWCR004-01 WMT SPM_CZ1.inp"
| 2 |  | SWCR004-01 WLT PSC_CZ2/SWCR004-01 WLT PSC_CZ2_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ2/SWCR004-01 WLT ECM_PSC_CZ2.inp | SWCR004-01 WLT ECM_SPM_CZ2/SWCR004-01 WLT ECM_SPM_CZ2.inp | SWCR004-01 WLT SPM_CZ2/SWCR004-01 WLT SPM_CZ2.inp | SWCR004-01 WMT ECM_PSC_CZ2/SWCR004-01 WMT ECM_PSC_CZ2.inp | SWCR004-01 WMT ECM_SPM_CZ2/SWCR004-01 WMT ECM_SPM_CZ2.inp | SWCR004-01 WMT SPM_CZ2/SWCR004-01 WMT SPM_CZ2.inp
| 3 |  | SWCR004-01 WLT PSC_CZ3/SWCR004-01 WLT PSC_CZ3_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ3/SWCR004-01 WLT ECM_PSC_CZ3.inp | SWCR004-01 WLT ECM_SPM_CZ3/SWCR004-01 WLT ECM_SPM_CZ3.inp | SWCR004-01 WLT SPM_CZ3/SWCR004-01 WLT SPM_CZ3.inp | SWCR004-01 WMT ECM_PSC_CZ3/SWCR004-01 WMT ECM_PSC_CZ3.inp | SWCR004-01 WMT ECM_SPM_CZ3/SWCR004-01 WMT ECM_SPM_CZ3.inp | SWCR004-01 WMT SPM_CZ3/SWCR004-01 WMT SPM_CZ3.inp
| 4 |  | SWCR004-01 WLT PSC_CZ4/SWCR004-01 WLT PSC_CZ4_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ4/SWCR004-01 WLT ECM_PSC_CZ4.inp | SWCR004-01 WLT ECM_SPM_CZ4/SWCR004-01 WLT ECM_SPM_CZ4.inp | SWCR004-01 WLT SPM_CZ4/SWCR004-01 WLT SPM_CZ4.inp | SWCR004-01 WMT ECM_PSC_CZ4/SWCR004-01 WMT ECM_PSC_CZ4.inp | SWCR004-01 WMT ECM_SPM_CZ4/SWCR004-01 WMT ECM_SPM_CZ4.inp | SWCR004-01 WMT SPM_CZ4/SWCR004-01 WMT SPM_CZ4.inp
| 5 |  | SWCR004-01 WLT PSC_CZ5/SWCR004-01 WLT PSC_CZ5_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ5/SWCR004-01 WLT ECM_PSC_CZ5.inp | SWCR004-01 WLT ECM_SPM_CZ5/SWCR004-01 WLT ECM_SPM_CZ5.inp | SWCR004-01 WLT SPM_CZ5/SWCR004-01 WLT SPM_CZ5.inp | SWCR004-01 WMT ECM_PSC_CZ5/SWCR004-01 WMT ECM_PSC_CZ5.inp | SWCR004-01 WMT ECM_SPM_CZ5/SWCR004-01 WMT ECM_SPM_CZ5.inp | SWCR004-01 WMT SPM_CZ5/SWCR004-01 WMT SPM_CZ5.inp
| 6 |  | SWCR004-01 WLT PSC_CZ6/SWCR004-01 WLT PSC_CZ6_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ6/SWCR004-01 WLT ECM_PSC_CZ6.inp | SWCR004-01 WLT ECM_SPM_CZ6/SWCR004-01 WLT ECM_SPM_CZ6.inp | SWCR004-01 WLT SPM_CZ6/SWCR004-01 WLT SPM_CZ6.inp | SWCR004-01 WMT ECM_PSC_CZ6/SWCR004-01 WMT ECM_PSC_CZ6.inp | SWCR004-01 WMT ECM_SPM_CZ6/SWCR004-01 WMT ECM_SPM_CZ6.inp | SWCR004-01 WMT SPM_CZ6/SWCR004-01 WMT SPM_CZ6.inp
| 7 |  | SWCR004-01 WLT PSC_CZ7/SWCR004-01 WLT PSC_CZ7_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ7/SWCR004-01 WLT ECM_PSC_CZ7.inp | SWCR004-01 WLT ECM_SPM_CZ7/SWCR004-01 WLT ECM_SPM_CZ7.inp | SWCR004-01 WLT SPM_CZ7/SWCR004-01 WLT SPM_CZ7.inp | SWCR004-01 WMT ECM_PSC_CZ7/SWCR004-01 WMT ECM_PSC_CZ7.inp | SWCR004-01 WMT ECM_SPM_CZ7/SWCR004-01 WMT ECM_SPM_CZ7.inp | SWCR004-01 WMT SPM_CZ7/SWCR004-01 WMT SPM_CZ7.inp
| 8 |  | SWCR004-01 WLT PSC_CZ8/SWCR004-01 WLT PSC_CZ8_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ8/SWCR004-01 WLT ECM_PSC_CZ8.inp | SWCR004-01 WLT ECM_SPM_CZ8/SWCR004-01 WLT ECM_SPM_CZ8.inp | SWCR004-01 WLT SPM_CZ8/SWCR004-01 WLT SPM_CZ8.inp | SWCR004-01 WMT ECM_PSC_CZ8/SWCR004-01 WMT ECM_PSC_CZ8.inp | SWCR004-01 WMT ECM_SPM_CZ8/SWCR004-01 WMT ECM_SPM_CZ8.inp | SWCR004-01 WMT SPM_CZ8/SWCR004-01 WMT SPM_CZ8.inp
| 9 |  | SWCR004-01 WLT PSC_CZ9/SWCR004-01 WLT PSC_CZ9_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ9/SWCR004-01 WLT ECM_PSC_CZ9.inp | SWCR004-01 WLT ECM_SPM_CZ9/SWCR004-01 WLT ECM_SPM_CZ9.inp | SWCR004-01 WLT SPM_CZ9/SWCR004-01 WLT SPM_CZ9.inp | SWCR004-01 WMT ECM_PSC_CZ9/SWCR004-01 WMT ECM_PSC_CZ9.inp | SWCR004-01 WMT ECM_SPM_CZ9/SWCR004-01 WMT ECM_SPM_CZ9.inp | SWCR004-01 WMT SPM_CZ9/SWCR004-01 WMT SPM_CZ9.inp
| 10 |  | SWCR004-01 WLT PSC_CZ10/SWCR004-01 WLT PSC_CZ10_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ10/SWCR004-01 WLT ECM_PSC_CZ10.inp | SWCR004-01 WLT ECM_SPM_CZ10/SWCR004-01 WLT ECM_SPM_CZ10.inp | SWCR004-01 WLT SPM_CZ10/SWCR004-01 WLT SPM_CZ10.inp | SWCR004-01 WMT ECM_PSC_CZ10/SWCR004-01 WMT ECM_PSC_CZ10.inp | SWCR004-01 WMT ECM_SPM_CZ10/SWCR004-01 WMT ECM_SPM_CZ10.inp | SWCR004-01 WMT SPM_CZ10/SWCR004-01 WMT SPM_CZ10.inp
| 11 |  | SWCR004-01 WLT PSC_CZ11/SWCR004-01 WLT PSC_CZ11_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ11/SWCR004-01 WLT ECM_PSC_CZ11.inp | SWCR004-01 WLT ECM_SPM_CZ11/SWCR004-01 WLT ECM_SPM_CZ11.inp | SWCR004-01 WLT SPM_CZ11/SWCR004-01 WLT SPM_CZ11.inp | SWCR004-01 WMT ECM_PSC_CZ11/SWCR004-01 WMT ECM_PSC_CZ11.inp | SWCR004-01 WMT ECM_SPM_CZ11/SWCR004-01 WMT ECM_SPM_CZ11.inp | SWCR004-01 WMT SPM_CZ11/SWCR004-01 WMT SPM_CZ11.inp
| 12 |  | SWCR004-01 WLT PSC_CZ12/SWCR004-01 WLT PSC_CZ12_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ12/SWCR004-01 WLT ECM_PSC_CZ12.inp | SWCR004-01 WLT ECM_SPM_CZ12/SWCR004-01 WLT ECM_SPM_CZ12.inp | SWCR004-01 WLT SPM_CZ12/SWCR004-01 WLT SPM_CZ12.inp | SWCR004-01 WMT ECM_PSC_CZ12/SWCR004-01 WMT ECM_PSC_CZ12.inp | SWCR004-01 WMT ECM_SPM_CZ12/SWCR004-01 WMT ECM_SPM_CZ12.inp | SWCR004-01 WMT SPM_CZ12/SWCR004-01 WMT SPM_CZ12.inp
| 13 |  | SWCR004-01 WLT PSC_CZ13/SWCR004-01 WLT PSC_CZ13_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ13/SWCR004-01 WLT ECM_PSC_CZ13.inp | SWCR004-01 WLT ECM_SPM_CZ13/SWCR004-01 WLT ECM_SPM_CZ13.inp | SWCR004-01 WLT SPM_CZ13/SWCR004-01 WLT SPM_CZ13.inp | SWCR004-01 WMT ECM_PSC_CZ13/SWCR004-01 WMT ECM_PSC_CZ13.inp | SWCR004-01 WMT ECM_SPM_CZ13/SWCR004-01 WMT ECM_SPM_CZ13.inp | SWCR004-01 WMT SPM_CZ13/SWCR004-01 WMT SPM_CZ13.inp
| 14 |  | SWCR004-01 WLT PSC_CZ14/SWCR004-01 WLT PSC_CZ14_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ14/SWCR004-01 WLT ECM_PSC_CZ14.inp | SWCR004-01 WLT ECM_SPM_CZ14/SWCR004-01 WLT ECM_SPM_CZ14.inp | SWCR004-01 WLT SPM_CZ14/SWCR004-01 WLT SPM_CZ14.inp | SWCR004-01 WMT ECM_PSC_CZ14/SWCR004-01 WMT ECM_PSC_CZ14.inp | SWCR004-01 WMT ECM_SPM_CZ14/SWCR004-01 WMT ECM_SPM_CZ14.inp | SWCR004-01 WMT SPM_CZ14/SWCR004-01 WMT SPM_CZ14.inp
| 15 |  | SWCR004-01 WLT PSC_CZ15/SWCR004-01 WLT PSC_CZ15_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ15/SWCR004-01 WLT ECM_PSC_CZ15.inp | SWCR004-01 WLT ECM_SPM_CZ15/SWCR004-01 WLT ECM_SPM_CZ15.inp | SWCR004-01 WLT SPM_CZ15/SWCR004-01 WLT SPM_CZ15.inp | SWCR004-01 WMT ECM_PSC_CZ15/SWCR004-01 WMT ECM_PSC_CZ15.inp | SWCR004-01 WMT ECM_SPM_CZ15/SWCR004-01 WMT ECM_SPM_CZ15.inp | SWCR004-01 WMT SPM_CZ15/SWCR004-01 WMT SPM_CZ15.inp
| 16 |  | SWCR004-01 WLT PSC_CZ16/SWCR004-01 WLT PSC_CZ16_Baseline.inp | SWCR004-01 WLT ECM_PSC_CZ16/SWCR004-01 WLT ECM_PSC_CZ16.inp | SWCR004-01 WLT ECM_SPM_CZ16/SWCR004-01 WLT ECM_SPM_CZ16.inp | SWCR004-01 WLT SPM_CZ16/SWCR004-01 WLT SPM_CZ16.inp | SWCR004-01 WMT ECM_PSC_CZ16/SWCR004-01 WMT ECM_PSC_CZ16.inp | SWCR004-01 WMT ECM_SPM_CZ16/SWCR004-01 WMT ECM_SPM_CZ16.inp | SWCR004-01 WMT SPM_CZ16/SWCR004-01 WMT SPM_CZ16.inp
Table of Supply-KW/flow values in models from 2018-Nov-30
|  | WLT/WMT | WLT | WLT | WLT | WLT | WMT | WMT | WMT
|  | Motor | PSC_Baseline | ECM_PSC | ECM_SPM | SPM | ECM_PSC | ECM_SPM | SPM
SYSTEM | Freezer_System |  | 6.084e-05 | 5.07e-05 | 7.61e-05 | 0.000169 | 6.084e-05 | 6.084e-05 | 6.084e-05
| Cooler_System |  | 8.619e-05 | 8.619e-05 | 8.619e-05 | 8.619e-05 | 7.18e-05 | 7.61e-05 | 0.000169
Inferred multipliers
SYSTEM | Freezer_System |  | 0.36 | 0.3 | 0.4503 | 1
| Cooler_System |  | 0.51 |  |  |  | 0.42485 | 0.4503 | 1
Matches DEER measure case
Matches draft 2018 workpaper
DEER/workpaper baseline

## ADL 1996
1996 Report
Arthur D. Little, Inc. 1996. Energy Savings Potential for Commercial Refrigeration Equipment. Prepared for Building Equipment Division Office of Building Technologies U.S. Department of Energy.
https://sites.uclouvain.be/energie-plus/fileadmin/resources/04_technique/14_froid_alimentaire/Etudes/bilan_energie_commerce_usa.pdf
Table 4-44
|  |  |  | Walk-in Freezer |  |  | Walk-in cooler
Evaporators
|  | Air flow (CFM) |  | 1680 |  |  | 6400
|  | Number fans |  | 2 |  |  | 8
|  | Fan wattage (W) |  | 90 |  |  | 100
|  | Fan motor type |  | Shaded pole (1/40 hp) |  |  | Shaded pole (1/20 hp)
|  | Total fan kW |  | 0.18 |  |  | 0.8
|  | Total fan kW/CFM |  | 0.00010714 |  |  | 0.000125
|  | Hi-Eff multiplier |  | 0.3 |  |  | 0.3
|  | Hi-Eff fan kW/CFM |  | 3.2143e-05 |  |  | 3.75e-05
|  | CFM per fan |  | 840 |  |  | 800
|  | DEER models by comparison |  | DEER2020 Freezer |  |  | DEER2020 Cooler |  |  | eQUEST freezer |  | eQUEST cooler
|  | Rated CFM |  | 5700 |  |  | 5937.5 |  |  | 5700 |  | 5937.5
|  | 1975-2003 baseline kW/CFM |  | 0.000169 |  |  | 0.000169 |  |  | 0.000169 |  | 0.000169
|  | Total fan W power |  | 963.3 |  |  | 1003.4375 |  |  | 963.3 |  | 1003.4375
|  | Single fan kW |  | 90 |  |  | 146.6152 | 100 | 90 | 90 |  | 146.6152 | 100
|  | Number fans (exact) |  | 10.7033 |  |  | 6.844 | 10.0344 | 11.1493 | 10.7033 |  | 6.844 | 10.0344
|  | Rounded number |  | 11 |  |  | 7 | 10 | 11 | 11 |  | 7 | 10
Table 5-2
|  | Motor output (W) | Motor output (HP) | Shaded Pole |  | PSC |  | ECM |  |  | Calculated efficiency |  |  |  |  | Hi-Eff wattage multiplier relative to SHP |  | Relative to PSC
|  |  |  | Wattage | OEM cost | Wattage | OEM cost | Wattage | OEM Cost |  | Shaded pole |  | PSC | ECM |  | PSC | ECM | ECM
|  | 6 | 0.0083333 | 40 | 7 | 15 | 25 | 8.5 | 35 |  | 15% |  | 40% | 70.59% |  | 0.375 | 0.2125 | 0.56667
|  | 9 | 0.0125 | 53 | 10 | 21 | 28 | 12.5 | 40 |  | 16.98% |  | 42.86% | 72% |  | 0.39623 | 0.23585 | 0.59524 | Fan W/CFM
|  | 15 | 0.020115 | 75 | 15 | 33 | 33 | 20.5 | 42 |  | 20% |  | 45.45% | 73.17% |  | 0.44 | 0.27333 | 0.62121 | SHP | PSC | ECM
|  | 20 | 0.025 | 90 | 20 | 42 | 35 | 27 | 45 |  | 22.22% |  | 47.62% | 74.07% |  | 0.46667 | 0.3 | 0.64286 | 169 | 78.8667 | 50.7
|  | 25 | 0.033525 | 110 | 25 | 51 | 37 | 33 | 48 |  | 22.73% |  | 49.02% | 75.76% |  | 0.46364 | 0.3 | 0.64706
|  | 37 | 0.05 | 146.6152 | 30 | 70 | 40 | 49 | 52 |  | 25.24% |  | 52.86% | 75.51% |  | 0.47744 | 0.33421 | 0.7 | 169 | 80.6874 | 56.4812
|  | 50 | 0.066667 |  |  | 90 | 43 | 65 | 54 |  |  |  | 55.56% | 76.92% |  |  |  | 0.72222
|  | 125 | 0.16667 |  |  | 202 | 51 | 155 | 64 |  |  |  | 61.88% | 80.65% |  |  |  | 0.76733
|  | 249 | 0.33333 |  |  | 370 | 57 | 304 | 71 |  |  |  | 67.3% | 81.91% |  |  |  | 0.82162
|  | 373 | 0.5 |  |  | 530 | 60 | 450 | 75 |  |  |  | 70.38% | 82.89% |  |  |  | 0.84906
[10 empty] | Min-Max | 15.0% to 22.7% |  | 40.0% to 70.4% | 70.6% to 82.9% |  | 0.375 to 0.477 | 0.213 to 0.334 | 0.567 to 0.849
Freezer
Cooler
Extrapolation
| Extrapolations |  | Fit to wattage |  | Fit to efficiency |  | Anecdotal table 4-44
|  | Motor output (W) | SHP wattage | Efficiency | SHP wattage | Efficiency | SHP wattage | Efficiency
|  | 6 | 41.4744 | 14.47% | 40.3087 | 14.89%
|  | 9 | 53.5617 | 16.8% | 52.3493 | 17.19%
|  | 15 | 78.2385 | 19.17% | 74.6313 | 20.1%
|  | 20 | 99.314 | 20.14% | 92.0144 | 21.74% | 90 | 22.22%
|  | 25 | 120.8545 | 20.69% | 108.6701 | 23.01%
|  | 37 | 174.4489 | 21.21% | 146.6152 | 25.24% | 100 | 37%
|  | 50 | 235.532 | 21.23% | 185.5328 | 26.95%
|  | 125 | 649.3145 | 19.25% | 388.6441 | 32.16%
|  | 249 | 1562.9217 | 15.93% | 690.0507 | 36.08%
|  | 373 | 2762.5225 | 13.5% | 971.7646 | 38.38%
|  | Error | 217.548 | 0.00095114 | 6.4813 | 3.8156e-05
Table 5-13
[5 empty] | Shaded pole |  |  |  | PSC |  |  |  | ECM |  |  | Hi-Eff wattage multiplier relative to SHP
|  | Motor output (W) |  | Total number | Total Cost (OEM) |  | Total Power (W) |  | Total Cost (OEM) |  | Total Power (W) |  | Total Cost (OEM) | Total Power (W) |  | PSC | ECM
|  | 6 |  | 85 |  |  | 3400 | 40 |  |  | 1275 | 15 |  | 720 | 8.4706 | 0.375 | 0.21176
|  | 9 |  | 100 |  |  | 5300 | 53 |  |  | 2100 | 21 |  | 1250 | 12.5 | 0.39623 | 0.23585
|  | 25 |  | 40 |  |  | 4400 | 110 |  |  | 2040 | 51 |  | 1320 | 33 | 0.46364 | 0.3
|  | Totals |  |  |  |  | 13100 |  |  |  | 5400 |  |  | 3290 |  | 0.41221 | 0.25115
Simple average
[16 empty] | 0.41162 | 0.2492
1999 Report
https://library.cee1.org/system/files/library/1103/268.pdf
Note on T144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I don't trust this data point (100 W, 1/20 HP), since this is an outlier from data in table 5-2.
Note on Q150: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is my attempt to calculate kW/CFM for an ECM, using only the data in the ADL 1996 report. Neither one the baseline nor the measure cases lines up with values proposed in the 2018 draft workpaper.
Note on U158: Nicholas Fette: Hypothetical fan count based on table 4-44 fan wattage
Note on V158: Nicholas Fette: Hypothetical fan count based on 1/40 HP fan wattage
Note on Z158: Nicholas Fette: Hypothetical fan count based on table 4-44 fan wattage
Note on Q160: Nicholas Fette: These numbers selected for normalizing savings per motor.
Note on AF172: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is a conservative choice for Hi-Eff factor representing coolers (at 1/20 HP, shaded pole to ECM upgrade).
Note on X178: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Here is the correct range for shaded pole motor efficiencies.