## Whole House Fans
DEER2024 EnergyPlus
MeasureID | MeasureName | DEER_MeasureID | MASControl3 corresponding measureID (if any) | Description | PreTechID (essential) | StdTechID (essential) | MsrTechID (essential) | VariTech (if applicable) | VariTech Notes | HVAC Type (per DEER-Res-Measures workbook-MC3 workbook) | Prototype Building that applies(per DEER-Res-Measures workbook-MC3 workbook) | Corresponding Class in EnergyPlus for this measure -Main Class | Corresponding Parameter in EnergyPlus for this measure | Corresponding Parameter values in EnergyPlus | Additional notes- for EP input
SWHC030 | Whole House Fan, Residential | WholeHouseFan-0.7CFM-ECM | WHFan-0.7-ECM |  |  | None | WHFan-0.7-ECM | ResNatVentPre | see DEER_Res_Tables.xlsm | rDXGF | SFm | ZoneVentilation:DesignFlowRate | Flow Rate per Zone Floor Area (ft3/min-ft2) | 0, 0.7, 1.5, 2, 3 [CFM/ft2] | Fan pressure rise is assumed 0.029 psi (200 Pa)
|  | WholeHouseFan-1.5CFM-ECM | WHFan-1.5-ECM |  |  |  | WHFan-1.5-ECM | ResNatVentPre |  | rDXGF | SFm
|  | WholeHouseFan-2.0CFM-ECM | WHFan-2.0-ECM |  |  |  | WHFan-2.0-ECM | ResNatVentPre |  | rDXGF | SFm
|  | WholeHouseFan-3.0CFM-ECM | WHFan-3.0-ECM |  |  |  | WHFan-3.0-ECM | ResNatVentPre |  | rDXGF | SFm
DEER2020 DOE2
MeasureID | MeasureName | DEER_MeasureID | MASControl3 corresponding measureID (if any) | Description | PreTechID (essential) | StdTechID (essential) | MsrTechID (essential) | VariTech (if applicable) | VariTech Notes
SWHC030 | Whole House Fan, Residential | WholeHouseFan-0.7CFM-ECM | WHFan-0.7-ECM |  | WHFan-NatVent, WHFan-1.5-PSC (only when CZ=08 to 14, vintage = 2014, 2017, 2020) |  | WHFan-0.7-ECM | ResNatVentPre | see DEER_Res_Tables.xlsm
|  | WholeHouseFan-0.7CFM-PSC | WHFan-0.7-PSC |  |  |  | WHFan-0.7-PSC | ResNatVentPre
|  | WholeHouseFan-1.5CFM-ECM | WHFan-1.5-ECM |  |  |  | WHFan-1.5-ECM | ResNatVentPre
|  | WholeHouseFan-1.5CFM-PSC | WHFan-1.5-PSC |  |  |  | WHFan-1.5-PSC | ResNatVentPre
|  | WholeHouseFan-2.0CFM-ECM | WHFan-2.0-ECM |  |  |  | WHFan-2.0-ECM | ResNatVentPre
|  | WholeHouseFan-2.0CFM-PSC | WHFan-2.0-PSC |  |  |  | WHFan-2.0-PSC | ResNatVentPre
|  | WholeHouseFan-3.0CFM-ECM | WHFan-3.0-ECM |  |  |  | WHFan-3.0-ECM | ResNatVentPre
|  | WholeHouseFan-3.0CFM-PSC | WHFan-3.0-PSC |  |  |  | WHFan-3.0-PSC | ResNatVentPre
UPDATES FROM MC3 Measures

## inputs
| sq ft | 1400
| CFM/SF | SF | CFM | W/cfm | W
WHFan-0.7-ECM | 0.7 | 1400 | 980 | 0.125 | 122.5
WHFan-1.5-ECM | 1.5 | 1400 | 2100 | 0.125 | 262.5
WHFan-2.0-ECM | 2 | 1400 | 2800 | 0.125 | 350
WHFan-3.0-ECM | 3 | 1400 | 4200 | 0.125 | 525

## Notes
Notes
Original internal mass object
Updates:
- The Whole House Fan W/CFM energy consumption assumptions were updated with new manufacturer's data.
- Eliminated the 0.5 schedule multiplier accounting for occupant behavior only opening windows half the time
- Reduced the delta T (WHF turns on when outdoor temp is greater than delta T below indoor temp) from 5F to 2F
- Allow whole house fan operation throughout the night. The 2022 CA-24 compliance manual states that the whole house fan should run all night to cool the thermal mass of the house, allowing the home to coast through the daytime cooling period without needing mechanical cooling. In new homes homeowners are provided a one page document telling them how to operate the whole house fan. It also notes that most windows have security features allowing them to be locked while slightly open.
- minimum setpoint 72
New construction:
- the airflow rate of the fan is 1.5 CFM/SF
Relevant prototypt updates:
- Updated the cooling enabled period to align with new CZ2022 weather, using ACM method
- Updated the thermostat set points, per the ACM.
-
Notes:
- previous EM&V (which study?) cited in all later CA studies used modeling and determined whole house fan savings at about 10% of cooling consumption, i.e. they offset 10% of the cooling run hours.
-
Natural Ventilation Notes:
- Natural ventilation uses the following parameters from the old DOE2 models
- ACH = 3
- Wind driven air exchange only, multiplier from the eQUEST model
- Available between 5am and 11pm
- New parameters
- setpoint of 68 when cooling mode (consistent w ACM) (was 72 previously)
- setpoint of 77 when in heating mode (well above heating setpoint)
- 2 degree delta T
- no probabiltiy of having windows open (previous was 0.5)

## GeneralLitReview
Whole House Fan Literature Survey for DEER 2023 Release
This worksheet contains notes from a literature survey conducted to support the Whole House Fan measure development.
Jen to update this
Whole House Fan Literature Survey for DEER 2017 Release
This worksheet contains notes from a literature survey conducted to support the Whole House Fan measure development.
NREL/ DOE Technology Fact Sheet: Whole House Fan
DOE/GO-10099-745; March 1999
Air flow:
CFM = 0.5 to 1.0 x FlrArea x ClgHt
|  | 4 | to | 8 | Range of cfm/sf
|  | 30 | to | 60 | ACH
Fan Power:
120 to 600 Watts
Green Building Adviser
Oct 26 2012
15 to 20 ACH
200 to 700 Watts
2000 to 6000 cfm
if area is 1000 to 3000, this is 2 cfm/sf
|  | ---> | 15 | ACH
Measured Natural Cooling Enhancement of a Whole House Fan
FSEC-PF-273-92
1991 Field test changing from natural ventilation-only to whole house fan
House did not have AC
24 inch model with 1/3rd hp motor
Design airflow 3100 cfm/ 1 inch static
Measured air flow and power
1150 cfm at low speed
2060 cfm at high speed
|  |  | 265 W low/ 350 Watts high |  |  |  | W | CFM
|  |  | 0.1699 | Actual W/cfm at high speed |  |  | 350 | 2060
House: cond floor area = 1300 sf
|  | 2.3846 | rated cfm/sf |  | 1.5846 | actual cfm/sf
|  | 17.8846 | ACH |  | 11.8846 | ACH
Ventilating Residences and Their Attics for Energy Conservation
Center for Building Technology, National Bureau of Standards
D. M. Burch and S. J. Treado, 1978
Physical tests in Houston
Use whole-house fan whenever:
TOA <= 82 F
RHoa <= 75%
|  | 1020 | sq ft conditioned area
|  | 439 | sq ft garage
|  | 2.5 | ton AC unit
|  | 13200 | cfm WWF at high speed
|  | 8840 | cfm of WWF at low spd
|  | 8 | clg ht (not provided in article)
|  | 8160 | volume
|  | 1.6176 | rated air changes / min
|  | 0.8 | reported air changes/min
|  | 48 | ACH | High ACH allows comfort at high indoor temperature
|  | 8 | velocity w/ AC, ft/min
|  | 40 | velocity at 48 ACH, ft/min
|  | 400 | AC cfm/ton
|  | 7.3529 | ACH for Air Conditioner fan
Building America Measure Guideline: Ventilation Cooling
D. Springer, et al, USDOE, April 2012
Whole House Fan simulation study
|  | 1527 | cfm
|  | 228 | W
|  | 0.14931 | W/cfm
Fan operates between 8 pm and 8 am if Tzone - Toa > 5 F
and Tzone > 65 F
|  | 2400 | sq ft house
|  | 0.63625 | cfm/sf
|  | 4.7719 | ACH
Indicates typical WHFan ACH can vary from 5 to 30 ACH

## Product Data
Whole House Fan Product Data from Manufacturer Literature for DEER 2023 Release | [13 empty] | The following values are used for the DEER 2023 modeling:
MFG | Model | CFM hi | CFM lo | Watt, hi | Watt, lo | R value | Motor | W/cfm hi | W/cfm lo | Min spd ratio |  | ECM/PSC |  | W/CFM
Tamarack | HV1000 | 1000 |  | 70 |  | 38 |  | 0.07 |  |  | QuietCool 1500 | 60.04% |  | 0.15 | PSC | from Building America Report used in DEER2017
Tamarack | HV1600 | 1600 | 1150 | 230 | 207 | 38 |  | 0.14375 | 0.18 | 71.88% | QuietCool 2250 | 57.41% |  | 0.10911 | ECM | scaled based on QuiedCool ECM vs PSC
Tamarack | HV3400 | 3400 | 1900 | 450 | 340 | 38 |  | 0.13235 | 0.17895 | 55.88% | QuietCool 3100 | 94.52% |  | the ECM W was updated from the DEER2017 release based on new manufacturer data, see left
AirScape | 3200 WHF | 3253 | 723 | 321 | 18 | 13 | ECM | 0.098678 | 0.024896 | 22.23% | QuietCool 4700 | 78.99%
AirScape | 3400 WHF | 3440 | 723 | 298 | 17 | 49 | ECM | 0.086628 | 0.023513 | 21.02% | Average: | 72.74%
AirScape | 5300 WHF | 5350 | 1367 | 825 | 34 | 49 | ECM | 0.15421 | 0.024872 | 25.55%
Centric Air | QA-Deluxe 4800 | 3209 | NA | 491 | 246 | 5 | ECM | 0.15301
Centric Air | QA-Deluxe 5500 | 3945 | NA | 662 | 480 | 5 | PSC | 0.16781
QuietCool | CL-1500 | 1100 | NA | 117 | NA | 5 | PSC | 0.10636
QuietCool | ES-1500 | 1010 | NA | 64.5 | NA | 5 | ECM | 0.063861
QuietCool | CL-2250 | 1770 | 1330 | 250 | 201 | 5 | PSC | 0.14124 | 0.15113 | 75.14%
QuietCool | ES-2250 | 1850 | 1420 | 150 | 79.5 | 5 | ECM | 0.081081 | 0.055986 | 76.76%
QuietCool | CL-3100 | 2380 | 2160 | 299 | 256 | 5 | PSC | 0.12563 | 0.11852 | 90.76%
QuietCool | ES-3100 | 2400 | 1500 | 285 | 80 | 5 | ECM | 0.11875
QuietCool | CL-4700 | 3230 | 2560 | 551 | 415 | 5 | PSC | 0.17059 | 0.16211 | 79.26%
QuietCool | ES-4700 | 3080 | 1620 | 415 | 75 | 5 | ECM | 0.13474 | 0.046296 | 52.6%
[7 empty] | ECM Average | 0.11137 | 0.096627
[7 empty] | PSC Average | 0.14233
[13 empty] | Flow [CFM/SF] | 0.7
Whole House Fan Product Data from Manufacturer Literature for DEER 2017 Release | [15 empty] | Fan Efficiency
MFG | Model | CFM hi | CFM lo | Watt, hi | Watt, lo | R value | Motor | W/cfm hi | W/cfm lo | Min spd ratio |  |  |  | ECM | PSC | eff = dp * q /P
Tamarack | HV1000 | 1000 |  | 70 |  | 38 |  | 0.07 | [5 empty] | 0.32433 | 0.23592 | eff
Tamarack | HV1600 | 1600 | 1150 | 230 | 207 | 38 |  | 0.14375 | 0.18 | 71.88% |  |  |  | 75 | 75 | dp | total pressure increase in the fan | Pa | 0.010877 | psi | <--This seems too high since the whole house fan should operate at a lower ESP than an HVAC fan
Tamarack | HV3400 | 3400 | 1900 | 450 | 340 | 38 |  | 0.13235 | 0.17895 | 55.88% |  |  |  | 0.46223 | 0.46223 | q | flow | m^3/s
AirScape | 1.0 WHF | 1047 | 600 | 85 | 55 | 14 |  | 0.081184 | 0.091667 | 57.31% |  |  |  | 106.8882 | 146.9481 | P | power | W |  |  | motor efficiency
AirScape | 3.5e WHF | 3500 | 800 | 385 | 20 | 10 |  | 0.11 | 0.025 | 22.86% |  |  |  | 979.6538 | 979.6538 |  | flow | cfm |  |  | impeller efficiency
AirScape | 5.0e WHF | 5064 | 1316 | 810 | 28 | 10 |  | 0.15995 | 0.021277 | 25.99% | [9 empty] | 0 | fan total efficiency
Kohilo | 1.5 | 1532 | NA | 168 | NA | backdraft damper |  | 0.10966 | [7 empty] | Area
Kohilo | 2.8 | 2850 | NA | 297 | NA | backdraft damper |  | 0.10421 | [7 empty] | 1400 | sq ft
QuietCool | HV1000 | 1104 | 552 | 78 | 39 | 6.8 |  | 0.070652 | 0.070652 | 50%
QuietCool | CL-4700 | 4672 | 3586 | 591 | 491 | 5 | PSC | 0.1265 | 0.13692 | 76.76%
QuietCool | ES-4700 | 4427 | 2050 | 494 | 64 | 5 | ECM | 0.11159 | 0.03122 | 46.31%
QuietCool | CL-3100 | 3190 | 1906 | 320 | 231 | 5 | PSC | 0.10031 | 0.1212 | 59.75%
QuietCool | ES-3100 | 3103 | NA | 264 | NA | 5 | ECM | 0.085079
QuietCool | CL-6400 | 6306 | 3226 | 703 | 329 | 5 | PSC | 0.11148 | 0.10198 | 51.16%
QuietCool | ES-6400 | 6328 | 2860 | 527 | 179 | 5 | ECM | 0.083281 | 0.062587 | 45.2%
[7 empty] | Average | 0.10667 | 0.092859
The following values are used for the DEER 2017 modeling:
[8 empty] | 0.15 | PSC | from Building America Report
[8 empty] | 0.12386 | ECM | scaled based on QuiedCool ECM vs PSC
ECM/PSC
[7 empty] | QuietCool 6400 | 74.7%
[7 empty] | QuietCool 4700 | 88.21%
[7 empty] | QuietCool 3100 | 84.81%
[7 empty] | Average: | 82.58%
[7 empty] | Alternate source: | 83.5% | avg of 1/3 and 1/2 hp motors
Note on J52: Doug Maddox: Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Final Report Submitted to: U.S. Department of Energy Energy Efficiency and Renewable Energy Building Technologies Program Navigant Consulting, Inc. September 23, 2009

## CA 2022 T-24
File: TN243494_20220609T115442_Final 2022 Energy Code Single-Family Residential Compliance Manual

## E-5152 attachment
Whole-house fan measure updates
Effective Program Year: 2023. Whole-house fans became a Title-24 code requirement in 2014 for single-family homes in climate zones CZ08 through CZ14. Resolution E-4795 was the most recent update of the whole-house measure resulting in new whole-house fan UES values for DEER2017 and the inclusion of whole-house fans in new construction baseline models in climate zones where they are required by code. The whole house fan is utilized in single-family homes and the eQUEST model for this measure assumes that the whole-house fan is on when outdoor cooling is available, the cooling load can be met by the whole-house fan, and the outdoor temperature is at least five degrees below the cooling thermostat setpoint. The whole-house fan will cool the space down to 70ºF, if possible, regardless of the actual cooling thermostat setpoint.
At the time of the DEER2017 update, a number of changes were needed for the specification of whole-house fan parameters including flow rates, fan power, control sequences, and improvements to the definition and distribution of thermal mass in the residential prototypes. The new whole-house fan measures considered a range of capacities and fan efficiencies. There has been some concern about the accuracy of whole-house fan unit energy savings developed using DOE2-based modeling, particularly because the results are approximately one-third of the CEC-developed savings results used in the publicly-owned utilities’ (POU) 2017 Technical Reference Manual. The CEC-developed savings are modeled using the 2013 version of the California Simulation Engine (CSE) that is the basis for CBECC-Res software. The CEC whole-house fan input assumptions are as follows such that the whole-house fan will:
turn on if outdoor temperature is at least five degrees cooler than the indoor temperature
cool the house to a fixed 68°F lower-limit setpoint, consistent with natural ventilation assumptions when the thermostat is in cooling mode
turn off if the lower setpoint limit is reached, the 5°F minimum indoor-outdoor temperature difference no longer exists, or if the time is between 11 p.m. and 6 a.m. (with windows assumed closed, for security reasons)
The CEC-modeled home used their 2,700 ft2 residential prototype with a whole-house fan airflow rate of 2,000 cfm, so the modeled ventilation rate was 0.74 cfm/ft2. The study noted a 25-percent derating of whole-house fan nominal airflow but provided no explanation for doing so. The study mentioned fan electricity consumption for a ducted economizer-type nighttime ventilation system but did not indicate the fan electricity consumption assumed for whole-house fans.
The DEER assumptions to model whole-house fans are very similar to those used by the CEC, though the lower limit setpoint is 70°F (causing slightly lower cooling savings, but also lowering the heating penalty). The DEER cooling availability schedule varies by climate zone and follows the 2017 T-24 Residential Alternative Compliance Manual (ACM) manual, allowing ventilation cooling only during shoulder months. DEER assumptions do not include a derating of nominal airflow, however it does assume that the windows will only be open half the time when there is an opportunity to use the whole-house fan. This is the only factor used to account for windows open for cooling or airflow and windows closed at night for security reasons. A 2006 survey of ventilation behavior found that 82 percent of respondents thought it was important to open the windows to cool the house and 70 percent thought it was important to open windows to save energy. The study also reported 92 percent of respondents thought it important to close windows for safety/security. The 50-percent probability assumption should be checked by calibrating the simulation results to measured energy savings.
The DEER modeled savings were compared to measured savings from two evaluation studies of whole-house fans installed in California homes. The first study, a 2005 impact evaluation of Northern California Power Agency programs, found annual whole house fan measure savings from 18 homes were 203 kWh +/- 65 kWh. These homes were presumably located in NCPA member areas in climate zones 4, 5, 11, and 12. The analysis method used billing data to report normalized annual consumption (NAC) on a per-home basis and compared consumption pre- and post-retrofit for homes installing exclusively whole house fans. The average savings of the sample with low pre-retrofit NAC (<1,000 kWh/yr) removed is 265 kWh. The annual DEER savings (average of all four PSC motor measures) for climate zones 11 and 12 average 141 kWh with a standard deviation of the 16 models at 53 kWh. The modeled savings are approximately 70% of the measured savings of the overall sample or 53% of the higher NAC portion of the sample.
The second study, a 2003 impact evaluation of the Statewide Low-Income Energy Efficiency (LIEE) Program showed average annual whole house fan measure savings from 88 homes was 108 kWh. Eighty seven of these 88 homes were located in PG&E territory. Since the program installed multiple measures, the cooling end-use saving measures were disaggregated based on engineering models which assigned 20% of the cooling savings to whole house fans. PGE climate zones include primarily CZs 1, 2, 3, 4, 11, 12, 13, and 16. The DEER savings from those climate zones averaged across the old and existing eras are 53 kWh, about half the measured savings. Central valley savings (CZs 11-12-13) are much higher and more closely grouped at 153 Wh. Because this study uses engineering analysis to disaggregate the cooling load into the component measure savings, it is given less weight than the previous study.
Given these studies, it seems that whole house fan measure savings are underestimated by the DEER models, and the assumption with the highest uncertainty is that occupants will open windows half the time when outdoor cooling is available. This assumption will be adjusted, and DEER savings for whole house fans will be re-modeled.
For transparency, the whole-house fan measure input assumptions are documented in Table A-4‑7 and Table A-4‑8.
a Climate zone 5 has three additional enabled periods: 3-Sep. to 17-Sep., 30-Sep. to 2-Oct., and 5-Oct. to 12-Oct.
b Climate zone 15 has one additional enabled period: 16-Dec. to 25-Dec.
Night Ventilation Cooling Compliance Option, Codes and Standards Enhancement Initiative, September 2011.
2017 Savings Estimation POU Technical Reference Manual published by the California Municipal Utilities Association.
The probability fraction is set to 100% on peak kW days for accuracy of peak savings calculations.
Price, Phillip and Max Sherman. Ventilation Behavior and Household Characteristics in New California Houses, LBNL #59620, 2006.
Mowris, Robert. Measurement and Verification Load Impact Study for NCPA SB5X Miscellaneous Rebate Programs, 2005. (M&V_Load_Impact_Study_for_NCPA_SB5X_Miscellaneous.pdf at http://calmac.org/results.asp?flag=&searchtext=NCPA+SB5X+Miscellaneous&Submit=Search)
KEMA-Xenergy. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program, 2003.
DOE2 Key words are documented in Volume 2 Dictionary file; specifically, VENT-METHOD is described on pg. 442. https://doe2.com/Download/DOE-23/DOE23Vol2-Dictionary_50d.pdf

## DEER2020
DEER2020
| BldgVint | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
WHFan-0.7-ECM | Ex | 36.2 | -19.1 | 65 | 10.7 | 110 | 185 | 337 | 252 | 241 | 228 | 161 | 204 | 100 | 128 | -14.3
WHFan-1.5-ECM | Ex | 25.5 | -35.3 | 43.3 | 8.31 | 65.5 | 176 | 325 | 228 | 245 | 263 | 147 | 239 | 126 | 124 | -91.2
WHFan-2.0-ECM | Ex | 19.4 | -39 | 31.9 | 6.87 | 44.1 | 179 | 320 | 199 | 235 | 250 | 127 | 218 | 123 | 95.5 | -122
WHFan-3.0-ECM | Ex | 12.8 | -41.5 | 15.1 | 6.96 | 33.3 | 182 | 305 | 172 | 212 | 222 | 96.9 | 188 | 118 | 49.9 | -154

## Min Indoor Setpoint
Whole House Fan Energy Savings - One Story | Energy Plus Savings | [5 empty] | DEER2020 - uses Min_Indoor_Temp of 68
(Expect higher savings for two-story buildings) | CZ2010 weather, 5 deg F delta T |  | CZ2022 weather, 2 deg F delta T |  |  |  | combination of one and two story | uses Min_Indoor_Temp of 70
Orange indicates whole house fans are required in CA T-24 2019 | 68 | 70 | 68 | 72 | 74 | 76 | DEER2020 | 2017 CMUA TRM | Notes
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -36.62 | 4.04 | -2383.81 | -2304.88 | -0.24 | -0.25 | N/A | N/A
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -48.54 | -2.05 | -2405.95 | -2307.59 | -0.24 | -0.27
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -52.82 | -2.82 | -2414.66 | -2308.94 | -0.29 | -0.28
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -62.41 | -7.87 | -2426.56 | -2312.77 | -0.18 | -0.32
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -158.79 | -108.92 | -176.97 | -56.02 | -0.76 | 47.77 | 36.2 |  | Slightly higher than DEER, still lower than POU.
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -194.83 | -135.5 | -332.39 | -139.74 | -53.36 | 20.84 | 25.5 | 55
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -211.06 | -148.22 | -394.56 | -173.54 | -75.8 | 7.91 | 19.4
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -242.71 | -171.68 | -481.41 | -220.16 | -108.18 | -10.11 | 12.8
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -12.18 | 62.94 |  | 254.71 | 326.3 | -0.02 | -19.1 |  | higher by a lot! Low cooling setpoint
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -45.06 | 40.9 |  | 224.51 | 328.21 | -0.03 | -35.3 | -142
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -66.45 | 27.07 |  | 206.49 | 322.79 | 0 | -39
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -104.88 | 4.78 |  | 180.65 | 310.01 | 0.01 | -41.5
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -105.81 | -57.71 |  | 5.26 | 59.87 | 108.91 | 65 |  | higher than DEER, still lower than POU
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -134.08 | -79.52 |  | -83.17 | 9.08 | 86.52 | 43.3 | 161
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -151.42 | -92.36 |  | -115.48 | -13.47 | 74 | 31.9
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -188.34 | -115.76 |  | -160.52 | -43.41 | 55.95 | 15.1
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -120.98 | -27.18 |  | 224.94 | 316.79 | -7.93 | 10.7 |  | higher by a lot! Low cooling setpoint
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -169.24 | -60.48 |  | 186.12 | 317.54 | -13.98 | 8.31 | -63
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -187.87 | -80.71 |  | 161.03 | 307.88 | -15.89 | 6.87
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -246.78 | -108.67 |  | 125.35 | 289.55 | -21.53 | 6.96
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 84.03 | 124.88 | 298.21 | 447.3 | 532.01 | 0.07 | 110 |  | higher by a lot! Low cooling setpoint
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 60.23 | 107.02 | 138.95 | 406.67 | 548.69 | 0 | 65.5 | N/A
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 44.52 | 93.64 | 71.9 | 376.81 | 534.43 | 0.06 | 44.1
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 17.75 | 74.51 | -15.72 | 324.34 | 503.42 | -0.05 | 33.3
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 78.44 | 106.1 | 85.35 | 229.22 | 310.58 | 77.46 | 185 |  | higher by a lot!
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 55.11 | 87.09 | -74.85 | 166.55 | 296.74 | 76.7 | 176 | N/A
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 40.8 | 74.09 | -129.65 | 138.75 | 281.37 | 74.66 | 179
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 14.07 | 53.12 | -214.31 | 86.52 | 246.49 | 69.01 | 182
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 58.82 | 84.72 |  | 212.69 | 267.93 | 324.84 | 337 |  | about the same
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 35.86 | 66.49 |  | 142.79 | 236.3 | 329 | 325 | 388
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 21.14 | 54.39 |  | 110.12 | 217.38 | 320.28 | 320
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -1.21 | 35.22 |  | 60.97 | 180.76 | 299.78 | 305
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -21.55 | 44.39 |  | 278.16 | 344.58 | 125.13 | 252 |  | higher than DEER, still lower than POU
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -53.72 | 20.08 |  | 232.26 | 345.56 | 130.61 | 228 | 451
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -73.04 | 5.26 |  | 194.34 | 324.8 | 126.91 | 199
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -111.79 | -15.03 |  | 142.87 | 291.34 | 118.08 | 172
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -5242.76 | -166.1 |  | 49.86 | 104.63 | 150 | 241 |  | lower by quite a bit, high cooling setpoint
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -8580.54 | -207.71 |  | -37.66 | 45.88 | 115.65 | 245 | 522
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -10998.55 | -228.05 |  | -81.71 | 20.08 | 100.88 | 235
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -16144.72 | -542.53 |  | -139.28 | -18.06 | 77.06 | 212
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -154.9 | 12.71 |  | 54.49 | 73.97 | 88.88 | 228 |  | lower by quite a bit
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -175.92 | -0.4 |  | 27.54 | 59.13 | 84.4 | 263 | 496
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -193.74 | -10.37 |  | 14.97 | 51.61 | 80.29 | 250
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -228.12 | -26.31 |  | -3.15 | 38.65 | 72.81 | 222
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 12.88 | 39.01 |  | 57.98 | 85.07 | 108.23 | 161 |  | lower than DEER. Lower than POU by a lot!, high cooling setpoint
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -4.93 | 25.67 |  | 13.47 | 56.85 | 95.48 | 147 | 567
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -16.59 | 16.82 |  | -5.77 | 44.4 | 88.41 | 127
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -32.77 | 1.97 |  | -30.86 | 26.16 | 74.49 | 96.9
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 51.09 | 69.31 |  | 103.9 | 126.89 | 145.62 | 204 |  | lower than DEER
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 40.16 | 61.75 |  | 70.63 | 107.91 | 139.62 | 239 | N/A
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 33.19 | 55.6 |  | 55.57 | 98.64 | 134.4 | 218 |  |  | ACM Cooling Setpoint kWh |  | With Natural Ventilation
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 21.86 | 46.64 |  | 34 | 83.55 | 124.55 | 188 |  |  | Total Site Energy [kWh] |  | Total Site Energy [kWh]
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql | [9 empty] | 32916.91 |  | 32916.91
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -3465.21 | -3449.33 |  | -142.33 | -54.58 | 8.79 | 100 |  | lower than DEER. Lower than POU by a lot! High cooling setpoint | 32858.6 | 58.31 | 33348.75 | -431.84
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -6029.57 | -5992.85 |  | -316.93 | -113.41 | -25.85 | 126 | 353
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -7802.21 | -7756.18 |  | -405.4 | -138.05 | -41.58 | 123
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -11687.39 | -11620.56 |  | -539.27 | -180.31 | -68.02 | 118
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -327.31 | 35.62 |  | 108.1 | 108.32 | 108.7 | 128 |  | lower than DEER. Lower than POU by a lot!
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -481.03 | 23.6 |  | 91.55 | 99.7 | 107.06 | 124 | 174
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -561.03 | 10.12 |  | 82.75 | 94.06 | 103.79 | 95.5
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -1861.62 | -37.01 |  | 66.65 | 83.8 | 98.49 | 49.9
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 14.05 | 33.52 |  | 46.91 | 59.4 | 65.38 | -14.3 |  | higher than DEER, still lower than POU
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 2.29 | 25.35 |  | 24.05 | 49.16 | 63.99 | -91.2 | 171
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -3.87 | 22.1 |  | 14.1 | 42.17 | 61.55 | -122
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -10.65 | 13.14 |  | -0.18 | 33.09 | 55.67 | -154
Differences current E+ model compared to DEER DOE2
- We are using CZ2022 weather
- We have changed the heating and cooling setpoints
- We allow heating and cooling on the same day, consistent with 2019 T-24 ACM
- We are using delta T of 2 degrees instead of 5 degrees
- DEER2020 used a factor of 0.5 - they assumed occupants would only use the fan half the time when cooling is available.
- Ask Mahsa to run E+ using CZ2010 weather and 68F Indoor Minimum and 70F and also using 5 deg delta T
- Maybe also use consistent heating and cooling setpoints. 68 and 78 ?
- check if we can use natural ventilation as a baseline.
- Have natual ventilation turned on in all cases
- use 76 indoor temp whf stpt
- for WHF measure, use ACM thermostat baseline and measure case
- When whf is baseline in NC use prototype thermostats and 5 deg Delta T

## New output
Whole House Fan Energy Savings - One Story | Energy Plus Savings | [6 empty] | DEER2020 - uses Min_Indoor_Temp of 68 |  |  | Note: whole house fan is turned off between 11pm and 6am
(Expect higher savings for two-story buildings) | CZ2010 weather, 5 deg F delta T |  | CZ2022 weather, 2 deg F delta T |  |  |  |  | combination of one and two story | uses Min_Indoor_Temp of 70
Orange indicates whole house fans are required in CA T-24 2019 | 68 | 70 | 1story | 2story | 74 | 76 |  | DEER2020 | 2017 CMUA TRM | Notes
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql |  |  | ACM thermostat
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -36.62 | 4.04 | 0 | 0 | -0.24 | -0.25 |  | N/A | N/A | OK
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -48.54 | -2.05 | 0 | 0 | -0.24 | -0.27
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -52.82 | -2.82 | 0 | 0 | -0.29 | -0.28
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -62.41 | -7.87 | 0 | 0 | -0.18 | -0.32
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -158.79 | -108.92 | 32.3 | 128.73 | -0.76 | 47.77 | 80.515 | 36.2 |  | OK
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -194.83 | -135.5 | 26.65 | 34.82 | -53.36 | 20.84 | 30.735 | 25.5 | 55
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -211.06 | -148.22 | 20.95 | -13.98 | -75.8 | 7.91 | 3.485 | 19.4
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -242.71 | -171.68 | 10.88 | -83.58 | -108.18 | -10.11 | -36.35 | 12.8
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -12.18 | 62.94 | 20.61 | -125.98 | 326.3 | -0.02 | -52.685 | -19.1 |  | OK
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -45.06 | 40.9 | 17.59 | -176.15 | 328.21 | -0.03 | -79.28 | -35.3 | -142
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -66.45 | 27.07 | 14.93 | -254.98 | 322.79 | 0 | -120.025 | -39
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -104.88 | 4.78 | 8.05 | -342.48 | 310.01 | 0.01 | -167.215 | -41.5
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql | [11 empty] | with precooling to 70
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -105.81 | -57.71 | 35.27 | 54.51 | 59.87 | 108.91 | 44.89 | 65 |  | slightly lower than previous DEER |  | -15.35
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -134.08 | -79.52 | 22.42 | -71.7 | 9.08 | 86.52 | -24.64 | 43.3 | 161 |  |  | -119.55
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -151.42 | -92.36 | 13.75 | -138.3 | -13.47 | 74 | -62.275 | 31.9 |  |  |  | -164
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -188.34 | -115.76 | -1.71 | -244.03 | -43.41 | 55.95 | -122.87 | 15.1 |  |  |  | -238.09
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -120.98 | -27.18 | 35.5 | 117.06 | 316.79 | -7.93 | 76.28 | 10.7 |  | higher |  | 8.67
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -169.24 | -60.48 | 24.09 | -62.14 | 317.54 | -13.98 | -19.025 | 8.31 | -63 |  |  | -179.79
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -187.87 | -80.71 | 17.26 | -167.09 | 307.88 | -15.89 | -74.915 | 6.87 |  |  |  | -274.9
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -246.78 | -108.67 | 6.85 | -228.53 | 289.55 | -21.53 | -110.84 | 6.96 |  |  |  | -331.17
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 84.03 | 124.88 | -10.59 | -156.6 | 532.01 | 0.07 | -83.595 | 110 |  | lower than previous DEER |  | -258.77
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 60.23 | 107.02 | -40.06 | -369.73 | 548.69 | 0 | -204.895 | 65.5 | N/A |  |  | -502.32
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 44.52 | 93.64 | -50.84 | -475.45 | 534.43 | 0.06 | -263.145 | 44.1 |  |  |  | -622.46
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 17.75 | 74.51 | -72.3 | -585.77 | 503.42 | -0.05 | -329.035 | 33.3 |  |  |  | -743.37
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 78.44 | 106.1 | 65.07 | 180.93 | 310.58 | 77.46 | 123 | 185 |  | lower than previous DEER |  | -33.69
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 55.11 | 87.09 | 43.52 | -28.55 | 296.74 | 76.7 | 7.485 | 176 | N/A |  |  | -233.48
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 40.8 | 74.09 | 28.53 | -142.65 | 281.37 | 74.66 | -57.06 | 179 |  |  |  | -340.23
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 14.07 | 53.12 | 4.46 | -275.7 | 246.49 | 69.01 | -135.62 | 182 |  |  |  | -463.93
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 58.82 | 84.72 | 112.2 | 304.33 | 267.93 | 324.84 | 208.265 | 337 |  | from midnight to noon the vent_min is 70F
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 35.86 | 66.49 | 92.03 | 60.51 | 236.3 | 329 | 76.27 | 325 | 388 | lower than previous DEER
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 21.14 | 54.39 | 78.69 | -62.87 | 217.38 | 320.28 | 7.91 | 320
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -1.21 | 35.22 | 51.98 | -241.03 | 180.76 | 299.78 | -94.525 | 305
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -21.55 | 44.39 | 253.85 | 691.95 | 344.58 | 125.13 | 472.9 | 252 |  | from midnight to noon the vent_min is 70F
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -53.72 | 20.08 | 241.98 | 486.3 | 345.56 | 130.61 | 364.14 | 228 | 451 | higher than previous DEER
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -73.04 | 5.26 | 223.37 | 351.12 | 324.8 | 126.91 | 287.245 | 199
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -111.79 | -15.03 | 193.41 | 141.42 | 291.34 | 118.08 | 167.415 | 172
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -5242.76 | -166.1 | 89.54 | 366.37 | 104.63 | 150 | 227.955 | 241 |  | similar to previous DEER
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -8580.54 | -207.71 | 80.32 | 267.46 | 45.88 | 115.65 | 173.89 | 245 | 522
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -10998.55 | -228.05 | 73.64 | 226.46 | 20.08 | 100.88 | 150.05 | 235
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -16144.72 | -542.53 | 59.28 | 153.76 | -18.06 | 77.06 | 106.52 | 212
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -154.9 | 12.71 | 33.68 | 116.04 | 73.97 | 88.88 | 74.86 | 228 |  | lower by quite a bit
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -175.92 | -0.4 | 29.56 | 63.82 | 59.13 | 84.4 | 46.69 | 263 | 496
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -193.74 | -10.37 | 26.72 | 40.83 | 51.61 | 80.29 | 33.775 | 250
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -228.12 | -26.31 | 19.1 | 4.42 | 38.65 | 72.81 | 11.76 | 222
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 12.88 | 39.01 | 29.55 | 118.66 | 85.07 | 108.23 | 74.105 | 161 |  | lower than DEER. Lower than POU by a lot!, high cooling setpoint
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -4.93 | 25.67 | 22.62 | 61.36 | 56.85 | 95.48 | 41.99 | 147 | 567
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -16.59 | 16.82 | 17.33 | 35.84 | 44.4 | 88.41 | 26.585 | 127
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -32.77 | 1.97 | 8.53 | -3.81 | 26.16 | 74.49 | 2.36 | 96.9
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 51.09 | 69.31 | 70.24 | 316.7 | 126.89 | 145.62 | 193.47 | 204 |  | similar to previous DEER
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 40.16 | 61.75 | 63.93 | 221.62 | 107.91 | 139.62 | 142.775 | 239 | N/A
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 33.19 | 55.6 | 57.28 | 172.51 | 98.64 | 134.4 | 114.895 | 218 |  |  |  |  | ACM Cooling Setpoint kWh |  | With Natural Ventilation
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 21.86 | 46.64 | 48.55 | 101.89 | 83.55 | 124.55 | 75.22 | 188 |  |  |  |  | Total Site Energy [kWh] |  | Total Site Energy [kWh]
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql | [12 empty] | 32916.91 |  | 32916.91
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -3465.21 | -3449.33 | 19.62 | 28.84 | -54.58 | 8.79 | 24.23 | 100 |  | lower than DEER. Lower than POU by a lot! High cooling setpoint |  |  | 32858.6 | 58.31 | 33348.75 | -431.84
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -6029.57 | -5992.85 | 11.79 | -49.06 | -113.41 | -25.85 | -18.635 | 126 | 353
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -7802.21 | -7756.18 | 7.02 | -84.38 | -138.05 | -41.58 | -38.68 | 123
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -11687.39 | -11620.56 | -2.46 | -137.64 | -180.31 | -68.02 | -70.05 | 118
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -327.31 | 35.62 | 57.55 | 181.02 | 108.32 | 108.7 | 119.285 | 128 |  | similar to previous DEER
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -481.03 | 23.6 | 50.46 | 122.17 | 99.7 | 107.06 | 86.315 | 124 | 174
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -561.03 | 10.12 | 46.35 | 93.22 | 94.06 | 103.79 | 69.785 | 95.5
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -1861.62 | -37.01 | 35.5 | 47.72 | 83.8 | 98.49 | 41.61 | 49.9
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 14.05 | 33.52 | 27.71 | 82.66 | 59.4 | 65.38 | 55.185 | -14.3 |  | higher than DEER, still lower than POU
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 2.29 | 25.35 | 20.05 | 58.13 | 49.16 | 63.99 | 39.09 | -91.2 | 171 | from midnight to noon the vent_min is 70F
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -3.87 | 22.1 | 18.26 | 40.06 | 42.17 | 61.55 | 29.16 | -122
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -10.65 | 13.14 | 9.62 | 19.72 | 33.09 | 55.67 | 14.67 | -154
Differences current E+ model compared to DEER DOE2
- We are using CZ2022 weather
- We have changed the heating and cooling setpoints
- We allow heating and cooling on the same day, consistent with 2019 T-24 ACM
- We are using delta T of 2 degrees instead of 5 degrees
- DEER2020 used a factor of 0.5 - they assumed occupants would only use the fan half the time when cooling is available.
- Have natual ventilation turned on in all cases
- for WHF measure, use ACM thermostat baseline and measure case
- When whf is baseline in NC use prototype thermostats and 5 deg Delta T
- use 76 indoor temp whf stpt in most climate zones. In a few climate (8, 9, 16) zones the WHF is allowed to cool to 70 deg in the morning between midnight and noon. But stays at 76 from after noon to midnight

## lower fan efficiency
We discovered that the HVAC fan efficiency was way too high in our models. So in V5 of the prototype we lower the fan efficiency to 0.25 total fan efficiency.
I also lowered the whole house fan efficiency because of lowering the external static pressure from 200Pa to 75Pa, much more reasonable for a whole house fan with no ductwork.
Also:
| Results for CZ12 | [7 empty] | allow whole house fan to run all night
whf setpoint is 72F
increased whf delta t to 5F
| Baseline |  |  |  | Measure Case 1.5 cfm/sf |  |  |  | Measure Case 1.5 cfm/sf
End Uses By Subcategory
|  | Subcategory | Electricity [kWh] | Natural Gas [kWh] |  | Subcategory | Electricity [kWh] | Natural Gas [kWh] |  | Subcategory | Electricity [kWh] | Natural Gas [kWh]
| Heating | General | 0 | 6786.99 | Heating | General | 0 | 6790.01 | Heating | General | 0 | 6803.86
| Cooling | General | 1731.43 | 0 | Cooling | General | 1652.89 | 0 | Cooling | General | 1564.77 | 0
| Interior Lighting | Interior Lighting | 1451.21 | 0 | Interior Lighting | Interior Lighting | 1451.21 | 0 | Interior Lighting | Interior Lighting | 1451.21 | 0
|  | Unconditioned | 106.28 | 0 |  | Unconditioned | 106.28 | 0 |  | Unconditioned | 106.28 | 0
| Exterior Lighting | Extreior Lights | 457.71 | 0 | Exterior Lighting | Extreior Lights | 457.71 | 0 | Exterior Lighting | Extreior Lights | 457.71 | 0
| Interior Equipment | dishwasher | 411.72 | 0 | Interior Equipment | dishwasher | 411.72 | 0 | Interior Equipment | dishwasher | 411.72 | 0
|  | refrigerator | 1337.35 | 0 |  | refrigerator | 1337.35 | 0 |  | refrigerator | 1337.35 | 0
|  | clothwasher | 210.18 | 0 |  | clothwasher | 210.18 | 0 |  | clothwasher | 210.18 | 0
|  | gas_dryer | 151.8 | 1114.61 |  | gas_dryer | 151.8 | 1114.61 |  | gas_dryer | 151.8 | 1114.61
|  | Misc | 6154.35 | 0 |  | Misc | 6154.35 | 0 |  | Misc | 6154.35 | 0
|  | gas_range | 0 | 949.24 |  | gas_range | 0 | 949.24 |  | gas_range | 0 | 949.24
| Exterior Equipment | General | 0 | 0 | Exterior Equipment | General | 0 | 0 | Exterior Equipment | General | 0 | 0
| Fans | Ventilation (simple) | 0 | 0 | Fans | Ventilation (simple) | 53.53 | 0 | Fans | Ventilation (simple) | 223.15 | 0
|  | General | 257.51 | 0 |  | General | 250.32 | 0 |  | General | 242.83 | 0
| Pumps | General | 0 | 0 | Pumps | General | 0 | 0 | Pumps | General | 0 | 0
| Heat Rejection | General | 0 | 0 | Heat Rejection | General | 0 | 0 | Heat Rejection | General | 0 | 0
| Humidification | General | 0 | 0 | Humidification | General | 0 | 0 | Humidification | General | 0 | 0
| Heat Recovery | General | 0 | 0 | Heat Recovery | General | 0 | 0 | Heat Recovery | General | 0 | 0
| Water Systems | Domestic Hot Water | 0 | 0 | Water Systems | Domestic Hot Water | 0 | 0 | Water Systems | Domestic Hot Water | 0 | 0
|  | General | 0 | 0 |  | General | 0 | 0 |  | General | 0 | 0
|  | Water Heater | 0 | 10623.13 |  | Water Heater | 0 | 10624.91 |  | Water Heater | 0 | 10633.05
| Refrigeration | General | 0 | 0 | Refrigeration | General | 0 | 0 | Refrigeration | General | 0 | 0
| Generators | General | 0 | 0 | Generators | General | 0 | 0 | Generators | General | 0 | 0
|  |  | 12269.54 | 19473.97 |  |  | 12237.34 | 19478.77 |  |  | 12311.35 | 19500.76
[7 empty] | 32.2 | -4.8 |  |  | -41.81 | -26.79
Same as above byt using Higher Thermal Mass: 400 sq m
| Results for CZ12 | [7 empty] | allow whole house fan to run all night
whf setpoint is 72F
increased whf delta t to 5F
| Baseline |  |  |  | Measure Case 1.5 cfm/sf |  |  |  | Measure Case 1.5 cfm/sf
|  | Subcategory | Electricity [kWh] | Natural Gas [kWh] |  | Subcategory | Electricity [kWh] | Natural Gas [kWh] |  | Subcategory | Electricity [kWh] | Natural Gas [kWh]
| Heating | General | 0 | 7653.47 | Heating | General |  |  | Heating | General | 0 | 7708.9
| Cooling | General | 1927.11 | 0 | Cooling | General |  |  | Cooling | General | 948.41 | 0
| Interior Lighting | Interior Lighting | 1451.21 | 0 | Interior Lighting | Interior Lighting |  |  | Interior Lighting | Interior Lighting | 1451.21 | 0
|  | Unconditioned | 106.28 | 0 |  | Unconditioned |  |  |  | Unconditioned | 106.28 | 0
| Exterior Lighting | Extreior Lights | 457.71 | 0 | Exterior Lighting | Extreior Lights |  |  | Exterior Lighting | Extreior Lights | 457.71 | 0
| Interior Equipment | dishwasher | 411.72 | 0 | Interior Equipment | dishwasher |  |  | Interior Equipment | dishwasher | 411.72 | 0
|  | refrigerator | 1337.35 | 0 |  | refrigerator |  |  |  | refrigerator | 1337.35 | 0
|  | clothwasher | 210.18 | 0 |  | clothwasher |  |  |  | clothwasher | 210.18 | 0
|  | gas_dryer | 151.8 | 1114.61 |  | gas_dryer |  |  |  | gas_dryer | 151.8 | 1114.61
|  | Misc | 6154.35 | 0 |  | Misc |  |  |  | Misc | 6154.35 | 0
|  | gas_range | 0 | 949.24 |  | gas_range |  |  |  | gas_range | 0 | 949.24
| Exterior Equipment | General | 0 | 0 | Exterior Equipment | General |  |  | Exterior Equipment | General | 0 | 0
| Fans | Ventilation (simple) | 0 | 0 | Fans | Ventilation (simple) |  |  | Fans | Ventilation (simple) | 378.41 | 0
|  | General | 331.61 | 0 |  | General |  |  |  | General | 240.63 | 0
| Pumps | General | 0 | 0 | Pumps | General |  |  | Pumps | General | 0 | 0
| Heat Rejection | General | 0 | 0 | Heat Rejection | General |  |  | Heat Rejection | General | 0 | 0
| Humidification | General | 0 | 0 | Humidification | General |  |  | Humidification | General | 0 | 0
| Heat Recovery | General | 0 | 0 | Heat Recovery | General |  |  | Heat Recovery | General | 0 | 0
| Water Systems | Domestic Hot Water | 0 | 0 | Water Systems | Domestic Hot Water |  |  | Water Systems | Domestic Hot Water | 0 | 0
|  | General | 0 | 0 |  | General |  |  |  | General | 0 | 0
|  | Water Heater | 0 | 10615.83 |  | Water Heater |  |  |  | Water Heater | 0 | 10633.65
| Refrigeration | General | 0 | 0 | Refrigeration | General |  |  | Refrigeration | General | 0 | 0
| Generators | General | 0 | 0 | Generators | General |  |  | Generators | General | 0 | 0
|  |  | 12539.32 | 20333.15 |  |  | 0 | 0 |  |  | 11848.05 | 20406.4
[7 empty] | 12539.32 | 20333.15 |  |  | 691.27 | -73.25
Same as above byt using Higher Thermal Mass: 300 sq m
| Results for CZ12 | [7 empty] | allow whole house fan to run all night
whf setpoint is 72F
increased whf delta t to 5F
| Baseline |  |  |  | Measure Case 1.5 cfm/sf |  |  |  | Measure Case 1.5 cfm/sf
|  | Subcategory | Electricity [kWh] | Natural Gas [kWh] |  | Subcategory | Electricity [kWh] | Natural Gas [kWh] |  | Subcategory | Electricity [kWh] | Natural Gas [kWh]
| Heating | General | 0 | 7494.12 | Heating | General |  |  | Heating | General | 0 | 7546.33
| Cooling | General | 1891.25 | 0 | Cooling | General |  |  | Cooling | General | 1107.5 | 0
| Interior Lighting | Interior Lighting | 1451.21 | 0 | Interior Lighting | Interior Lighting |  |  | Interior Lighting | Interior Lighting | 1451.21 | 0
|  | Unconditioned | 106.28 | 0 |  | Unconditioned |  |  |  | Unconditioned | 106.28 | 0
| Exterior Lighting | Extreior Lights | 457.71 | 0 | Exterior Lighting | Extreior Lights |  |  | Exterior Lighting | Extreior Lights | 457.71 | 0
| Interior Equipment | dishwasher | 411.72 | 0 | Interior Equipment | dishwasher |  |  | Interior Equipment | dishwasher | 411.72 | 0
|  | refrigerator | 1337.35 | 0 |  | refrigerator |  |  |  | refrigerator | 1337.35 | 0
|  | clothwasher | 210.18 | 0 |  | clothwasher |  |  |  | clothwasher | 210.18 | 0
|  | gas_dryer | 151.8 | 1114.61 |  | gas_dryer |  |  |  | gas_dryer | 151.8 | 1114.61
|  | Misc | 6154.35 | 0 |  | Misc |  |  |  | Misc | 6154.35 | 0
|  | gas_range | 0 | 949.24 |  | gas_range |  |  |  | gas_range | 0 | 949.24
| Exterior Equipment | General | 0 | 0 | Exterior Equipment | General |  |  | Exterior Equipment | General | 0 | 0
| Fans | Ventilation (simple) | 0 | 0 | Fans | Ventilation (simple) |  |  | Fans | Ventilation (simple) | 349.98 | 0
|  | General | 319.93 | 0 |  | General |  |  |  | General | 247.45 | 0
| Pumps | General | 0 | 0 | Pumps | General |  |  | Pumps | General | 0 | 0
| Heat Rejection | General | 0 | 0 | Heat Rejection | General |  |  | Heat Rejection | General | 0 | 0
| Humidification | General | 0 | 0 | Humidification | General |  |  | Humidification | General | 0 | 0
| Heat Recovery | General | 0 | 0 | Heat Recovery | General |  |  | Heat Recovery | General | 0 | 0
| Water Systems | Domestic Hot Water | 0 | 0 | Water Systems | Domestic Hot Water |  |  | Water Systems | Domestic Hot Water | 0 | 0
|  | General | 0 | 0 |  | General |  |  |  | General | 0 | 0
|  | Water Heater | 0 | 10617.14 |  | Water Heater |  |  |  | Water Heater | 0 | 10633.32
| Refrigeration | General | 0 | 0 | Refrigeration | General |  |  | Refrigeration | General | 0 | 0
| Generators | General | 0 | 0 | Generators | General |  |  | Generators | General | 0 | 0
| Total |  | 12491.78 | 20175.11 |  |  | 0 | 0 |  |  | 11985.53 | 20243.5
[7 empty] | 12491.78 | 20175.11 |  |  | 506.25 | -68.39

## WHF always enabled
Whole House Fan Energy Savings - One Story | Energy Plus Savings | [6 empty] | DEER2020 - uses Min_Indoor_Temp of 68 |  |  | Calibrated prototype thermostat setpoints
(Expect higher savings for two-story buildings) | CZ2010 weather, 5 deg F delta T |  | CZ2022 weather, 2 deg F delta T |  |  |  |  | combination of one and two story | uses Min_Indoor_Temp of 70 |  | whf setpoint 76
Orange indicates whole house fans are required in CA T-24 2019 | 68 | 70 | 1story | 2story | 74 | 76 |  | DEER2020 | 2017 CMUA TRM | Notes
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql |  |  | ACM thermostat
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -36.62 | 4.04 | 0 | 0 | -0.24 | -0.25 |  | N/A | N/A | OK
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -48.54 | -2.05 | 0 | 0 | -0.24 | -0.27
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -52.82 | -2.82 | 0 | 0 | -0.29 | -0.28
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -62.41 | -7.87 | 0 | 0 | -0.18 | -0.32
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -158.79 | -108.92 | 32.3 | 128.73 | -0.76 | 47.77 | 80.515 | 36.2 |  | OK
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -194.83 | -135.5 | 26.65 | 34.82 | -53.36 | 20.84 | 30.735 | 25.5 | 55
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -211.06 | -148.22 | 20.95 | -13.98 | -75.8 | 7.91 | 3.485 | 19.4
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -242.71 | -171.68 | 10.88 | -83.58 | -108.18 | -10.11 | -36.35 | 12.8
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -12.18 | 62.94 | 20.61 | -125.98 | 326.3 | -0.02 | -52.685 | -19.1 |  | OK
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -45.06 | 40.9 | 17.59 | -176.15 | 328.21 | -0.03 | -79.28 | -35.3 | -142
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -66.45 | 27.07 | 14.93 | -254.98 | 322.79 | 0 | -120.025 | -39
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -104.88 | 4.78 | 8.05 | -342.48 | 310.01 | 0.01 | -167.215 | -41.5
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql | [11 empty] | with precooling to 70
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -105.81 | -57.71 | 35.27 | 54.51 | 59.87 | 108.91 | 44.89 | 65 |  | slightly lower than previous DEER |  | -15.35
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -134.08 | -79.52 | 22.42 | -71.7 | 9.08 | 86.52 | -24.64 | 43.3 | 161 |  |  | -119.55
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -151.42 | -92.36 | 13.75 | -138.3 | -13.47 | 74 | -62.275 | 31.9 |  |  |  | -164
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -188.34 | -115.76 | -1.71 | -244.03 | -43.41 | 55.95 | -122.87 | 15.1 |  |  |  | -238.09
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -120.98 | -27.18 | 35.5 | 117.06 | 316.79 | -7.93 | 76.28 | 10.7 |  | higher |  | 8.67
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -169.24 | -60.48 | 24.09 | -62.14 | 317.54 | -13.98 | -19.025 | 8.31 | -63 |  |  | -179.79
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -187.87 | -80.71 | 17.26 | -167.09 | 307.88 | -15.89 | -74.915 | 6.87 |  |  |  | -274.9
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -246.78 | -108.67 | 6.85 | -228.53 | 289.55 | -21.53 | -110.84 | 6.96 |  |  |  | -331.17
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 84.03 | 124.88 | -10.59 | -156.6 | 532.01 | 0.07 | -83.595 | 110 |  | lower than previous DEER |  | -258.77
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 60.23 | 107.02 | -40.06 | -369.73 | 548.69 | 0 | -204.895 | 65.5 | N/A |  |  | -502.32
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 44.52 | 93.64 | -50.84 | -475.45 | 534.43 | 0.06 | -263.145 | 44.1 |  |  |  | -622.46
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 17.75 | 74.51 | -72.3 | -585.77 | 503.42 | -0.05 | -329.035 | 33.3 |  |  |  | -743.37
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 78.44 | 106.1 | 65.07 | 180.93 | 310.58 | 77.46 | 123 | 185 |  | lower than previous DEER |  | -33.69
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 55.11 | 87.09 | 43.52 | -28.55 | 296.74 | 76.7 | 7.485 | 176 | N/A |  |  | -233.48
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 40.8 | 74.09 | 28.53 | -142.65 | 281.37 | 74.66 | -57.06 | 179 |  |  |  | -340.23
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 14.07 | 53.12 | 4.46 | -275.7 | 246.49 | 69.01 | -135.62 | 182 |  |  |  | -463.93
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 58.82 | 84.72 | 112.2 | 304.33 | 267.93 | 324.84 | 208.265 | 337 |  | from midnight to noon the vent_min is 70F
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 35.86 | 66.49 | 92.03 | 60.51 | 236.3 | 329 | 76.27 | 325 | 388 | lower than previous DEER
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 21.14 | 54.39 | 78.69 | -62.87 | 217.38 | 320.28 | 7.91 | 320
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -1.21 | 35.22 | 51.98 | -241.03 | 180.76 | 299.78 | -94.525 | 305
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -21.55 | 44.39 | 253.85 | 691.95 | 344.58 | 125.13 | 472.9 | 252 |  | from midnight to noon the vent_min is 70F
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -53.72 | 20.08 | 241.98 | 486.3 | 345.56 | 130.61 | 364.14 | 228 | 451 | higher than previous DEER
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -73.04 | 5.26 | 223.37 | 351.12 | 324.8 | 126.91 | 287.245 | 199
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -111.79 | -15.03 | 193.41 | 141.42 | 291.34 | 118.08 | 167.415 | 172
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -5242.76 | -166.1 | 89.54 | 366.37 | 104.63 | 150 | 227.955 | 241 |  | similar to previous DEER
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -8580.54 | -207.71 | 80.32 | 267.46 | 45.88 | 115.65 | 173.89 | 245 | 522
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -10998.55 | -228.05 | 73.64 | 226.46 | 20.08 | 100.88 | 150.05 | 235
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -16144.72 | -542.53 | 59.28 | 153.76 | -18.06 | 77.06 | 106.52 | 212
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -154.9 | 12.71 | 33.68 | 116.04 | 73.97 | 88.88 | 74.86 | 228 |  | lower by quite a bit
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -175.92 | -0.4 | 29.56 | 63.82 | 59.13 | 84.4 | 46.69 | 263 | 496
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -193.74 | -10.37 | 26.72 | 40.83 | 51.61 | 80.29 | 33.775 | 250
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -228.12 | -26.31 | 19.1 | 4.42 | 38.65 | 72.81 | 11.76 | 222
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 12.88 | 39.01 | 29.55 | 118.66 | 85.07 | 108.23 | 74.105 | 161 |  | lower than DEER. Lower than POU by a lot!, high cooling setpoint
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -4.93 | 25.67 | 22.62 | 61.36 | 56.85 | 95.48 | 41.99 | 147 | 567
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -16.59 | 16.82 | 17.33 | 35.84 | 44.4 | 88.41 | 26.585 | 127
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -32.77 | 1.97 | 8.53 | -3.81 | 26.16 | 74.49 | 2.36 | 96.9
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 51.09 | 69.31 | 70.24 | 316.7 | 126.89 | 145.62 | 193.47 | 204 |  | similar to previous DEER
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 40.16 | 61.75 | 63.93 | 221.62 | 107.91 | 139.62 | 142.775 | 239 | N/A
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 33.19 | 55.6 | 57.28 | 172.51 | 98.64 | 134.4 | 114.895 | 218 |  |  |  |  | ACM Cooling Setpoint kWh |  | With Natural Ventilation
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 21.86 | 46.64 | 48.55 | 101.89 | 83.55 | 124.55 | 75.22 | 188 |  |  |  |  | Total Site Energy [kWh] |  | Total Site Energy [kWh]
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql | [12 empty] | 32916.91 |  | 32916.91
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -3465.21 | -3449.33 | 19.62 | 28.84 | -54.58 | 8.79 | 24.23 | 100 |  | lower than DEER. Lower than POU by a lot! High cooling setpoint |  |  | 32858.6 | 58.31 | 33348.75 | -431.84
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -6029.57 | -5992.85 | 11.79 | -49.06 | -113.41 | -25.85 | -18.635 | 126 | 353
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -7802.21 | -7756.18 | 7.02 | -84.38 | -138.05 | -41.58 | -38.68 | 123
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -11687.39 | -11620.56 | -2.46 | -137.64 | -180.31 | -68.02 | -70.05 | 118
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -327.31 | 35.62 | 57.55 | 181.02 | 108.32 | 108.7 | 119.285 | 128 |  | similar to previous DEER
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -481.03 | 23.6 | 50.46 | 122.17 | 99.7 | 107.06 | 86.315 | 124 | 174
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -561.03 | 10.12 | 46.35 | 93.22 | 94.06 | 103.79 | 69.785 | 95.5
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -1861.62 | -37.01 | 35.5 | 47.72 | 83.8 | 98.49 | 41.61 | 49.9
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 14.05 | 33.52 | 27.71 | 82.66 | 59.4 | 65.38 | 55.185 | -14.3 |  | higher than DEER, still lower than POU
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 2.29 | 25.35 | 20.05 | 58.13 | 49.16 | 63.99 | 39.09 | -91.2 | 171 | from midnight to noon the vent_min is 70F
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -3.87 | 22.1 | 18.26 | 40.06 | 42.17 | 61.55 | 29.16 | -122
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -10.65 | 13.14 | 9.62 | 19.72 | 33.09 | 55.67 | 14.67 | -154
Differences current E+ model compared to DEER DOE2
- We are using CZ2022 weather
- We have changed the heating and cooling setpoints
- We allow heating and cooling on the same day, consistent with 2019 T-24 ACM
- We are using delta T of 2 degrees instead of 5 degrees
- DEER2020 used a factor of 0.5 - they assumed occupants would only use the fan half the time when cooling is available.
- Have natual ventilation turned on in all cases
- for WHF measure, use ACM thermostat baseline and measure case
- When whf is baseline in NC use prototype thermostats and 5 deg Delta T
- use 76 indoor temp whf stpt in most climate zones. In a few climate (8, 9, 16) zones the WHF is allowed to cool to 70 deg in the morning between midnight and noon. But stays at 76 from after noon to midnight
- Use 5 deg Delta T in all cases
- Use 72 minimum indoor setpoint except in CZ 8 and 9 where we use 75
- Allow whole house fan to run all night (ie available all the time)
new things to try:
- Don't have whf operate the day before goining into heating mode
-

## more thermal mass
Whole House Fan Energy Savings - One Story | Energy Plus Savings | [6 empty] | DEER2020 - uses Min_Indoor_Temp of 68 |  |  | ACM thermostat setpoints
(Expect higher savings for two-story buildings) | CZ2010 weather, 5 deg F delta T |  | CZ2022 weather, 5 deg F delta T |  |  |  |  | combination of one and two story | uses Min_Indoor_Temp of 70 |  | whf setpoint 72 in CZ 10-16 all the time and also in 1-9 during 6am to 9am. All other time periods in CZ1-9 whf setpoint is 78
Orange indicates whole house fans are required in CA T-24 2019 | 68 | 70 | 1story | 2story | old-74 | 76 |  | DEER2020 | 2017 CMUA TRM | Notes
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql |  |  | ACM thermostat
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -36.62 | 4.04 | 0 | 0 | -0.24 | -0.25 |  | N/A | N/A | N/A
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -48.54 | -2.05 | 0 | 0 | -0.24 | -0.27
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -52.82 | -2.82 | 0 | 0 | -0.29 | -0.28
CZ01/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -62.41 | -7.87 | 0 | 0 | -0.18 | -0.32
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -158.79 | -108.92 | -27.13 | -38.02 | -0.76 | 47.77 | -32.575 | 36.2 |  | OK
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -194.83 | -135.5 | -35.65 | -52.85 | -53.36 | 20.84 | -44.25 | 25.5 | 55
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -211.06 | -148.22 | -35.87 | -59.67 | -75.8 | 7.91 | -47.77 | 19.4
CZ02/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -242.71 | -171.68 | -37.69 | -74.65 | -108.18 | -10.11 | -56.17 | 12.8
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -12.18 | 62.94 | -19.42 | -14.66 | 326.3 | -0.02 | -17.04 | -19.1 |  | Not OK
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -45.06 | 40.9 | -32.4 | -36.18 | 328.21 | -0.03 | -34.29 | -35.3 | -142
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -66.45 | 27.07 | -27.11 | -43.65 | 322.79 | 0 | -35.38 | -39
CZ03/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -104.88 | 4.78 | -41.57 | -64.85 | 310.01 | 0.01 | -53.21 | -41.5
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql | [11 empty] | with precooling to 70
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -105.81 | -57.71 | -0.82 | -48.11 | 59.87 | 108.91 | -24.465 | 65 |  | Not OK |  | -15.35
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -134.08 | -79.52 | -3.59 | -70.35 | 9.08 | 86.52 | -36.97 | 43.3 | 161 |  |  | -119.55
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -151.42 | -92.36 | -4.7 | -78.04 | -13.47 | 74 | -41.37 | 31.9 |  |  |  | -164
CZ04/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -188.34 | -115.76 | -3.96 | -95.44 | -43.41 | 55.95 | -49.7 | 15.1 |  |  |  | -238.09
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -120.98 | -27.18 | 1.38 | 41.09 | 316.79 | -7.93 | 21.235 | 10.7 |  | OK |  | 8.67
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -169.24 | -60.48 | -1.24 | 26.79 | 317.54 | -13.98 | 12.775 | 8.31 | -63 |  |  | -179.79
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -187.87 | -80.71 | -1.78 | 15.68 | 307.88 | -15.89 | 6.95 | 6.87 |  |  |  | -274.9
CZ05/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -246.78 | -108.67 | -3.98 | 7.18 | 289.55 | -21.53 | 1.6 | 6.96 |  |  |  | -331.17
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 84.03 | 124.88 | 2.28 | -131.19 | 532.01 | 0.07 | -64.455 | 110 |  | Not OK |  | -258.77
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 60.23 | 107.02 | 1.35 | -170.75 | 548.69 | 0 | -84.7 | 65.5 | N/A |  |  | -502.32
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 44.52 | 93.64 | 0.56 | -188.49 | 534.43 | 0.06 | -93.965 | 44.1 |  |  |  | -622.46
CZ06/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 17.75 | 74.51 | -0.73 | -228.14 | 503.42 | -0.05 | -114.435 | 33.3 |  |  |  | -743.37
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 78.44 | 106.1 | 13.04 | -52.99 | 310.58 | 77.46 | -19.975 | 185 |  | OK |  | -33.69
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 55.11 | 87.09 | 12 | -84.96 | 296.74 | 76.7 | -36.48 | 176 | N/A |  |  | -233.48
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 40.8 | 74.09 | 10.97 | -100.87 | 281.37 | 74.66 | -44.95 | 179 |  |  |  | -340.23
CZ07/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 14.07 | 53.12 | 8.46 | -135.52 | 246.49 | 69.01 | -63.53 | 182 |  |  |  | -463.93
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 58.82 | 84.72 | 27.36 | 8.92 | 267.93 | 324.84 | 18.14 | 337 |  | Not OK
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 35.86 | 66.49 | 25.91 | -16.12 | 236.3 | 329 | 4.895 | 325 | 388 | lower than previous DEER
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 21.14 | 54.39 | 25.22 | -29.01 | 217.38 | 320.28 | -1.895 | 320
CZ08/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -1.21 | 35.22 | 22.83 | -57.33 | 180.76 | 299.78 | -17.25 | 305
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -21.55 | 44.39 | 111.43 | 218.36 | 344.58 | 125.13 | 164.895 | 252 |  | OK
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -53.72 | 20.08 | 108.59 | 165.09 | 345.56 | 130.61 | 136.84 | 228 | 451
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -73.04 | 5.26 | 106.53 | 145.5 | 324.8 | 126.91 | 126.015 | 199
CZ09/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -111.79 | -15.03 | 101.96 | 110.97 | 291.34 | 118.08 | 106.465 | 172
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -5242.76 | -166.1 | 265.04 | 593.11 | 104.63 | 150 | 429.075 | 241 |  | OK
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -8580.54 | -207.71 | 255.86 | 593.84 | 45.88 | 115.65 | 424.85 | 245 | 522
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -10998.55 | -228.05 | 248.72 | 575.23 | 20.08 | 100.88 | 411.975 | 235
CZ10/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -16144.72 | -542.53 | 231.72 | 569.11 | -18.06 | 77.06 | 400.415 | 212
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -154.9 | 12.71 | 175.87 | 283.4 | 73.97 | 88.88 | 229.635 | 228 |  | OK
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -175.92 | -0.4 | 171.48 | 284.73 | 59.13 | 84.4 | 228.105 | 263 | 496
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -193.74 | -10.37 | 166.38 | 279.21 | 51.61 | 80.29 | 222.795 | 250
CZ11/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -228.12 | -26.31 | 157.92 | 274.24 | 38.65 | 72.81 | 216.08 | 222
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 12.88 | 39.01 | 148.45 | 257.7 | 85.07 | 108.23 | 203.075 | 161 |  | OK
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -4.93 | 25.67 | 142.15 | 255.83 | 56.85 | 95.48 | 198.99 | 147 | 567
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -16.59 | 16.82 | 137.27 | 250.76 | 44.4 | 88.41 | 194.015 | 127
CZ12/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -32.77 | 1.97 | 127.2 | 237.52 | 26.16 | 74.49 | 182.36 | 96.9
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 51.09 | 69.31 | 247.34 | 455.01 | 126.89 | 145.62 | 351.175 | 204 |  | OK
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 40.16 | 61.75 | 243.33 | 458.2 | 107.91 | 139.62 | 350.765 | 239 | N/A
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | 33.19 | 55.6 | 238.39 | 456.9 | 98.64 | 134.4 | 347.645 | 218 |  |  |  |  | ACM Cooling Setpoint kWh |  | With Natural Ventilation
CZ13/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | 21.86 | 46.64 | 228.14 | 437.93 | 83.55 | 124.55 | 333.035 | 188 |  |  |  |  | Total Site Energy [kWh] |  | Total Site Energy [kWh]
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql | [12 empty] | 32916.91 |  | 32916.91
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -3465.21 | -3449.33 | 94.96 | 127.54 | -54.58 | 8.79 | 111.25 | 100 |  | OK |  |  | 32858.6 | 58.31 | 33348.75 | -431.84
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -6029.57 | -5992.85 | 88.42 | 115.54 | -113.41 | -25.85 | 101.98 | 126 | 353
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -7802.21 | -7756.18 | 82.73 | 107.81 | -138.05 | -41.58 | 95.27 | 123
CZ14/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -11687.39 | -11620.56 | 72.23 | 85.95 | -180.31 | -68.02 | 79.09 | 118
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | -327.31 | 35.62 | 217.39 | 373.89 | 108.32 | 108.7 | 295.64 | 128 |  | OK
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | -481.03 | 23.6 | 215.47 | 371.31 | 99.7 | 107.06 | 293.39 | 124 | 174
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -561.03 | 10.12 | 211.26 | 367.84 | 94.06 | 103.79 | 289.55 | 95.5
CZ15/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -1861.62 | -37.01 | 203.94 | 357.27 | 83.8 | 98.49 | 280.605 | 49.9
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_baseline/instance-out.sql
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_0.7/instance-out.sql | 14.05 | 33.52 | 73.48 | 424.85 | 59.4 | 65.38 | 249.165 | -14.3 |  | OK
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_1.5/instance-out.sql | 2.29 | 25.35 | 56.59 | 446.95 | 49.16 | 63.99 | 251.77 | -91.2 | 171
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_2/instance-out.sql | -3.87 | 22.1 | 32.95 | 438.31 | 42.17 | 61.55 | 235.63 | -122
CZ16/SFm-rDXGF-Ex-WHFan/WHFans_ECM_3/instance-out.sql | -10.65 | 13.14 | 29.75 | 455.45 | 33.09 | 55.67 | 242.6 | -154
Differences current E+ model compared to DEER DOE2
- We are using CZ2022 weather
- We have changed the heating and cooling setpoints
- We allow heating and cooling on the same day, consistent with 2019 T-24 ACM
- DEER2020 used a factor of 0.5 - they assumed occupants would only use the fan half the time when cooling is available.
Things that are consistent with previous
- natual ventilation turned on in all cases
- inside/outside delta T of 5 deg to trigger whf operation
-
Additionally we are using:
- for WHF measure, use ACM thermostat baseline and measure case
- use 72 indoor temp whf stpt in most climate zones. In climate zones 1-9 fan energy was too high and not offsetting sufficient cooling. So, we only do pre-cooling (to 72) in CZ1-9 in the AM (6am-9am) Otherwise in those czs the WHF only cools to 77 deg, same as the cooling setpoint
- We allow the whole house fan to run all night if called for
- We increased internal thermal mass of the model from 10 sq m to 100 sq m