## Measures_2025-01-14
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | StdCostID | RUL_ID | LegacyID | MeasQualifierGroup | StartDate | ExpiryDate | ReviewStatus | MeasID_SCE | MeasID_PGE | MeasID_SDG | MeasID_SCG | MeasType | ReviewComment | FilingSpec | ClaimSpec | IsProposed | LastModBy | Created | CreatedComment | CreatedBy | LastModComment | WeatherSim | FuelSubID | Changes Needed
2023 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-15p0seer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 15 (EER = 12.5), EIR = 0.222, fan W/cfm = 0.28, one-speed fan, no economizer | DEER2023 | D23v1a | 2023-09-22 12:09 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-15p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18tolt33 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18tolt33 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, no economizer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 15 (EER = 13.0), EIR = 0.222, fan W/cfm = 0.28, one-speed fan, no economizer | NRes-PkgAC-18tolt33kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-18tolt33kBtuh-1Sp-S14.0 | NRes-PkgAC-18tolt33kBtuh-1Sp-S15.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:09 | Narrowed size range not requiring economizers per Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-16p0seer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, no economizer | DEER2023 | D23v1a | 2023-09-22 12:09 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-16p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18tolt33 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18tolt33 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, no economizer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, no economizer | NRes-PkgAC-18tolt33kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-18tolt33kBtuh-1Sp-S14.0 | NRes-PkgAC-18tolt33kBtuh-2Sp-S16.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:09 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-17p0seer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, no economizer | DEER2023 | D23v1a | 2023-09-22 12:09 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-17p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18tolt33 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18tolt33 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, no economizer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, no economizer | NRes-PkgAC-18tolt33kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-18tolt33kBtuh-1Sp-S14.0 | NRes-PkgAC-18tolt33kBtuh-2Sp-S17.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:09 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-18p0seer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, no economizer | DEER2023 | D23v1a | 2023-09-22 12:09 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-18p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18tolt33 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18tolt33 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, no economizer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, no economizer | NRes-PkgAC-18tolt33kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-18tolt33kBtuh-1Sp-S14.0 | NRes-PkgAC-18tolt33kBtuh-2Sp-S18.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:09 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-15p0seer-wEcono | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 15 (EER = 12.9), EIR = 0.234, fan W/cfm = 0.28, one-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-03 17:07 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-15p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 33-lt55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 33 - lt55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 15 (EER = 12.7), EIR = 0.230, fan W/cfm = 0.28, one-speed fan, with economizer | NRes-PkgAC-33tolt55kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-33tolt55kBtuh-1Sp-S14.0-wEcon | NRes-PkgAC-33tolt55kBtuh-1Sp-S15.0-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Set ClaimSpec and FilingSpec flags to TRUE | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-16p0seer-wEcono | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-03 17:07 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-16p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 33-lt55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 33 - lt55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-PkgAC-33tolt55kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-33tolt55kBtuh-1Sp-S14.0-wEcon | NRes-PkgAC-33tolt55kBtuh-2Sp-S16.0-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Set ClaimSpec and FilingSpec flags to TRUE | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-17p0seer-wEcono | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-03 17:07 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-17p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 33-lt55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 33 - lt55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-PkgAC-33tolt55kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-33tolt55kBtuh-1Sp-S14.0-wEcon | NRes-PkgAC-33tolt55kBtuh-2Sp-S17.0-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Set ClaimSpec and FilingSpec flags to TRUE | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-18p0seer-wEcono | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-03 17:07 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-18p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 33-lt55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 33 - lt55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-PkgAC-33tolt55kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-33tolt55kBtuh-1Sp-S14.0-wEcon | NRes-PkgAC-33tolt55kBtuh-2Sp-S18.0-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Set ClaimSpec and FilingSpec flags to TRUE | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 15 (EER = 12.6), EIR = 0.236, fan W/cfm = 0.25, two-speed fan, with economizer (pre-existing vintages do not include economizer) | DEER2023 | D23v0 | 2022-09-20 14:09 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 11.7), two-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 15 (EER = 12.6), EIR = 0.236, fan W/cfm = 0.25, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0 | StdNResPkgAC-55to65kBtu/h-S14.0 | MsrNResPkgAC-55to65kBtu/h-S15.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-09-20 14:09 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-PreEconByVint | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 15 (EER = 12.6), EIR = 0.236, fan W/cfm = 0.25, two-speed fan, with economizer (most pre-existing vintages do not include economizer; 2014 does) | DEER2023 | D23v0 | 2022-02-04 18:39 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 11.7), two-speed fan, w/economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 15 (EER = 12.6), EIR = 0.236, fan W/cfm = 0.25, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0-EconByVint | StdNResPkgAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNResPkgAC-55to65kBtu/h-2Sp-S15.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-04 18:39 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 15 (EER = 12.6), EIR = 0.236, fan W/cfm = 0.25, two-speed fan, with economizer (pre-existing vintages include economizer) | DEER2023 | D23v0 | 2022-02-04 18:39 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, w/ economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/economizer; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 15 (EER = 12.6), EIR = 0.236, fan W/cfm = 0.25, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0-Econ | StdNResPkgAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNResPkgAC-55to65kBtu/h-2Sp-S15.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-04 18:39 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer (pre-existing vintages do not include economizer) | DEER2023 | D23v0 | 2022-09-20 14:09 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 11.7), two-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0 | StdNResPkgAC-55to65kBtu/h-S14.0 | MsrNResPkgAC-55to65kBtu/h-S16.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-09-20 14:09 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-PreEconByVint | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer (most pre-existing vintages do not include economizer; 2014 does) | DEER2023 | D23v0 | 2022-02-04 18:39 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 11.7), two-speed fan, w/economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0-EconByVint | StdNResPkgAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNResPkgAC-55to65kBtu/h-2Sp-S16.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-04 18:39 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer (pre-existing vintages include economizer) | DEER2023 | D23v0 | 2021-11-01 19:45 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, w/ economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/economizer; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0-Econ | StdNResPkgAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNResPkgAC-55to65kBtu/h-2Sp-S16.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer (pre-existing vintages do not include economizer) | DEER2023 | D23v0 | 2022-09-20 14:09 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 11.7), two-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0 | StdNResPkgAC-55to65kBtu/h-S14.0 | MsrNResPkgAC-55to65kBtu/h-S17.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-09-20 14:09 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-PreEconByVint | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer (most pre-existing vintages do not include economizer; 2014 does) | DEER2023 | D23v0 | 2021-11-01 19:45 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 11.7), two-speed fan, w/economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0-EconByVint | StdNResPkgAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNResPkgAC-55to65kBtu/h-2Sp-S17.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer (pre-existing vintages include economizer) | DEER2023 | D23v0 | 2021-11-01 19:45 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, w/ economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/economizer; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0-Econ | StdNResPkgAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNResPkgAC-55to65kBtu/h-2Sp-S17.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer (pre-existing vintages do not include economizer) | DEER2023 | D23v0 | 2022-09-20 14:09 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 11.7), two-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0 | StdNResPkgAC-55to65kBtu/h-S14.0 | MsrNResPkgAC-55to65kBtu/h-S18.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-09-20 14:09 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-PreEconByVint | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer (most pre-existing vintages do not include economizer; 2014 does) | DEER2023 | D23v0 | 2021-11-01 19:45 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 11.7), two-speed fan, w/economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0-EconByVint | StdNResPkgAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNResPkgAC-55to65kBtu/h-2Sp-S18.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | Com SEER-rated packaged air conditioner, size range: 55 - 65 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer (pre-existing vintages include economizer) | DEER2023 | D23v0 | 2021-11-01 19:45 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 55-65 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, w/ economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/economizer; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged air conditioners, size range: 55 - 65 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | PreNResPkgAC-55to65kBtu/h-1to2Sp-S11.6to14.0-Econ | StdNResPkgAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNResPkgAC-55to65kBtu/h-2Sp-S18.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | Com SEER-rated packaged air conditioner, size range: 18 - 55 kBtu/h, SEER = 15 (EER = 12.9), EIR = 0.234, fan W/cfm = 0.25, one-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:39 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 15 (EER = 12.9), EIR = 0.234, fan W/cfm = 0.25, one-speed fan, without economizer | PreNResPkgAC-lt55kBtu/h-1Sp-S11.6to14.0 | StdNResPkgAC-lt55kBtu/h-1Sp-S14.0 | MsrNResPkgAC-lt55kBtu/h-1Sp-S15.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | Com SEER-rated packaged air conditioner, size range: 18 - 55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:39 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, less than 55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | PreNResPkgAC-lt55kBtu/h-1Sp-S11.6to14.0 | StdNResPkgAC-lt55kBtu/h-1Sp-S14.0 | MsrNResPkgAC-lt55kBtu/h-2Sp-S16.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | Com SEER-rated packaged air conditioner, size range: 18 - 55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:39 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | PreNResPkgAC-lt55kBtu/h-1Sp-S11.6to14.0 | StdNResPkgAC-lt55kBtu/h-1Sp-S14.0 | MsrNResPkgAC-lt55kBtu/h-2Sp-S17.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | Com SEER-rated packaged air conditioner, size range: 18 - 55 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:39 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner,18-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | PreNResPkgAC-lt55kBtu/h-1Sp-S11.6to14.0 | StdNResPkgAC-lt55kBtu/h-1Sp-S14.0 | MsrNResPkgAC-lt55kBtu/h-2Sp-S18.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airAC-Split-18tolt33kBtuh-15p0seer | Com SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, fan W/cfm = 0.28, one-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airAC-Split-18tolt33kBtuh-15p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18tolt33 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/cfm = 0.28, one-speed fan, without economizers | NRes-SplitAC-18tolt33kBtu/h-1Sp-S11.5toS14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S15.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Split-18tolt33kBtuh-16p0seer | Com SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airAC-Split-18tolt33kBtuh-16p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18tolt33 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/cfm = 0.27, two-speed fan, without economizers | NRes-SplitAC-18tolt33kBtu/h-1Sp-S11.5toS14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S16.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Split-18tolt33kBtuh-17p0seer | Com SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airAC-Split-18tolt33kBtuh-17p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18tolt33 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/cfm = 0.27, two-speed fan, without economizers | NRes-SplitAC-18tolt33kBtu/h-1Sp-S11.5toS14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S17.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Split-18tolt33kBtuh-18p0seer | Com SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airAC-Split-18tolt33kBtuh-18p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18tolt33 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/cfm = 0.27, two-speed fan, without economizers | NRes-SplitAC-18tolt33kBtu/h-1Sp-S11.5toS14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S18.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
1786 | NE-HVAC-airAC-Split-33tolt55kBtuh-15p0seer-wEcono | Commercial SEER-rated split-system air conditioner, size range: 33 - lt55 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, fan W/cfm = 0.28, one-speed fan, with economizer | DEER2023 | D23v1 | 2023-08-23 09:17 | NE-HVAC-airAC-Split-33tolt55kBtuh-15p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split air conditioner, 33-lt55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Commercial SEER-rated split air conditioner, size range: 33 - lt55 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, with economizer | Commercial SEER-rated split air conditioner, Size Range: 33 - lt55 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/cfm = 0.28, one-speed fan, with economizer | NRes-SplitAC-33tolt55kBtu/h-1Sp-S11.6to14.0 | NRes-SplitAC-33tolt55kBtu/h-1Sp-S14.0-wEcono | NRes-SplitAC-33tolt55kBtu/h-1Sp-S15.0-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-17 16:05 | Updated based on economizer required by Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Correcting StartDate. | CZ2022 | None | TRUE
1787 | NE-HVAC-airAC-Split-33tolt55kBtuh-16p0seer-wEcono | Commercial SEER-rated split-system air conditioners, size range: 33 - lt55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-08-23 09:17 | NE-HVAC-airAC-Split-33tolt55kBtuh-16p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split air conditioner, 33-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Commercial SEER-rated split air conditioner, size range: 33 - 55 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, with economizer | Commercial SEER-rated split-system air conditioner, Size Range: 33 - lt55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitAC-33tolt55kBtu/h-1Sp-S11.6to14.0 | NRes-SplitAC-33tolt55kBtu/h-1Sp-S14.0-wEcono | NRes-SplitAC-33tolt55kBtu/h-1Sp-S16.0-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-17 16:05 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Correcting StartDate. | CZ2022 | None | TRUE
1788 | NE-HVAC-airAC-Split-33tolt55kBtuh-17p0seer-wEcono | Commercial SEER-rated split-system air conditioners, size range: 33 - lt55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-08-23 09:17 | NE-HVAC-airAC-Split-33tolt55kBtuh-17p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split air conditioner, 33-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Commercial SEER-rated split air conditioner, size range: 33 - 55 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, with economizer | Commercial SEER-rated split-system air conditioner, size range: 33 - lt55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitAC-33tolt55kBtu/h-1Sp-S11.6to14.0 | NRes-SplitAC-33tolt55kBtu/h-1Sp-S14.0-wEcono | NRes-SplitAC-33tolt55kBtu/h-1Sp-S17.0-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-17 16:05 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Correcting StartDate. | CZ2022 | None | TRUE
1789 | NE-HVAC-airAC-Split-33tolt55kBtuh-18p0seer-wEcono | Commercial SEER-rated split-system air conditioners, size range: 18 - 45 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-08-23 09:17 | NE-HVAC-airAC-Split-33tolt55kBtuh-18p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split air conditioner, 33-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Commercial SEER-rated split air conditioner, size range: 33 - 55 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, with economizer | Commercial SEER-rated split-system air conditioner, size range: 33 - lt55 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitAC-33tolt55kBtu/h-1Sp-S11.6to14.0 | NRes-SplitAC-33tolt55kBtu/h-1Sp-S14.0-wEcono | NRes-SplitAC-33tolt55kBtu/h-1Sp-S18.0-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-17 16:05 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Correcting StartDate. | CZ2022 | None | TRUE
2023 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | Com SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, fan W/cfm = 0.25, one-speed fan, without economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 45-55 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 11.82), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/cfm = 0.25, one-speed fan, without economizers | PreNRes-SplitAC-45to55kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-45to55kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-45to55kBtu/h-1Sp-S15.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | Com SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 45-55 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 11.82), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/cfm = 0.27, two-speed fan, without economizers | PreNRes-SplitAC-45to55kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-45to55kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-45to55kBtu/h-2Sp-S16.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | Com SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 45-55 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 11.82), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/cfm = 0.27, two-speed fan, without economizers | PreNRes-SplitAC-45to55kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-45to55kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-45to55kBtu/h-2Sp-S17.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | Com SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 45-55 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 11.82), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/cfm = 0.27, two-speed fan, without economizers | PreNRes-SplitAC-45to55kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-45to55kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-45to55kBtu/h-2Sp-S18.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-PreEconByVint | Com SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 15 (EER = 12.6), EIR = 0.236, fan W/cfm = 0.25, two-speed fan, with economizer (all pre-existing vintages--except2014--do not have economizer) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 55-65 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 11.7), two-speed fan, w/economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/cfm = 0.29, two-speed fan, with economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/cfm = 0.25, two-speed fan, with economizers | PreNRes-SplitAC-55to65kBtu/h-1to2Sp-S11.5toS14.0-EconByVint | StdNRes-SplitAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNRes-SplitAC-55to65kBtu/h-2Sp-S15.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | Com SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 15 (EER = 12.6), EIR = 0.236, fan W/cfm = 0.25, two-speed fan, with economizer (all pre-existing vintages have economizers) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 55-65 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, w/economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/economizers; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/cfm = 0.29, two-speed fan, with economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/cfm = 0.25, two-speed fan, with economizers | PreNRes-SplitAC-55to65kBtu/h-1to2Sp-S11.5toS14.0-Econ | StdNRes-SplitAC-55to65kBtu/h-2Sp-S14.0 | MsrNRes-SplitAC-55to65kBtu/h-2Sp-S15.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-PreEconByVint | Com SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer (all pre-existing vintages--except2014--do not have economizer) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 55-65 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 11.7), two-speed fan, w/economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/cfm = 0.29, two-speed fan, with economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/cfm = 0.27, two-speed fan, with economizers | PreNRes-SplitAC-55to65kBtu/h-1to2Sp-S11.5toS14.0-EconByVint | StdNRes-SplitAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNRes-SplitAC-55to65kBtu/h-2Sp-S16.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | Com SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer (all pre-existing vintages have economizers) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 55-65 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, w/economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/economizers; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/cfm = 0.29, two-speed fan, with economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/cfm = 0.27, two-speed fan, with economizers | PreNRes-SplitAC-55to65kBtu/h-1to2Sp-S11.5toS14.0-Econ | StdNRes-SplitAC-55to65kBtu/h-2Sp-S14.0 | MsrNRes-SplitAC-55to65kBtu/h-2Sp-S16.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-PreEconByVint | Com SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer (all pre-existing vintages--except2014--do not have economizer) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 55-65 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 11.7), two-speed fan, w/economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/cfm = 0.29, two-speed fan, with economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/cfm = 0.27, two-speed fan, with economizers | PreNRes-SplitAC-55to65kBtu/h-1to2Sp-S11.5toS14.0-EconByVint | StdNRes-SplitAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNRes-SplitAC-55to65kBtu/h-2Sp-S17.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | Com SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer (all pre-existing vintages have economizers) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 55-65 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, w/economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/economizers; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/cfm = 0.29, two-speed fan, with economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/cfm = 0.27, two-speed fan, with economizers | PreNRes-SplitAC-55to65kBtu/h-1to2Sp-S11.5toS14.0-Econ | StdNRes-SplitAC-55to65kBtu/h-2Sp-S14.0 | MsrNRes-SplitAC-55to65kBtu/h-2Sp-S17.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-PreEconByVint | Com SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer (all pre-existing vintages--except2014--do not have economizer) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 55-65 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 11.7), two-speed fan, w/economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/cfm = 0.29, two-speed fan, with economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/cfm = 0.27, two-speed fan, with economizers | PreNRes-SplitAC-55to65kBtu/h-1to2Sp-S11.5toS14.0-EconByVint | StdNRes-SplitAC-55to65kBtu/h-2Sp-S14.0-Econ | MsrNRes-SplitAC-55to65kBtu/h-2Sp-S18.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | Com SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer (all pre-existing vintages have economizers) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 55-65 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, w/economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/economizers; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/cfm = 0.29, two-speed fan, with economizers | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/cfm = 0.27, two-speed fan, with economizers | PreNRes-SplitAC-55to65kBtu/h-1to2Sp-S11.5toS14.0-Econ | StdNRes-SplitAC-55to65kBtu/h-2Sp-S14.0 | MsrNRes-SplitAC-55to65kBtu/h-2Sp-S18.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | Com SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, fan W/cfm = 0.25, one-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:51 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, less than 45 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/cfm = 0.25, one-speed fan, without economizers | PreNRes-SplitAC-lt45kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-lt45kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-lt45kBtu/h-1Sp-S15.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | Com SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:51 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, less than 45 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/cfm = 0.27, two-speed fan, without economizers | PreNRes-SplitAC-lt45kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-lt45kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-lt45kBtu/h-1Sp-S16.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | Com SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:51 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, less than 45 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/cfm = 0.27, two-speed fan, without economizers | PreNRes-SplitAC-lt45kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-lt45kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-lt45kBtu/h-1Sp-S17.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | Com SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:51 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, less than 45 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/cfm = 0.27, two-speed fan, without economizers | PreNRes-SplitAC-lt45kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-lt45kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-lt45kBtu/h-1Sp-S18.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer-wPreEcono | EER-rated packaged air conditioner, size range: 135 - 240 kBtu/h, EER = 11.5, min IEER = 13, EIR = 0.255, fan W/cfm = 0.41, two-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 135-240 kBtu/h; Pre-2005: EER = 9.7, one-speed fan, w/economizer; 2006 - 2009: EER = 9.7, one-speed fan, w/economizer; 2010 - 2013: EER = 10.8, one-speed fan, w/economizer; 2014 - 2015: EER = 10.8, IEER = 12.2, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 135 - 240 kBtu/h, EER = 10.8, IEER = 12.2, EIR = 0.274, fan W/cfm = 0.41, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 135 - 240 kBtu/h, EER = 11.5, min IEER = 13, EIR = 0.255, fan W/cfm = 0.41, two-speed fan, with economizer | PreNRes-PkgAC-135to240kBtu/h-1to2SpH-E9.7to10.8-Econ | StdNRes-PkgAC-135to240kBtu/h-2SpP-E10.8-Econ | MsrNRes-PkgAC-135to240kBtu/h-2SpP-E11.5-Econ | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer-wPreEcono | EER-rated packaged air conditioner, size range: 135 - 240 kBtu/h, EER = 12, min IEER = 13.5, EIR = 0.243, fan W/cfm = 0.41, two-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 135-240 kBtu/h; Pre-2005: EER = 9.7, one-speed fan, w/economizer; 2006 - 2009: EER = 9.7, one-speed fan, w/economizer; 2010 - 2013: EER = 10.8, one-speed fan, w/economizer; 2014 - 2015: EER = 10.8, IEER = 12.2, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 135 - 240 kBtu/h, EER = 10.8, IEER = 12.2, EIR = 0.274, fan W/cfm = 0.41, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 135 - 240 kBtu/h, EER = 12, min IEER = 13.5, EIR = 0.243, fan W/cfm = 0.41, two-speed fan, with economizer | PreNRes-PkgAC-135to240kBtu/h-1to2SpH-E9.7to10.8-Econ | StdNRes-PkgAC-135to240kBtu/h-2SpP-E10.8-Econ | MsrNRes-PkgAC-135to240kBtu/h-2SpP-E12.0-Econ | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer-wPreEcono | EER-rated packaged air conditioner, size range: 135 - 240 kBtu/h, EER = 12.5, min IEER = 14, EIR = 0.231, fan W/cfm = 0.41, two-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 135-240 kBtu/h; Pre-2005: EER = 9.7, one-speed fan, w/economizer; 2006 - 2009: EER = 9.7, one-speed fan, w/economizer; 2010 - 2013: EER = 10.8, one-speed fan, w/economizer; 2014 - 2015: EER = 10.8, IEER = 12.2, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 135 - 240 kBtu/h, EER = 10.8, IEER = 12.2, EIR = 0.274, fan W/cfm = 0.41, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 135 - 240 kBtu/h, EER = 12.5, min IEER = 14, EIR = 0.231, fan W/cfm = 0.41, two-speed fan, with economizer | PreNRes-PkgAC-135to240kBtu/h-1to2SpH-E9.7to10.8-Econ | StdNRes-PkgAC-135to240kBtu/h-2SpP-E10.8-Econ | MsrNRes-PkgAC-135to240kBtu/h-2SpP-E12.5-Econ | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 10.8, min IEER = 12.2, EIR = 0.255, fan W/CFM = 0.61, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-05-27 18:53 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-rated packaged air conditioner, 240-760 kBtu/h; mix of single-zone 9.8 EER and multi-zone 10.0 EER system configurations where applicable | EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, mix of single-zone 9.8 EER and multi-zone 10.0 EER system configurations where applicable | EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 10.8, mix of single-zone and multi-zone system configurations where applicable | PreNRes-PVVAC+PkgAC-240to760kBtu/h-VarSpH+1to2SpH-E10.0+E9.8-byBldgType | StdNRes-PVVAC+PkgAC-240to760kBtu/h-VarSpP+2SpP-E10.0+E9.8-byBldgType | MsrNRes-PVVAC+PkgAC-240to760kBtu/h-VarSpP+2SpP-E10.8-byBldgType | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-05-27 18:53 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_MZ | Multi-zone EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 10.8, min IEER = 12.2, EIR = 0.255, fan W/cfm = 0.61, variable-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_MZ | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 240-760 kBtu/h; Pre-2005: EER = 10.0 (IEER = 11.3), variable-speed fan, w/economizer; 2006 - 2009: EER = 10.0, variable-speed fan, w/economizer; 2010 - 2013: EER = 10.0, variable-speed fan, w/economizer; 2014 - 2015: EER = 10.0, IEER 11.6, variable-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 10.0 IEER = 11.4, EIR = 0.282, variable-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 10.8, min IEER 12.2, EIR = 0.255, variable-speed fan, with economizer | PreNRes-PVVAC-240to760kBtu/h-VarSpH-E10.0-Econ | StdNRes-PVVAC-240to760kBtu/h-VarSpP-E10.0-Econ | MsrNRes-PVVAC-240to760kBtu/h-VarSpP-E10.8-Econ | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Component |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_SZ | Single-zone EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 10.8, min IEER = 12.2, EIR = 0.255, fan W/cfm = 0.61, two-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_SZ | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 240-760 kBtu/h; Pre-2005: EER = 9.8 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/economizer; 2006 - 2009: EER = 9.8, one-speed fan, w/economizer; 2010 - 2013: EER = 9.8, one-speed fan, w/economizer; 2014 - 2015: EER = 9.8, IEER 11.4, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 9.8, IEER = 11.4, EIR = 0.286, fan W/cfm = 0.61, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 10.8, min IEER 12.2, EIR = 0.255, fan W/cfm = 0.61, two-speed fan, with economizer | PreNRes-PkgAC-240to760kBtu/h-1to2SpH-E9.8-Econ | StdNRes-PkgAC-240to760kBtu/h-2SpP-E9.8-Econ | MsrNRes-PkgAC-240to760kBtu/h-2SpP-E10.8 | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Component |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, fan W/CFM = 0.61, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-05-27 18:53 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-rated packaged air conditioner, 240-760 kBtu/h; mix of single-zone 9.8 EER and multi-zone 10.0 EER system configurations where applicable | EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, mix of single-zone 9.8 EER and multi-zone 10.0 EER system configurations where applicable | EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 11.5, mix of single-zone and multi-zone system configurations where applicable | PreNRes-PVVAC+PkgAC-240to760kBtu/h-VarSpH+1to2SpH-E10.0+E9.8-byBldgType | StdNRes-PVVAC+PkgAC-240to760kBtu/h-VarSpP+2SpP-E10.0+E9.8-byBldgType | MsrNRes-PVVAC+PkgAC-240to760kBtu/h-VarSpP+2SpP-E11.5-byBldgType | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-05-27 18:53 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_MZ | Multi-zone EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, fan W/cfm = 0.61, variable-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_MZ | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 240-760 kBtu/h; Pre-2005: EER = 10.0 (IEER = 11.3), variable-speed fan, w/economizer; 2006 - 2009: EER = 10.0, variable-speed fan, w/economizer; 2010 - 2013: EER = 10.0, variable-speed fan, w/economizer; 2014 - 2015: EER = 10.0, IEER 11.6, variable-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 10.0 IEER = 11.4, EIR = 0.282, variable-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, variable-speed fan, with economizer | PreNRes-PVVAC-240to760kBtu/h-VarSpH-E10.0-Econ | StdNRes-PVVAC-240to760kBtu/h-VarSpP-E10.0-Econ | MsrNRes-PVVAC-240to760kBtu/h-VarSpP-E11.5-Econ | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Component |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_SZ | Single-zone EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, fan W/cfm = 0.61, two-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_SZ | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 240-760 kBtu/h; Pre-2005: EER = 9.8 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/economizer; 2006 - 2009: EER = 9.8, one-speed fan, w/economizer; 2010 - 2013: EER = 9.8, one-speed fan, w/economizer; 2014 - 2015: EER = 9.8, IEER 11.4, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 9.8, IEER = 11.4, EIR = 0.286, fan W/cfm = 0.61, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, fan W/cfm = 0.61, two-speed fan, with economizer | PreNRes-PkgAC-240to760kBtu/h-1to2SpH-E9.8-Econ | StdNRes-PkgAC-240to760kBtu/h-2SpP-E9.8-Econ | MsrNRes-PkgAC-240to760kBtu/h-2SpP-E11.5 | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Component |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, fan W/CFM = 0.61, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-05-27 18:53 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-rated packaged air conditioner, 240-760 kBtu/h; mix of single-zone 9.8 EER and multi-zone 10.0 EER system configurations where applicable | EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, mix of single-zone 9.8 EER and multi-zone 10.0 EER system configurations where applicable | EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 12.5, mix of single-zone and multi-zone system configurations where applicable | PreNRes-PVVAC+PkgAC-240to760kBtu/h-VarSpH+1to2SpH-E10.0+E9.8-byBldgType | StdNRes-PVVAC+PkgAC-240to760kBtu/h-VarSpP+2SpP-E10.0+E9.8-byBldgType | MsrNRes-PVVAC+PkgAC-240to760kBtu/h-VarSpP+2SpP-E12.5-byBldgType | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-05-27 18:53 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_MZ | Multi-zone EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, fan W/cfm = 0.61, variable-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_MZ | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 240-760 kBtu/h; Pre-2005: EER = 10.0 (IEER = 11.3), variable-speed fan, w/economizer; 2006 - 2009: EER = 10.0, variable-speed fan, w/economizer; 2010 - 2013: EER = 10.0, variable-speed fan, w/economizer; 2014 - 2015: EER = 10.0, IEER 11.6, variable-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 10.0 IEER = 11.4, EIR = 0.282, variable-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, variable-speed fan, with economizer | PreNRes-PVVAC-240to760kBtu/h-VarSpH-E10.0-Econ | StdNRes-PVVAC-240to760kBtu/h-VarSpP-E10.0-Econ | MsrNRes-PVVAC-240to760kBtu/h-VarSpP-E12.5-Econ | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Component |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_SZ | Single-zone EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, fan W/cfm = 0.61, two-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_SZ | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 240-760 kBtu/h; Pre-2005: EER = 9.8 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/economizer; 2006 - 2009: EER = 9.8, one-speed fan, w/economizer; 2010 - 2013: EER = 9.8, one-speed fan, w/economizer; 2014 - 2015: EER = 9.8, IEER 11.4, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 9.8, IEER = 11.4, EIR = 0.286, fan W/cfm = 0.61, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 240 - 760 kBtu/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, fan W/cfm = 0.61, two-speed fan, with economizer | PreNRes-PkgAC-240to760kBtu/h-1to2SpH-E9.8-Econ | StdNRes-PkgAC-240to760kBtu/h-2SpP-E9.8-Econ | MsrNRes-PkgAC-240to760kBtu/h-2SpP-E12.5 | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Component |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-PreEconByVint | EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11.5, min IEER = 13, EIR = 0.26, fan W/cfm = 0.4, two-speed fan (most pre-existing vintages do not include economizer; 2014 does) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 65-134 kBtu/h; Pre-2005: EER = 10.0, one-speed fan, no economizer; 2006 - 2009: EER = 10.0, one-speed fan, no economizer; 2010 - 2013: EER = 11, one-speed fan, no economizer; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11, IEER = 12.7, EIR = 0.273, fan W/cfm = 0.4, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11.5, min IEER = 13, EIR = 0.26, fan W/cfm = 0.4, two-speed fan, with economizer | PreNRes-SpltPkgAC-65to134kBtu/h-1to2Sp-E10.0to11.0-EconByVint | StdNRes-SpltPkgAC-65to134kBtu/h-2Sp-E11.0-Econ | MsrNRes-SpltPkgAC-65to134kBtu/h-2Sp-E11.5-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-wPreEcono | EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11.5, min IEER = 13, EIR = 0.26, fan W/cfm = 0.4, two-speed fan, with economizer (pre-existing vintages include economizer) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 65-134 kBtu/h; Pre-2005: EER = 10.0, one-speed fan, w/economizer; 2006 - 2009: EER = 10.0, one-speed fan, w/economizer; 2010 - 2013: EER = 11, one-speed fan, w/economizer; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11, IEER = 12.7, EIR = 0.273, fan W/cfm = 0.4, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11.5, min IEER = 13, EIR = 0.26, fan W/cfm = 0.4, two-speed fan, with economizer | PreNRes-SpltPkgAC-65to134kBtu/h-E10.0to11.0-Econ | StdNRes-SpltPkgAC-65to134kBtu/h-2Sp-E11.0-Econ | MsrNRes-SpltPkgAC-65to134kBtu/h-2Sp-E11.5-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-PreEconByVint | EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 12, min IEER = 13.5 EIR = 0.247, fan W/cfm = 0.4, two-speed fan, with economizer (most pre-existing vintages do not include economizer; 2014 does) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 65-134 kBtu/h; Pre-2005: EER = 10.0, one-speed fan, no economizer; 2006 - 2009: EER = 10.0, one-speed fan, no economizer; 2010 - 2013: EER = 11, one-speed fan, no economizer; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11, IEER = 12.7, EIR = 0.273, fan W/cfm = 0.4, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 12, min IEER = 13.5 EIR = 0.247, fan W/cfm = 0.4, two-speed fan, with economizer | PreNRes-SpltPkgAC-65to134kBtu/h-1to2Sp-E10.0to11.0-EconByVint | StdNRes-SpltPkgAC-65to134kBtu/h-2Sp-E11.0-Econ | MsrNRes-SpltPkgAC-65to134kBtu/h-2Sp-E12.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-wPreEcono | EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 12, min IEER = 13.5 EIR = 0.247, fan W/cfm = 0.4, two-speed fan, with economizer (pre-existing vintages include economizer) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 65-134 kBtu/h; Pre-2005: EER = 10.0, one-speed fan, w/economizer; 2006 - 2009: EER = 10.0, one-speed fan, w/economizer; 2010 - 2013: EER = 11, one-speed fan, w/economizer; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11, IEER = 12.7, EIR = 0.273, fan W/cfm = 0.4, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 12, min IEER = 13.5 EIR = 0.247, fan W/cfm = 0.4, two-speed fan, with economizer | PreNRes-SpltPkgAC-65to134kBtu/h-E10.0to11.0-Econ | StdNRes-SpltPkgAC-65to134kBtu/h-2Sp-E11.0-Econ | MsrNRes-SpltPkgAC-65to134kBtu/h-2Sp-E12.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-PreEconByVint | EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 12.5, min IEER = 14, EIR = 0.236, fan W/cfm = 0.4, two-speed fan, with economizer (most pre-existing vintages do not include economizer; 2014 does) | DEER2023 | D23v0 | 2022-09-19 12:03 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-PreEconByVint | Deem-DEER | CrossMeasWtd | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 65-134 kBtu/h; Pre-2005: EER = 10.0, one-speed fan, no economizer; 2006 - 2009: EER = 10.0, one-speed fan, no economizer; 2010 - 2013: EER = 11, one-speed fan, no economizer; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11, IEER = 12.7, EIR = 0.273, fan W/cfm = 0.4, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 12.5, min IEER = 14, EIR = 0.236, fan W/cfm = 0.4, two-speed fan, with economizer | PreNRes-SpltPkgAC-65to134kBtu/h-1to2Sp-E10.0to11.0-EconByVint | StdNRes-SpltPkgAC-65to134kBtu/h-2Sp-E11.0-Econ | MsrNRes-SpltPkgAC-65to134kBtu/h-2Sp-E12.5-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-wPreEcono | EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 12.5, min IEER = 14, EIR = 0.236, fan W/cfm = 0.4, two-speed fan, with economizer (pre-existing vintages include economizer) | DEER2023 | D23v0 | 2022-09-19 12:03 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-wPreEcono | Deem-DEER | CrossMeasWtd | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 65-134 kBtu/h; Pre-2005: EER = 10.0, one-speed fan, w/economizer; 2006 - 2009: EER = 10.0, one-speed fan, w/economizer; 2010 - 2013: EER = 11, one-speed fan, w/economizer; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11, IEER = 12.7, EIR = 0.273, fan W/cfm = 0.4, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 12.5, min IEER = 14, EIR = 0.236, fan W/cfm = 0.4, two-speed fan, with economizer | PreNRes-SpltPkgAC-65to134kBtu/h-E10.0to11.0-Econ | StdNRes-SpltPkgAC-65to134kBtu/h-2Sp-E11.0-Econ | MsrNRes-SpltPkgAC-65to134kBtu/h-2Sp-E12.5-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-PreEconByVint | EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 13, min IEER = 15, EIR = 0.226, fan W/cfm = 0.4, two-speed fan, with economizer (most pre-existing vintages do not include economizer; 2014 does) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 65-134 kBtu/h; Pre-2005: EER = 10.0, one-speed fan, no economizer; 2006 - 2009: EER = 10.0, one-speed fan, no economizer; 2010 - 2013: EER = 11, one-speed fan, no economizer; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11, IEER = 12.7, EIR = 0.273, fan W/cfm = 0.4, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 13, min IEER = 15, EIR = 0.226, fan W/cfm = 0.4, two-speed fan, with economizer | PreNRes-SpltPkgAC-65to134kBtu/h-1to2Sp-E10.0to11.0-EconByVint | StdNRes-SpltPkgAC-65to134kBtu/h-2Sp-E11.0-Econ | MsrNRes-SpltPkgAC-65to134kBtu/h-2Sp-E13.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-wPreEcono | EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 13, min IEER = 15, EIR = 0.226, fan W/cfm = 0.4, two-speed fan, with economizer (pre-existing vintages include economizer) | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 65-134 kBtu/h; Pre-2005: EER = 10.0, one-speed fan, w/economizer; 2006 - 2009: EER = 10.0, one-speed fan, w/economizer; 2010 - 2013: EER = 11, one-speed fan, w/economizer; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 11, IEER = 12.7, EIR = 0.273, fan W/cfm = 0.4, two-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 65 - 134 kBtu/h, EER = 13, min IEER = 15, EIR = 0.226, fan W/cfm = 0.4, two-speed fan, with economizer | PreNRes-SpltPkgAC-65to134kBtu/h-E10.0to11.0-Econ | StdNRes-SpltPkgAC-65to134kBtu/h-2Sp-E11.0-Econ | MsrNRes-SpltPkgAC-65to134kBtu/h-2Sp-E13.0-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | EER-rated packaged air conditioner, size range: 760 - kBtu/h, EER = 10.2, min IEER = 11.6, EIR = 0.273, fan W/cfm = 0.61, variable-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 760+ kBtu/h; Pre-2005: EER = 9.2, variable-speed fan, w/economizer; 2006 - 2009: EER = 9.2, variable-speed fan, w/economizer; 2010 - 2013: EER = 9.5, variable-speed fan, w/economizer; 2014 - 2015: EER = 9.5, IEER = 11, variable-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 760+ kBtu/h, EER = 9.5, IEER = 11, EIR = 0.297, variable-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 760+ kBtu/h, EER = 10.2, min IEER = 11.6, EIR = 0.273, variable-speed fan, with economizer | PreNRes-PVVAC-gte760kBtu/h-VarSpHorP-E9.2to9.7-Econ | StdNRes-PVVAC-gte760kBtu/h-VarSpP-E9.7-Econ | MsrNRes-PVVAC-gte760kBtu/h-VarSpP-E10.2-Econ | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | EER-rated packaged air conditioner, size range: 760 - kBtu/h, EER = 11, min IEER = 12.3, EIR = 0.249, fan W/cfm = 0.61, variable-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 760+ kBtu/h; Pre-2005: EER = 9.2, variable-speed fan, w/economizer; 2006 - 2009: EER = 9.2, variable-speed fan, w/economizer; 2010 - 2013: EER = 9.5, variable-speed fan, w/economizer; 2014 - 2015: EER = 9.5, IEER = 11, variable-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 760+ kBtu/h, EER = 9.5, IEER = 11, EIR = 0.297, variable-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 760+ kBtu/h, EER = 11, min IEER = 12.3, EIR = 0.249, variable-speed fan, with economizer | PreNRes-PVVAC-gte760kBtu/h-VarSpHorP-E9.2to9.7-Econ | StdNRes-PVVAC-gte760kBtu/h-VarSpP-E9.7-Econ | MsrNRes-PVVAC-gte760kBtu/h-VarSpP-E11.0-Econ | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | EER-rated packaged air conditioner, size range: 760 - kBtu/h, EER = 12, min IEER = 13.8, EIR = 0.224, fan W/cfm = 0.61, variable-speed fan, with economizer | DEER2023 | D23v0 | 2021-11-01 20:02 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | Com EER-rated packaged air conditioner, 760+ kBtu/h; Pre-2005: EER = 9.2, variable-speed fan, w/economizer; 2006 - 2009: EER = 9.2, variable-speed fan, w/economizer; 2010 - 2013: EER = 9.5, variable-speed fan, w/economizer; 2014 - 2015: EER = 9.5, IEER = 11, variable-speed fan, w/economizer | Com EER-rated packaged air conditioner, size range: 760+ kBtu/h, EER = 9.5, IEER = 11, EIR = 0.297, variable-speed fan, with economizer | Com EER-rated packaged air conditioner, size range: 760+ kBtu/h, EER = 12, min IEER = 13.8, EIR = 0.224, variable-speed fan, with economizer | PreNRes-PVVAC-gte760kBtu/h-VarSpHorP-E9.2to9.7-Econ | StdNRes-PVVAC-gte760kBtu/h-VarSpP-E9.7-Econ | MsrNRes-PVVAC-gte760kBtu/h-VarSpP-E12.0-Econ | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-15p0seer-8p2hspf | Commercial SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 15.0 (HSPF = 8.2), EIR = 0.222, fan W/cfm = 0.28, one-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-15p0seer-8p2hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 18tolt33 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 15 (HSPF = 8.2), EIR = 0.222, fan W/cfm = 0.28, one-speed fan, without economizer | NRes-PkgHP-18tolt33kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-18tolt33kBtuh-S14.0-H8.0-1Sp | NRes-PkgHP-18tolt33kBtuh-S15.0-H8.2-1Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-16p0seer-8p5hspf | Commercial SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 16.0 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-16p0seer-8p5hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 18tolt33 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | NRes-PkgHP-18tolt33kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-18tolt33kBtuh-S14.0-H8.0-1Sp | NRes-PkgHP-18tolt33kBtuh-S16.0-H8.5-2Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-17p0seer-9p0hspf | Commercial SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 17.0 (HSPF = 9.0), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-17p0seer-9p0hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 18tolt33 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 17 (HSPF = 9.0), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, without economizer | NRes-PkgHP-18tolt33kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-18tolt33kBtuh-S14.0-H8.0-1Sp | NRes-PkgHP-18tolt33kBtuh-S17.0-H9.0-2Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-15p0seer-8p2hspf-wEcono | Commercial SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 15.0 (HSPF = 8.2), EIR = 0.230, fan W/cfm = 0.28, one-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-03 17:07 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-15p0seer-8p2hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 33 - lt55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 15 (HSPF = 8.2), EIR = 0.230, fan W/cfm = 0.28, one-speed fan, with economizer | NRes-PkgHP-33tolt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-33tolt55kBtuh-S14.0-H8.0-1Sp-wEcon | NRes-PkgHP-33tolt55kBtuh-S15.0-H8.2-1Sp-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Set ClaimSpec and FilingSpec flags to TRUE | CZ2022 | None | TRUE
2023 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-16p0seer-8p5hspf-wEcono | Commercial SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 16.0 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-03 17:07 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-16p0seer-8p5hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 33 - lt55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-PkgHP-33tolt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-33tolt55kBtuh-S14.0-H8.0-1Sp-wEcon | NRes-PkgHP-33tolt55kBtuh-S16.0-H8.5-2Sp-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Set ClaimSpec and FilingSpec flags to TRUE | CZ2022 | None | TRUE
2023 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-17p0seer-9p0hspf-wEcono | Commercial SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 17.0 (HSPF = 9.0), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-03 17:07 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-17p0seer-9p0hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 33 - lt55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 17 (HSPF = 9.0), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-PkgHP-33tolt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-33tolt55kBtuh-S14.0-H8.0-1Sp-wEcon | NRes-PkgHP-33tolt55kBtuh-S17.0-H9.0-2Sp-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Set ClaimSpec and FilingSpec flags to TRUE | CZ2022 | None | TRUE
2023 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-PreEconByVint | Commercial SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 15.0 (HSPF = 8.2), EIR = 0.256, fan W/cfm = 0.25, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 55-65 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), two-speed fan, w/economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 15.0 (HSPF = 8.2), EIR = 0.256, fan W/cfm = 0.25, two-speed fan, with economizer | PreNRes-PkgHP-55-65kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp-EconByVint | StdNRes-PkgHP-55to65kBtuh-S14.0-H8.0-2Sp-Econ | MsrNRes-PkgHP-55to65kBtuh-S15.0-H8.2-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono | Commercial SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 15.0 (HSPF = 8.2), EIR = 0.256, fan W/cfm = 0.25, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 55-65 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, w/economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, w/economizer; Recent: SEER = 14.0 (HSPF = 8.0), two-speed fan, w/economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 15.0 (HSPF = 8.2), EIR = 0.256, fan W/cfm = 0.25, two-speed fan, with economizer | PreNRes-PkgHP-55-65kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp-Econ | StdNRes-PkgHP-55to65kBtuh-S14.0-H8.0-2Sp-Econ | MsrNRes-PkgHP-55to65kBtuh-S15.0-H8.2-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-PreEconByVint | Commercial SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 16.0 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 55-65 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), two-speed fan, w/economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | PreNRes-PkgHP-55-65kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp-EconByVint | StdNRes-PkgHP-55to65kBtuh-S14.0-H8.0-2Sp-Econ | MsrNRes-PkgHP-55to65kBtuh-S16.0-H8.5-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono | Commercial SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 16.0 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 55-65 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, w/economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, w/economizer; Recent: SEER = 14.0 (HSPF = 8.0), two-speed fan, w/economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | PreNRes-PkgHP-55-65kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp-Econ | StdNRes-PkgHP-55to65kBtuh-S14.0-H8.0-2Sp-Econ | MsrNRes-PkgHP-55to65kBtuh-S16.0-H8.5-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-PreEconByVint | Commercial SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 17.0 (HSPF = 9.0), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 55-65 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), two-speed fan, w/economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | PreNRes-PkgHP-55-65kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp-EconByVint | StdNRes-PkgHP-55to65kBtuh-S14.0-H8.0-2Sp-Econ | MsrNRes-PkgHP-55to65kBtuh-S17.0-H9.0-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono | Commercial SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 17.0 (HSPF = 9.0), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 55-65 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, w/economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, w/economizer; Recent: SEER = 14.0 (HSPF = 8.0), two-speed fan, w/economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 55 - 65 kBtu/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | PreNRes-PkgHP-55-65kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp-Econ | StdNRes-PkgHP-55to65kBtuh-S14.0-H8.0-2Sp-Econ | MsrNRes-PkgHP-55to65kBtuh-S17.0-H9.0-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | Commercial SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 15.0 (HSPF = 8.2), EIR = 0.226, fan W/cfm = 0.29, one-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:39 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, less than 55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer; | Com SEER-rated packaged heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, fan W/cfm = 0.29, one-speed fan, without economizer | PreNRes-PkgHP-lt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | StdNRes-PkgHP-lt55kBtuh-S14.0-H8.0-1Sp | MsrNRes-PkgHP-lt55kBtuh-S15.0-H8.2-1Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | Commercial SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 16.0 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:39 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, less than 55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer; | Com SEER-rated packaged heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | PreNRes-PkgHP-lt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | StdNRes-PkgHP-lt55kBtuh-S14.0-H8.0-1Sp | MsrNRes-PkgHP-lt55kBtuh-S16.0-H8.5-2Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | Commercial SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 17.0 (HSPF = 9.0), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:39 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, less than 55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer; | Com SEER-rated packaged heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | PreNRes-PkgHP-lt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | StdNRes-PkgHP-lt55kBtuh-S14.0-H8.0-1Sp | MsrNRes-PkgHP-lt55kBtuh-S17.0-H9.0-2Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airHP-Split-18tolt33kBtuh-15p0seer-8p7hspf | Commercial SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 15.0 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.28, one-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airHP-Split-18tolt33kBtuh-15p0seer-8p7hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 18tolt33 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.28, one-speed fan, without economizer | NRes-SplitHP-18tolt33kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-18tolt33kBtuh-S14.0-H8.2-1Sp | NRes-SplitHP-18tolt33kBtuh-S15.0-H8.7-1Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airHP-Split-18tolt33kBtuh-16p0seer-9p0hspf | Commercial SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 16.0 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airHP-Split-18tolt33kBtuh-16p0seer-9p0hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 18tolt33 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | NRes-SplitHP-18tolt33kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-18tolt33kBtuh-S14.0-H8.2-1Sp | NRes-SplitHP-18tolt33kBtuh-S16.0-H9.0-2Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airHP-Split-18tolt33kBtuh-17p0seer-9p4hspf | Commercial SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 17.0 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airHP-Split-18tolt33kBtuh-17p0seer-9p4hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 18tolt33 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | NRes-SplitHP-18tolt33kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-18tolt33kBtuh-S14.0-H8.2-1Sp | NRes-SplitHP-18tolt33kBtuh-S17.0-H9.4-2Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airHP-Split-18tolt33kBtuh-18p0seer-9p7hspf | Commercial SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 18.0 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2023-09-22 12:10 | NE-HVAC-airHP-Split-18tolt33kBtuh-18p0seer-9p7hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 18tolt33 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | NRes-SplitHP-18tolt33kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-18tolt33kBtuh-S14.0-H8.2-1Sp | NRes-SplitHP-18tolt33kBtuh-S18.0-H9.7-2Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
1790 | NE-HVAC-airHP-Split-33tolt55kBtuh-15p0seer-8p7hspf-wEcono | Commercial SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 15.0 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.28, one-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-26 16:30 | NE-HVAC-airHP-Split-33tolt55kBtuh-15p0seer-8p7hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 33 - lt55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.283, one-speed fan, with economizer | NRes-SplitHP-33tolt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-33tolt55kBtuh-S14.0-H8.2-1Sp-wEcono | NRes-SplitHP-33tolt55kBtuh-S15.0-H8.7-1Sp-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-26 16:30 | Narrowed size range not requiring economizers per Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
1791 | NE-HVAC-airHP-Split-33tolt55kBtuh-16p0seer-9p0hspf-wEcono | Commercial SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 16.0 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-26 16:30 | NE-HVAC-airHP-Split-33tolt55kBtuh-16p0seer-9p0hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 33 - lt55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitHP-33tolt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-33tolt55kBtuh-S14.0-H8.2-1Sp-wEcono | NRes-SplitHP-33tolt55kBtuh-S16.0-H9.0-2Sp-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-26 16:30 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
1792 | NE-HVAC-airHP-Split-33tolt55kBtuh-17p0seer-9p4hspf-wEcono | Commercial SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 17.0 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-26 16:30 | NE-HVAC-airHP-Split-33tolt55kBtuh-17p0seer-9p4hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 33 - lt55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitHP-33tolt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-33tolt55kBtuh-S14.0-H8.2-1Sp-wEcono | NRes-SplitHP-33tolt55kBtuh-S17.0-H9.4-2Sp-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-26 16:30 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
1793 | NE-HVAC-airHP-Split-33tolt55kBtuh-18p0seer-9p7hspf-wEcono | Commercial SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 18.0 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2023-07-26 16:30 | NE-HVAC-airHP-Split-33tolt55kBtuh-18p0seer-9p7hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 33 - lt55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitHP-33tolt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-33tolt55kBtuh-S14.0-H8.2-1Sp-wEcono | NRes-SplitHP-33tolt55kBtuh-S18.0-H9.7-2Sp-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2023-10-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-26 16:30 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team |  | CZ2022 | None | TRUE
2023 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-PreEconByVint | Commercial SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 15.0 (HSPF = 8.7), EIR = 0.256, fan W/cfm = 0.25, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 55-65 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), two-speed fan, w/economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, fan W/cfm = 0.25, two-speed fan, with economizer | PreNRes-SplitHP-55to65kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp-EconByVint | StdNRes-SplitHP-55to65kBtuh-S14.0-H8.2-2Sp-Econ | MsrNRes-SplitHP-55to65kBtuh-S15.0-H8.7-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono | Commercial SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 15.0 (HSPF = 8.7), EIR = 0.256, fan W/cfm = 0.25, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 55-65 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, w/economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, w/economizer; Recent: SEER = 14.0 (HSPF = 8.2), two-speed fan, w/economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, fan W/cfm = 0.25, two-speed fan, with economizer | PreNRes-SplitHP-55to65kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp-Econ | StdNRes-SplitHP-55to65kBtuh-S14.0-H8.2-2Sp-Econ | MsrNRes-SplitHP-55to65kBtuh-S15.0-H8.7-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-PreEconByVint | Commercial SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 16.0 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 55-65 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), two-speed fan, w/economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | PreNRes-SplitHP-55to65kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp-EconByVint | StdNRes-SplitHP-55to65kBtuh-S14.0-H8.2-2Sp-Econ | MsrNRes-SplitHP-55to65kBtuh-S16.0-H9.0-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono | Commercial SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 16.0 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 55-65 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, w/economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, w/economizer; Recent: SEER = 14.0 (HSPF = 8.2), two-speed fan, w/economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | PreNRes-SplitHP-55to65kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp-Econ | StdNRes-SplitHP-55to65kBtuh-S14.0-H8.2-2Sp-Econ | MsrNRes-SplitHP-55to65kBtuh-S16.0-H9.0-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-PreEconByVint | Commercial SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 17.0 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 55-65 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), two-speed fan, w/economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | PreNRes-SplitHP-55to65kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp-EconByVint | StdNRes-SplitHP-55to65kBtuh-S14.0-H8.2-2Sp-Econ | MsrNRes-SplitHP-55to65kBtuh-S17.0-H9.4-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono | Commercial SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 17.0 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 55-65 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, w/economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, w/economizer; Recent: SEER = 14.0 (HSPF = 8.2), two-speed fan, w/economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | PreNRes-SplitHP-55to65kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp-Econ | StdNRes-SplitHP-55to65kBtuh-S14.0-H8.2-2Sp-Econ | MsrNRes-SplitHP-55to65kBtuh-S17.0-H9.4-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-PreEconByVint | Commercial SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 18.0 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-PreEconByVint | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 55-65 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), two-speed fan, w/economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | PreNRes-SplitHP-55to65kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp-EconByVint | StdNRes-SplitHP-55to65kBtuh-S14.0-H8.2-2Sp-Econ | MsrNRes-SplitHP-55to65kBtuh-S18.0-H9.7-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono | Commercial SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 18.0 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v0 | 2022-02-08 17:28 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 55-65 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, w/economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, w/economizer; Recent: SEER = 14.0 (HSPF = 8.2), two-speed fan, w/economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.27, fan W/cfm = 0.29, two-speed fan, with economizer | Com SEER-rated split heat pump, size range: 55 - 65 kBtu/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | PreNRes-SplitHP-55to65kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp-Econ | StdNRes-SplitHP-55to65kBtuh-S14.0-H8.2-2Sp-Econ | MsrNRes-SplitHP-55to65kBtuh-S18.0-H9.7-2Sp-Econ | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team |  |  |  | FALSE
2023 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | Commercial SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 15.0 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.25, one-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:51 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, less than 55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.25, one-speed fan, without economizer | PreNRes-SplitHP-lt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | StdNRes-SplitHP-lt55kBtuh-S14.0-H8.2-1Sp | MsrNRes-SplitHP-lt55kBtuh-S15.0-H8.7-1Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | Commercial SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 16.0 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:51 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, less than 55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | PreNRes-SplitHP-lt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | StdNRes-SplitHP-lt55kBtuh-S14.0-H8.2-1Sp | MsrNRes-SplitHP-lt55kBtuh-S16.0-H9.0-2Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | Commercial SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 17.0 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:51 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, less than 55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | PreNRes-SplitHP-lt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | StdNRes-SplitHP-lt55kBtuh-S14.0-H8.2-1Sp | MsrNRes-SplitHP-lt55kBtuh-S17.0-H9.4-2Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | Commercial SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 18.0 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2023-07-02 20:51 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, less than 55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | PreNRes-SplitHP-lt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | StdNRes-SplitHP-lt55kBtuh-S14.0-H8.2-1Sp | MsrNRes-SplitHP-lt55kBtuh-S18.0-H9.7-2Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2023-09-30 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Expired due to lack of economizer required by 2022 Title-24 |  |  | TRUE
2023 | NE-HVAC-airHP-SpltPkg-135to239kBtuh-10p8eer-3p48cop | Commercial EER-rated Heat Pumps, Size Range: 135-239 kBtu/h, EER = 10.8, COP = 3.48; w/Econo; 2-spd Fan | DEER2023 | D23 v1 | 2023-05-12 09:20 | NE-HVAC-airHP-SpltPkg-135to239kBtuh-10p8eer-3p48cop | Deem-DEER | Standard | None |  |  | None |  | TRUE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgEER |  | HVAC-airHP | Splt/Pkg HP (135-239 kBtuh) EER and COP based on vintage | Splt/Pkg HP EER = 10.4 (135-239 kBtuh), COP = 3.3; w/Econo; 2-spd Fan | Splt/Pkg HP EER = 10.8 (135-239 kBtuh), COP = 3.48; w/Econo; 2-spd Fan | HVAC-airHP-SpltPkg-135to239kBtuh-ByVint | HVAC-airHP-SpltPkg-135to239kBtuh-10.4eer-3.30cop-wEcono | HVAC-airHP-SpltPkg-135to239kBtuh-10.8eer-3p48cop-wEcono | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-10-19 12:04 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Changing IsProposed to false for DEER 2023 records. | CZ2022 | None | FALSE
2023 | NE-HVAC-airHP-SpltPkg-135to239kBtuh-11p2eer-3p51cop | Commercial EER-rated Heat Pumps, Size Range: 135-239 kBtu/h, EER = 11.2, COP = 3.51; w/Econo; 2-spd Fan | DEER2023 | D23 v1 | 2023-05-12 09:20 | NE-HVAC-airHP-SpltPkg-135to239kBtuh-11p2eer-3p51cop | Deem-DEER | Standard | None |  |  | None |  | TRUE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgEER |  | HVAC-airHP | Splt/Pkg HP (135-239 kBtuh) EER and COP based on vintage | Splt/Pkg HP EER = 10.4 (135-239 kBtuh), COP = 3.3; w/Econo; 2-spd Fan | Splt/Pkg HP EER = 11.2 (135-239 kBtuh), COP = 3.51; w/Econo; 2-spd Fan | HVAC-airHP-SpltPkg-135to239kBtuh-ByVint | HVAC-airHP-SpltPkg-135to239kBtuh-10.4eer-3.30cop-wEcono | HVAC-airHP-SpltPkg-135to239kBtuh-11.2eer-3p51cop-wEcono | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-10-19 12:04 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Changing IsProposed to false for DEER 2023 records. | CZ2022 | None | FALSE
2023 | NE-HVAC-airHP-SpltPkg-240to759kBtuh-10p0eer-3p30cop | Commercial EER-rated Heat Pumps, Size Range: 240-759 kBtu/h, EER = 10.0, COP = 3.20; w/Econo; 2-spd Fan | DEER2023 | D23 v1 | 2023-01-27 14:54 | NE-HVAC-airHP-SpltPkg-240to759kBtuh-10p0eer-3p30cop | Deem-DEER | Standard | None |  |  | None |  | TRUE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgEER |  | HVAC-airHP | Pkg HP (240-759 kBtuh) EER and COP based on vintage | Pkg HP EER = 9.3 (240-759 kBtuh), COP = 3.2; w/Econo; 2-spd Fan | Pkg HP EER = 10.0 (240-759 kBtuh), COP = 3.2; w/Econo; 2-spd Fan | HVAC-airHP-SpltPkg-240to759kBtuh-ByVint | HVAC-airHP-SpltPkg-240to759kBtuh-9.3eer-3.20cop-wEcono | HVAC-airHP-SpltPkg-240to759kBtuh-10.0eer-3p2cop-wEcono | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-10-19 12:04 | Re-simulated using CZ2022 weather data, Modeled using COP = 3.3 although descriptions say 3.2 to be consistent with the federal minimum. (It is thought that Title 24 erroneously pre-empted federal code by requiring COP = 3.3.) | Deemed Ex Ante Team | Aligning WeatherSim and FuelSubID with corresponding EnergyImpact records. | CZ2022 | None | FALSE
2023 | NE-HVAC-airHP-SpltPkg-240to759kBtuh-9p7eer-3p30cop | Commercial EER-rated Heat Pumps, Size Range: 240-759 kBtu/h, EER = 9.7, COP = 3.20; w/Econo; 2-spd Fan | DEER2023 | D23 v1 | 2023-01-27 14:54 | NE-HVAC-airHP-SpltPkg-240to759kBtuh-9p7eer-3p30cop | Deem-DEER | Standard | None |  |  | None |  | TRUE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgEER |  | HVAC-airHP | Pkg HP (240-759 kBtuh) EER and COP based on vintage | Pkg HP EER = 9.3 (240-759 kBtuh), COP = 3.2; w/Econo; 2-spd Fan | Pkg HP EER = 9.7 (240-759 kBtuh), COP = 3.2; w/Econo; 2-spd Fan | HVAC-airHP-SpltPkg-240to759kBtuh-ByVint | HVAC-airHP-SpltPkg-240to759kBtuh-9.3eer-3.20cop-wEcono | HVAC-airHP-SpltPkg-240to759kBtuh-9.7eer-3p2cop-wEcono | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-10-19 12:04 | Re-simulated using CZ2022 weather data, Modeled using COP = 3.3 although descriptions say 3.2 to be consistent with the federal minimum. (It is thought that Title 24 erroneously pre-empted federal code by requiring COP = 3.3.) | Deemed Ex Ante Team | Aligning WeatherSim and FuelSubID with corresponding EnergyImpact records. | CZ2022 | None | FALSE
2023 | NE-HVAC-airHP-SpltPkg-65to134kBtuh-11p5eer-3p50cop | Commercial EER-rated Heat Pumps, Size Range: 65 - 135 kBtu/h, EER = 11.5, COP = 3.50; w/Econo; 2-spd Fan | DEER2023 | D23 v1 | 2023-05-12 09:20 | NE-HVAC-airHP-SpltPkg-65to134kBtuh-11p5eer-3p50cop | Deem-DEER | Standard | None |  |  | None |  | TRUE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgEER |  | HVAC-airHP | Splt/Pkg HP (65-135 kBtuh) EER and COP based on vintage | Splt/Pkg HP EER = 11.0 (65-135 kBtuh), COP = 3.4; w/Econo; 2-spd Fan | Splt/Pkg HP EER = 11.5 (65-135 kBtuh), COP = 3.50; w/Econo; 2-spd Fan | HVAC-airHP-SpltPkg-65to134kBtuh-ByVint | HVAC-airHP-SpltPkg-65to134kBtuh-11.0eer-3.40cop-wEcono | HVAC-airHP-SpltPkg-65to134kBtuh-11.5eer-3p50cop-wEcono | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-10-19 12:04 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Changing IsProposed to false for DEER 2023 records. | CZ2022 | None | FALSE
2023 | NE-HVAC-airHP-SpltPkg-65to134kBtuh-11p5eer-3p50cop-wPreEcono | Commercial EER-rated Heat Pumps, Size Range: 65 - 135 kBtu/h, EER = 11.5, COP = 3.50; w/Econo; 2-spd Fan | DEER2023 | D23 v1 | 2023-05-12 09:20 | NE-HVAC-airHP-SpltPkg-65to134kBtuh-11p5eer-3p50cop-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | TRUE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgEER |  | HVAC-airHP | Splt/Pkg HP (65-135 kBtuh) EER and COP based on vintage, w/Econo | Splt/Pkg HP EER = 11.0 (65-135 kBtuh), COP = 3.4; w/Econo; 2-spd Fan | Splt/Pkg HP EER = 11.5 (65-135 kBtuh), COP = 3.50; w/Econo; 2-spd Fan | HVAC-airHP-SpltPkg-65to134kBtuh-ByVint-PreEcono | HVAC-airHP-SpltPkg-65to134kBtuh-11.0eer-3.40cop-wEcono | HVAC-airHP-SpltPkg-65to134kBtuh-11.5eer-3p50cop-wEcono | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-10-19 12:04 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Changing IsProposed to false for DEER 2023 records. | CZ2022 | None | FALSE
2023 | NE-HVAC-airHP-SpltPkg-65to134kBtuh-12p0eer-3p55cop | Commercial EER-rated Heat Pumps, Size Range: 65 - 135 kBtu/h, EER = 12.0, COP = 3.55; w/Econo; 2-spd Fan | DEER2023 | D23 v1 | 2023-05-12 09:20 | NE-HVAC-airHP-SpltPkg-65to134kBtuh-12p0eer-3p55cop | Deem-DEER | Standard | None |  |  | None |  | TRUE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgEER |  | HVAC-airHP | Splt/Pkg HP (65-135 kBtuh) EER and COP based on vintage | Splt/Pkg HP EER = 11.0 (65-135 kBtuh), COP = 3.4; w/Econo; 2-spd Fan | Splt/Pkg HP EER = 12.0 (65-135 kBtuh), COP = 3.55; w/Econo; 2-spd Fan | HVAC-airHP-SpltPkg-65to134kBtuh-ByVint | HVAC-airHP-SpltPkg-65to134kBtuh-11.0eer-3.40cop-wEcono | HVAC-airHP-SpltPkg-65to134kBtuh-12.0eer-3p55cop-wEcono | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-10-19 12:04 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Changing IsProposed to false for DEER 2023 records. | CZ2022 | None | FALSE
2023 | NE-HVAC-airHP-SpltPkg-65to134kBtuh-12p0eer-3p55cop-wPreEcono | Commercial EER-rated Heat Pumps, Size Range: 65 - 135 kBtu/h, EER = 12.0, COP = 3.55; w/Econo; 2-spd Fan | DEER2023 | D23 v1 | 2023-01-27 14:54 | NE-HVAC-airHP-SpltPkg-65to134kBtuh-12p0eer-3p55cop-wPreEcono | Deem-DEER | Standard | None |  |  | None |  | TRUE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgEER |  | HVAC-airHP | Splt/Pkg HP (65-135 kBtuh) EER and COP based on vintage, w/Econo | Splt/Pkg HP EER = 11.0 (65-135 kBtuh), COP = 3.4; w/Econo; 2-spd Fan | Splt/Pkg HP EER = 12.0 (65-135 kBtuh), COP = 3.55; w/Econo; 2-spd Fan | HVAC-airHP-SpltPkg-65to134kBtuh-ByVint-PreEcono | HVAC-airHP-SpltPkg-65to134kBtuh-11.0eer-3.40cop-wEcono | HVAC-airHP-SpltPkg-65to134kBtuh-12.0eer-3p55cop-wEcono | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  | None | 2023-01-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-10-19 12:04 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Aligning WeatherSim and FuelSubID with corresponding EnergyImpact records. | CZ2022 | None | FALSE

## Change ExpiryDate=2024-01-31
VersionSource | MeasureID | StartDate | ExpiryDate
D23v0 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | 2023-01-01 | 2023-09-30 | ('NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer', | ('NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer','NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer','NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer','NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer','NE-HVAC-airAC-Split-lt45kBtuh-15p0seer','NE-HVAC-airAC-Split-lt45kBtuh-16p0seer','NE-HVAC-airAC-Split-lt45kBtuh-17p0seer','NE-HVAC-airAC-Split-lt45kBtuh-18p0seer','NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf','NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf','NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf','NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf','NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf','NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf','NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf') | ('NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer','NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer','NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer','NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer','NE-HVAC-airAC-Split-lt45kBtuh-15p0seer','NE-HVAC-airAC-Split-lt45kBtuh-16p0seer','NE-HVAC-airAC-Split-lt45kBtuh-17p0seer','NE-HVAC-airAC-Split-lt45kBtuh-18p0seer','NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf','NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf','NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf','NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf','NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf','NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf','NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf')
D23v0 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer',
D23v0 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer',
D23v0 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer',
D23v0 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airAC-Split-lt45kBtuh-15p0seer',
D23v0 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airAC-Split-lt45kBtuh-16p0seer',
D23v0 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airAC-Split-lt45kBtuh-17p0seer',
D23v0 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airAC-Split-lt45kBtuh-18p0seer',
D23v0 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf',
D23v0 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf',
D23v0 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf',
D23v0 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf',
D23v0 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf',
D23v0 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf',
D23v0 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | 2023-01-01 | 2023-09-30 | 'NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf')
Grand Total

## Changed ExpiryDates
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | StdCostID | RUL_ID | LegacyID | MeasQualifierGroup | StartDate | ExpiryDate | ReviewStatus | MeasID_SCE | MeasID_PGE | MeasID_SDG | MeasID_SCG | MeasType | ReviewComment | FilingSpec | ClaimSpec | IsProposed | LastModBy | Created | CreatedComment | CreatedBy | LastModComment | WeatherSim | FuelSubID
2023 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | Com SEER-rated packaged air conditioner, size range: 18 - 55 kBtu/h, SEER = 15 (EER = 12.9), EIR = 0.234, fan W/cfm = 0.25, one-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 15 (EER = 12.9), EIR = 0.234, fan W/cfm = 0.25, one-speed fan, without economizer | PreNResPkgAC-lt55kBtu/h-1Sp-S11.6to14.0 | StdNResPkgAC-lt55kBtu/h-1Sp-S14.0 | MsrNResPkgAC-lt55kBtu/h-1Sp-S15.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | Com SEER-rated packaged air conditioner, size range: 18 - 55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, less than 55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | PreNResPkgAC-lt55kBtu/h-1Sp-S11.6to14.0 | StdNResPkgAC-lt55kBtu/h-1Sp-S14.0 | MsrNResPkgAC-lt55kBtu/h-2Sp-S16.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | Com SEER-rated packaged air conditioner, size range: 18 - 55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | PreNResPkgAC-lt55kBtu/h-1Sp-S11.6to14.0 | StdNResPkgAC-lt55kBtu/h-1Sp-S14.0 | MsrNResPkgAC-lt55kBtu/h-2Sp-S17.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | Com SEER-rated packaged air conditioner, size range: 18 - 55 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner,18-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged air conditioners, size range: 18 - 55 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | PreNResPkgAC-lt55kBtu/h-1Sp-S11.6to14.0 | StdNResPkgAC-lt55kBtu/h-1Sp-S14.0 | MsrNResPkgAC-lt55kBtu/h-2Sp-S18.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 19:45 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | Com SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, fan W/cfm = 0.25, one-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, less than 45 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/cfm = 0.25, one-speed fan, without economizers | PreNRes-SplitAC-lt45kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-lt45kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-lt45kBtu/h-1Sp-S15.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | Com SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, less than 45 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/cfm = 0.27, two-speed fan, without economizers | PreNRes-SplitAC-lt45kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-lt45kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-lt45kBtu/h-1Sp-S16.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | Com SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, less than 45 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/cfm = 0.27, two-speed fan, without economizers | PreNRes-SplitAC-lt45kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-lt45kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-lt45kBtu/h-1Sp-S17.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | Com SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, less than 45 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/cfm = 0.27, two-speed fan, without economizers | PreNRes-SplitAC-lt45kBtu/h-1Sp-S11.5toS14.0 | StdNRes-SplitAC-lt45kBtu/h-1Sp-S14.0 | MsrNRes-SplitAC-lt45kBtu/h-1Sp-S18.0 | Available |  | TRUE | TRUE |  |  |  | HVAC-airAC |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2021-11-01 20:02 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | Commercial SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 15.0 (HSPF = 8.2), EIR = 0.226, fan W/cfm = 0.29, one-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, less than 55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer; | Com SEER-rated packaged heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, fan W/cfm = 0.29, one-speed fan, without economizer | PreNRes-PkgHP-lt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | StdNRes-PkgHP-lt55kBtuh-S14.0-H8.0-1Sp | MsrNRes-PkgHP-lt55kBtuh-S15.0-H8.2-1Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | Commercial SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 16.0 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, less than 55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer; | Com SEER-rated packaged heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | PreNRes-PkgHP-lt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | StdNRes-PkgHP-lt55kBtuh-S14.0-H8.0-1Sp | MsrNRes-PkgHP-lt55kBtuh-S16.0-H8.5-2Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | Commercial SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 17.0 (HSPF = 9.0), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, less than 55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer; | Com SEER-rated packaged heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18 - 65 kBtu/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | PreNRes-PkgHP-lt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | StdNRes-PkgHP-lt55kBtuh-S14.0-H8.0-1Sp | MsrNRes-PkgHP-lt55kBtuh-S17.0-H9.0-2Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | Commercial SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 15.0 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.25, one-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, less than 55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.25, one-speed fan, without economizer | PreNRes-SplitHP-lt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | StdNRes-SplitHP-lt55kBtuh-S14.0-H8.2-1Sp | MsrNRes-SplitHP-lt55kBtuh-S15.0-H8.7-1Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | Commercial SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 16.0 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, less than 55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | PreNRes-SplitHP-lt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | StdNRes-SplitHP-lt55kBtuh-S14.0-H8.2-1Sp | MsrNRes-SplitHP-lt55kBtuh-S16.0-H9.0-2Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | Commercial SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 17.0 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, less than 55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | PreNRes-SplitHP-lt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | StdNRes-SplitHP-lt55kBtuh-S14.0-H8.2-1Sp | MsrNRes-SplitHP-lt55kBtuh-S17.0-H9.4-2Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24
2023 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | Commercial SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 18.0 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v0 | 2025-01-14 12:45 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, less than 55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18 - 55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18 - 65 kBtu/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | PreNRes-SplitHP-lt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | StdNRes-SplitHP-lt55kBtuh-S14.0-H8.2-1Sp | MsrNRes-SplitHP-lt55kBtuh-S18.0-H9.7-2Sp | Available |  | TRUE | TRUE |  |  |  | HVAC-airHP |  |  | 2023-01-01 | 2024-01-31 | [5 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2022-02-08 17:28 | Re-simulated using CZ2022 weather data | Deemed Ex Ante Team | Pushed back ExpiryDate; expired due to lack of economizer required by 2022 Title-24

## Change StartDate=2024-02-01
VersionSource | MeasureID | StartDate | ExpiryDate
D23v1a | NE-HVAC-airAC-Pkg-18tolt33kBtuh-15p0seer | 2023-10-01 | (blank) | ('NE-HVAC-airAC-Pkg-18tolt33kBtuh-15p0seer', | ('NE-HVAC-airAC-Pkg-18tolt33kBtuh-15p0seer','NE-HVAC-airAC-Pkg-18tolt33kBtuh-16p0seer','NE-HVAC-airAC-Pkg-18tolt33kBtuh-17p0seer','NE-HVAC-airAC-Pkg-18tolt33kBtuh-18p0seer','NE-HVAC-airAC-Split-18tolt33kBtuh-15p0seer','NE-HVAC-airAC-Split-18tolt33kBtuh-16p0seer','NE-HVAC-airAC-Split-18tolt33kBtuh-17p0seer','NE-HVAC-airAC-Split-18tolt33kBtuh-18p0seer','NE-HVAC-airHP-Pkg-18tolt33kBtuh-15p0seer-8p2hspf','NE-HVAC-airHP-Pkg-18tolt33kBtuh-16p0seer-8p5hspf','NE-HVAC-airHP-Pkg-18tolt33kBtuh-17p0seer-9p0hspf','NE-HVAC-airHP-Split-18tolt33kBtuh-15p0seer-8p7hspf','NE-HVAC-airHP-Split-18tolt33kBtuh-16p0seer-9p0hspf','NE-HVAC-airHP-Split-18tolt33kBtuh-17p0seer-9p4hspf','NE-HVAC-airHP-Split-18tolt33kBtuh-18p0seer-9p7hspf','NE-HVAC-airAC-Pkg-33tolt55kBtuh-15p0seer-wEcono','NE-HVAC-airAC-Pkg-33tolt55kBtuh-16p0seer-wEcono','NE-HVAC-airAC-Pkg-33tolt55kBtuh-17p0seer-wEcono','NE-HVAC-airAC-Pkg-33tolt55kBtuh-18p0seer-wEcono','NE-HVAC-airAC-Split-33tolt55kBtuh-15p0seer-wEcono','NE-HVAC-airAC-Split-33tolt55kBtuh-16p0seer-wEcono','NE-HVAC-airAC-Split-33tolt55kBtuh-17p0seer-wEcono','NE-HVAC-airAC-Split-33tolt55kBtuh-18p0seer-wEcono','NE-HVAC-airHP-Pkg-33tolt55kBtuh-15p0seer-8p2hspf-wEcono','NE-HVAC-airHP-Pkg-33tolt55kBtuh-16p0seer-8p5hspf-wEcono','NE-HVAC-airHP-Pkg-33tolt55kBtuh-17p0seer-9p0hspf-wEcono','NE-HVAC-airHP-Split-33tolt55kBtuh-15p0seer-8p7hspf-wEcono','NE-HVAC-airHP-Split-33tolt55kBtuh-16p0seer-9p0hspf-wEcono','NE-HVAC-airHP-Split-33tolt55kBtuh-17p0seer-9p4hspf-wEcono','NE-HVAC-airHP-Split-33tolt55kBtuh-18p0seer-9p7hspf-wEcono') | ('NE-HVAC-airAC-Pkg-18tolt33kBtuh-15p0seer','NE-HVAC-airAC-Pkg-18tolt33kBtuh-16p0seer','NE-HVAC-airAC-Pkg-18tolt33kBtuh-17p0seer','NE-HVAC-airAC-Pkg-18tolt33kBtuh-18p0seer','NE-HVAC-airAC-Split-18tolt33kBtuh-15p0seer','NE-HVAC-airAC-Split-18tolt33kBtuh-16p0seer','NE-HVAC-airAC-Split-18tolt33kBtuh-17p0seer','NE-HVAC-airAC-Split-18tolt33kBtuh-18p0seer','NE-HVAC-airHP-Pkg-18tolt33kBtuh-15p0seer-8p2hspf','NE-HVAC-airHP-Pkg-18tolt33kBtuh-16p0seer-8p5hspf','NE-HVAC-airHP-Pkg-18tolt33kBtuh-17p0seer-9p0hspf','NE-HVAC-airHP-Split-18tolt33kBtuh-15p0seer-8p7hspf','NE-HVAC-airHP-Split-18tolt33kBtuh-16p0seer-9p0hspf','NE-HVAC-airHP-Split-18tolt33kBtuh-17p0seer-9p4hspf','NE-HVAC-airHP-Split-18tolt33kBtuh-18p0seer-9p7hspf','NE-HVAC-airAC-Pkg-33tolt55kBtuh-15p0seer-wEcono','NE-HVAC-airAC-Pkg-33tolt55kBtuh-16p0seer-wEcono','NE-HVAC-airAC-Pkg-33tolt55kBtuh-17p0seer-wEcono','NE-HVAC-airAC-Pkg-33tolt55kBtuh-18p0seer-wEcono','NE-HVAC-airAC-Split-33tolt55kBtuh-15p0seer-wEcono','NE-HVAC-airAC-Split-33tolt55kBtuh-16p0seer-wEcono','NE-HVAC-airAC-Split-33tolt55kBtuh-17p0seer-wEcono','NE-HVAC-airAC-Split-33tolt55kBtuh-18p0seer-wEcono','NE-HVAC-airHP-Pkg-33tolt55kBtuh-15p0seer-8p2hspf-wEcono','NE-HVAC-airHP-Pkg-33tolt55kBtuh-16p0seer-8p5hspf-wEcono','NE-HVAC-airHP-Pkg-33tolt55kBtuh-17p0seer-9p0hspf-wEcono','NE-HVAC-airHP-Split-33tolt55kBtuh-15p0seer-8p7hspf-wEcono','NE-HVAC-airHP-Split-33tolt55kBtuh-16p0seer-9p0hspf-wEcono','NE-HVAC-airHP-Split-33tolt55kBtuh-17p0seer-9p4hspf-wEcono','NE-HVAC-airHP-Split-33tolt55kBtuh-18p0seer-9p7hspf-wEcono')
D23v1a | NE-HVAC-airAC-Pkg-18tolt33kBtuh-16p0seer | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Pkg-18tolt33kBtuh-16p0seer',
D23v1a | NE-HVAC-airAC-Pkg-18tolt33kBtuh-17p0seer | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Pkg-18tolt33kBtuh-17p0seer',
D23v1a | NE-HVAC-airAC-Pkg-18tolt33kBtuh-18p0seer | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Pkg-18tolt33kBtuh-18p0seer',
D23v1a | NE-HVAC-airAC-Split-18tolt33kBtuh-15p0seer | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Split-18tolt33kBtuh-15p0seer',
D23v1a | NE-HVAC-airAC-Split-18tolt33kBtuh-16p0seer | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Split-18tolt33kBtuh-16p0seer',
D23v1a | NE-HVAC-airAC-Split-18tolt33kBtuh-17p0seer | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Split-18tolt33kBtuh-17p0seer',
D23v1a | NE-HVAC-airAC-Split-18tolt33kBtuh-18p0seer | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Split-18tolt33kBtuh-18p0seer',
D23v1a | NE-HVAC-airHP-Pkg-18tolt33kBtuh-15p0seer-8p2hspf | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Pkg-18tolt33kBtuh-15p0seer-8p2hspf',
D23v1a | NE-HVAC-airHP-Pkg-18tolt33kBtuh-16p0seer-8p5hspf | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Pkg-18tolt33kBtuh-16p0seer-8p5hspf',
D23v1a | NE-HVAC-airHP-Pkg-18tolt33kBtuh-17p0seer-9p0hspf | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Pkg-18tolt33kBtuh-17p0seer-9p0hspf',
D23v1a | NE-HVAC-airHP-Split-18tolt33kBtuh-15p0seer-8p7hspf | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Split-18tolt33kBtuh-15p0seer-8p7hspf',
D23v1a | NE-HVAC-airHP-Split-18tolt33kBtuh-16p0seer-9p0hspf | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Split-18tolt33kBtuh-16p0seer-9p0hspf',
D23v1a | NE-HVAC-airHP-Split-18tolt33kBtuh-17p0seer-9p4hspf | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Split-18tolt33kBtuh-17p0seer-9p4hspf',
D23v1a | NE-HVAC-airHP-Split-18tolt33kBtuh-18p0seer-9p7hspf | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Split-18tolt33kBtuh-18p0seer-9p7hspf',
D23v1 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-15p0seer-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Pkg-33tolt55kBtuh-15p0seer-wEcono',
D23v1 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-16p0seer-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Pkg-33tolt55kBtuh-16p0seer-wEcono',
D23v1 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-17p0seer-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Pkg-33tolt55kBtuh-17p0seer-wEcono',
D23v1 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-18p0seer-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Pkg-33tolt55kBtuh-18p0seer-wEcono',
D23v1 | NE-HVAC-airAC-Split-33tolt55kBtuh-15p0seer-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Split-33tolt55kBtuh-15p0seer-wEcono',
D23v1 | NE-HVAC-airAC-Split-33tolt55kBtuh-16p0seer-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Split-33tolt55kBtuh-16p0seer-wEcono',
D23v1 | NE-HVAC-airAC-Split-33tolt55kBtuh-17p0seer-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Split-33tolt55kBtuh-17p0seer-wEcono',
D23v1 | NE-HVAC-airAC-Split-33tolt55kBtuh-18p0seer-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airAC-Split-33tolt55kBtuh-18p0seer-wEcono',
D23v1 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-15p0seer-8p2hspf-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Pkg-33tolt55kBtuh-15p0seer-8p2hspf-wEcono',
D23v1 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-16p0seer-8p5hspf-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Pkg-33tolt55kBtuh-16p0seer-8p5hspf-wEcono',
D23v1 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-17p0seer-9p0hspf-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Pkg-33tolt55kBtuh-17p0seer-9p0hspf-wEcono',
D23v1 | NE-HVAC-airHP-Split-33tolt55kBtuh-15p0seer-8p7hspf-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Split-33tolt55kBtuh-15p0seer-8p7hspf-wEcono',
D23v1 | NE-HVAC-airHP-Split-33tolt55kBtuh-16p0seer-9p0hspf-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Split-33tolt55kBtuh-16p0seer-9p0hspf-wEcono',
D23v1 | NE-HVAC-airHP-Split-33tolt55kBtuh-17p0seer-9p4hspf-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Split-33tolt55kBtuh-17p0seer-9p4hspf-wEcono',
D23v1 | NE-HVAC-airHP-Split-33tolt55kBtuh-18p0seer-9p7hspf-wEcono | 2023-10-01 | (blank) | 'NE-HVAC-airHP-Split-33tolt55kBtuh-18p0seer-9p7hspf-wEcono')
Grand Total

## Changed StartDates
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | StdCostID | RUL_ID | LegacyID | MeasQualifierGroup | StartDate | ExpiryDate | ReviewStatus | MeasID_SCE | MeasID_PGE | MeasID_SDG | MeasID_SCG | MeasType | ReviewComment | FilingSpec | ClaimSpec | IsProposed | LastModBy | Created | CreatedComment | CreatedBy | LastModComment | WeatherSim | FuelSubID
2023 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-15p0seer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 15 (EER = 12.5), EIR = 0.222, fan W/cfm = 0.28, one-speed fan, no economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-15p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18tolt33 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18tolt33 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, no economizer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 15 (EER = 13.0), EIR = 0.222, fan W/cfm = 0.28, one-speed fan, no economizer | NRes-PkgAC-18tolt33kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-18tolt33kBtuh-1Sp-S14.0 | NRes-PkgAC-18tolt33kBtuh-1Sp-S15.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:09 | Narrowed size range not requiring economizers per Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-16p0seer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, no economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-16p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18tolt33 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18tolt33 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, no economizer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, no economizer | NRes-PkgAC-18tolt33kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-18tolt33kBtuh-1Sp-S14.0 | NRes-PkgAC-18tolt33kBtuh-2Sp-S16.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:09 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-17p0seer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, no economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-17p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18tolt33 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18tolt33 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, no economizer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, no economizer | NRes-PkgAC-18tolt33kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-18tolt33kBtuh-1Sp-S14.0 | NRes-PkgAC-18tolt33kBtuh-2Sp-S17.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:09 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-18p0seer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, no economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airAC-Pkg-18tolt33kBtuh-18p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 18tolt33 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 18tolt33 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, no economizer | Com SEER-rated packaged air conditioner, size range: 18tolt33 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, no economizer | NRes-PkgAC-18tolt33kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-18tolt33kBtuh-1Sp-S14.0 | NRes-PkgAC-18tolt33kBtuh-2Sp-S18.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:09 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-15p0seer-wEcono | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 15 (EER = 12.9), EIR = 0.234, fan W/cfm = 0.28, one-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-15p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 33-lt55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 33 - lt55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 15 (EER = 12.7), EIR = 0.230, fan W/cfm = 0.28, one-speed fan, with economizer | NRes-PkgAC-33tolt55kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-33tolt55kBtuh-1Sp-S14.0-wEcon | NRes-PkgAC-33tolt55kBtuh-1Sp-S15.0-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-16p0seer-wEcono | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-16p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 33-lt55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 33 - lt55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-PkgAC-33tolt55kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-33tolt55kBtuh-1Sp-S14.0-wEcon | NRes-PkgAC-33tolt55kBtuh-2Sp-S16.0-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-17p0seer-wEcono | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-17p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 33-lt55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 33 - lt55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-PkgAC-33tolt55kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-33tolt55kBtuh-1Sp-S14.0-wEcon | NRes-PkgAC-33tolt55kBtuh-2Sp-S17.0-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-18p0seer-wEcono | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airAC-Pkg-33tolt55kBtuh-18p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-rated packaged air conditioner, 33-lt55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Com SEER-rated packaged air conditioners, size range: 33 - lt55 kBtu/h, SEER = 14 (EER = 12), EIR = 0.246, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged air conditioner, size range: 33 - lt55 kBtu/h, SEER = 18 (EER = 14.0), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-PkgAC-33tolt55kBtuh-1Sp-S11.6to14.0 | NRes-PkgAC-33tolt55kBtuh-1Sp-S14.0-wEcon | NRes-PkgAC-33tolt55kBtuh-2Sp-S18.0-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Split-18tolt33kBtuh-15p0seer | Com SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, fan W/cfm = 0.28, one-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airAC-Split-18tolt33kBtuh-15p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18tolt33 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/cfm = 0.28, one-speed fan, without economizers | NRes-SplitAC-18tolt33kBtu/h-1Sp-S11.5toS14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S15.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Split-18tolt33kBtuh-16p0seer | Com SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airAC-Split-18tolt33kBtuh-16p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18tolt33 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/cfm = 0.27, two-speed fan, without economizers | NRes-SplitAC-18tolt33kBtu/h-1Sp-S11.5toS14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S16.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Split-18tolt33kBtuh-17p0seer | Com SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airAC-Split-18tolt33kBtuh-17p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18tolt33 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/cfm = 0.27, two-speed fan, without economizers | NRes-SplitAC-18tolt33kBtu/h-1Sp-S11.5toS14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S17.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airAC-Split-18tolt33kBtuh-18p0seer | Com SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airAC-Split-18tolt33kBtuh-18p0seer | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18tolt33 kBtu/h; pre-2001: SEER = 11.5, one-speed fan, no economizers; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no economizers; 2014: SEER = 14 (EER = 12.17), one-speed fan, no economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, without economizers | Commercial SEER-rated split Air Conditioners, Size Range: 18tolt33 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/cfm = 0.27, two-speed fan, without economizers | NRes-SplitAC-18tolt33kBtu/h-1Sp-S11.5toS14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S14.0 | NRes-SplitAC-18tolt33kBtu/h-1Sp-S18.0 | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
1786 | NE-HVAC-airAC-Split-33tolt55kBtuh-15p0seer-wEcono | Commercial SEER-rated split-system air conditioner, size range: 33 - lt55 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, fan W/cfm = 0.28, one-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airAC-Split-33tolt55kBtuh-15p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split air conditioner, 33-lt55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Commercial SEER-rated split air conditioner, size range: 33 - lt55 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, with economizer | Commercial SEER-rated split air conditioner, Size Range: 33 - lt55 kBtu/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/cfm = 0.28, one-speed fan, with economizer | NRes-SplitAC-33tolt55kBtu/h-1Sp-S11.6to14.0 | NRes-SplitAC-33tolt55kBtu/h-1Sp-S14.0-wEcono | NRes-SplitAC-33tolt55kBtu/h-1Sp-S15.0-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-17 16:05 | Updated based on economizer required by Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
1787 | NE-HVAC-airAC-Split-33tolt55kBtuh-16p0seer-wEcono | Commercial SEER-rated split-system air conditioners, size range: 33 - lt55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airAC-Split-33tolt55kBtuh-16p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split air conditioner, 33-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Commercial SEER-rated split air conditioner, size range: 33 - 55 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, with economizer | Commercial SEER-rated split-system air conditioner, Size Range: 33 - lt55 kBtu/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitAC-33tolt55kBtu/h-1Sp-S11.6to14.0 | NRes-SplitAC-33tolt55kBtu/h-1Sp-S14.0-wEcono | NRes-SplitAC-33tolt55kBtu/h-1Sp-S16.0-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-17 16:05 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
1788 | NE-HVAC-airAC-Split-33tolt55kBtuh-17p0seer-wEcono | Commercial SEER-rated split-system air conditioners, size range: 33 - lt55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airAC-Split-33tolt55kBtuh-17p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split air conditioner, 33-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Commercial SEER-rated split air conditioner, size range: 33 - 55 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, with economizer | Commercial SEER-rated split-system air conditioner, size range: 33 - lt55 kBtu/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitAC-33tolt55kBtu/h-1Sp-S11.6to14.0 | NRes-SplitAC-33tolt55kBtu/h-1Sp-S14.0-wEcono | NRes-SplitAC-33tolt55kBtu/h-1Sp-S17.0-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-17 16:05 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
1789 | NE-HVAC-airAC-Split-33tolt55kBtuh-18p0seer-wEcono | Commercial SEER-rated split-system air conditioners, size range: 18 - 45 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airAC-Split-33tolt55kBtuh-18p0seer-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split air conditioner, 33-55 kBtu/h; pre-2001: SEER = 11.6, one-speed fan, no economizer; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no economizer; 2014: SEER = 14 (EER = 12.04), one-speed fan, no economizer | Commercial SEER-rated split air conditioner, size range: 33 - 55 kBtu/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/cfm = 0.29, one-speed fan, with economizer | Commercial SEER-rated split-system air conditioner, size range: 33 - lt55 kBtu/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitAC-33tolt55kBtu/h-1Sp-S11.6to14.0 | NRes-SplitAC-33tolt55kBtu/h-1Sp-S14.0-wEcono | NRes-SplitAC-33tolt55kBtu/h-1Sp-S18.0-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airAC |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-17 16:05 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-15p0seer-8p2hspf | Commercial SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 15.0 (HSPF = 8.2), EIR = 0.222, fan W/cfm = 0.28, one-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-15p0seer-8p2hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 18tolt33 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 15 (HSPF = 8.2), EIR = 0.222, fan W/cfm = 0.28, one-speed fan, without economizer | NRes-PkgHP-18tolt33kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-18tolt33kBtuh-S14.0-H8.0-1Sp | NRes-PkgHP-18tolt33kBtuh-S15.0-H8.2-1Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-16p0seer-8p5hspf | Commercial SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 16.0 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-16p0seer-8p5hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 18tolt33 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | NRes-PkgHP-18tolt33kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-18tolt33kBtuh-S14.0-H8.0-1Sp | NRes-PkgHP-18tolt33kBtuh-S16.0-H8.5-2Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-17p0seer-9p0hspf | Commercial SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 17.0 (HSPF = 9.0), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airHP-Pkg-18tolt33kBtuh-17p0seer-9p0hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 18tolt33 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated packaged heat pump, size range: 18tolt33 kBtu/h, SEER = 17 (HSPF = 9.0), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, without economizer | NRes-PkgHP-18tolt33kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-18tolt33kBtuh-S14.0-H8.0-1Sp | NRes-PkgHP-18tolt33kBtuh-S17.0-H9.0-2Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-15p0seer-8p2hspf-wEcono | Commercial SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 15.0 (HSPF = 8.2), EIR = 0.230, fan W/cfm = 0.28, one-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-15p0seer-8p2hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 33 - lt55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 15 (HSPF = 8.2), EIR = 0.230, fan W/cfm = 0.28, one-speed fan, with economizer | NRes-PkgHP-33tolt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-33tolt55kBtuh-S14.0-H8.0-1Sp-wEcon | NRes-PkgHP-33tolt55kBtuh-S15.0-H8.2-1Sp-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-16p0seer-8p5hspf-wEcono | Commercial SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 16.0 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-16p0seer-8p5hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 33 - lt55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-PkgHP-33tolt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-33tolt55kBtuh-S14.0-H8.0-1Sp-wEcon | NRes-PkgHP-33tolt55kBtuh-S16.0-H8.5-2Sp-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-17p0seer-9p0hspf-wEcono | Commercial SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 17.0 (HSPF = 9.0), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airHP-Pkg-33tolt55kBtuh-17p0seer-9p0hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | TRUE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-rated packaged heat pump, 33 - lt55 kBtu/h; Old: SEER = 9.7 (HSPF = 6.6), one-speed fan, no economizer; Ex: SEER = 13 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.0), one-speed fan, no economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.0), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated packaged heat pump, size range: 33 - lt55 kBtu/h, SEER = 17 (HSPF = 9.0), EIR = 0.222, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-PkgHP-33tolt55kBtuh-S9.7to14.0-H6.6to8.0-1to2Sp | NRes-PkgHP-33tolt55kBtuh-S14.0-H8.0-1Sp-wEcon | NRes-PkgHP-33tolt55kBtuh-S17.0-H9.0-2Sp-wEcon | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-03 17:06 | Updated based on economizer required by Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airHP-Split-18tolt33kBtuh-15p0seer-8p7hspf | Commercial SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 15.0 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.28, one-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airHP-Split-18tolt33kBtuh-15p0seer-8p7hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 18tolt33 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.28, one-speed fan, without economizer | NRes-SplitHP-18tolt33kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-18tolt33kBtuh-S14.0-H8.2-1Sp | NRes-SplitHP-18tolt33kBtuh-S15.0-H8.7-1Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airHP-Split-18tolt33kBtuh-16p0seer-9p0hspf | Commercial SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 16.0 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airHP-Split-18tolt33kBtuh-16p0seer-9p0hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 18tolt33 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, without economizer | NRes-SplitHP-18tolt33kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-18tolt33kBtuh-S14.0-H8.2-1Sp | NRes-SplitHP-18tolt33kBtuh-S16.0-H9.0-2Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airHP-Split-18tolt33kBtuh-17p0seer-9p4hspf | Commercial SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 17.0 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airHP-Split-18tolt33kBtuh-17p0seer-9p4hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 18tolt33 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, without economizer | NRes-SplitHP-18tolt33kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-18tolt33kBtuh-S14.0-H8.2-1Sp | NRes-SplitHP-18tolt33kBtuh-S17.0-H9.4-2Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
2023 | NE-HVAC-airHP-Split-18tolt33kBtuh-18p0seer-9p7hspf | Commercial SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 18.0 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | DEER2023 | D23v1a | 2025-01-14 13:08 | NE-HVAC-airHP-Split-18tolt33kBtuh-18p0seer-9p7hspf | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 18tolt33 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, without economizer | Com SEER-rated split heat pump, size range: 18tolt33 kBtu/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, without economizer | NRes-SplitHP-18tolt33kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-18tolt33kBtuh-S14.0-H8.2-1Sp | NRes-SplitHP-18tolt33kBtuh-S18.0-H9.7-2Sp | Available | D23v1a indicates that these records are previously named to be size "lt55kbuth" and are now renamed as "18tolt33kbtuh" to fit code requirement, no rerun was done for this size because simulation model results were similar | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-09-22 12:10 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
1790 | NE-HVAC-airHP-Split-33tolt55kBtuh-15p0seer-8p7hspf-wEcono | Commercial SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 15.0 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.28, one-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airHP-Split-33tolt55kBtuh-15p0seer-8p7hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 33 - lt55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, fan W/cfm = 0.283, one-speed fan, with economizer | NRes-SplitHP-33tolt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-33tolt55kBtuh-S14.0-H8.2-1Sp-wEcono | NRes-SplitHP-33tolt55kBtuh-S15.0-H8.7-1Sp-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-26 16:30 | Narrowed size range not requiring economizers per Title 24 in 2023; revised W/cfm from 0.251 to 0.283. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
1791 | NE-HVAC-airHP-Split-33tolt55kBtuh-16p0seer-9p0hspf-wEcono | Commercial SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 16.0 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airHP-Split-33tolt55kBtuh-16p0seer-9p0hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 33 - lt55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitHP-33tolt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-33tolt55kBtuh-S14.0-H8.2-1Sp-wEcono | NRes-SplitHP-33tolt55kBtuh-S16.0-H9.0-2Sp-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-26 16:30 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
1792 | NE-HVAC-airHP-Split-33tolt55kBtuh-17p0seer-9p4hspf-wEcono | Commercial SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 17.0 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airHP-Split-33tolt55kBtuh-17p0seer-9p4hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 33 - lt55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitHP-33tolt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-33tolt55kBtuh-S14.0-H8.2-1Sp-wEcono | NRes-SplitHP-33tolt55kBtuh-S17.0-H9.4-2Sp-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-26 16:30 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None
1793 | NE-HVAC-airHP-Split-33tolt55kBtuh-18p0seer-9p7hspf-wEcono | Commercial SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 18.0 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | DEER2023 | D23v1 | 2025-01-14 13:08 | NE-HVAC-airHP-Split-33tolt55kBtuh-18p0seer-9p7hspf-wEcono | Deem-DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-rated split heat pump, 33 - lt55 kBtu/h; Old: SEER = 10.0 (HSPF = 6.8), one-speed fan, no economizer; Ex: SEER = 13.0 (HSPF = 7.7), one-speed fan, no economizer; Recent: SEER = 14.0 (HSPF = 8.2), one-speed fan, no economizer; | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 14.0 (HSPF = 8.2), EIR = 0.245, fan W/cfm = 0.29, one-speed fan, with economizer | Com SEER-rated split heat pump, size range: 33 - lt55 kBtu/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, fan W/cfm = 0.27, two-speed fan, with economizer | NRes-SplitHP-33tolt55kBtuh-S10.0to14.0-H6.8to8.2-1to2Sp | NRes-SplitHP-33tolt55kBtuh-S14.0-H8.2-1Sp-wEcono | NRes-SplitHP-33tolt55kBtuh-S18.0-H9.7-2Sp-wEcono | Available |  | FALSE | FALSE |  |  |  | HVAC-airHP |  |  | 2024-02-01 | [6 empty] | Standard |  | TRUE | TRUE | FALSE | Deemed Ex Ante Team | 2023-07-26 16:30 | Narrowed size range not requiring economizers per Title 24 in 2023. | Deemed Ex Ante Team | Pushed back start date | CZ2022 | None