## ResidentialShell
2019 Title-24 Updates for Residential Building Shell
Window U-Factor |  | Window SHGC |  | Wall Overall U-Value |  | Radiant Barrier |  | Insulation at Roof Deck
DEER2017 | DEER2020 | DEER2017 | DEER2020 | DEER2017 | DEER2020 | DEER2017 | DEER2020 | DEER2017 | DEER2020
0.32 | 0.3 | 0.79 | 0.79 | 0.051 | 0.048 | Not Req'd | Not Req'd | 0 | 0
0.32 | 0.3 | 0.25 | 0.23 | 0.051 | 0.048 | Required | Required | 0 | 0
0.32 | 0.3 | 0.79 | 0.79 | 0.051 | 0.048 | Required | Required | 0 | 0
0.32 | 0.3 | 0.25 | 0.23 | 0.051 | 0.048 | Required | Not Req'd | R-8 Continuous | R-19 Between Rafters
0.32 | 0.3 | 0.79 | 0.79 | 0.051 | 0.048 | Required | Required | 0 | 0
0.32 | 0.3 | 0.25 | 0.23 | 0.065 | 0.056 | Required | Required | 0 | 0
0.32 | 0.3 | 0.25 | 0.23 | 0.065 | 0.056 | Required | Required | 0 | 0
0.32 | 0.3 | 0.25 | 0.23 | 0.051 | 0.048 | Required | Not Req'd | R-8 Continuous | R-19 Between Rafters
0.32 | 0.3 | 0.25 | 0.23 | 0.051 | 0.048 | Required | Not Req'd | R-8 Continuous | R-19 Between Rafters
0.32 | 0.3 | 0.25 | 0.23 | 0.051 | 0.048 | Required | Not Req'd | R-8 Continuous | R-19 Between Rafters
0.32 | 0.3 | 0.25 | 0.23 | 0.051 | 0.048 | Required | Not Req'd | R-8 Continuous | R-19 Between Rafters
0.32 | 0.3 | 0.25 | 0.23 | 0.051 | 0.048 | Required | Not Req'd | R-8 Continuous | R-19 Between Rafters
0.32 | 0.3 | 0.25 | 0.23 | 0.051 | 0.048 | Required | Not Req'd | R-8 Continuous | R-19 Between Rafters
0.32 | 0.3 | 0.25 | 0.23 | 0.051 | 0.048 | Required | Not Req'd | R-8 Continuous | R-19 Between Rafters
0.32 | 0.3 | 0.25 | 0.23 | 0.051 | 0.048 | Required | Not Req'd | R-8 Continuous | R-19 Between Rafters
0.32 | 0.3 | 0.25 | 0.79 | 0.051 | 0.048 | Not Req'd | Not Req'd | R-8 Continuous | R-19 Between Rafters
Note: R-19 between rafters is equivalent to about R-16 continuous
Averages:
0.32 | 0.3 | 0.358 | 0.342 | 0.05275 | 0.049
Change: | -6.25% |  | -4.469% |  | -7.109%

## CoolingTowerFan
DEER Vintage | Tower Type | fan type | gpm/ton | gpm/hp | hp/ton | kW/ton | Tower EIR
Pre 2020 | closed-circuit | axial fan | 2 | 14 | 0.14286 | 0.11584 | 0.032946
2020 | closed-circuit | axial fan | 2 | 16.1 | 0.12422 | 0.10073 | 0.028649
Pre 2020 | open tower | axial fan | 2 | 42.1 | 0.047506 | 0.038521 | 0.010956
2020 | open tower | axial fan | 2 | 60 | 0.033333 | 0.027029 | 0.0076875

## ComExhaust
|  | Previous DEER | Title 24-2019 Minimum | DEER2020
ActArea | BldgType | cfm/sf | cfm/sf | cfm/sf | DEER2020 Basis
Shop | Any | 0.2 | 0.5 | 0.5 | T24-2019
LockerRoom | ESe | 0.3 | 0.25 | 0.25 | T24-2019
IndLowBay | EUn | 0.25 | NA | 0.25 | Previous DEER
Laundry | Htl | 0.5 | NA | 0.5 | Previous DEER
Kitchen | RSD | 0.33 | 0.7 | 0.33 | Based on previous DEER. Kitchen exhaust in the DEER prototypes is based on general exhaust. Hood exhaust is assumed to be handled by dedicated makeup air units, which are excluded from the simulations.
| HSP | 1 | 0.7 | 1
| Htl | 1 | 0.7 | 1
| EPr | 1 | 0.7 | 1
| RFF | 0.33 | 0.7 | 0.33
| ESe | 0.5 | 0.7 | 0.5
| Nrs | 1 | 0.7 | 1
| ECC | NA | 0.7 | 0.5
| EUn | 0.5 | 0.7 | 0.5
| RtL | 0.33 | 0.7 | NA

## ComLighting
These changes can imply a fraction of LED lighting in the baseline for many areas
Lighting Power Density, W/sq ft
ActArea | T24-2016 | T24-2019 | Change
Other | 0.5 | 0.4 | -0.1
Auditorium | 1.4 | 0.7 | -0.7
AutoRepair | 0.9 | 0.55 | -0.35
Classroom | 1.2 | 0.7 | -0.5
Conference | 1.2 | 0.85 | -0.35
Corridor | 0.6 | 0.6 | 0
Stairway | 0.6 | 0.5 | -0.1
Dining | 1 | 0.55 | -0.45
GrocSales | 1.2 | 1.05 | -0.15
Gymnasium | 1 | 0.5 | -0.5
HotelLobby | 0.95 | 0.85 | -0.1
IndHighBay | 1 | 0.65 | -0.35
IndLowBay | 0.9 | 0.6 | -0.3
IndPrecision | 1.2 | 0.85 | -0.35
Kitchen | 1.2 | 0.95 | -0.25
Laboratory | 1.4 | 1 | -0.4
Laundry | 0.7 | 0.45 | -0.25
LibraryReading | 1.1 | 0.8 | -0.3
LibraryStacks | 1.5 | 1.1 | -0.4
Lobby | 0.95 | 0.85 | -0.1
LockerRoom | 0.7 | 0.45 | -0.25
Mall_Atria | 0.95 | 0.9 | -0.05
MechElecRoom | 0.55 | 0.4 | -0.15
OfficeOpen | 1.05 | 0.8 | -0.25
OfficeSmall | 1.3 | 0.9 | -0.4
RefWalkInCool | 0.7 | 0.45 | -0.25
RefWalkInFreeze | 0.7 | 0.45 | -0.25
RelWorship | 1.5 | 0.95 | -0.55
Restroom | 0.6 | 0.65 | 0.05
RetailSales | 1.2 | 1 | -0.2
StorageSmlCond | 0.6 | 0.45 | -0.15
StorageUncond | 0.6 | 0.45 | -0.15
TheaterMovie | 0.9 | 0.6 | -0.3
TheaterPerform | 1.4 | 1 | -0.4
ConventionLarge | 1.2 | 0.85 | -0.35
Cafeteria | 1 | 0.4 | -0.6
ConventionSmall | 1.2 | 0.85 | -0.35
CopyRoom | 1.3 | 0.5 | -0.8
PatientRoom | 0.8 | 0.55 | -0.25
MedClinicalCare | 1.2 | 1.15 | -0.05
Hsp Intensive care/ICU | 1.2 | 1.15 | -0.05
HspNursing | 1.2 | 0.75 | -0.45
HspOutPatient | 1.2 | 1.15 | -0.05
HspSurgery | 1.2 | 1.9 | 0.7
HspSurgOutptLab | 1.2 | 1.15 | -0.05
CivicMtgPlace | 1.3 | 1 | -0.3
HotelFunction | 1.4 | 0.85 | -0.55
LabEquipmentRoom |  | 1 | 1
LoungeArea | 0.9 | 0.65 | -0.25
VideoConfStudio | 1.2 | 0.9 | -0.3
WaitingArea | 0.8 | 0.65 | -0.15
Note on C42: Unrated in T24-2016