## HVAC ER 2013-2016
Data Request for Information on Equipment Removed as Part of SCE's Package HVAC Early Retirement Program
This spreadsheet represents equipment data for claimed years 2013 through 2016 for HVAC Early Retirement “to code” claims.
• Manufacturer
• Model number
• Manufacture year
• Nominal cooling capacity
• Building type
• Climate zone
Please note: Manufacturer's listed efficiency rating and rated efficiency value of the existing units was not collected as part of the program requirement.
Data request A.12-07-004-ED-SCE-EE Stats- 27475 - Early Retirement
Claim Year | IOUMeaName | Manufacturer | Model Number | Manufacturer Year | Nominal Cooling Capacity | IOUBuildingType | BuildingTypeCode | IOUClimateZone | EER | Efficiency Requirement | VAV, CV, or UNK | Notes | Vnt | Age of Unit
2014 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHGD1140F76CE8D3001RTGP | 1995 | 1434000 | Miscellaneous Commercial | MIC | 10 | 8.2 | 8.2 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes, high cap. Evap coil | 3 | 19
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHGD114 | 2001 | 1260000 | Office - Small | OFS | 6 | 9.2 | 9.2 EER 9.4 IPLV | UNK | Model Number Incomplete | 3 | 15
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | unknown | 6BJK08-0963-XXXXX-XXSE | 1981 | 1212000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 34
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHGDW40D | 1994 | 1173000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 22
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | McQuay | RPS090BY | 1982 | 1130208 | Office - Small | OFS | 6 | 7.5 | 7.5 EER | UNK |  | 2 | 33
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | 5XHEC9040B76AD7D3001MNRTB | 1988 | 1080000 | Manufacturing - Light Industrial | MLI | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 27
2014 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHGC9040 | 1997 | 1080000 | Miscellaneous Commercial | MIC | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 17
2014 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHGC9040F76CD8D3001RTGP | 1995 | 1014000 | Miscellaneous Commercial | MIC | 10 | 8.2 | 8.2 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 19
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Mammoth | CEBFP853SZ | 1983 | 960000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 33
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | McQuay | RPS080BY | 2000 | 960000 | Office - Small | OFS | 6 | 8.2 | 8.2 EER 7.5 IPLV | UNK |  | 3 | 16
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SAHCC754073C85D | 1998 | 905040 | Retail - Small | RtS | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 18
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SAHCC754073C85D | 1998 | 905040 | Retail - Small | RtS | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 18
2014 | ≥760 kBtu/hr 10.4 EER or 14 IEER Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC7510J77C9AD3D01 | 1989 | 904210 | Office - Small | OFS | 9 | 8.0 | 8.0 EER 7.2 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 25
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC7540T66C9BD300100D00G0KL00RT00000 | 1999 | 901288 | Retail - Single-Story Large | RTL | 6 | 8.2 | 8.2 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 17
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC7540U78C9BD300100DE0G00L00RT000000 | 1999 | 901288 | Office - Small | OFS | 6 | 8.2 | 8.2 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 17
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SAHCC7540BC6A85D3A01NE | 1985 | 900000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 30
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC75 | 1996 | 900000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 19
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC75 | 1999 | 900000 | Miscellaneous Commercial | MIC | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 16
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC75 | 1999 | 900000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 17
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC754 | 1998 | 900000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 18
2014 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC7540 | 1996 | 900000 | Miscellaneous Commercial | MIC | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 18
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC7540N77C8AD3001GRT | 1997 | 900000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 18
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC7540N77C8AD3001RT | 1997 | 900000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 18
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC7540U78C9B | 1999 | 900000 | Office - Small | OFS | 6 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 17
2014 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SXHFC754OU | 1999 | 900000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 15
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | GOVERNAIR | TLIO-T2028 | 0 | 900000 | Transportation - Communication - Utilities | TCU | 6 |  |  | UNK |  | 0 | 2015
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC754OU78C9BD300100 | 1999 | 875900 | Office - Small | OFS | 6 | 8.2 | 8.2 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 17
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC754E57F89D | 1994 | 855000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 22
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50D5074-60 | 1989 | 850800 | Office - Small | OFS | 9 | 8.0 | 8.0 EER 7.2 IPLV | UNK |  | 2 | 27
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK704-6015L | 1989 | 850800 | Office - Small | OFS | 9 | 8.0 | 8.0 EER 7.2 IPLV | VAV | Variable Volume | 2 | 27
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | COPELAND | LPS-60 | 0 | 840000 | Office - Small | OFS | 10 |  |  | UNK |  | 0 | 2015
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | COPELAND | LPS-65 | 0 | 840000 | Office - Small | OFS | 10 |  |  | UNK |  | 0 | 2015
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | COPELAND | LPS-65 | 0 | 840000 | Office - Small | OFS | 10 |  |  | UNK |  | 0 | 2015
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | McQuay | RPS070BY | 1989 | 840000 | Office - Small | OFS | 6 | 8.0 | 8.0 EER 7.2 IPLV | UNK |  | 2 | 27
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SFHLF704LF44C8AD7 | 1995 | 840000 | Assembly | ASM | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK |  | 3 | 21
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC7040 | 1998 | 840000 | Miscellaneous Commercial | MIC | 8 | 8.2 | 8.2 EER 7.5 IPLV | UNK | Model Number Incomplete | 3 | 17
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC7040P77A9AD6001RT8 | 1998 | 840000 | Miscellaneous Commercial | MIC | 8 | 8.2 | 8.2 EER 7.5 IPLV | VAV | VAV Supply Air Temperature Control with VFD w/o Bypass | 3 | 17
2015 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC7040P88A9AD6001RT8 | 1998 | 840000 | Miscellaneous Commercial | MIC | 8 | 8.2 | 8.2 EER 7.5 IPLV | VAV | VAV Supply Air Temperature Control with VFD w/o Bypass | 3 | 17
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50EK-064---600GD | 1998 | 780000 | Miscellaneous Commercial | MIC | 8 | 8.2 | 8.2 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 17
2016 | ≥760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TSI | 20AOCD70 | 1991 | 774000 | Office - Small | OfS | 9 | 8.2 | 8.2 EER 7.5 IPLV | UNK |  | 2 | 25
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK064-600DS | 1998 | 720000 | Miscellaneous Commercial | MIC | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Volume | 3 | 17
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL064-600SA | 1986 | 720000 | Health/Medical - Clinic | CLI | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50EK-064 | 1998 | 720000 | Office - Small | OfS | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 18
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Mammoth | CEBP-602-2060 | 1981 | 720000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 33
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Mammoth | CEBP-602-2060 | 1981 | 720000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 33
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SAHCC6040B06A75D3A06B | 1984 | 720000 | Miscellaneous Commercial | MIC | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 31
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SAHCC6040BC6A75D3A000B | 1984 | 720000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 32
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SAHFC6040Y78C8AD7F000B0000H0000RT008000 | 2001 | 720000 | Office - Small | OFS | 6 | 9.5 | 9.5 EER 9.7 IPLV | VAV | VAV Supply Air Temperature Control with VFD and Bypass | 3 | 14
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SCHCC60 | 1989 | 720000 | Office - Small | OFS | 10 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 27
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC6040JD7A89DSD00GMNT | 1990 | 720000 | Office - Small | OFS | 10 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 25
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC6040TC6A8AD3A01NB | 1991 | 720000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 24
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC6040TC6A8AD3A01NB | 1991 | 720000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 24
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SXHCC6040TC6A9BD3A01NGB | 1991 | 720000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 24
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SXHCC6040Z56CBA | 1993 | 720000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 23
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC604E56C79D3D01AMNTBG | 1987 | 720000 | Miscellaneous Commercial | MIC | 6 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 27
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC60 | 1996 | 720000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 19
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC60 | 1996 | 720000 | Health/Medical - Clinic | CLI | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 19
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC60 | 1997 | 720000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 18
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC60 | 1998 | 720000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 18
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC6040 | 1997 | 720000 | Office - Small | OfS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 18
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC6040K56C8AD3001GRT | 1997 | 720000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 17
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC6040M56C8AD3F01DGRTP | 1997 | 720000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 18
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC6040N45C89D3001GRT | 1997 | 720000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 18
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SAHCC6040C53C7 | 1998 | 700000 | Retail - Small | RtS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 18
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SAHCC6040C53C7 | 1998 | 700000 | Retail - Small | RtS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 18
2014 | 240-760 kBtu/hr 11.1 EER or 13.1 IEER Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC601J77C9AD3D01 | 1989 | 700000 | Office - Small | OFS | 9 | 8.2 | 8.2 EER 7.2 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 25
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL064600SC | 1984 | 689000 | Office - Small | OfS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 31
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL064600SC | 1989 | 689000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 25
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL064-600SC | 1998 | 662500 | Education - University | EUN | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 16
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC55 | 1990 | 660000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 25
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC5540G68A7BD3A01N | 1988 | 660000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 26
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC5540JD8A7ADSD00GMNT | 1990 | 660000 | Office - Small | OFS | 10 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 25
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SXHCC5540Z56CBA | 1993 | 660000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 23
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC55TOS68A7AD3D01GNT | 1989 | 660000 | Retail - Single-Story Large | RTL | 9 | 8.2 | 8.2 EER 7.2 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 25
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC5540710 | 2006 | 660000 | Office - Small | OFS | 8 | 9.5 | 9.5 EER 9.7 IPLV | UNK |  | 5 | 10
2014 | ≥ 20 ton To Code Savings Portion Package/Split System Air Conditioner Condenser | Carrier | 50BJ054600 | 1986 | 648000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 28
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | McQuay | RDT050CSY | 1995 | 611171 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 19
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DD054600AA | 1986 | 600000 | Office - Large | OFL | 6 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK054-600DS | 1998 | 600000 | Miscellaneous Commercial | MIC | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Volume | 3 | 17
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL054600HH | 1996 | 600000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 20
2014 | 240-760 kBtu/hr 10.8 EER or 12 IEER Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL054600XC | 1986 | 600000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 28
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL054600XC | 1986 | 600000 | Manufacturing - Light Industrial | MLI | 6 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50EK-054 | 1998 | 600000 | Office - Small | OfS | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 18
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50EK054600fd | 1999 | 600000 | Office - Small | OfS | 6 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 17
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50LJQ006260 | 1992 | 600000 | Manufacturing - Light Industrial | MLI | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 23
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | Cannot Read tag | 1989 | 600000 | Office - Small | OFS | 10 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 26
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | COPELAND | LPS-35 | 0 | 600000 | Office - Small | OFS | 10 |  |  | UNK |  | 0 | 2015
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | COPELAND | LPS-35 | 0 | 600000 | Office - Small | OFS | 10 |  |  | UNK |  | 0 | 2015
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | NOT LEGIBLE | 1985 | 600000 | Office - Large | OFL | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | McQuay | RPS060BY | 1985 | 600000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER | UNK |  | 2 | 30
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | McQuay | RPS060BY | 1985 | 600000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER | UNK |  | 2 | 30
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SFHCC504LP56A7AD3A01ENTRY | 1991 | 600000 | Health/Medical - Clinic | CLI | 6 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 23
2015 | ≥ 20 ton To Code Savings Portion Package/Split System Air Conditioner Condenser | Trane | SWUA-5004-RAX | 1984 | 600000 | Miscellaneous Commercial | MIC | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 31
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXCC5040J68A7AD3D01GNT | 1989 | 600000 | Retail - Single-Story Large | RTL | 9 | 8.2 | 8.2 EER 7.2 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 26
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC5040G58A7BD3A01N | 1988 | 600000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 26
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC5040M10 | 1990 | 600000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 26
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC5040E46A | 1995 | 600000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 19
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC5040F | 1995 | 600000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 21
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC5040N56C6AD3001GRT | 1997 | 600000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 18
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | TCH600A40A2B4NC3A | 1995 | 600000 | Office - Small | OFS | 9 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 3 | 21
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC5040415A | 1993 | 580000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 23
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC5040E77A6A0300 | 1988 | 565000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 28
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL054 | 1989 | 559600 | Education - University | EUN | 8 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 25
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL054600HH | 1981 | 559600 | Education - University | EUN | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 33
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SXHCC5040V68A79D3DOWN | 1988 | 551000 | Office - Large | OFL | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 27
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Mammoth | CEBP-452-2060 | 1987 | 550000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 28
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC5040E77A6AD3A01MNRIB | 1988 | 545000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 28
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50EK-044---610RD | 1998 | 540000 | Miscellaneous Commercial | MIC | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 17
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50ek054600fd | 1999 | 540000 | Transportation - Communication - Utilities | TCU | 6 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 16
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Mammoth | CEBP-452-2060 | 1985 | 540000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 30
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Air Handler-ITT/Nesbit, CondensingUnit- Carrier | PSC50032000KSAOAAJOOA/38AH-054 | 1973 | 540000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 1 | 41
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC504 | 1987 | 540000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC5040CDA504 | 1987 | 540000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD600A4LE1ABNC50BC | 2000 | 540000 | Office - Large | OFL | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 16
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | McQuay | RPS041BY | 0 | 533000 | Office - Small | OFS | 6 |  |  | UNK |  | 0 | 2016
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL054600HH | 1987 | 525000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 28
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DD044 | 1991 | 480000 | Office - Small | OfS | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 24
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DF044640AA | 1981 | 480000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 33
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50A3B040 | 1998 | 480000 | Office - Small | OfS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 18
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50AY-040-F-611EE | 2006 | 480000 | Health/Medical - Clinic | CLI | 6 | 9.5 | 9.5 EER 9.7 IPLV | UNK |  | 5 | 9
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL044500XC | 1985 | 480000 | Miscellaneous Commercial | MIC | 6 | 7.5 | 7.5 EER | UNK |  | 2 | 30
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL-044-600 | 1992 | 480000 | Retail - Multistory Large | RT3 | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 23
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50EK-044---6105A | 1998 | 480000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 18
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50EK044610ED | 1998 | 480000 | Office - Small | OFS | 9 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 18
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50EK-044---610ED | 1998 | 480000 | Miscellaneous Commercial | MIC | 6 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 17
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50EK-044-610FD | 2000 | 480000 | Miscellaneous Commercial | MIC | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 15
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50EY-044---610EA | 2001 | 480000 | Health/Medical - Clinic | CLI | 6 | 9.5 | 9.5 EER 9.7 IPLV | UNK |  | 3 | 14
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D2SV480A46SDA | 1996 | 480000 | Office - Small | OFS | 9 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 19
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D2SV480A4ASDA | 1996 | 480000 | Office - Small | OFS | 9 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 19
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SAHA40040K64A44DC4BF | 1981 | 480000 | Office - Large | OFL | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 34
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SAHCC4040A43C54D3D02MNTB | 1983 | 480000 | Education - University | EUN | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 31
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SFHCC404LZ46 | 1993 | 480000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 21
2015 | ≥ 20 ton To Code Savings Portion Package/Split System Air Conditioner Condenser | Trane | SWUA-4004-RAX | 1984 | 480000 | Miscellaneous Commercial | MIC | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 31
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC40 | 1993 | 480000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 23
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC4010E58A7BD01GMNTB | 1988 | 480000 | Retail - Single-Story Large | RTL | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 27
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC4040GC7A6AD3C01 | 1988 | 480000 | Miscellaneous Commercial | MIC | 6 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 26
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC4040GC7A6AD3CD1 | 1988 | 480000 | Miscellaneous Commercial | MIC | 6 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 26
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC4040GC7A6AD3CD1 | 1988 | 480000 | Miscellaneous Commercial | MIC | 6 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 26
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC4040GC7AGA23001N1 | 1988 | 480000 | Miscellaneous Commercial | MIC | 6 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 26
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SXHFC40 | 1997 | 480000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 17
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | TCH480A40A2B3NC2A | 1995 | 480000 | Office - Small | OFS | 9 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Constant Volume w/ Discharge Air Control | 3 | 21
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Technical Systems | unknown | 0 | 480000 | Office - Small | OfS | 8 |  |  | UNK |  | 0 | 2016
2015 | ≥ 20 ton To Code Savings Portion Package/Split System Air Conditioner Condenser | Synder General | VSC040B | 0 | 480000 | Health/Medical - Clinic | CLI | 6 |  |  | UNK |  | 0 | 2015
2016 | ≥ 20 ton To Code Savings Portion Package/Split System Air Conditioner Condenser | SnyderGeneral | VSC040B | 0 | 480000 | Office - Small | OFS | 6 |  |  | UNK |  | 0 | 2016
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD480A4LC2A3LC1H | 1998 | 480000 | Education - Secondary School | ESE | 10 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume w/Zone Temperature Control | 3 | 18
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48EWD044-610EA | 1997 | 462000 | Office - Small | OFS | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 18
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | 4DK3-2500-TSK | 0 | 460000 | Office - Small | OFS | 10 |  |  | UNK |  | 0 | 2015
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | 4DK3-2500-TSK | 0 | 460000 | Office - Small | OFS | 10 |  |  | UNK |  | 0 | 2015
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK-044-600DL | 1989 | 460000 | Office - Small | OFS | 9 | 8.2 | 8.2 EER 7.2 IPLV | VAV | Variable Volume | 2 | 26
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL044600SA | 1986 | 456000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER | UNK |  | 2 | 30
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL-044-600XC | 1990 | 451600 | Education - University | EUN | 8 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 24
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48MA024 | 1998 | 450000 | Office - Large | OFL | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 16
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DF044610 | 1992 | 432000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 22
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48EYD038-E | 1999 | 420000 | Agricultural | AGR | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 16
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DL044600TC | 1986 | 420000 | Retail - Single-Story Large | RTL | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH420A4LC2A2CC1HJ | 1998 | 420000 | Education - Secondary School | ESE | 10 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume w/Zone Temperature Control | 3 | 18
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | McQuay | CUR351ETYC | 1983 | 419000 | Retail - Single-Story Large | RTL | 10 | 7.5 | 7.5 EER | UNK |  | 2 | 31
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48EKD038 | 2000 | 402000 | Miscellaneous Commercial | MIC | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 15
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Daikin | RPS0309 | 1987 | 388000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Daikin | RPS030BW | 1987 | 388000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D1SC36046EPB | 1996 | 365000 | Health/Medical - Clinic | CLI | 9 | 8.5 | 8.5 EER 7.5 IPLV | CV | Cont. Air | 3 | 19
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DF034C | 1994 | 360000 | Manufacturing - Light Industrial | MLI | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 20
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DF034 | 1995 | 360000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 21
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50Df034-620 | 1986 | 360000 | Health/Medical - Clinic | CLI | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DF034-620HH | 1990 | 360000 | Office - Small | OFS | 9 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 25
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DF034620XC | 1987 | 360000 | Miscellaneous Commercial | MIC | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 28
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DF034620XC | 1986 | 360000 | Retail - Single-Story Large | RTL | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50EK034611DD | 1995 | 360000 | Office - Small | OFS | 9 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 21
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50FY-034-B-600CA | 1999 | 360000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 16
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | YORK | D2SC360G40046ECA | 1994 | 360000 | Assembly | ASM | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV | Cont. Air | 3 | 21
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Air Fam | LPM2-35B/tripdeckenergy saver | 1974 | 360000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 1 | 40
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SFHA3004LI54A55DJOBFLP | 1981 | 360000 | Office - Large | OFL | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 34
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SFHCC304LA46A55D1AOOF | 1981 | 360000 | Office - Large | OFL | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 34
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SFHLF304LF36C5CD7 | 1995 | 360000 | Assembly | ASM | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 21
2014 | 240-760 kBtu/hr 11.1 EER or 13.1 IEER Air Source Unitary Air Conditioner DX Equipment | Trane | SXHCC3010N | 1990 | 360000 | Transportation - Communication - Utilities | TCU | 6 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 24
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SXHCC3040DC7A56D3C01NRTB | 1987 | 360000 | Education - University | EUN | 8 | 7.5 | 7.5 EER | VAV | VAV S/A Temp Control w/ Inlet guide vanes | 2 | 29
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | TCD360A40C2B6EE4F | 1998 | 360000 | Education - University | EUN | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV Supply Air Temperature Control w/Variable Frequency Drive w/o Bypass | 3 | 18
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD360A4LE2A2EC100 | 2000 | 360000 | Education - Secondary School | ESE | 10 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume w/Zone Temperature Control | 3 | 15
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK-034-600CK | 1989 | 346000 | Office - Small | OFS | 9 | 8.2 | 8.2 EER 7.2 IPLV | VAV | Variable Volume | 2 | 26
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK-034-600CK | 1989 | 346000 | Office - Small | OFS | 9 | 8.2 | 8.2 EER 7.2 IPLV | VAV | Variable Volume | 2 | 26
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | TCD330A40C2B6DE4F | 1997 | 330000 | Education - University | EUN | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | VAV Supply Air Temperature Control w/Variable Frequency Drive w/o Bypass | 3 | 19
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48EYD030-E | 1999 | 324000 | Agricultural | AGR | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 16
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK030600AD | 1990 | 324000 | Office - Small | OFS | 9 | 8.2 | 8.2 EER 7.2 IPLV | VAV | Variable Volume | 2 | 25
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | CVA1-300-1G | 1981 | 306000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 34
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | CVA1-300-1G | 1981 | 306000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 34
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 38AH-028---600AA | 1995 | 300000 | Office - Small | OfS | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 21
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJD028 | 0 | 300000 | Office - Small | OFS | 9 |  |  | CV | Constant Volume | 0 | 2016
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJD028 | 1990 | 300000 | Grocery | GRO | 6 | 8.2 | 8.2 EER 7.2 IPLV | CV | Constant Volume | 2 | 26
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJD028 | 1992 | 300000 | Manufacturing - Light Industrial | MLI | 10 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume | 2 | 24
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJD028600AC | 1991 | 300000 | Manufacturing - Light Industrial | MLI | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume | 2 | 23
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD28 | 0 | 300000 | Assembly | ASM | 6 |  |  | CV | Constant Volume | 0 | 2014
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DF028-620 | 1985 | 300000 | Health/Medical - Clinic | CLI | 9 | 7.5 | 7.5 EER | UNK |  | 2 | 30
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK-028-600MD | 1984 | 300000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | VAV | Variable Volume | 2 | 32
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK-028-600MD | 1995 | 300000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Volume | 3 | 21
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK030600AD | 1990 | 300000 | Office - Small | OFS | 9 | 8.2 | 8.2 EER 7.2 IPLV | VAV | Variable Volume | 2 | 25
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50EK034C610DD | 2000 | 300000 | Office - Small | OFS | 6 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Air Volume | 3 | 15
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SFHB250045LJ | 1987 | 300000 | Assembly | ASM | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SFHB2504LK20F42D04 | 1990 | 300000 | Retail - Single-Story Large | RTL | 10 | 8.2 | 8.2 EER 7.2 IPLV | VAV | Space Pressure Control with Exhaust VFD w/o Bypass | 2 | 25
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH300B4LOFA | 1998 | 300000 | Education - Secondary School | ESE | 10 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 18
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Norsaire | NPCC-8DWX-1-S-3 | 1997 | 288000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 19
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DF028C | 1990 | 287500 | Manufacturing - Light Industrial | MLI | 9 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 24
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJD028 | 1993 | 280000 | Retail - Single-Story Large | RTL | 6 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume | 3 | 23
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD028 | 1997 | 268000 | Manufacturing - Light Industrial | MLI | 9 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume | 3 | 18
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD028 | 2001 | 268000 | Assembly | ASM | 8 | 9.5 | 9.5 EER 9.7 IPLV | CV | Constant Volume | 3 | 15
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD028 | 2001 | 268000 | Assembly | ASM | 8 | 9.5 | 9.5 EER 9.7 IPLV | CV | Constant Volume | 3 | 15
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD241C4LCAB | 1999 | 250000 | Education - Primary School | EPR | 6 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 16
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD241C4LGAB | 1999 | 250000 | Education - Primary School | EPR | 6 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 16
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48DJD024 | 1990 | 249000 | Education - Community College | ECC | 9 | 8.2 | 8.2 EER 7.2 IPLV | CV | Constant Volume | 2 | 26
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 39ED-011 | 1992 | 240000 | Education - Primary School | EPR | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 24
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DKD024 | 0 | 240000 | Office - Small | OFS | 9 |  |  | VAV | Variable Air Volume | 0 | 2016
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD025 | 1996 | 240000 | Miscellaneous Commercial | MIC | 10 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 19
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48MA-024---630KA | 0 | 240000 | Education - Primary School | EPR | 8 |  |  | UNK |  | 0 | 2015
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48MA-024---630KA | 0 | 240000 | Education - Primary School | EPR | 8 |  |  | UNK |  | 0 | 2015
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD024 | 1996 | 240000 | Education - Primary School | EPR | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume | 3 | 19
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD024 | 1996 | 240000 | Restaurant - Sit-Down | RSD | 10 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume | 3 | 20
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJF024 | 1998 | 240000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume | 3 | 18
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DJ-024-600AC | 1992 | 240000 | Retail - Multistory Large | RT3 | 9 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume | 2 | 23
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK024300AD | 1990 | 240000 | Office - Small | OFS | 9 | 8.2 | 8.2 EER 7.2 IPLV | VAV | Variable Volume | 2 | 25
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK024600AD | 1990 | 240000 | Office - Small | OFS | 9 | 8.2 | 8.2 EER 7.2 IPLV | VAV | Variable Volume | 2 | 25
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50EQ024 | 1994 | 240000 | Manufacturing - Light Industrial | MLI | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 21
2014 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 579G240450YACD | 1981 | 240000 | Office - Small | OFS | 10 | 7.5 | 7.5 EER | UNK |  | 2 | 33
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | BYC200G4L0CC | 1991 | 240000 | Retail - Single-Story Large | RTL | 10 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 24
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | YORK | D2CG240N24046ECA | 1992 | 240000 | Miscellaneous Commercial | MIC | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 23
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | SnyderGeneral | R201EFLC | 1988 | 240000 | Office - Large | OFL | 10 | 7.5 | 7.5 EER | UNK |  | 2 | 28
2015 | 55to65kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Trane | RAUA-2003-B | 1974 | 240000 | Office - Small | OfS | 9 | 7.5 | 7.5 EER | UNK |  | 1 | 41
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SFHB2003L10F21D04 | 0 | 240000 | Education - Primary School | EPR | 8 |  |  | UNK |  | 0 | 2015
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | SFHB2004LG20F22S00 | 0 | 240000 | Assembly | ASM | 6 |  |  | UNK |  | 0 | 2015
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SFHB2004LK20F31D04 | 1990 | 240000 | Retail - Single-Story Large | RTL | 10 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 25
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SFHB200BLK20F022D04 | 0 | 240000 | Office - Small | OFS | 9 |  |  | UNK |  | 0 | 2016
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD240B4LAFA | 1998 | 240000 | Office - Small | OfS | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 18
2016 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD240B4LAFA | 1998 | 240000 | Office - Small | OfS | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 18
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD241C4L0AB | 1999 | 240000 | Industrial | IND | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 16
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD241C4LBAA | 1998 | 240000 | Education - Secondary School | ESE | 10 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 18
2015 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH240B3LBBA | 1992 | 240000 | Lodging - Motel | MTL | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 23
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJD024-- | 1991 | 238000 | Education - Community College | ECC | 10 | 8.5 | 8.5 EER 7.5 IPLV | CV | Constant Volume | 2 | 24
2014 | 240-760 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50DK-024- - A600MC | 1992 | 237000 | Retail - Single-Story Large | RTL | 9 | 8.5 | 8.5 EER 7.5 IPLV | VAV | Variable Volume | 2 | 22
2014 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP020 | 1994 | 212000 | Education - Primary School | EPR | 10 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 20
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | BYC200GA | 1987 | 210000 | Assembly | ASM | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD210C3L0BA | 1997 | 208000 | Education - Primary School | EPR | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD211C4LGAB | 1999 | 208000 | Education - Primary School | EPR | 6 | 8.5 | 8.5 EER | CV |  | 3 | 16
2015 | 135-240 kBtu/hr To Code Savings Portion Water-Source Heat Pump | Friedrich | V200-32 | 1989 | 200000 | Assembly | ASM | 15 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 26
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48DP016630 | 0 | 191480 | Education - Primary School | EPR | 8 |  |  | CV |  | 0 | 2015
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP - Payne | 579DP120231 | 1984 | 183000 | Miscellaneous Commercial | MIC | 10 | 7.5 | 7.5 EER | UNK |  | 2 | 30
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD180B3LOEA | 1997 | 183000 | Education - Primary School | EPR | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD180B3LOEA | 1997 | 183000 | Education - Primary School | EPR | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48MA-016---630KA | 0 | 182000 | Education - Primary School | EPR | 8 |  |  | UNK |  | 0 | 2015
2014 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 5590180 | 1983 | 180000 | Transportation - Communication - Utilities | TCU | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 31
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48DP016620 | 1990 | 180000 | Retail - Single-Story Large | RTL | 10 | 8.2 | 8.2 EER 7.2 IPLV | CV |  | 2 | 26
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48EJE017 | 0 | 180000 | Office - Small | OFS | 9 |  |  | CV |  | 0 | 2016
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD017 | 1997 | 180000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD017 | 2000 | 180000 | Education - Secondary School | ESE | 10 | 8.5 | 8.5 EER | CV |  | 3 | 15
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJE017-500QA | 1997 | 180000 | Education - Secondary School | ESE | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJF017 | 1997 | 180000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD016 | 1998 | 180000 | Office - Small | OFS | 9 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 18
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD016 | 1999 | 180000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER | CV |  | 3 | 17
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD016550QA | 2000 | 180000 | Office - Large | OFL | 6 | 8.5 | 8.5 EER | CV |  | 3 | 15
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50PQ016 | 1994 | 180000 | Manufacturing - Light Industrial | MLI | 9 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 22
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ-016 | 1988 | 180000 | Manufacturing - Light Industrial | MLI | 8 | 7.5 | 7.5 EER | CV |  | 2 | 27
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ-016 | 1998 | 180000 | Manufacturing - Light Industrial | MLI | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 17
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ016610MA | 1995 | 180000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 21
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | PAYNE | 579DPW180270AU | 1991 | 180000 | Education - Primary School | EPR | 14 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 24
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV120180 | 1992 | 180000 | Education - Primary School | EPR | 16 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 24
2015 | 135-240 kBtu/hr To Code Savings Portion Water-Source Heat Pump | a/c systems | C2ED180A25A | 1987 | 180000 | Assembly | ASM | 15 | 7.5 | 7.5 EER | UNK |  | 2 | 28
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D1HG180N24025ECA | 1981 | 180000 | Office - Large | OFL | 10 | 7.5 | 7.5 EER | UNK |  | 2 | 35
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Norsaire | NPPC-6DWX-1-S-3 | 1987 | 180000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | UNK |  | 2 | 29
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | TCD180B400EA | 1997 | 180000 | Transportation - Communication - Utilities | TCU | 6 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 18
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | TCH180B400FA | 2000 | 180000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER | CV |  | 3 | 15
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | TWA180B300BA | 1995 | 180000 | Office - Large | OFL | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 21
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | TWA180B300BA | 1995 | 180000 | Office - Large | OFL | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 21
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD180B320FA | 1998 | 180000 | Education - Community College | ECC | 6 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 17
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | YCD180B4LGBA | 1992 | 180000 | Assembly | ASM | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 2 | 24
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD181C4LGAA | 1999 | 180000 | Education - Primary School | EPR | 6 | 8.5 | 8.5 EER | CV |  | 3 | 17
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH180B3LBBA | 1992 | 180000 | Lodging - Motel | MTL | 9 | 8.5 | 8.5 EER 7.5 IPLV | VAV |  | 2 | 23
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH181C4LBAA | 1998 | 180000 | Education - Secondary School | ESE | 10 | 8.5 | 8.5 EER 7.5 IPLV | VAV |  | 3 | 18
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP016630 | 1992 | 178000 | Miscellaneous Commercial | MIC | 6 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 2 | 23
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP016630 | 1992 | 178000 | Miscellaneous Commercial | MIC | 6 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 2 | 23
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX INDUSTRIES | CHP16-1853-4G | 1993 | 178000 | Retail - Single-Story Large | RtL | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 22
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TMD016 | 2007 | 176000 | Office - Small | OFS | 6 | 9.7 | 9.7 EER | UNK |  | 5 | 9
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50HJ-017---500QA | 1996 | 175000 | Miscellaneous Commercial | MIC | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48DPO-16530 | 1992 | 174000 | Education - Primary School | EPR | 9 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 2 | 24
2014 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD016 | 1995 | 174000 | Education - Primary School | EPR | 9 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2014 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ016 | 1999 | 172000 | Assembly | ASM | 15 | 8.5 | 8.5 EER | CV |  | 3 | 15
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48DP016520MA | 1998 | 165000 | Assembly | ASM | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 18
2014 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48 HJD014-561 | 2002 | 150000 | Office - Small | OFS | 10 | 9.7 | 9.7 EER | CV |  | 4 | 12
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP014 | 1986 | 150000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER | CV |  | 2 | 29
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48DP014620 | 1990 | 150000 | Retail - Single-Story Large | RTL | 10 | 8.2 | 8.2 EER 7.2 IPLV | CV |  | 2 | 26
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DPE014510 | 1992 | 150000 | Office - Small | OFS | 14 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 2 | 24
2014 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DPE014600 | 1990 | 150000 | Manufacturing - Light Industrial | MLI | 8 | 8.2 | 8.2 EER 7.2 IPLV | CV |  | 2 | 24
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD014-531AA | 1997 | 150000 | Education - Secondary School | ESE | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48hjd014641 | 2000 | 150000 | Miscellaneous Commercial | MIC | 8 | 8.5 | 8.5 EER | CV |  | 3 | 15
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD014---641GA | 2000 | 150000 | Manufacturing - Light Industrial | MLI | 6 | 8.5 | 8.5 EER | CV |  | 3 | 15
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 559DE150000 | 1991 | 150000 | Office - Small | OFS | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 25
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 579C150300 | 1984 | 150000 | Miscellaneous Commercial | MIC | 10 | 7.5 | 7.5 EER | UNK |  | 2 | 30
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 579DP150231 | 1985 | 150000 | Miscellaneous Commercial | MIC | 10 | 7.5 | 7.5 EER | UNK |  | 2 | 30
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV150225 | 1992 | 150000 | Education - Primary School | EPR | 16 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 23
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV150225 | 1992 | 150000 | Education - Primary School | EPR | 16 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 23
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D2CG150 | 0 | 150000 | Education - Secondary School | ESE | 14 |  |  | UNK |  | 0 | 2016
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D2EG150N16525MFP | 2000 | 150000 | Restaurant - Sit-Down | RSD | 8 | 8.5 | 8.5 EER | UNK |  | 3 | 16
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D4CG150N16525MFC | 1994 | 150000 | Restaurant - Sit-Down | RSD | 10 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 22
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | DH150N15Q2BMA3 | 1995 | 150000 | Restaurant - Sit-Down | RSD | 8 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 21
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Rheem | RRGF-200125DLR | 1998 | 150000 | Manufacturing - Light Industrial | MLI | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 18
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX | TGA150S2BS1G | 2008 | 150000 | Office - Small | OfS | 8 | 9.7 | 9.7 EER | UNK |  | 5 | 8
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX | TGA150S2BS1G | 2008 | 150000 | Office - Small | OfS | 8 | 9.7 | 9.7 EER | UNK |  | 5 | 8
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD150C3LOBB | 2000 | 150000 | Restaurant - Sit-Down | RSD | 8 | 8.5 | 8.5 EER | CV |  | 3 | 16
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | YCD150D4LGBB | 1994 | 150000 | Assembly | ASM | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 22
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH151C4LOAA | 1998 | 150000 | Education - Secondary School | ESE | 10 | 8.5 | 8.5 EER 7.5 IPLV | VAV |  | 3 | 18
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | WCD150B40AFA | 2002 | 146000 | Manufacturing - Light Industrial | MLI | 10 | 9.7 | 9.7 EER | UNK |  | 4 | 14
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | WCD150B40AFA | 2002 | 146000 | Manufacturing - Light Industrial | MLI | 10 | 9.7 | 9.7 EER | UNK |  | 4 | 14
2014 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | LGA150SH1Y | 1996 | 145000 | Retail - Small | RTS | 6 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 3 | 18
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP014 | 1984 | 144000 | Assembly | ASM | 8 | 7.5 | 7.5 EER | CV |  | 2 | 31
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DPE 0141 - b | 1992 | 144000 | Education - Primary School | EPr | 9 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 2 | 23
2016 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD014641 | 1997 | 144000 | Office - Small | OFS | 8 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | BYC170G4LOCA | 1987 | 144000 | Miscellaneous Commercial | MIC | 10 | 7.5 | 7.5 EER | UNK |  | 2 | 28
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | GCS16-1603-270-4G | 1992 | 144000 | Education - Primary School | EPR | 9 | 8.5 | 8.5 EER 7.5 IPLV | UNK |  | 2 | 23
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | BYC170G4 | 1990 | 143000 | Office - Small | OFS | 8 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 25
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48DR014620MA | 1988 | 142000 | Education - Primary School | EPr | 14 | 7.5 | 7.5 EER | UNK |  | 2 | 27
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD014 | 1996 | 142000 | Restaurant - Sit-Down | RSD | 10 | 8.5 | 8.5 EER 7.5 IPLV | CV |  | 3 | 19
2014 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ014 | 1987 | 140000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | CV |  | 2 | 27
2014 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ014 | 1987 | 140000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER | CV |  | 2 | 27
2015 | 135-240 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ014600 | 1983 | 140000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER | CV |  | 2 | 32
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | GCS16-1353-270-5G | 1990 | 135300 | Education - Primary School | EPR | 9 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 25
2014 | 65-135 kBtu/hr 12 EER or 13.8 IEER Air Source Unitary Air Conditioner DX Equipment | Lennox | CHA16-1353-3X | 1990 | 135000 | Manufacturing - Light Industrial | MLI | 6 | 8.2 | 8.2 EER 7.2 IPLV | UNK |  | 2 | 24
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | LGA120SH1Y | 1996 | 126000 | Retail - Small | RTS | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP012-610 | 1984 | 120000 | Education - Primary School | EPR | 10 | 7.5 | 7.5 EER |  |  |  | 30
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DD012B | 1986 | 120000 | Office - Large | OFL | 6 | 7.5 | 7.5 EER |  |  |  | 29
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP012 | 1985 | 120000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 29
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP012 | 1989 | 120000 | Education - Secondary School | ESE | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 26
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP012 | 1991 | 120000 | Manufacturing - Light Industrial | MLI | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48DP012520MA | 1998 | 120000 | Assembly | ASM | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP-012---620MA | 1989 | 120000 | Office - Small | OFS | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 26
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD012 | 1995 | 120000 | Industrial | IND | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD012- 531 | 1999 | 120000 | Office - Large | OFL | 8 | 8.9 | 8.9 EER |  |  |  | 15
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD012-531AA | 1997 | 120000 | Education - Secondary School | ESE | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD012571HQ | 2003 | 120000 | Assembly | ASM | 6 | 10.3 | 10.3 EER |  |  |  | 13
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD012-62AA | 1994 | 120000 | Office - Small | OFS | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 20
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD012-631 | 1996 | 120000 | Miscellaneous Commercial | MiC | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD012---631-- | 1995 | 120000 | Miscellaneous Commercial | MIC | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 20
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD012---641-- | 1997 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD012---651-- | 1999 | 120000 | Agricultural | AGR | 6 | 8.9 | 8.9 EER |  |  |  | 16
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | carrier | 48hje017 | 1996 | 120000 | Manufacturing - Light Industrial | MLI | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HUD012-G31 | 0 | 120000 | Office - Small | OFS | 9 | [5 empty] | 2016
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48LJD012500 | 1991 | 120000 | Miscellaneous Commercial | MIC | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 24
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TFD012 | 2001 | 120000 | Office - Small | OFS | 6 | 10.3 | 10.3 EER |  |  |  | 14
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD012611 | 1996 | 120000 | Manufacturing - Light Industrial | MLI | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD012-611GA | 1998 | 120000 | Office - Small | OfS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD012-611QA | 1998 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD012621GA | 2000 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER |  |  |  | 16
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD012---621GA | 2000 | 120000 | Manufacturing - Light Industrial | MLI | 6 | 8.9 | 8.9 EER |  |  |  | 15
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJF012-611QA | 1998 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJF012-611QA | 1998 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ012 | 1999 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER |  |  |  | 17
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ012---631-- | 2004 | 120000 | Office - Small | OFS | 6 | 10.3 | 10.3 EER |  |  |  | 11
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50JH01225651` | 1994 | 120000 | Assembly | ASM | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50LJQ012 | 1994 | 120000 | Manufacturing - Light Industrial | MLI | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50LJQ012 | 1994 | 120000 | Manufacturing - Light Industrial | MLI | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50LJQ012 | 1995 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50LJQ012631GA | 1995 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50LJQ012---631GA | 1994 | 120000 | Assembly | ASM | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ012 | 1987 | 120000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 27
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ012 | 1987 | 120000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 27
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ012510 | 0 | 120000 | Retail - Single-Story Large | RTL | 10 | [5 empty] | 2015
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ012510 | 1990 | 120000 | Retail - Single-Story Large | RTL | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 26
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ012510MA | 1990 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 24
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ-012-600 | 1988 | 120000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 28
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ012600 | 1989 | 120000 | Miscellaneous Commercial | MIC | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 25
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ0126000AA | 1987 | 120000 | Manufacturing - Light Industrial | MLI | 8 | 7.5 | 7.5 EER |  |  |  | 27
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ012600AAA | 1990 | 120000 | Office - Small | OFS | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 25
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ012600MA | 1987 | 120000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER |  |  |  | 28
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ012600MA | 1990 | 120000 | Office - Small | OFS | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 25
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50RQ010600 | 1971 | 120000 | Office - Small | OFS | 6 | [5 empty] | 44
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50RQ010600 | 1983 | 120000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER |  |  |  | 32
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TCQ012601GA | 2000 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER |  |  |  | 15
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50TJQ012601 | 1996 | 120000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 566CPX135000AAAA/515C120CVHFS | 1983 | 120000 | Education - Primary School | EPR | 8 | 7.5 | 7.5 EER |  |  |  | 31
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 579C120300 | 1983 | 120000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER |  |  |  | 31
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 579DEW120231AAC | 1980 | 120000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER |  |  |  | 35
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | PAYNE | 580CPV120 | 1991 | 120000 | Education - Primary School | EPR | 14 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 24
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | PAYNE | 580CPV120 | 1991 | 120000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 24
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV120180 | 1992 | 120000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV120180 | 1992 | 120000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Bryant | 581BPV120180AJ | 2002 | 120000 | Restaurant - Sit-Down | RSD | 6 | 10.3 | 10.3 EER |  |  |  | 13
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Air Distribution Associates | ADA-RBG-120-23-2102-HO | 1981 | 120000 | Office - Small | OFS | 16 | 7.5 | 7.5 EER |  |  |  | 33
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | BDP542EX120 | 1990 | 120000 | Manufacturing - Light Industrial | MLI | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 26
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | BYC100G3L0AA | 1985 | 120000 | Restaurant - Sit-Down | RSD | 8 | 7.5 | 7.5 EER |  |  |  | 31
2014 | 65-135 kBtu/hr 12 EER or 13.8 IEER Air Source Unitary Air Conditioner DX Equipment | Trane | BYC120F430F0 | 1983 | 120000 | Manufacturing - Light Industrial | MLI | 6 | 7.5 | 7.5 EER |  |  |  | 31
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | BYC130G3L0DC | 0 | 120000 | Education - Primary School | EPR | 8 | [5 empty] | 2015
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | BYC130G4L0DB | 1987 | 120000 | Miscellaneous Commercial | MIC | 10 | 7.5 | 7.5 EER |  |  |  | 28
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | McQuay | CUR100FE05 | 1983 | 120000 | Retail - Single-Story Large | RTL | 10 | 7.5 | 7.5 EER |  |  |  | 31
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D1EG120N16525MBF | 1993 | 120000 | Restaurant - Sit-Down | RSD | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | unknown | D2CG120 | 0 | 120000 | Education - Secondary School | ESe | 14 | [5 empty] | 2015
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D3CG120N16546JSD | 1996 | 120000 | Manufacturing - Light Industrial | MLI | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D4CG120N16525JSA | 1982 | 120000 | Office - Large | OFL | 9 | 7.5 | 7.5 EER |  |  |  | 34
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D4CG120N16525MKA | 2000 | 120000 | Restaurant - Sit-Down | RSD | 10 | 8.9 | 8.9 EER |  |  |  | 16
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | YORK | D4CG120N16546JSA | 2000 | 120000 | Office - Small | OFS | 9 | 8.9 | 8.9 EER |  |  |  | 15
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | DH120N15S2BMA3 | 1995 | 120000 | Restaurant - Sit-Down | RSD | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Lennox/Goodman | LCS13DC-60/AH120-00 | 1983 | 120000 | Education - Primary School | EPR | 8 | 7.5 | 7.5 EER |  |  |  | 31
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | RHEEM | NamePlateFaded | 1990 | 120000 | Miscellaneous Commercial | MIC | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 25
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Rheem | RKKL-B120CL | 1994 | 120000 | Health/Medical - Clinic | CLI | 14 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX | TGA120H2BS1G | 2008 | 120000 | Office - Small | OfS | 8 | 10.3 | 10.3 EER |  |  |  | 8
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | HCGQ | UNREADABLE | 1984 | 120000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER |  |  |  | 32
2015 | 65-135 kBtu/hr To Code Savings Portion Water-Source Heat Pump | Friedrich | V120-322 | 1994 | 120000 | Assembly | ASM | 15 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD120B4BA | 1994 | 120000 | Assembly | ASM | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD120B4L3AA | 1991 | 120000 | Retail - Single-Story Large | RTL | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 24
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD120C3MOAC | 1998 | 120000 | Education - Community College | ECC | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 17
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD120C4LAAB | 1998 | 120000 | Office - Small | OfS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH121C4LFAA | 1999 | 120000 | Education - Primary School | EPR | 6 | 8.9 | 8.9 EER |  |  |  | 17
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJD012-500 | 1989 | 119000 | Restaurant - Sit-Down | RSD | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 27
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48MD012A-501 | 2006 | 119000 | Restaurant - Sit-Down | RSD | 8 | 10.3 | 10.3 EER |  |  |  | 10
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD012-511GA | 1997 | 119000 | Restaurant - Sit-Down | RSD | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50QP012600MA | 1985 | 119000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 30
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50TCD12A2A6A0A0A0 | 2002 | 119000 | Assembly | ASM | 8 | 10.3 | 10.3 EER |  |  |  | 14
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | BYC100G3L0AA | 1986 | 119000 | Restaurant - Sit-Down | RSD | 8 | 7.5 | 7.5 EER |  |  |  | 29
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | CHA16-1353-5G | 1992 | 119000 | Transportation - Communication - Utilities | TCU | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX | CHP161353G | 1993 | 119000 | Assembly | ASM | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | GCS16-1353-270-5G | 1990 | 119000 | Education - Primary School | EPR | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 24
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | GCS16-1353-270-6G | 1991 | 119000 | Education - Secondary School | ESE | 14 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 25
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | RHEEM | RRGF-200100CLR | 1986 | 119000 | Restaurant - Sit-Down | RSD | 6 | 7.5 | 7.5 EER |  |  |  | 30
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD120C3L0AC | 1985 | 119000 | Restaurant - Sit-Down | RSD | 8 | 7.5 | 7.5 EER |  |  |  | 30
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48TJD012501 | 1993 | 118000 | Miscellaneous Commercial | MIC | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ012-631 | 2004 | 118000 | Office - Small | OFS | 8 | [5 empty] | 12
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50PQ012 | 1986 | 118000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 30
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | SPCA-C106-A | 1988 | 118000 | Retail - Single-Story Large | RTL | 6 | 7.5 | 7.5 EER |  |  |  | 27
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD012 | 1995 | 117000 | Education - Primary School | EPR | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50HJQ012-501 | 1995 | 116000 | Health/Medical - Nursing Home | Nrs | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 20
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | BYC130G4 | 1990 | 115000 | Office - Small | OFS | 8 | [5 empty] | 25
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP012 | 1987 | 113000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 28
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50QJ012510GA | 1990 | 113000 | Health/Medical - Nursing Home | Nrs | 9 | [5 empty] | 25
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | YORK | DM120N15A2AAA1A | 2002 | 113000 | Office - Large | OFL | 6 | 10.3 | 10.3 EER |  |  |  | 12
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD121C3LBAA | 2008 | 113000 | Office - Large | OFL | 15 | [5 empty] | 8
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX | GCS14-1353-290A-2C | 0 | 112000 | Office - Small | OFS | 9 | [5 empty] | 2016
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP01 | 1988 | 110000 | Miscellaneous Commercial | MIC | 6 | 7.5 | 7.5 EER |  |  |  | 27
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DP012 | 1984 | 110000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 31
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | GCS16-1353-270-5Y | 1990 | 110000 | Restaurant - Sit-Down | RSD | 8 | [5 empty] | 25
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD009 | 1997 | 102000 | Education - Primary School | EPR | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 17
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD009-531 | 1997 | 102000 | Assembly | ASM | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 17
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD009-531AA | 1997 | 102000 | Education - Secondary School | ESE | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD009-621 | 1994 | 102000 | Office - Small | OFS | 13 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 20
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD009 | 2000 | 102000 | Office - Large | OFL | 6 | 8.9 | 8.9 EER |  |  |  | 16
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD009521 | 2000 | 102000 | Office - Large | OFL | 14 | 8.9 | 8.9 EER |  |  |  | 14
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD009611 | 1999 | 102000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER |  |  |  | 17
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD009---621 | 2000 | 102000 | Manufacturing - Light Industrial | MLI | 6 | 8.9 | 8.9 EER |  |  |  | 15
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV102 | 1992 | 102000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | BTC100GA | 1987 | 102000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 29
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX | TGA102H2BS1G | 2007 | 102000 | Office - Small | OfS | 8 | [5 empty] | 9
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH090C3LOAA | 1997 | 102000 | Education - Secondary School | ESE | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH103C4LFAB | 1999 | 101000 | Education - Primary School | EPR | 6 | 8.9 | 8.9 EER |  |  |  | 16
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48LJD008610 | 1992 | 100000 | Office - Small | OFS | 13 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV090125 | 1992 | 100000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV090125 | 1992 | 100000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV090125 | 1992 | 100000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | BTC100G400DC | 1985 | 100000 | Transportation - Communication - Utilities | TCU | 10 | 7.5 | 7.5 EER |  |  |  | 29
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | BTC100G400DC | 1994 | 100000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD103C3L0AA | 2006 | 99000 | Office - Large | OFL | 15 | [5 empty] | 10
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48TJD009551 | 1997 | 98000 | Miscellaneous Commercial | MIC | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48DJ009610GA | 1990 | 96000 | Assembly | ASM | 10 | [5 empty] | 25
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HV008-610 | 1984 | 95400 | Education - Primary School | EPR | 10 | 7.5 | 7.5 EER |  |  |  | 30
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | GCS16-953-200-3G | 1990 | 95300 | Education - Primary School | EPR | 9 | [5 empty] | 25
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580ZPV0072115 | 1992 | 93150 | Education - Primary School | EPr | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580ZPV072115 | 1992 | 93150 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50LJQ008610 | 1992 | 92000 | Miscellaneous Commercial | MIC | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV072115 | 1992 | 92000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD090C3L0BE | 1997 | 92000 | Education - Primary School | EPR | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48LDE008600AA | 1988 | 91000 | Education - Primary School | EPr | 14 | 7.5 | 7.5 EER |  |  |  | 27
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJD008 | 1991 | 90000 | Manufacturing - Light Industrial | MLI | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJD008620 | 1994 | 90000 | Office - Small | OfS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD008---521 | 1994 | 90000 | Office - Small | OFS | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD008---521-- | 1994 | 90000 | Miscellaneous Commercial | MIC | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD008-531 | 1999 | 90000 | Office - Large | OFL | 8 | 8.9 | 8.9 EER |  |  |  | 15
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD008---531 | 2000 | 90000 | Education - University | EUN | 9 | 8.9 | 8.9 EER |  |  |  | 15
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD008-531AA | 1997 | 90000 | Education - Secondary School | ESE | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD008---541 | 2004 | 90000 | Office - Large | OFL | 15 | [5 empty] | 12
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD008621 | 1994 | 90000 | Office - Small | OFS | 13 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 20
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD008631 | 1997 | 90000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD008-631 | 1997 | 90000 | Miscellaneous Commercial | MiC | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD008---631-- | 1998 | 90000 | Manufacturing - Light Industrial | MLI | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 16
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48LDD008, 48HJD008 | 1987 | 90000 | Manufacturing - Light Industrial | MLI | 8 | 7.5 | 7.5 EER |  |  |  | 27
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48LDD008650 | 1988 | 90000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER |  |  |  | 27
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48LDE008500 | 1998 | 90000 | Assembly | ASM | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48LDE008600 | 1989 | 90000 | Education - Secondary School | ESE | 10 | [5 empty] | 26
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48LDE008690 | 1988 | 90000 | Education - Secondary School | ESE | 10 | 7.5 | 7.5 EER |  |  |  | 27
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48LV008610 | 1988 | 90000 | Education - Secondary School | ESE | 10 | 7.5 | 7.5 EER |  |  |  | 27
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TFD008 | 2000 | 90000 | Office - Large | OFL | 6 | 8.9 | 8.9 EER |  |  |  | 16
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48TFD008---601GA | 2001 | 90000 | Manufacturing - Light Industrial | MLI | 9 | 10.3 | 10.3 EER |  |  |  | 14
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD008-521GA | 1998 | 90000 | Education - Primary School | EPR | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TJD008---521GA | 2000 | 90000 | Office - Large | OFL | 15 | 8.9 | 8.9 EER |  |  |  | 16
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD008---611GA | 1996 | 90000 | Office - Small | OfS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 20
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD008---611GA | 1997 | 90000 | Office - Small | OfS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD008621GA | 2000 | 90000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER |  |  |  | 16
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD008-621GA | 1998 | 90000 | Office - Small | OfS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD008---621GA | 1998 | 90000 | Office - Small | OfS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD008---621GA | 2000 | 90000 | Manufacturing - Light Industrial | MLI | 6 | 8.9 | 8.9 EER |  |  |  | 15
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TMD008A5 | 0 | 90000 | Office - Small | OFS | 6 | [5 empty] | 2015
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TMD008-A-501 | 2002 | 90000 | Office - Small | OFS | 10 | 10.3 | 10.3 EER |  |  |  | 12
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48TMD008-A-601 | 2007 | 90000 | Miscellaneous Commercial | MiC | 9 | [5 empty] | 8
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJ008631HQ | 2006 | 90000 | Lodging - Hotel | HTL | 6 | [5 empty] | 9
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ008 | 1998 | 90000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ008 | 2000 | 90000 | Office - Small | OFS | 10 | 8.9 | 8.9 EER |  |  |  | 16
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ008601 | 1995 | 90000 | Manufacturing - Light Industrial | MLI | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 20
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | carrier | 50HJQ008---601-- | 1996 | 90000 | Miscellaneous Commercial | MIC | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50LJQ008 | 1994 | 90000 | Office - Small | OFS | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50QD008 | 1990 | 90000 | Manufacturing - Light Industrial | MLI | 8 | [5 empty] | 26
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50QD008-610LD | 1985 | 90000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 30
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50QD008610MA | 1987 | 90000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER |  |  |  | 28
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50QJ008600 | 1989 | 90000 | Miscellaneous Commercial | MIC | 10 | [5 empty] | 25
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50QJ008600 | 1989 | 90000 | Miscellaneous Commercial | MIC | 10 | [5 empty] | 25
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50QJ008610MA | 1990 | 90000 | Office - Small | OFS | 6 | [5 empty] | 25
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50QJ-008---631GA | 1993 | 90000 | Office - Small | OFS | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50TCQD008A2A6A0 | 2008 | 90000 | Office - Small | OfS | 8 | [5 empty] | 8
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TFQ008 | 2001 | 90000 | Transportation - Communication - Utilities | TCU | 8 | 10.3 | 10.3 EER |  |  |  | 13
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TFQ008-501GA | 2001 | 90000 | Retail - Single-Story Large | RTL | 8 | 10.3 | 10.3 EER |  |  |  | 15
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TFQ008601GA | 2000 | 90000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER |  |  |  | 15
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ008 | 1996 | 90000 | Education - Primary School | EPR | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ008 | 1996 | 90000 | Education - Primary School | EPR | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ008 | 1996 | 90000 | Education - Primary School | EPR | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ008 | 1996 | 90000 | Education - Primary School | EPR | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ008 | 1996 | 90000 | Education - Primary School | EPR | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ008 | 1999 | 90000 | Manufacturing - Light Industrial | MLI | 6 | 8.9 | 8.9 EER |  |  |  | 16
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50TJQ008601 | 1996 | 90000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50tjq008-601 | 1996 | 90000 | Miscellaneous Commercial | MIC | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ008-601GA | 1998 | 90000 | Office - Small | OfS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 542D090 | 1983 | 90000 | Transportation - Communication - Utilities | TCU | 8 | 7.5 | 7.5 EER |  |  |  | 31
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 542FP090000 | 1988 | 90000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 27
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | day & night | 548CEX090000 | 1994 | 90000 | Office - Small | OFS | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 548CEX090000DAA | 1996 | 90000 | Transportation - Communication - Utilities | TCU | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 579DPW09146ACAS | 1986 | 90000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER |  |  |  | 29
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | PAYNE | 580CPV090 | 1991 | 90000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 24
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV090125 | 1992 | 90000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV090125 | 1992 | 90000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580CPV09125 | 1992 | 90000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Bryant | 580CPW90125 | 2000 | 90000 | Health/Medical - Clinic | CLI | 10 | 8.9 | 8.9 EER |  |  |  | 15
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BRYANT | 580FEV090125AAGA | 2000 | 90000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER |  |  |  | 16
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 585EP090146 | 1984 | 90000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER |  |  |  | 32
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 585EP090146 | 1984 | 90000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER |  |  |  | 32
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP/Carrier | 585EPW090146AGAS | 1986 | 90000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER |  |  |  | 28
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | BICH090--- | 1989 | 90000 | Office - Small | OFS | 6 | [5 empty] | 26
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | BICH090H46 | 1989 | 90000 | Office - Small | OFS | 6 | [5 empty] | 26
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | General Electric | BWC090C2002A | 1979 | 90000 | Office - Large | OFL | 6 | 6.1 | 6.1 EER |  |  |  | 36
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | BWC090F300 | 1988 | 90000 | Retail - Single-Story Large | RTL | 8 | 7.5 | 7.5 EER |  |  |  | 27
2014 | 65-135 kBtu/hr 12 EER or 13.8 IEER Air Source Unitary Air Conditioner DX Equipment | York | BYC090F424F0 | 1984 | 90000 | Manufacturing - Light Industrial | MLI | 6 | 7.5 | 7.5 EER |  |  |  | 30
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | CHP-10-953 | 1982 | 90000 | Education - Primary School | EPR | 14 | 7.5 | 7.5 EER |  |  |  | 34
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | unknown | D2CG090 | 0 | 90000 | Education - Secondary School | ESE | 14 | [5 empty] | 2015
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | unknown | D2CG090 | 0 | 90000 | Education - Secondary School | ESE | 14 | [5 empty] | 2015
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D3CE090A46JSC | 1997 | 90000 | Manufacturing - Light Industrial | MLI | 14 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D3CG090N16525E | 1986 | 90000 | Office - Small | OFS | 9 | 7.5 | 7.5 EER |  |  |  | 29
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D4CG090N13025 | 1982 | 90000 | Office - Large | OFL | 8 | 7.5 | 7.5 EER |  |  |  | 33
2014 | 65-135 kBtu/hr 12.5 EER or 14.8 IEER Air Source Unitary Air Conditioner DX Equipment | York | D4CG090N16546A | 2000 | 90000 | Manufacturing - Light Industrial | MLI | 9 | 8.9 | 8.9 EER |  |  |  | 14
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX | GCS11-953-120A-26 | 0 | 90000 | Office - Small | OFS | 9 | [5 empty] | 2016
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX | GCS16-953-200-60 | 1993 | 90000 | Education - Primary School | EPR | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | NA | 1970 | 90000 | Miscellaneous Commercial | MIC | 8 | [5 empty] | 45
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Rheem | RRGE-225-075CKR | 1985 | 90000 | Miscellaneous Commercial | MIC | 9 | 7.5 | 7.5 EER |  |  |  | 29
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | RHEEM | RRGF131075CLR | 1996 | 90000 | Miscellaneous Commercial | MIC | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Frigiking | RTA-90-225-37-l | 1982 | 90000 | Restaurant - Sit-Down | RSD | 9 | 7.5 | 7.5 EER |  |  |  | 33
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX | TGA90H2BS1G | 2008 | 90000 | Office - Small | OfS | 8 | [5 empty] | 8
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | WCD090A400AB | 1991 | 90000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 25
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | WCH090C300BC | 1995 | 90000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD090 | 1998 | 90000 | Restaurant - Sit-Down | RSD | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD090C3LOBE | 2000 | 90000 | Restaurant - Sit-Down | RSD | 8 | 8.9 | 8.9 EER |  |  |  | 16
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD090C4LABE | 1998 | 90000 | Office - Small | OfS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | YCD090C4LGAA | 1994 | 90000 | Assembly | ASM | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD090C4LOAA | 1993 | 90000 | Office - Small | OFS | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH075C3L0AA | 1992 | 90000 | Lodging - Motel | MTL | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH090C3L0BE | 1998 | 90000 | Education - Community College | ECC | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 17
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH090C4LOBE | 1998 | 90000 | Office - Small | OfS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | TRANE | YCH090D3LOBE | 1998 | 90000 | Office - Small | OFS | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 17
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJD008620 | 1991 | 89000 | Manufacturing - Light Industrial | MLI | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 25
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HF008U531 | 2000 | 89000 | Assembly | ASM | 6 | 8.9 | 8.9 EER |  |  |  | 16
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD008541 | 2002 | 89000 | Assembly | ASM | 6 | 10.3 | 10.3 EER |  |  |  | 14
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD008---631-- | 1996 | 89000 | Miscellaneous Commercial | MIC | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD008---631-- | 1999 | 89000 | Office - Small | OFS | 9 | 8.9 | 8.9 EER |  |  |  | 17
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD008-521GA | 1989 | 89000 | Restaurant - Sit-Down | RSD | 6 | [5 empty] | 27
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48TJD008-521QA | 1998 | 89000 | Miscellaneous Commercial | MIC | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 16
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD008-521QA | 1999 | 89000 | Miscellaneous Commercial | MIC | 8 | 8.9 | 8.9 EER |  |  |  | 15
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | York | D3CG090N16525MBE | 1995 | 89000 | Restaurant - Sit-Down | RSD | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | GCS11-953-120A | 1980 | 89000 | Restaurant - Sit-Down | RSD | 14 | 7.5 | 7.5 EER |  |  |  | 35
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | GCS16-953-200-3G | 1991 | 89000 | Education - Secondary School | ESE | 14 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 25
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | ICP | PGE090H224AA | 2008 | 89000 | Assembly | ASM | 6 | [5 empty] | 8
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | RHEEM | Unreadable | 1990 | 89000 | Restaurant - Sit-Down | RSD | 6 | [5 empty] | 26
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | RHEEM | UNREADABLE | 1992 | 89000 | Assembly | ASM | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 24
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD091D36BBE | 2008 | 89000 | Office - Large | OFL | 15 | [5 empty] | 8
2014 | 65-135 kBtu/hr 11.5 EER or 12.8 IEER Air Source Unitary Air Conditioner DX Equipment | Comfortmaker | PGA090H2H | 1997 | 88400 | Retail - Small | RTS | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 17
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ008 | 1997 | 88000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 17
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ008---601-- | 2001 | 88000 | Miscellaneous Commercial | MIC | 6 | 10.3 | 10.3 EER |  |  |  | 14
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | CHA16-953-4G | 1993 | 88000 | Transportation - Communication - Utilities | TCU | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | GCS16-953-200-3G | 1990 | 88000 | Education - Primary School | EPR | 10 | [5 empty] | 24
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HH008 | 1987 | 87000 | Education - Primary School | EPR | 10 | 7.5 | 7.5 EER |  |  |  | 27
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48LZ008510 | 1985 | 87000 | Office - Large | OFL | 10 | 7.5 | 7.5 EER |  |  |  | 30
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50QD08 | 1987 | 87000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 27
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Lennox | GCS16-953200-3Y | 1990 | 87000 | Restaurant - Sit-Down | RSD | 8 | [5 empty] | 25
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ008, 50HJQ008 | 1998 | 86000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 16
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD008-531 | 1997 | 85000 | Health/Medical - Nursing Home | Nrs | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | unknown | Unknown | 1987 | 84000 | Education - Primary School | EPR | 10 | 7.5 | 7.5 EER |  |  |  | 27
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD091D4LGBE | 1999 | 81000 | Education - Primary School | EPR | 6 | 8.9 | 8.9 EER |  |  |  | 16
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48SBA048080601 | 1992 | 80000 | Office - Small | OFS | 13 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50RQ008600 | 1983 | 80000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER |  |  |  | 32
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HD007 | 0 | 75500 | Education - Primary School | EPR | 10 | [5 empty] | 2014
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | WCD075C300AA | 1992 | 75000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | WCD075C300BA | 1994 | 75000 | Grocery | GRO | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 22
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD075C4LOAA | 1993 | 75000 | Office - Small | OFS | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD007-531 | 2001 | 74000 | Office - Large | OFL | 10 | 10.3 | 10.3 EER |  |  |  | 14
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ007 | 1998 | 74000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 16
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580CPV060074 | 1992 | 74000 | Education - Primary School | EPr | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580CPV060074 | 1992 | 74000 | Education - Primary School | EPr | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD007---611-- | 1999 | 73000 | Office - Small | OFS | 9 | 8.9 | 8.9 EER |  |  |  | 17
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48HJD-007-611 | 1993 | 73000 | Office - Small | OFS | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD007501 | 1993 | 73000 | Office - Large | OFL | 10 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 580BPV072115ABAS | 1990 | 73000 | Office - Small | OFS | 14 | [5 empty] | 25
2014 | 65-135 kBtu/hr 12 EER or 13.8 IEER Air Source Unitary Air Conditioner DX Equipment | York | D2CG072N07946AA | 1998 | 73000 | Manufacturing - Light Industrial | MLI | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 16
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | PGE10C72D125LB-6A | 1990 | 73000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 25
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Amana | 360C09020 | 1999 | 72000 | Miscellaneous Commercial | MIC | 9 | 8.9 | 8.9 EER |  |  |  | 16
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48djs007500 | 1987 | 72000 | Miscellaneous Commercial | MIC | 9 | 7.5 | 7.5 EER |  |  |  | 28
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HD007640 | 1988 | 72000 | Office - Small | OFS | 6 | 7.5 | 7.5 EER |  |  |  | 27
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HH007540 | 1988 | 72000 | Office - Small | OFS | 8 | 7.5 | 7.5 EER |  |  |  | 27
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD007 | 1997 | 72000 | Education - Primary School | EPR | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 17
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD007---631-- | 1997 | 72000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD007---631-- | 2000 | 72000 | Education - Secondary School | ESE | 10 | 8.9 | 8.9 EER |  |  |  | 15
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD007 | 2000 | 72000 | Office - Large | OFL | 6 | 8.9 | 8.9 EER |  |  |  | 16
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD007---501-- | 1995 | 72000 | Manufacturing - Light Industrial | MLI | 6 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 21
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD007-521 | 1997 | 72000 | Education - Secondary School | ESE | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TJD007---621-- | 2000 | 72000 | Manufacturing - Light Industrial | MLI | 6 | 8.9 | 8.9 EER |  |  |  | 15
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJ-007-14726-1 | 1996 | 72000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 20
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ007 | 1996 | 72000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 20
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 50HJQ007 | 2003 | 72000 | Office - Small | OFS | 8 | 10.3 | 10.3 EER |  |  |  | 12
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | cARRIER | 50HJQ007601 | 1999 | 72000 | Manufacturing - Light Industrial | MLI | 9 | 8.9 | 8.9 EER |  |  |  | 16
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HJQ007---601-- | 2000 | 72000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER |  |  |  | 16
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HKQ007-501 | 1997 | 72000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | cARRIER | 50TFQ007-6 | 2002 | 72000 | Manufacturing - Light Industrial | MLI | 9 | 10.3 | 10.3 EER |  |  |  | 13
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TFQ007611 | 2002 | 72000 | Office - Small | OFS | 8 | 10.3 | 10.3 EER |  |  |  | 14
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ007---611 | 1998 | 72000 | Manufacturing - Light Industrial | MLI | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580CPV060074 | 1992 | 72000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580ZPV072115 | 1992 | 72000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580ZPV72115 | 1992 | 72000 | Education - Primary School | EPR | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | BDP | 580ZPVO72115 | 1992 | 72000 | Education - Primary School | EPr | 16 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 23
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Armstrong | PGE10672D125LB-6A | 1984 | 72000 | Office - Small | OfS | 8 | 7.5 | 7.5 EER |  |  |  | 32
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | ICP | PHH072H0A00AAA | 2008 | 72000 | Office - Small | OFS | 8 | [5 empty] | 8
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | LENNOX | TGA072S2B51G | 2008 | 72000 | Office - Small | OfS | 8 | [5 empty] | 8
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD075C3LOAA | 1997 | 72000 | Education - Secondary School | ESE | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCH075C3LOAA | 1997 | 72000 | Education - Secondary School | ESE | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 19
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48DJE007510 | 1990 | 71000 | Office - Large | OFL | 10 | [5 empty] | 24
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48HJD007651 | 2001 | 70000 | Office - Small | OFS | 6 | 10.3 | 10.3 EER |  |  |  | 14
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 48TD007-601 | 2001 | 70000 | Office - Small | OFS | 6 | 10.3 | 10.3 EER |  |  |  | 14
2015 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | CARRIER | 48TJD007-501 | 1995 | 70000 | Health/Medical - Nursing Home | Nrs | 9 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 20
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50HCQ007---601 | 1999 | 70000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER |  |  |  | 17
2014 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ007 | 1998 | 70000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 16
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Carrier | 50TJQ007---611 | 1998 | 70000 | Office - Small | OFS | 8 | 8.9 | 8.9 EER 8.3 IPLV |  |  |  | 18
2016 | 65-135 kBtu/hr To Code Savings Portion Air Source Unitary Air Conditioner DX Equipment | Trane | YCD074C3LBBE | 2009 | 68000 | Office - Large | OFL | 15 | [5 empty] | 7
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS16-653-75-3G | 1990 | 65300 | Education - Primary School | EPR | 9 | [5 empty] | 25
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 48SB060080601 | 1992 | 64000 | Office - Small | OFS | 13 | 9.7 | 9.7 SEER |  |  |  | 22
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48HJD006 | 1995 | 63000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48HJD006 | 1997 | 63000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 17
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48HJD006---631 | 1999 | 63000 | Office - Small | OFS | 13 | [5 empty] | 15
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50LJQ006 | 1995 | 62000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJD006-631 | 1997 | 61000 | Miscellaneous Commercial | MiC | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50HJQ006(7) 549BEX060 | 1997 | 61000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 17
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCH061C3L0BD | 1995 | 61000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50QJ006520 | 1991 | 60500 | Education - Community College | ECC | 9 | 9.7 | 9.7 SEER |  |  |  | 25
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Payne | 0 | 0 | 60000 | Office - Small | OFS | 6 | [5 empty] | 2015
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Rheem | 0 | 0 | 60000 | Manufacturing - Light Industrial | MLI | 9 | [5 empty] | 2015
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Rheem | 0 | 0 | 60000 | Manufacturing - Light Industrial | MLI | 9 | [5 empty] | 2016
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Rheem | 0 | 0 | 60000 | Manufacturing - Light Industrial | MLI | 9 | [5 empty] | 2016
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 0 | 1998 | 60000 | Retail - Single-Story Large | RTL | 9 | 9.7 | 9.7 SEER |  |  |  | 17
2015 | 45to55kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Lennox | 12ACB60-3P | 1999 | 60000 | Education - Secondary School | ESe | 9 | [5 empty] | 16
2015 | 55to65kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Carrier | 38 CK 060 640 | 1993 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2015 | 55to65kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Carrier | 38 CK 060 670 | 1993 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2015 | 55to65kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Carrier | 38CK060540 | 1993 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2015 | 45to55kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | CARRIER | 38CKC060370 | 2004 | 60000 | Manufacturing - Light Industrial | MLI | 9 | [5 empty] | 11
2016 | <55kBtu/hr To Code Savings Portion Split System Heat Pump | Carrier | 38QR060C | 2003 | 60000 | Office - Small | OFS | 6 | [5 empty] | 13
2016 | 55to65kBtu/hr To Code Savings Portion Split System Heat Pump | Carrier | 38YRA060300 | 2000 | 60000 | Office - Small | OFS | 10 | [5 empty] | 16
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 485B - 060 10060 | 1992 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48BL006 | 1981 | 60000 | Office - Small | OfS | 9 | 6.8 | 6.8 EER |  |  |  | 35
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48DJD006600 | 1989 | 60000 | Retail - Single-Story Large | RTL | 14 | [5 empty] | 26
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48DP006A400AC | 1989 | 60000 | Office - Small | OFS | 6 | [5 empty] | 26
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GS-060090501 | 1999 | 60000 | Office - Small | OFS | 8 | [5 empty] | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GS-060090501 / 48GSN060090501 | 2000 | 60000 | Office - Large | OFL | 9 | [5 empty] | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48GSN060090501 | 2000 | 60000 | Assembly | ASM | 8 | [5 empty] | 16
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48GXN060090611-- | 2007 | 60000 | Lodging - Hotel | HTL | 6 | [5 empty] | 7
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HCMA06 | 1990 | 60000 | Office - Small | OFS | 16 | [5 empty] | 25
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJD006 | 2008 | 60000 | Assembly | ASM | 6 | [5 empty] | 8
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48HJD0063 | 1994 | 60000 | Industrial | IND | 9 | 9.7 | 9.7 SEER |  |  |  | 20
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48HJD006-521-- | 1994 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 20
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJD006---631-- | 2000 | 60000 | Education - Secondary School | ESE | 10 | [5 empty] | 15
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJD006B541 | 1990 | 60000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 25
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJL006541 | 2006 | 60000 | Assembly | ASM | 9 | [5 empty] | 10
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | carrier | 48HJL006---541 | 2002 | 60000 | Office - Small | OFS | 10 | [5 empty] | 12
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJL006---541-- | 2008 | 60000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 7
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJM006-M-41 | 2004 | 60000 | Health/Medical - Hospital | HSP | 6 | [5 empty] | 12
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LDE006600 | 1989 | 60000 | Education - Secondary School | ESE | 10 | [5 empty] | 26
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LDT006690 | 1988 | 60000 | Education - Secondary School | ESE | 10 | 6.8 | 6.8 EER |  |  |  | 27
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LDT006691 | 1988 | 60000 | Office - Small | OFS | 6 | 6.8 | 6.8 EER |  |  |  | 27
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48LH006 | 1999 | 60000 | Office - Small | OFS | 6 | [5 empty] | 15
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | CARRIER | 48LH006500 | 0 | 60000 | Assembly | ASM | 10 | [5 empty] | 2014
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 48LHA006500 | 1985 | 60000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 31
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48MNT060 | 1990 | 60000 | Office - Small | OFS | 16 | [5 empty] | 25
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48MNT060 | 1990 | 60000 | Office - Small | OFS | 16 | [5 empty] | 25
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48NLT060 | 2000 | 60000 | Education - Secondary School | ESE | 8 | [5 empty] | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48NMX060301BE | 1993 | 60000 | Assembly | ASM | 8 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 48SB0600805 | 1992 | 60000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48SB0600V | 1993 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48SS-060 | 1991 | 60000 | Restaurant - Sit-Down | RSD | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48SS-060080511AA | 1995 | 60000 | Education - Community College | ECC | 9 | 9.7 | 9.7 SEER |  |  |  | 21
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48TFD006-601GA | 2001 | 60000 | Manufacturing - Light Industrial | MLI | 9 | [5 empty] | 14
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TFL006-A-611 | 2005 | 60000 | Restaurant - Sit-Down | RSD | 6 | [5 empty] | 10
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TJ006-6-GA | 1994 | 60000 | Retail - Single-Story Large | RTL | 9 | 9.7 | 9.7 SEER |  |  |  | 21
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TJD006---611GA | 2000 | 60000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 15
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TJE006-601QA | 1998 | 60000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50EG006A610DA | 1993 | 60000 | Office - Small | OfS | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50EZ-A60---60-- | 2012 | 60000 | Transportation - Communication - Utilities | TCU | 6 | [5 empty] | 3
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50HJ-060-601AB | 1994 | 60000 | Transportation - Communication - Utilities | TCU | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50HJ-060-601AB | 1995 | 60000 | Transportation - Communication - Utilities | TCU | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJ-060-601AB | 1995 | 60000 | Transportation - Communication - Utilities | TCU | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJQ006 | 1997 | 60000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJQ006 | 2000 | 60000 | Office - Small | OFS | 10 | [5 empty] | 16
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJQ006 | 2001 | 60000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 14
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJQ006-501 | 1997 | 60000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50HJQ006---501-- | 1997 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 17
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | carrier | 50hjq006601 | 1997 | 60000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | carrier | 50hjq006601 | 1997 | 60000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJQ006--B601-- | 2001 | 60000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 14
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS060 | 1996 | 60000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS-060---301AB | 2001 | 60000 | Miscellaneous Commercial | MIC | 10 | [5 empty] | 14
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50HS060501AB | 1998 | 60000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS060-6 | 1995 | 60000 | Manufacturing - Light Industrial | MLI | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50HS-060---601AA | 1998 | 60000 | Manufacturing - Light Industrial | MLI | 6 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50hs-060-601ab | 1996 | 60000 | Manufacturing - Light Industrial | MLI | 10 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50JS060501 | 2001 | 60000 | Office - Small | OFS | 8 | [5 empty] | 15
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50JS060601 | 2001 | 60000 | Office - Small | OFS | 6 | [5 empty] | 14
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50JS-060-601 | 2005 | 60000 | Office - Small | OFS | 6 | [5 empty] | 10
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50JS-060---601 | 2004 | 60000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 11
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50NQ-060---511 | 1992 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50NQ060600 | 1990 | 60000 | Manufacturing - Light Industrial | MLI | 10 | [5 empty] | 25
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QD006620VA | 1986 | 60000 | Miscellaneous Commercial | MIC | 6 | 6.8 | 6.8 EER |  |  |  | 29
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QD006620VA | 1987 | 60000 | Office - Small | OFS | 6 | 6.8 | 6.8 EER |  |  |  | 28
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QD00662VA | 1987 | 60000 | Office - Small | OFS | 6 | 6.8 | 6.8 EER |  |  |  | 28
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50QH006600 | 1983 | 60000 | Office - Small | OFS | 6 | 6.8 | 6.8 EER |  |  |  | 32
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QH006620DA | 1987 | 60000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 29
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QJ00600 | 1989 | 60000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 26
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QJ006620GA | 1990 | 60000 | Office - Small | OFS | 6 | [5 empty] | 25
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QJQ06600 | 1989 | 60000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 26
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QQ060 | 1989 | 60000 | Office - Large | OFL | 9 | [5 empty] | 26
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50TJQ006 | 1996 | 60000 | Education - Primary School | EPR | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50TJQ006 | 1996 | 60000 | Education - Primary School | EPR | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50TJQ006 | 1996 | 60000 | Miscellaneous Commercial | MIC | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50TJQ006---501GA | 1999 | 60000 | Office - Small | OFS | 8 | [5 empty] | 17
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50TJQ06 | 1999 | 60000 | Office - Small | OFS | 6 | [5 empty] | 17
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50YQD060 | 1991 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 24
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Day & Night | 517GNX06000AAP | 1985 | 60000 | Education - Community College | ECC | 8 | 6.8 | 6.8 EER |  |  |  | 29
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 520CPV060074 | 1993 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | CARRIER | 541DB060 | 1986 | 60000 | Office - Small | OFS | 8 | 6.8 | 6.8 EER |  |  |  | 28
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | BDP | 542EP060 | 1983 | 60000 | Transportation - Communication - Utilities | TCU | 8 | 6.8 | 6.8 EER |  |  |  | 31
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 542ER060000AAAP | 1981 | 60000 | Miscellaneous Commercial | MIC | 9 | 6.8 | 6.8 EER |  |  |  | 34
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | 542GE060 | 1988 | 60000 | Education - Primary School | EPR | 8 | 6.8 | 6.8 EER |  |  |  | 27
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 549BEX060 | 1998 | 60000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 16
2015 | 55to65kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Day and Night | 561AE060-E | 1993 | 60000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Day & Night | 580AP0608013 | 1989 | 60000 | Education - University | EUN | 9 | [5 empty] | 26
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Day & Night | 580AP0608013 | 1989 | 60000 | Education - University | EUN | 9 | [5 empty] | 26
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | BDP | 580BPV060115ACAR | 1990 | 60000 | Transportation - Communication - Utilities | TCU | 6 | [5 empty] | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580CPV060074 | 1992 | 60000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580CPV060074 | 1992 | 60000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580CPV060074 | 1992 | 60000 | Education - Primary School | EPr | 16 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580CPV060074 | 1992 | 60000 | Education - Primary School | EPr | 16 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580CPV060074 | 1992 | 60000 | Education - Primary School | EPr | 16 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580CPV060074 | 1992 | 60000 | Education - Primary School | EPr | 16 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BRYANT | 580DPV060074ABAB | 1992 | 60000 | Education - Primary School | EPr | 16 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Bryant | 582APW060090NAAG | 2006 | 60000 | Office - Small | OfS | 16 | [5 empty] | 10
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Bryant | 582APW060115AAAG | 1990 | 60000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 25
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584AP060100AB | 1991 | 60000 | Miscellaneous Commercial | MIC | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | PAYNE | 584APW060 | 1991 | 60000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | PAYNE | 584APW060 | 1991 | 60000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Day & Night | 584APW06000800AAAR | 1991 | 60000 | Industrial | IND | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Day & Night | 584APW060100 | 1991 | 60000 | Office - Small | OFS | 10 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 585HB060100ABAG | 1985 | 60000 | Health/Medical - Clinic | CLI | 6 | 6.8 | 6.8 EER |  |  |  | 30
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 585HE060100 | 1987 | 60000 | Education - Primary School | EPr | 14 | 6.8 | 6.8 EER |  |  |  | 28
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Day and Night | 585HPW060100ACEG | 1987 | 60000 | Office - Large | OFL | 10 | 6.8 | 6.8 EER |  |  |  | 27
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | BDP | 585JE060100 | 1985 | 60000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 29
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | BDP | 585JE060100 | 1985 | 60000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 29
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | BDP/Day and Night (Carrier) | 585JPW060100ABEG | 1986 | 60000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 28
2014 | <65kBtu/hr 15 SEER (12 EER/12.5 EER) Package/Split System Air Conditioner DX Equipment | BDP/Carrier | 588APW060090 (588APW06080ABBG) | 1994 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 20
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Bryant | 601APX0600000AAAG | 2008 | 60000 | Office - Small | OFS | 6 | [5 empty] | 6
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | PAYNE | 654AEX060000AAEG | 1990 | 60000 | Office - Small | OfS | 8 | [5 empty] | 26
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | 655APX060000AAAG | 1994 | 60000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 22
2015 | <65kBtu/hr To Code Savings Portion Water-Source Heat Pump | Friedrich | 803-060H | 1991 | 60000 | Assembly | ASM | 15 | 9.7 | 9.7 SEER |  |  |  | 24
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | York | B1HH024A06A | 2003 | 60000 | Transportation - Communication - Utilities | TCU | 8 | [5 empty] | 11
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | York | B1HH060A46B | 1998 | 60000 | Transportation - Communication - Utilities | TCU | 8 | 9.7 | 9.7 SEER |  |  |  | 16
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | York | B1HH060A46B | 2001 | 60000 | Transportation - Communication - Utilities | TCU | 8 | [5 empty] | 13
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | York | B2CH060A25A | 1989 | 60000 | Office - Small | OFS | 6 | [5 empty] | 26
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | York | B3CH060A25A | 1994 | 60000 | Miscellaneous Commercial | MIC | 6 | 9.7 | 9.7 SEER |  |  |  | 21
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | General Electric | BWC060C300B | 1979 | 60000 | Office - Large | OFL | 6 | 6.1 | 6.1 EER |  |  |  | 36
2015 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Tempstar | CA5060VKA1 | 1988 | 60000 | Miscellaneous Commercial | MIC | 16 | 6.8 | 6.8 EER |  |  |  | 27
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | CHP 15-511-1P | 1993 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | LENNOX | CHP15-311-1P | 1985 | 60000 | Office - Large | OFL | 10 | 6.8 | 6.8 EER |  |  |  | 30
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | CHP15-512-1P | 1993 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | CHP-15-513-1P | 1993 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | CHP15-653-1G | 1986 | 60000 | Office - Large | OFL | 6 | 6.8 | 6.8 EER |  |  |  | 29
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | CHP15-653-1Y | 1986 | 60000 | Manufacturing - Light Industrial | MLI | 10 | 6.8 | 6.8 EER |  |  |  | 29
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D1HG6060N09925MBB | 2000 | 60000 | Restaurant - Sit-Down | RSD | 8 | [5 empty] | 16
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D1NH060N06525C | 2006 | 60000 | Office - Large | OFL | 10 | [5 empty] | 9
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | York | D2NA060N06525D | 2001 | 60000 | Office - Small | OFS | 9 | [5 empty] | 13
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D3CG060 | 0 | 60000 | Education - Secondary School | ESE | 14 | [5 empty] | 2015
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D3CG060 | 0 | 60000 | Education - Secondary School | ESE | 14 | [5 empty] | 2015
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | YORK | D3NZ060N09025NXA | 2009 | 60000 | Office - Small | OFS | 10 | [5 empty] | 7
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D7CG060N07925A | 1999 | 60000 | Office - Large | OFL | 8 | [5 empty] | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D7CG060N07925MBB | 1999 | 60000 | Restaurant - Sit-Down | RSD | 10 | [5 empty] | 17
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | YORK | DJ060N08N2AAA3A | 2007 | 60000 | Transportation - Communication - Utilities | TCU | 8 | [5 empty] | 8
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS10X-651-75-3P | 1987 | 60000 | Manufacturing - Light Industrial | MLI | 8 | 6.8 | 6.8 EER |  |  |  | 28
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS16-060-120 | 1993 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS16-653-75-3G | 1991 | 60000 | Education - Secondary School | ESE | 14 | 9.7 | 9.7 SEER |  |  |  | 25
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS16-653-75-5G | 1992 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS16-653-75-5G | 1992 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS16-653-75-5G | 1992 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS653-12A | 0 | 60000 | Office - Small | OFS | 9 | [5 empty] | 2016
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | GCSOX-653-73-3 | 1998 | 60000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | 55to65kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Lennox | HS 24 - 653 - 1G | 1993 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2015 | 55to65kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Lennox | HS26-60-6G | 1992 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | LGA060SS1Y | 1999 | 60000 | Office - Small | OFS | 8 | [5 empty] | 17
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | N/R | 1992 | 60000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Payne | PA10JA060-A | 1987 | 60000 | Education - Primary School | EPR | 9 | 6.8 | 6.8 EER |  |  |  | 29
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | GOODMAN | PGB060100-1 | 1999 | 60000 | Health/Medical - Clinic | CLI | 9 | [5 empty] | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | ICP | PHF060200EHPFM60L00E | 1994 | 60000 | Assembly | ASM | 8 | 9.7 | 9.7 SEER |  |  |  | 22
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | PY3GEAA60090NA | 2011 | 60000 | Office - Small | OFS | 8 | [5 empty] | 5
2015 | 55to65kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Amana | RCB60B28 | 1999 | 60000 | Education - Secondary School | ESE | 9 | [5 empty] | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Rheem | RKMAA060DM10E | 2006 | 60000 | Assembly | ASM | 9 | [5 empty] | 10
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | RPND-058D | 1992 | 60000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Rheem | RRGG10E61CLR | 1998 | 60000 | Assembly | ASM | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Amana | SPCC600901A | 1988 | 60000 | Education - University | EUN | 9 | 6.8 | 6.8 EER |  |  |  | 27
2015 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Tempstar | T2A360GKA100 | 2006 | 60000 | Miscellaneous Commercial | MIC | 16 | [5 empty] | 9
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | unknown | 1995 | 60000 | Education - Primary School | EPR | 8 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC060F300BF | 2000 | 60000 | Education - Community College | ECC | 6 | [5 empty] | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC060F400BB | 1997 | 60000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC060F400BF | 1999 | 60000 | Office - Small | OFS | 6 | [5 empty] | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCD060a300BA | 1990 | 60000 | Education - Secondary School | ESE | 8 | [5 empty] | 26
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | WCD060C300BB | 1994 | 60000 | Grocery | GRO | 10 | 9.7 | 9.7 SEER |  |  |  | 22
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCD060C300BC | 1996 | 60000 | Grocery | GRO | 6 | 9.7 | 9.7 SEER |  |  |  | 20
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | YORK | XP060C00N1AAA2 | 1989 | 60000 | Office - Large | OFL | 10 | [5 empty] | 25
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | XXXXXXXX | 0 | 60000 | Miscellaneous Commercial | MIC | 10 | [5 empty] | 2015
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCC060F3M0BF | 1998 | 60000 | Education - Community College | ECC | 6 | 9.7 | 9.7 SEER |  |  |  | 17
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | ycc060F3m0BF | 1999 | 60000 | Miscellaneous Commercial | MiC | 9 | [5 empty] | 16
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCC060F3M0BH | 2001 | 60000 | Office - Large | OFL | 10 | [5 empty] | 14
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCC060F3MOBA | 1997 | 60000 | Education - Secondary School | ESE | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCC060F4MOBF | 1998 | 60000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | TRANE | YCD060A3L0AA | 0 | 60000 | Education - Primary School | EPR | 8 | [5 empty] | 2015
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCD060A4L0AB | 1990 | 60000 | Office - Small | OFS | 8 | [5 empty] | 26
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCD060C4LABE | 1998 | 60000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Trane | YCD060C4LOAA & | 1993 | 60000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCD061C3LBBE | 2008 | 60000 | Office - Large | OFL | 15 | [5 empty] | 8
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | TRANE | YCD60C4LGAA | 1994 | 60000 | Assembly | ASM | 8 | 9.7 | 9.7 SEER |  |  |  | 22
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Trane | YCL060 | 1987 | 60000 | Education - Secondary School | ESE | 8 | 6.8 | 6.8 EER |  |  |  | 27
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48DJD006520 | 1989 | 59500 | Office - Small | OFS | 8 | [5 empty] | 26
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS16-651-125-1P | 0 | 59500 | Office - Small | OFS | 9 | [5 empty] | 2016
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48TJD006 | 1994 | 59200 | Office - Small | OFS | 13 | 9.7 | 9.7 SEER |  |  |  | 20
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580CPV060074 | 1992 | 59200 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 23
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Day and Night | 580AP00**00 | 1989 | 59000 | Office - Large | OFL | 10 | [5 empty] | 25
2015 | 55to65kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Carrier | 38EDD060300 | 0 | 58500 | Education - Primary School | EPR | 9 | [5 empty] | 2015
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Payne | 654AE060AB | 1991 | 58500 | Manufacturing - Light Industrial | MLI | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Lennox | GCS10X653753G | 1987 | 58500 | Industrial | IND | 9 | 6.8 | 6.8 EER |  |  |  | 27
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Lennox | GCS16-653-125-5G: | 1990 | 58500 | Education - Primary School | EPR | 10 | [5 empty] | 24
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Lennox | GCS16-653-125-5G: | 1990 | 58500 | Education - Primary School | EPR | 10 | [5 empty] | 24
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Lennox | GCS16-653-125-5G: | 1990 | 58500 | Education - Primary School | EPR | 10 | [5 empty] | 24
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Lennox | GCS16-653-125-5G: | 1990 | 58500 | Education - Primary School | EPR | 10 | [5 empty] | 24
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS16-653-75-5Y | 1992 | 58500 | Education - Primary School | EPr | 8 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | RRGF135065CKR | 1990 | 58500 | Transportation - Communication - Utilities | TCU | 8 | [5 empty] | 25
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48LDT006-610: | 1984 | 58000 | Education - Primary School | EPR | 10 | 6.8 | 6.8 EER |  |  |  | 30
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48GS06009050 | 0 | 58000 | Miscellaneous Commercial | MIC | 10 | [5 empty] | 2015
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48HDT006-610 | 1984 | 58000 | Education - Primary School | EPR | 10 | 6.8 | 6.8 EER |  |  |  | 30
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD006-611 | 1993 | 58000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LDT006510 | 1985 | 58000 | Office - Large | OFL | 10 | 6.8 | 6.8 EER |  |  |  | 30
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48LDT006-610 | 1984 | 58000 | Education - Primary School | EPR | 10 | 6.8 | 6.8 EER |  |  |  | 30
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48LDT006-610: | 1984 | 58000 | Education - Primary School | EPR | 10 | 6.8 | 6.8 EER |  |  |  | 30
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48LDT006-610: | 1984 | 58000 | Education - Primary School | EPR | 10 | 6.8 | 6.8 EER |  |  |  | 30
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50HJQ006-511 | 2002 | 58000 | Health/Medical - Nursing Home | Nrs | 9 | [5 empty] | 13
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJQ006MC611HQ | 2003 | 58000 | Office - Small | OFS | 6 | [5 empty] | 12
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS-060-501 | 1993 | 58000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50LJQ006-520 | 1992 | 58000 | Miscellaneous Commercial | MIC | 10 | 9.7 | 9.7 SEER |  |  |  | 23
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50QJ006610 | 1989 | 58000 | Miscellaneous Commercial | MIC | 10 | [5 empty] | 25
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QJ006610 | 1989 | 58000 | Retail - Single-Story Large | RTL | 10 | [5 empty] | 26
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QJ006650 | 1992 | 58000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 24
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Day & Night | 50QQ060* | 1989 | 58000 | Office - Small | OFS | 6 | [5 empty] | 25
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50TJQ006 | 1999 | 58000 | Office - Small | OFS | 8 | [5 empty] | 17
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | BDP | 542EP060 | 1986 | 58000 | Office - Small | OFS | 6 | 6.8 | 6.8 EER |  |  |  | 30
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | BDP | 542EPX060000AAAP | 1986 | 58000 | Miscellaneous Commercial | MIC | 6 | 6.8 | 6.8 EER |  |  |  | 29
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 585EPC60100 | 1985 | 58000 | Office - Small | OfS | 16 | 6.8 | 6.8 EER |  |  |  | 31
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 585EPC60100 | 1985 | 58000 | Office - Small | OfS | 16 | 6.8 | 6.8 EER |  |  |  | 31
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 585epc60100 | 1985 | 58000 | Office - Small | OFS | 16 | 6.8 | 6.8 EER |  |  |  | 31
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 585epc60100 | 1985 | 58000 | Office - Small | OFS | 16 | 6.8 | 6.8 EER |  |  |  | 31
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 585epc60100 | 1985 | 58000 | Office - Small | OFS | 16 | 6.8 | 6.8 EER |  |  |  | 31
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | YORK | B3HP60A06A | 0 | 58000 | Office - Large | OFL | 10 | [5 empty] | 2015
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS9-653-120 A | 1980 | 58000 | Restaurant - Sit-Down | RSD | 14 | 6.8 | 6.8 EER |  |  |  | 35
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Ruud | UPND-058c | 1991 | 58000 | Miscellaneous Commercial | MIC | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCD061C4LCBF | 1999 | 58000 | Education - Primary School | EPR | 6 | [5 empty] | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48DJD006550 | 1992 | 57500 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48DJD006550 | 1992 | 57500 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48DJD006550 | 1992 | 57500 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD006---531-- | 1999 | 57500 | Office - Small | OFS | 9 | [5 empty] | 17
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD006---531-- | 2000 | 57500 | Office - Small | OFS | 9 | [5 empty] | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD006---631-- | 1999 | 57500 | Office - Small | OFS | 9 | [5 empty] | 17
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | CARRIER | 48TJD006-5010QA | 1998 | 57500 | Miscellaneous Commercial | MIC | 8 | 9.7 | 9.7 SEER |  |  |  | 16
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TJD006501GA | 1993 | 57500 | Office - Large | OFL | 10 | 9.7 | 9.7 SEER |  |  |  | 23
2014 | 55-64kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48TJD006-501QA | 1998 | 57500 | Miscellaneous Commercial | MIC | 8 | 9.7 | 9.7 SEER |  |  |  | 16
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50HS060601 | 1997 | 57500 | Miscellaneous Commercial | MIC | 8 | 9.7 | 9.7 SEER |  |  |  | 17
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50NQ060610 | 1991 | 57500 | Manufacturing - Light Industrial | MLI | 6 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580BPV060115ACAR | 1990 | 57500 | Office - Small | OFS | 14 | [5 empty] | 25
2016 | 55to65kBtu/hr To Code Savings Portion Split System Heat Pump | Carrier | 38YKB060300 | 1992 | 57000 | Office - Large | OFL | 10 | 9.7 | 9.7 SEER |  |  |  | 24
2014 | <65kBtu/hr 16 SEER (12.4 EER/13 EER) Package/Split System Air Conditioner DX Equipment | Carrier | 48TJD006611GA | 1999 | 57000 | Office - Large | OFL | 6 | [5 empty] | 15
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJQ006---601 | 1999 | 57000 | Office - Small | OFS | 8 | [5 empty] | 17
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QJ006500 | 1987 | 57000 | Restaurant - Fast Food | RFF | 9 | 6.8 | 6.8 EER |  |  |  | 28
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50QQ-060 | 1995 | 57000 | Health/Medical - Clinic | Cli | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50TJQ006 | 1998 | 57000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 16
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50TJQ006-301GA | 1998 | 57000 | Assembly | Asm | 9 | 9.7 | 9.7 SEER |  |  |  | 17
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50TJQ006---601GA | 1998 | 57000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | PAYNE | 654ANX060000 | 1992 | 57000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | 655APX060 | 1990 | 57000 | Health/Medical - Clinic | CLI | 9 | [5 empty] | 25
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48DJD005630 | 0 | 56000 | Education - Primary School | EPr | 8 | [5 empty] | 2015
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48DJD007630 | 0 | 56000 | Education - Primary School | EPR | 8 | [5 empty] | 2015
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48NLT06051B | 1992 | 56000 | Miscellaneous Commercial | MIC | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2014 | 55-64kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50QV06 | 1985 | 56000 | Office - Small | OFS | 8 | 6.8 | 6.8 EER |  |  |  | 29
2016 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Rheem | RRCF-5318756L3 | 1986 | 56000 | Restaurant - Sit-Down | RSD | 6 | 6.8 | 6.8 EER |  |  |  | 30
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48SS060080531-AA | 1998 | 55500 | Health/Medical - Clinic | CLI | 14 | 9.7 | 9.7 SEER |  |  |  | 17
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Bard | PH1060-B | 2006 | 55500 | Health/Medical - Clinic | CLI | 10 | [5 empty] | 9
2015 | 55to65kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCD060A4 | 1990 | 53000 | Office - Small | OFS | 8 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS16-513-125-1G | 1990 | 51300 | Education - Primary School | EPR | 9 | [5 empty] | 25
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD005---611-- | 1993 | 50000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48TJD005501 | 0 | 49000 | Miscellaneous Commercial | MIC | 10 | [5 empty] | 2015
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | TRANE | YCD048C4L0BF | 0 | 49000 | Office - Small | OFS | 9 | [5 empty] | 2016
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48SB036060601 | 1994 | 48600 | Office - Small | OFS | 13 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48DJD005530 | 1992 | 48500 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48DJD005530 | 1992 | 48500 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48DJD005530 | 1992 | 48500 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48HJD005 | 1995 | 48500 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD005---531-- | 1999 | 48500 | Office - Small | OFS | 9 | [5 empty] | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD005---531-- | 2000 | 48500 | Office - Small | OFS | 9 | [5 empty] | 16
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD005---611-- | 1999 | 48500 | Office - Small | OFS | 9 | [5 empty] | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD005---631-- | 1999 | 48500 | Office - Small | OFS | 9 | [5 empty] | 17
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48ljd005620 | 1992 | 48500 | Miscellaneous Commercial | MIC | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TJD005501GA | 1993 | 48500 | Office - Large | OFL | 10 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | RHEEM | HC-160-48-43C | 1975 | 48500 | Manufacturing - Light Industrial | MLI | 9 | [5 empty] | 40
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 0 | 0 | 48000 | Manufacturing - Light Industrial | MLI | 9 | [5 empty] | 2016
2016 | 45to55kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | LENNOX | 10AC36-7P | 1993 | 48000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Split System Heat Pump | Carrier | 38EZA042510/FB4ANF048000AFA | 2002 | 48000 | Office - Large | OFL | 6 | [5 empty] | 13
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | CARRIER | 38HPC048 | 1996 | 48000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 485DN048090301 | 2006 | 48000 | Health/Medical - Nursing Home | NRS | 10 | [5 empty] | 10
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48C1042520C | 1978 | 48000 | Miscellaneous Commercial | MIC | 10 | 6.1 | 6.1 EER |  |  |  | 37
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48DJD005 | 1989 | 48000 | Office - Small | OFS | 8 | [5 empty] | 26
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48DJD005530 | 0 | 48000 | Education - Primary School | EPr | 8 | [5 empty] | 2015
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 48DJD005610 | 1991 | 48000 | Manufacturing - Light Industrial | MLI | 8 | 9.7 | 9.7 SEER |  |  |  | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48DJD005630 | 0 | 48000 | Education - Primary School | EPr | 8 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GSN048090 | 2001 | 48000 | Office - Small | OFS | 6 | [5 empty] | 14
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GSN048090311 | 2005 | 48000 | Office - Large | OFL | 6 | [5 empty] | 10
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48HJD005 | 1997 | 48000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD005 | 1998 | 48000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJD005-321 | 1994 | 48000 | Health/Medical - Clinic | CLI | 8 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJD005-531AA | 1997 | 48000 | Education - Secondary School | ESE | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD005---611-- | 1993 | 48000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJD005---631-- | 2000 | 48000 | Education - Secondary School | ESE | 10 | [5 empty] | 15
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier / RHEEM | 48HJD005B541 | 1990 | 48000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJL005651 | 2001 | 48000 | Office - Small | OFS | 6 | [5 empty] | 14
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48KLA048090-601 | 1985 | 48000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 30
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48KLA048-500BE | 1985 | 48000 | Miscellaneous Commercial | MIC | 10 | 6.8 | 6.8 EER |  |  |  | 30
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LDJ005320 | 1992 | 48000 | Assembly | ASM | 8 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LJD005620 | 1992 | 48000 | Miscellaneous Commercial | MIC | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LJD005620 | 1992 | 48000 | Miscellaneous Commercial | MIC | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48NLT048620 | 1991 | 48000 | Miscellaneous Commercial | MIC | 6 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48TFD005 | 2001 | 48000 | Manufacturing - Light Industrial | MLI | 9 | [5 empty] | 14
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TJD005---611GA | 1997 | 48000 | Manufacturing - Light Industrial | MLI | 6 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TJE005---601 | 1996 | 48000 | Restaurant - Sit-Down | RSD | 10 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48XPN048 | 2006 | 48000 | Manufacturing - Light Industrial | MLI | 8 | [5 empty] | 9
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJ005641HQ | 2006 | 48000 | Lodging - Hotel | HTL | 6 | [5 empty] | 9
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJ-048-601AB | 1995 | 48000 | Transportation - Communication - Utilities | TCU | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJQ005 | 1998 | 48000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50HJQ007-621 | 2006 | 48000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 10
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS048 | 1994 | 48000 | Industrial | IND | 9 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS048 | 1995 | 48000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS048 | 1996 | 48000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS-048---621AB | 1998 | 48000 | Manufacturing - Light Industrial | MLI | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50LJQ005 | 1996 | 48000 | Education - Primary School | EPR | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50LJQ005 | 1996 | 48000 | Education - Primary School | EPR | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50LJQ005541GA | 1994 | 48000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50LQJ005 | 1996 | 48000 | Education - Primary School | EPR | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50MQ048501 | 1990 | 48000 | Office - Small | OFS | 8 | [5 empty] | 24
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Day & Night | 50NQ048 | 1990 | 48000 | Manufacturing - Light Industrial | MLI | 8 | [5 empty] | 26
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50NQ-048--6 | 1991 | 48000 | Miscellaneous Commercial | MIC | 6 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50TFQ005-A-611 | 2002 | 48000 | Office - Small | OFS | 8 | [5 empty] | 14
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50TJQ005 | 1996 | 48000 | Education - Primary School | EPR | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | unknown | 50YQ048610 | 0 | 48000 | Office - Small | OFS | 6 | [5 empty] | 2016
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | 542GE048 | 1987 | 48000 | Education - Primary School | EPR | 8 | 6.8 | 6.8 EER |  |  |  | 28
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 548APW048 | 1991 | 48000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Bryan | 548FEX0480000ABGA | 2006 | 48000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 10
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Bryan | 548FEX0480000ABGA | 2006 | 48000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 10
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 548FEX048000ABGA | 2006 | 48000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 10
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | 564bpx048000 | 1992 | 48000 | Miscellaneous Commercial | MIC | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Day & Night | 584AN048080 | 1994 | 48000 | Assembly | ASM | 10 | 9.7 | 9.7 SEER |  |  |  | 21
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048 | 1991 | 48000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048 | 1991 | 48000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048 | 1991 | 48000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048 | 1991 | 48000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048 | 1991 | 48000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048 | 1991 | 48000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPr | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPr | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APWO48080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 585B048125YACR | 1979 | 48000 | Office - Small | OFS | 6 | 6.1 | 6.1 EER |  |  |  | 36
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 585CPW048100AAEG | 1982 | 48000 | Retail - Single-Story Large | RTL | 9 | 6.8 | 6.8 EER |  |  |  | 33
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier/Payne | 585JE048080 | 1985 | 48000 | Manufacturing - Light Industrial | MLI | 8 | 6.8 | 6.8 EER |  |  |  | 29
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | BDP | 585JE048080 | 1985 | 48000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 29
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | BDP | 585JE048080 | 1985 | 48000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 29
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Day & Night | 585JP048080 | 1985 | 48000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 31
2014 | <65kBtu/hr 15 SEER (12 EER/12.5 EER) Package/Split System Air Conditioner DX Equipment | BDP/Carrier | 588APW048080 | 1994 | 48000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 20
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 58APW048080 | 1991 | 48000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | PAYNE | 654AEX048000AAAEG | 1990 | 48000 | Office - Small | OfS | 8 | [5 empty] | 26
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 655ANX030-14522-1 | 1994 | 48000 | Transportation - Communication - Utilities | TCU | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | York | B1HH060A46B | 2004 | 48000 | Transportation - Communication - Utilities | TCU | 8 | [5 empty] | 10
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | York | B3HP048A46A | 2008 | 48000 | Office - Small | OFS | 10 | [5 empty] | 8
2016 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | EVCON | BRCS048B | 2002 | 48000 | Office - Small | OFS | 9 | [5 empty] | 14
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | General Electric | BWC048C300B | 1978 | 48000 | Office - Large | OFL | 6 | 6.1 | 6.1 EER |  |  |  | 37
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | CHP15-513-1Y | 2000 | 48000 | Education - Secondary School | ESE | 8 | [5 empty] | 16
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | CHP15-513-3G | 1989 | 48000 | Office - Small | OFS | 9 | [5 empty] | 26
2015 | 55to65kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | CHP16-513-1Y | 1990 | 48000 | Office - Small | OFS | 9 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | LENNOX | CPH15-511-1P | 0 | 48000 | Office - Large | OFL | 10 | [5 empty] | 2015
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D1G048N06025EBB | 1981 | 48000 | Office - Large | OFL | 10 | 6.8 | 6.8 EER |  |  |  | 35
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D1NA048N06546C | 1999 | 48000 | Office - Small | OfS | 9 | [5 empty] | 17
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D3CG048 | 0 | 48000 | Education - Secondary School | ESE | 14 | [5 empty] | 2015
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS16-5111251P1G | 0 | 48000 | Office - Small | OFS | 9 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS16-513 | 1993 | 48000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS16-513-75-5G | 1993 | 48000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | 45to55kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Lennox | HS16-511V-5P | 1986 | 48000 | Education - Primary School | EPR | 8 | 6.8 | 6.8 EER |  |  |  | 30
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | N/A | 1984 | 48000 | Manufacturing - Light Industrial | MLI | 8 | 6.8 | 6.8 EER |  |  |  | 31
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | non-legible | 1990 | 48000 | Retail - Single-Story Large | RTL | 10 | [5 empty] | 25
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | Not legible | 0 | 48000 | Office - Small | OFS | 10 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | Not legible | 0 | 48000 | Office - Small | OFS | 10 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | Not legible | 0 | 48000 | Office - Small | OFS | 10 | [5 empty] | 2016
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | ICP Commercial | PGB048D1HC | 1999 | 48000 | Assembly | ASM | 10 | [5 empty] | 15
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Arco Air | PGF048H080A | 1999 | 48000 | Health/Medical - Nursing Home | NRS | 10 | [5 empty] | 16
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | HEIL | PHAD47NIKZ | 0 | 48000 | Office - Large | OFL | 10 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Split System Heat Pump | Rheem | RPFA-048DAS | 1981 | 48000 | Manufacturing - Light Industrial | MLI | 6 | 6.8 | 6.8 EER |  |  |  | 34
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | RPNC-048C-000 | 1988 | 48000 | Office - Small | OFS | 8 | 6.8 | 6.8 EER |  |  |  | 28
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Rheem | RRGG05E07DCR | 1998 | 48000 | Manufacturing - Light Industrial | MLI | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | TCD049C300BC | 1997 | 48000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | TGA048S2B51G | 2008 | 48000 | Office - Small | OfS | 8 | [5 empty] | 8
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | RUUD | UKKA-A060CK10X | 2001 | 48000 | Miscellaneous Commercial | MIC | 9 | [5 empty] | 14
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Nordyne | unreadable | 0 | 48000 | Retail - Single-Story Large | RTL | 9 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Nordyne | unreadable | 0 | 48000 | Retail - Single-Story Large | RTL | 9 | [5 empty] | 2016
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC048F300AB | 1992 | 48000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC048F300BB | 0 | 48000 | Education - Primary School | EPR | 6 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC048F300BF | 2000 | 48000 | Education - Community College | ECC | 6 | [5 empty] | 16
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | TRANE | WCC048F400BG | 2001 | 48000 | Office - Small | OfS | 8 | [5 empty] | 15
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCD048A400BA | 1991 | 48000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 25
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | TRANE | WSCO48A4ROA25000 | 2002 | 48000 | Office - Small | OfS | 8 | [5 empty] | 14
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCC048 | 1993 | 48000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCC048F3MMOBA | 1997 | 48000 | Education - Secondary School | ESE | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Trane | YCC048F4H0BA | 1992 | 48000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 22
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCC048F4HOBF | 1998 | 48000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | YORK | YCD048A3L0AA | 0 | 48000 | Education - Primary School | EPR | 8 | [5 empty] | 2015
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCD048A4L08B | 1990 | 48000 | Office - Small | OfS | 8 | [5 empty] | 26
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | TRANE | YCD-048C3LOBF | 0 | 48000 | Office - Small | OFS | 9 | [5 empty] | 2016
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJD005---521-- | 1994 | 47900 | Miscellaneous Commercial | MIC | 9 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50HS-048-14510-1 | 1994 | 47500 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50HS-XX-14518-1 | 1994 | 47500 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50TJQ005 | 1999 | 47500 | Office - Small | OFS | 8 | [5 empty] | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 585JP048125 | 1986 | 47500 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 30
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | NOT LEGIBLE | 0 | 47500 | Education - Primary School | EPR | 9 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | unknown1 | 0 | 47500 | Office - Small | OFS | 9 | [5 empty] | 2016
2015 | 45to55kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Carrier | 38HDC048310 | 1996 | 47000 | Miscellaneous Commercial | MIC | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48TJD005511GA | 2000 | 47000 | Office - Large | OFL | 14 | [5 empty] | 14
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48TJD005601 | 1997 | 47000 | Office - Small | OFS | 13 | 9.7 | 9.7 SEER |  |  |  | 17
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50JHQ005 | 1997 | 47000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 17
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50LJQ005 | 1995 | 47000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50LJQ005541GA | 1994 | 47000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50LJQ005620 | 1999 | 47000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 16
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50LJQ006541CA | 1994 | 47000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50TJQ005501GA | 1998 | 47000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | LENNOX | CHP10-511-2P | 1985 | 47000 | Office - Large | OFL | 10 | 6.8 | 6.8 EER |  |  |  | 30
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48LDT005-610: | 1984 | 46500 | Education - Primary School | EPR | 10 | 6.8 | 6.8 EER |  |  |  | 30
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LDT005510 | 1985 | 46500 | Office - Large | OFL | 10 | 6.8 | 6.8 EER |  |  |  | 30
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48LDT005-610: | 1984 | 46500 | Education - Primary School | EPR | 10 | 6.8 | 6.8 EER |  |  |  | 30
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48LDT005-610: | 1984 | 46500 | Education - Primary School | EPR | 10 | 6.8 | 6.8 EER |  |  |  | 30
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJQ005---601 | 1998 | 46500 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50TJQ005 | 1999 | 46500 | Office - Small | OFS | 8 | [5 empty] | 15
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50TJQ005---601GA | 1998 | 46500 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Lennox | GCS16-513-125-1G: | 1990 | 46500 | Education - Primary School | EPR | 10 | [5 empty] | 24
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS16-513-75-3Y | 1992 | 46500 | Education - Primary School | EPr | 8 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD005-531 | 1996 | 46000 | Miscellaneous Commercial | MiC | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJD005-631 | 1996 | 46000 | Miscellaneous Commercial | MiC | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50HJQ005 | 1997 | 46000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 17
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 580APW048080AAAG | 1989 | 46000 | Miscellaneous Commercial | MIC | 8 | [5 empty] | 26
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS9-513-I20A--- | 0 | 46000 | Retail - Small | RTS | 6 | [5 empty] | 2015
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Lennox | CHA15-513-4X | 1989 | 44300 | Office - Small | OFS | 6 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GSN042060601-- | 2005 | 42000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 10
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48KLA142-300BE | 1985 | 42000 | Miscellaneous Commercial | MIC | 10 | 6.8 | 6.8 EER |  |  |  | 30
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48SS-042060531AA | 1995 | 42000 | Manufacturing - Light Industrial | MLI | 6 | 9.7 | 9.7 SEER |  |  |  | 21
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS042 | 1994 | 42000 | Industrial | IND | 9 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS042 | 1995 | 42000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 21
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS-042---311AB | 2000 | 42000 | Miscellaneous Commercial | MIC | 10 | [5 empty] | 15
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50JSo42601 | 2005 | 42000 | Assembly | ASM | 9 | [5 empty] | 10
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50NQ-042--3 | 1992 | 42000 | Education - Community College | ECC | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | 50QQ042650 | 0 | 42000 | Office - Small | OFS | 8 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | BDP | 542EB042 | 1989 | 42000 | Education - Primary School | EPr | 8 | [5 empty] | 27
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 542ep042 | 1984 | 42000 | Miscellaneous Commercial | MIC | 9 | 6.8 | 6.8 EER |  |  |  | 31
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | 542GE042 | 1988 | 42000 | Education - Primary School | EPR | 8 | 6.8 | 6.8 EER |  |  |  | 27
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 542GN042-C | 1989 | 42000 | Education - Secondary School | ESE | 8 | [5 empty] | 27
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APOW42 | 1991 | 42000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW042 | 1991 | 42000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW042 | 1991 | 42000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW042 | 1991 | 42000 | Education - Primary School | EPR | 14 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | PAYNE | 584APW042 | 1991 | 42000 | Education - Primary School | EPR | 16 | 9.7 | 9.7 SEER |  |  |  | 24
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | BDP | 585EP042060 | 1984 | 42000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 30
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | BDP/Carrier | 585HJ042060 | 1983 | 42000 | Education - Primary School | EPR | 8 | 6.8 | 6.8 EER |  |  |  | 31
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | 654BPX0420000 | 1992 | 42000 | Miscellaneous Commercial | MIC | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | General Electric | BWC042C300B | 1979 | 42000 | Office - Large | OFL | 6 | 6.1 | 6.1 EER |  |  |  | 36
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | BWCO42 | 1992 | 42000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Bard | PH1142 | 1996 | 42000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | payne | unknown | 1995 | 42000 | Education - Primary School | EPR | 8 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | rheem | UNREADABLE | 1988 | 42000 | Office - Small | OFS | 10 | 6.8 | 6.8 EER |  |  |  | 28
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | TRANE | YCC042A3L0AA | 0 | 42000 | Education - Primary School | EPR | 8 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | TRANE | YCC042A3L0AA | 0 | 42000 | Education - Primary School | EPR | 8 | [5 empty] | 2015
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCC042F3MOBA | 1997 | 42000 | Education - Secondary School | ESE | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50QQ-042 | 1995 | 41500 | Health/Medical - Clinic | CLI | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS16-411-50-1P | 1990 | 41100 | Education - Primary School | EPR | 9 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | CHP15-463-1G | 1988 | 41000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 27
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Day & Night | 50QQ042* | 1989 | 40500 | Office - Small | OFS | 6 | [5 empty] | 25
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48SB030040301 | 1993 | 40000 | Office - Small | OFS | 13 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | LENNOX | CHP10-461 | 0 | 40000 | Office - Small | OFS | 9 | [5 empty] | 2016
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJE004531 | 1998 | 38000 | Miscellaneous Commercial | MIC | 10 | 9.7 | 9.7 SEER |  |  |  | 17
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48TJE004501 | 1993 | 38000 | Miscellaneous Commercial | MIC | 10 | 9.7 | 9.7 SEER |  |  |  | 22
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48KLA036-600CE | 1986 | 37000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 29
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS16-411-50-1G | 0 | 37000 | Office - Small | OFS | 9 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS16413-50-1G | 0 | 37000 | Office - Small | OFS | 9 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS16-413-50-1G | 0 | 37000 | Education - Secondary School | ESE | 9 | [5 empty] | 2016
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50DJ004630 | 2002 | 36400 | Grocery | GRO | 10 | [5 empty] | 12
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50LJQ004 | 1994 | 36400 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50LJQ004620 | 1992 | 36400 | Miscellaneous Commercial | MIC | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50TJQ004501GA | 1997 | 36400 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | BDP Company | 542EP036 | 1981 | 36400 | Office - Small | OFS | 8 | 6.8 | 6.8 EER |  |  |  | 34
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | H23B243ABCA | 1985 | 36400 | Education - Primary School | EPR | 10 | 6.8 | 6.8 EER |  |  |  | 29
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | M#50HJQ004 | 2002 | 36400 | Grocery | GRO | 15 | [5 empty] | 12
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | American Standard Inc. | WCC036F300BD | 1999 | 36400 | Office - Small | OFS | 8 | [5 empty] | 16
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | unknown | 0 | 0 | 36000 | Education - Primary School | EPR | 9 | [5 empty] | 2015
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Rheem | 0 | 0 | 36000 | Manufacturing - Light Industrial | MLI | 9 | [5 empty] | 2016
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | General Electric | 0 | 1979 | 36000 | Office - Large | OFL | 6 | 6.1 | 6.1 EER |  |  |  | 36
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | York | "B1HH036A46B " | 2003 | 36000 | Transportation - Communication - Utilities | TCU | 8 | [5 empty] | 11
2016 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | BDP | 36RAC156 | 1965 | 36000 | Office - Small | OfS | 16 | 6.1 | 6.1 EER |  |  |  | 51
2016 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Payne | 36RAC-156 | 1965 | 36000 | Office - Small | OFS | 16 | 6.1 | 6.1 EER |  |  |  | 51
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 38BRC036 | 2003 | 36000 | Office - Small | OFS | 9 | [5 empty] | 11
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | CARRIER | 38HPC036 | 1986 | 36000 | Office - Small | OFS | 8 | 6.8 | 6.8 EER |  |  |  | 28
2016 | <55kBtu/hr To Code Savings Portion Split System Heat Pump | Carrier | 38YRA036310 | 2000 | 36000 | Office - Small | OFS | 10 | [5 empty] | 16
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 48DJE004630 | 1991 | 36000 | Manufacturing - Light Industrial | MLI | 8 | 9.7 | 9.7 SEER |  |  |  | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GS-036 | 2003 | 36000 | Miscellaneous Commercial | MIC | 9 | [5 empty] | 12
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GS0360601 | 1999 | 36000 | Retail - Single-Story Large | RtL | 9 | [5 empty] | 16
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HCMA04 | 1990 | 36000 | Office - Small | OFS | 16 | [5 empty] | 25
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJE004---531-- | 1999 | 36000 | Office - Small | OFS | 9 | [5 empty] | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJE004---531-- | 2000 | 36000 | Office - Small | OFS | 9 | [5 empty] | 16
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJE004-631 | 1997 | 36000 | Miscellaneous Commercial | MiC | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJE004---631-- | 1997 | 36000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJE004---631-- | 1999 | 36000 | Office - Small | OFS | 9 | [5 empty] | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48HJE004---631-- | 1999 | 36000 | Office - Small | OFS | 9 | [5 empty] | 17
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJE004---631-- | 2000 | 36000 | Education - Secondary School | ESE | 10 | [5 empty] | 15
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJE004---641HE | 2003 | 36000 | Education - Secondary School | ESE | 10 | [5 empty] | 12
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJE004B541 | 1990 | 36000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48HJM004---541-- | 2008 | 36000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 7
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48KLA036 | 1985 | 36000 | Education - Primary School | EPR | 10 | 6.8 | 6.8 EER |  |  |  | 29
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48KLA036 | 1985 | 36000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 30
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48KLAA03651 | 0 | 36000 | Assembly | ASM | 10 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LDT004670 | 1987 | 36000 | Office - Small | OFS | 6 | 6.8 | 6.8 EER |  |  |  | 28
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LDT004670 | 1987 | 36000 | Office - Small | OFS | 6 | 6.8 | 6.8 EER |  |  |  | 28
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LDT004670 | 1988 | 36000 | Education - Secondary School | ESE | 10 | 6.8 | 6.8 EER |  |  |  | 27
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48LJE004620 | 1992 | 36000 | Miscellaneous Commercial | MIC | 6 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48MNT036 | 1990 | 36000 | Office - Small | OFS | 16 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48MNT036 | 1990 | 36000 | Office - Small | OFS | 16 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48MNT036 | 1990 | 36000 | Office - Small | OFS | 16 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48MNT036 | 1990 | 36000 | Office - Small | OFS | 16 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48MNT036 | 1990 | 36000 | Office - Small | OFS | 16 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48MNT036 | 1990 | 36000 | Office - Small | OFS | 16 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48MNT036 | 1990 | 36000 | Office - Small | OFS | 16 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48NLT036 | 2003 | 36000 | Education - Secondary School | ESE | 10 | [5 empty] | 12
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48NMT036 | 1990 | 36000 | Office - Small | OFS | 16 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48NMT036 | 1990 | 36000 | Office - Small | OFS | 16 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48SS036060331 | 1997 | 36000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48SS-036060501 | 1993 | 36000 | Education - Community College | ECC | 9 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TJE004---611GA | 2000 | 36000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 15
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | 4WCC3036A3000AB | 2012 | 36000 | Office - Small | OFS | 9 | [5 empty] | 3
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | DAY & NIGHT | 500AP036060 | 0 | 36000 | Education - Community College | ECC | 9 | [5 empty] | 2016
2016 | <65kBtu/hr To Code Savings Portion Water-Source Heat Pump | Carrier | 50BA004600 | 1968 | 36000 | Manufacturing - Light Industrial | MLI | 14 | [5 empty] | 48
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50EZ-036---311-- | 2008 | 36000 | Office - Small | OFS | 6 | [5 empty] | 7
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50HJQ004 | 1997 | 36000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HJQ004 | 1998 | 36000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS036 | 1995 | 36000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS036 | 1996 | 36000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS036 | 1997 | 36000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50HS-036-311AB | 1999 | 36000 | Office - Small | OFS | 6 | [5 empty] | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS-036---601AB | 1998 | 36000 | Manufacturing - Light Industrial | MLI | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50HX036611AB | 1997 | 36000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50JS036301 | 2002 | 36000 | Education - Secondary School | ESE | 9 | [5 empty] | 13
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50JS-036-601 | 2005 | 36000 | Miscellaneous Commercial | MIC | 8 | [5 empty] | 10
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50LJQ004541GA | 1994 | 36000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50NQ036 | 1993 | 36000 | Assembly | ASM | 6 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50YQ036310 | 1991 | 36000 | Manufacturing - Light Industrial | MLI | 10 | 9.7 | 9.7 SEER |  |  |  | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50YQD036 | 1990 | 36000 | Office - Small | OFS | 6 | [5 empty] | 25
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | BDP | 5423P036 | 1978 | 36000 | Office - Small | OFS | 8 | 6.1 | 6.1 EER |  |  |  | 38
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Bryant | 542ej036 | 1984 | 36000 | Miscellaneous Commercial | MIC | 9 | 6.8 | 6.8 EER |  |  |  | 31
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Bryant | 542ejx036 | 1984 | 36000 | Miscellaneous Commercial | MIC | 9 | 6.8 | 6.8 EER |  |  |  | 31
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 542EP036 | 1982 | 36000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 33
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | BDP | 542EPX036000AAE | 1973 | 36000 | Office - Small | OFS | 8 | [5 empty] | 43
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Payne | 542GE036 | 1988 | 36000 | Education - Primary School | EPR | 8 | 6.8 | 6.8 EER |  |  |  | 27
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Day & Night | 542GNX036000F | 1987 | 36000 | Education - Primary School | EPR | 9 | 6.8 | 6.8 EER |  |  |  | 29
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | BDP | 543EP036 | 1984 | 36000 | Miscellaneous Commercial | MIC | 9 | 6.8 | 6.8 EER |  |  |  | 31
2016 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Payne | 567GJ036 | 1986 | 36000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 30
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Day & Night | 580AP036060 | 1989 | 36000 | Education - University | EUN | 9 | [5 empty] | 26
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 580BPV03604AAF | 1990 | 36000 | Office - Small | OFS | 14 | [5 empty] | 25
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | BDP | 580BPV036074AACF | 1989 | 36000 | Transportation - Communication - Utilities | TCU | 6 | [5 empty] | 25
2014 | <65kBtu/hr 14 SEER (11.6 EER/12 EER) Package/Split System Air Conditioner DX Equipment | BDP/Carrier | 588APW036060 | 1994 | 36000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | PAYNE | 654BNX036000 | 0 | 36000 | Education - Primary School | EPR | 9 | [5 empty] | 2016
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 655AEX036-000AACF | 1995 | 36000 | Transportation - Communication - Utilities | TCU | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | BDP/Carrier | 655ANX036000AAAF | 1994 | 36000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | <55kBtu/hr To Code Savings Portion Split System Heat Pump | Carrier | 661A(B)J036-B(C) FB4ANA036 | 1993 | 36000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 23
2015 | <55kBtu/hr To Code Savings Portion Split System Heat Pump | CARRIER | 690AN036-B | 1991 | 36000 | Retail - Single-Story Large | RTL | 6 | 9.7 | 9.7 SEER |  |  |  | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | York | B1CH036A46B | 1988 | 36000 | Manufacturing - Light Industrial | MLI | 6 | 6.8 | 6.8 EER |  |  |  | 27
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | York | B1HA036A25B | 1998 | 36000 | Office - Small | OFS | 6 | 9.7 | 9.7 SEER |  |  |  | 17
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | B1HH036A06B | 2005 | 36000 | Health/Medical - Clinic | CLI | 8 | [5 empty] | 10
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | York | B1HH036A46B | 2003 | 36000 | Transportation - Communication - Utilities | TCU | 8 | [5 empty] | 11
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | York | B1HH048A46B | 1994 | 36000 | Transportation - Communication - Utilities | TCU | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | York | B3CH036A25B | 1994 | 36000 | Miscellaneous Commercial | MIC | 6 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | BWCO36 | 1992 | 36000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | CHP-10-463 | 1982 | 36000 | Education - Primary School | EPR | 14 | 6.8 | 6.8 EER |  |  |  | 34
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D1HG036N04025BDA | 1981 | 36000 | Office - Large | OFL | 10 | 6.8 | 6.8 EER |  |  |  | 35
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D1NH036N08628C | 1981 | 36000 | Office - Large | OFL | 8 | 6.8 | 6.8 EER |  |  |  | 34
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | YORK | D2NZ036N05625NXA | 0 | 36000 | Education - Primary School | EPR | 8 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D3CG036 | 0 | 36000 | Education - Secondary School | ESE | 14 | [5 empty] | 2015
2015 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Lennox | G2003X-75-3 | 1993 | 36000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Goodman | GPH1436H41DA | 2014 | 36000 | Manufacturing - Light Industrial | MLI | 8 | [5 empty] | 2
2016 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | LENNOX | HS18-413 | 1987 | 36000 | Education - Primary School | EPR | 9 | 6.8 | 6.8 EER |  |  |  | 29
2016 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | LENNOX | HS-18-513 | 1987 | 36000 | Education - Primary School | EPR | 9 | 6.8 | 6.8 EER |  |  |  | 29
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | RUUD | Label not legible | 0 | 36000 | Office - Small | OFS | 9 | [5 empty] | 2016
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | N/A | 1984 | 36000 | Manufacturing - Light Industrial | MLI | 8 | 6.8 | 6.8 EER |  |  |  | 31
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | N/R | 1990 | 36000 | Office - Small | OFS | 8 | [5 empty] | 26
2016 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Payne | PA10JA036-A | 2000 | 36000 | Office - Small | OFS | 9 | [5 empty] | 16
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | GOODMAN | pgb036050-1a | 1999 | 36000 | Health/Medical - Clinic | CLI | 9 | [5 empty] | 16
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Bard | PH1136 | 1996 | 36000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | PHD336000H000C1 | 2012 | 36000 | Office - Small | OFS | 9 | [5 empty] | 3
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | ICP Commercial | PHD336000L000 | 1994 | 36000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 22
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Armstrong | PHP10B36DA-2A | 1984 | 36000 | Office - Small | OfS | 8 | 6.8 | 6.8 EER |  |  |  | 32
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Rheem | RKKAA036108E | 1991 | 36000 | Assembly | ASM | 9 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Rheem | RRGD | 1989 | 36000 | Office - Small | OFS | 8 | [5 empty] | 27
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | RRNC03600-0000 | 1990 | 36000 | Health/Medical - Clinic | CLI | 8 | [5 empty] | 25
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Amana | SPCG360903A | 1999 | 36000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 15
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | TGA036S2DS1P | 2008 | 36000 | Office - Small | OfS | 8 | [5 empty] | 8
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | WCC036F300AB | 1992 | 36000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC036F300BB | 0 | 36000 | Education - Primary School | EPR | 6 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC036F300BD | 1998 | 36000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC036F300BD | 1999 | 36000 | Education - Community College | ECC | 6 | [5 empty] | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | TRANE | WCC036F300BE | 1975 | 36000 | Office - Small | OFS | 8 | [5 empty] | 41
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC036F300BF | 2003 | 36000 | Office - Small | OFS | 9 | [5 empty] | 12
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC036F400BE | 1998 | 36000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCD036a100aa | 1988 | 36000 | Education - Secondary School | ESE | 8 | 6.8 | 6.8 EER |  |  |  | 28
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCD036A400AB | 1991 | 36000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 25
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCX036A100BB | 2000 | 36000 | Education - Secondary School | ESE | 8 | [5 empty] | 16
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WPC036F100AA | 2004 | 36000 | Office - Small | OFS | 9 | [5 empty] | 11
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCC036F1M0BF | 1998 | 36000 | Education - Community College | ECC | 6 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCC036F3MOBA | 1997 | 36000 | Education - Secondary School | ESE | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YCD036 | 1998 | 36000 | Restaurant - Sit-Down | RSD | 6 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | TRANE | YCD036A3L0AA | 0 | 36000 | Education - Primary School | EPR | 8 | [5 empty] | 2015
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | TRANE | YCD036C4LGAA | 1994 | 36000 | Assembly | ASM | 8 | 9.7 | 9.7 SEER |  |  |  | 22
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Trane | YHC036A4RMAO | 2002 | 36000 | Office - Small | OFS | 10 | [5 empty] | 14
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Lennox | GSC-413-100 | 1990 | 35900 | Education - Primary School | EPR | 10 | [5 empty] | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50HJQ004-511 | 2002 | 35600 | Health/Medical - Nursing Home | Nrs | 9 | [5 empty] | 13
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50HS036-301 | 1995 | 35600 | Health/Medical - Clinic | CLI | 10 | 9.7 | 9.7 SEER |  |  |  | 20
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50TJQ004 | 1998 | 35600 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 16
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50TJQ004-601GA | 1998 | 35600 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Day & Night | 50QQ036* | 1989 | 35200 | Office - Small | OFS | 6 | [5 empty] | 25
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48DJE004500 | 1990 | 35000 | Office - Large | OFL | 10 | [5 empty] | 24
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48GL03620CA | 1978 | 35000 | Miscellaneous Commercial | MIC | 10 | 6.1 | 6.1 EER |  |  |  | 37
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48TJD0046141GA | 1999 | 35000 | Office - Small | OFS | 6 | [5 empty] | 16
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48TJE004-501GA | 1996 | 35000 | Health/Medical - Nursing Home | Nrs | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48TJE004511GA | 2000 | 35000 | Office - Large | OFL | 14 | [5 empty] | 14
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50JX-036-601 | 2001 | 35000 | Office - Small | OFS | 8 | [5 empty] | 13
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50NQ036310 | 0 | 35000 | Education - Community College | ECC | 9 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50HJQ004---501-- | 1997 | 34600 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | YORK | D6NZ036N05625NXA | 0 | 34500 | Education - Primary School | EPR | 8 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | YORK | D6NZ036N05625NXA | 0 | 34500 | Education - Primary School | EPR | 8 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 585CE036075 | 1982 | 34200 | Retail - Single-Story Large | RtL | 9 | 6.8 | 6.8 EER |  |  |  | 33
2015 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | Carrier | 38hdc036310 | 1996 | 34000 | Miscellaneous Commercial | MIC | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | CARRIER | 50HS-036-14518-1 | 1994 | 34000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 22
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | ICP | HHP036AKC3 | 2003 | 33000 | Office - Small | OFS | 6 | [5 empty] | 13
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48DN024040301 | 2006 | 32800 | Office - Small | OFS | 13 | [5 empty] | 8
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48SS024040311 | 1994 | 32800 | Office - Small | OFS | 13 | 9.7 | 9.7 SEER |  |  |  | 20
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48GS018040301 | 1999 | 32600 | Office - Small | OFS | 13 | [5 empty] | 15
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Lennox | GCS16H-311-75-1P | 1990 | 31100 | Education - Primary School | EPR | 9 | [5 empty] | 25
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | CHP-10-311 | 1982 | 31000 | Education - Primary School | EPR | 14 | 6.8 | 6.8 EER |  |  |  | 34
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GXN0300040301CU | 1990 | 30000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 25
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48NMX030---301BE | 1993 | 30000 | Assembly | ASM | 8 | 9.7 | 9.7 SEER |  |  |  | 23
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48SS-030040321 | 1995 | 30000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | 4WCC030A1000AA | 2009 | 30000 | Office - Small | OFS | 9 | [5 empty] | 6
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS030 | 1996 | 30000 | Retail - Small | RtS | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS-030---311AB | 1998 | 30000 | Manufacturing - Light Industrial | MLI | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS-030---311AB | 1997 | 30000 | Office - Large | OFL | 15 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50NQ | 1990 | 30000 | Office - Small | OFS | 9 | [5 empty] | 26
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50NQ030301 | 1990 | 30000 | Manufacturing - Light Industrial | MLI | 10 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50NQ030301 | 1990 | 30000 | Manufacturing - Light Industrial | MLI | 10 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50QQ030340 | 1987 | 30000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 28
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 542EJ030 | 1982 | 30000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 33
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 542EJ030 | 1983 | 30000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 32
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | BDP | 542EJ030 | 1984 | 30000 | Miscellaneous Commercial | MIC | 9 | 6.8 | 6.8 EER |  |  |  | 31
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Bryant | 542ejx030 | 1984 | 30000 | Miscellaneous Commercial | MIC | 9 | 6.8 | 6.8 EER |  |  |  | 31
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 542EJX030 | 1985 | 30000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 29
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 5854030060YAC | 1977 | 30000 | Health/Medical - Clinic | CLI | 6 | 6.1 | 6.1 EER |  |  |  | 38
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Day & Night | 585HJ003040 | 1986 | 30000 | Office - Small | OfS | 9 | 6.8 | 6.8 EER |  |  |  | 29
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 655ANX030-14522-1 | 1994 | 30000 | Transportation - Communication - Utilities | TCU | 8 | 9.7 | 9.7 SEER |  |  |  | 20
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 655ANX030-14528-1 | 1994 | 30000 | Transportation - Communication - Utilities | TCU | 8 | 9.7 | 9.7 SEER |  |  |  | 21
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | unknown | B1HA030A06B | 0 | 30000 | Office - Small | OFS | 6 | [5 empty] | 2016
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | General Electric | BWC030B100B0 | 1979 | 30000 | Office - Large | OFL | 6 | 6.1 | 6.1 EER |  |  |  | 36
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | LENNOX | CHP15-311-1P | 0 | 30000 | Office - Large | OFL | 10 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D1HS030 | 0 | 30000 | Education - Secondary School | ESE | 14 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D1hS030 | 0 | 30000 | Education - Secondary School | ESE | 14 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | York | D1Ns030 | 0 | 30000 | Education - Secondary School | ESe | 14 | [5 empty] | 2015
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | DINA030N0360614 | 1996 | 30000 | Assembly | ASM | 6 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Goodman | PH0301D | 1998 | 30000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | bard | ph11301 | 1999 | 30000 | Office - Small | OFS | 8 | [5 empty] | 17
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | PHD330000K000C1 | 2011 | 30000 | Office - Small | OFS | 9 | [5 empty] | 4
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | TGA030S2DS1P | 2008 | 30000 | Office - Small | OfS | 8 | [5 empty] | 8
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC030F100BB | 0 | 30000 | Education - Primary School | EPR | 6 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC030F100BD | 1998 | 30000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC030F100BG | 2002 | 30000 | Office - Small | OFS | 9 | [5 empty] | 13
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC030F100BH | 2005 | 30000 | Office - Small | OFS | 9 | [5 empty] | 10
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCX030G100BA | 2003 | 30000 | Office - Small | OFS | 9 | [5 empty] | 12
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | WRKAA030JK06X | 1997 | 30000 | Assembly | ASM | 6 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48SX030060331AA | 1996 | 29800 | Miscellaneous Commercial | MiC | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Day & Night | 50QQ030* | 1989 | 29800 | Office - Small | OFS | 6 | [5 empty] | 25
2016 | <55kBtu/hr To Code Savings Portion Split System Heat Pump | Carrier | 38YCC030310 | 2000 | 29600 | Office - Small | OFS | 8 | [5 empty] | 16
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48GXN030040301 | 2000 | 29000 | Office - Small | OFS | 9 | [5 empty] | 16
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50HS-030 | 1995 | 29000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | A8GX030040301 | 1999 | 29000 | Office - Small | OFS | 9 | [5 empty] | 17
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | LENNOX | CHP15311-1P | 1985 | 29000 | Office - Large | OFL | 10 | 6.8 | 6.8 EER |  |  |  | 29
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Day & Night | 654BNX030000AAAE | 1992 | 27000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 23
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | RPNC030J000 | 1986 | 27000 | Office - Small | OFS | 8 | 6.8 | 6.8 EER |  |  |  | 30
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | CHP-15-261-5P | 1989 | 24800 | Office - Small | OFS | 9 | [5 empty] | 26
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 0 | 1988 | 24000 | Office - Small | OFS | 6 | 6.8 | 6.8 EER |  |  |  | 27
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | BDP | 0 | 1988 | 24000 | Office - Small | OFS | 6 | 6.8 | 6.8 EER |  |  |  | 27
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GSN024040301-- | 2000 | 24000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 15
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GXN0240040301CU | 1990 | 24000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 25
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48NLT024300 | 1989 | 24000 | Education - Secondary School | ESE | 10 | [5 empty] | 26
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48SX-024040321AA | 1996 | 24000 | Office - Small | OFS | 9 | 9.7 | 9.7 SEER |  |  |  | 20
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | 4WCC3024 | 0 | 24000 | Education - Primary School | EPR | 6 | [5 empty] | 2016
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | 4WCC3024A1000AA | 2012 | 24000 | Office - Small | OFS | 9 | [5 empty] | 3
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS-018---301AB | 2000 | 24000 | Education - Community College | ECC | 6 | [5 empty] | 15
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS024 | 1997 | 24000 | Education - Primary School | EPR | 6 | 9.7 | 9.7 SEER |  |  |  | 19
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | carrier | 50HS024001 | 1997 | 24000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HS-024---311AB | 2001 | 24000 | Miscellaneous Commercial | MIC | 10 | [5 empty] | 14
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50-HS-024-311AB | 1995 | 24000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 21
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50HX-024---311CU | 2000 | 24000 | Miscellaneous Commercial | MIC | 6 | [5 empty] | 15
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | cARRIER | 50QQ024 | 1988 | 24000 | Office - Large | OFL | 9 | 6.8 | 6.8 EER |  |  |  | 27
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 50Y0024300 | 1983 | 24000 | Office - Small | OFS | 6 | 6.8 | 6.8 EER |  |  |  | 32
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50YQ024 | 1985 | 24000 | Manufacturing - Light Industrial | MLI | 9 | 6.8 | 6.8 EER |  |  |  | 31
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 542EJ024 | 1983 | 24000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 32
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | BDP | 542EJW024 | 1984 | 24000 | Miscellaneous Commercial | MIC | 9 | 6.8 | 6.8 EER |  |  |  | 31
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | BDP | 542EJX024 | 1981 | 24000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 33
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Payne | 580AN024040AAA | 1989 | 24000 | Office - Small | OFS | 9 | [5 empty] | 27
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Payne | 584ANW024040AAAE | 1990 | 24000 | Office - Small | OFS | 9 | [5 empty] | 26
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | BDP | 585HJ024040 | 1985 | 24000 | Miscellaneous Commercial | MIC | 8 | 6.8 | 6.8 EER |  |  |  | 29
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | BDP/Carrier | 585HJ024040 | 1987 | 24000 | Office - Small | OFS | 9 | 6.8 | 6.8 EER |  |  |  | 27
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | PAYNE | 6548N024AA | 1990 | 24000 | Office - Small | OfS | 8 | [5 empty] | 26
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Bryant | 655ANX024000ABCD | 1999 | 24000 | Office - Small | OFS | 6 | [5 empty] | 15
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Bryant | 6ANX024 | 2008 | 24000 | Office - Small | OFS | 6 | [5 empty] | 6
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | LENNOX | CHA152611P | 1987 | 24000 | Miscellaneous Commercial | MIC | 6 | 6.8 | 6.8 EER |  |  |  | 28
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Lennox | CHP15-261-1P | 2000 | 24000 | Education - Secondary School | ESE | 8 | [5 empty] | 16
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | D1NH024N03606C | 1981 | 24000 | Office - Large | OFL | 8 | 6.8 | 6.8 EER |  |  |  | 34
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | unknown | D1Ns024 | 0 | 24000 | Education - Secondary School | ESe | 14 | [5 empty] | 2015
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Bryant | EJW024 | 1984 | 24000 | Miscellaneous Commercial | MIC | 9 | 6.8 | 6.8 EER |  |  |  | 31
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Bard | PH1124 | 1996 | 24000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | rpnd024j000 | 1989 | 24000 | Office - Small | OFS | 10 | [5 empty] | 27
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | RHEEM | RRGG05N24JKR | 1990 | 24000 | Office - Small | OFS | 9 | [5 empty] | 26
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | York | TGA024S2DS1P | 2008 | 24000 | Office - Small | OfS | 8 | [5 empty] | 8
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC024F100BD | 1998 | 24000 | Office - Small | OfS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC024F100BD | 1998 | 24000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 18
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC024F100BG | 2002 | 24000 | Office - Small | OFS | 9 | [5 empty] | 13
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Trane | WCC024F100BH | 2004 | 24000 | Office - Small | OFS | 9 | [5 empty] | 11
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | WRKAA024YTK04X | 1997 | 24000 | Assembly | ASM | 6 | 9.7 | 9.7 SEER |  |  |  | 19
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48SX-024040321AA | 1996 | 23400 | Miscellaneous Commercial | MiC | 9 | 9.7 | 9.7 SEER |  |  |  | 19
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48SX-024040321AB | 1997 | 23400 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48GS-018040301 | 1999 | 23000 | Office - Small | OFS | 9 | [5 empty] | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48GX024040301 | 1999 | 23000 | Office - Small | OFS | 9 | [5 empty] | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | LENNOX | GCS16-H-261-50-1G | 0 | 23000 | Education - Secondary School | ESE | 9 | [5 empty] | 2016
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | RPNC024J000 | 1985 | 21000 | Office - Small | OFS | 8 | 6.8 | 6.8 EER |  |  |  | 31
2016 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Rheem | RPNC024J000 | 1987 | 21000 | Office - Small | OFS | 8 | 6.8 | 6.8 EER |  |  |  | 29
2015 | <55kBtu/hr To Code Savings Portion Split System Heat Pump | Carrier | 40YR018300 38YG018310 | 1991 | 18000 | Office - Small | OFS | 8 | 9.7 | 9.7 SEER |  |  |  | 24
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | CARRIER | 48GS-018040301 | 1999 | 18000 | Office - Small | OFS | 9 | [5 empty] | 17
2016 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GS-018040301--- | 2000 | 18000 | Manufacturing - Light Industrial | MLI | 9 | [5 empty] | 16
2015 | <55kBtu/hr To Code Savings Portion Package System Air Conditioner DX Equipment | Carrier | 48GSN018040301-- | 2000 | 18000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 15
2014 | <55kBtu/hr To Code Savings Portion Heat Pump | Carrier | 50HS018301 | 1997 | 18000 | Miscellaneous Commercial | MIC | 8 | 9.7 | 9.7 SEER |  |  |  | 17
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 50JS-018---301 | 2001 | 18000 | Manufacturing - Light Industrial | MLI | 6 | [5 empty] | 14
2015 | <55kBtu/hr To Code Savings Portion Package System Heat Pump | Carrier | 655ANX018-14520-1 | 2003 | 18000 | Transportation - Communication - Utilities | TCU | 8 | [5 empty] | 12
2015 | <45kBtu/hr To Code Savings Portion Split System Air Conditioner DX Equipment | BDP | 691ANX018 | 1990 | 18000 | Office - Small | OFS | 14 | [5 empty] | 25
2014 | <55kBtu/hr To Code Savings Portion Package/Split System Air Conditioner DX Equipment | Carrier | 48SS-018040321 | 1995 | 17000 | Education - Primary School | EPR | 9 | 9.7 | 9.7 SEER |  |  |  | 19

## Category Tbl
|  | 1 | 2 | 3 | 4 | 5 | 0
|  | Installed System Capacity by Equipment Vintage (Btu/hr) | [6 empty] | Percent
|  | Before 1978 | 1978 - 1992 | 1993 - 2001 | 2002 - 2005 | 2006 - 2009 | Unknown | Total | of Known
>=760kBtu | VAV | 0 | 3735010 | 9386476 | 0 | 0 | 0 | 13121486 | 100%
| CV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| UNK | 0 | 5767008 | 15118080 | 0 | 0 | 3420000 | 24305088
240>=kBtu<760 | VAV | 0 | 15417000 | 13410000 | 0 | 0 | 240000 | 29067000 | 80.06%
| CV | 0 | 1389000 | 5249000 | 0 | 0 | 600000 | 7238000 | 19.94%
| UNK | 1140000 | 28774300 | 17839671 | 0 | 1140000 | 5293000 | 54186971
135>=kBtu<240 | VAV | 0 | 417000 | 330000 | 0 | 0 | 0 | 747000 | 7.879%
| CV | 0 | 2616000 | 5596000 | 150000 | 0 | 371480 | 8733480 | 92.12%
| UNK | 0 | 3266300 | 923000 | 292000 | 476000 | 332000 | 5289300
|  | Weighted Average EER | Code Minimum EER
|  |  | 7.5 | 8 | 8.2 | 8.5 | 9.2 | 9.5 | 9.7 | Total
>=760 kBtu | VAV | 8.0676 | 1980000 | 1755010 | 9386476 | 0 | 0 | 0 | 0 | 13121486
| CV | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNK | 8.1335 | 3302208 | 1690800 | 14632080 | 0 | 1260000 | 0 | 0 | 20885088
240>= kBtu <760 | VAV | 8.1956 | 8141000 | 0 | 4516000 | 15450000 | 0 | 720000 | 0 | 28827000 | 81.28%
| CV | 8.5559 | 0 | 0 | 549000 | 5553000 | 0 | 536000 | 0 | 6638000
| UNK | 8.0806 | 20054600 | 0 | 6907700 | 20311671 | 0 | 1620000 | 0 | 48893971
135>= kBtu <240 | VAV | 8.5 | 0 | 0 | 0 | 747000 | 0 | 0 | 0 | 747000
| CV | 8.3974 | 894000 | 0 | 480000 | 6838000 | 0 | 0 | 150000 | 8362000
| UNK | 8.3061 | 1699000 | 0 | 613300 | 1877000 | 0 | 0 | 768000 | 4957300

## ClaimsVsAge
|  |  |  | 0 | 65 | 135 | 240 | 760
|  |  |  | 65 | 135 | 240 | 760 | 9999
Number of Claims for each Unit Size Range (kBtu/hr)
Age |  | Age, Yrs | All | 0 to < 65 | 65 to < 135 | 135 to < 240 | 240 to < 760 | >= 760
0 | 4 | 0 to < 4 | 5 | 5 | 0 | 0 | 0 | 0 | 0.3888% | 0.7375% | 0% | 0% | 0% | 0%
5 | 9 | 5 to < 9 | 30 | 18 | 10 | 2 | 0 | 0 | 2.333% | 2.655% | 3.195% | 1.961% | 0% | 0%
10 | 15 | 10 to < 15 | 94 | 65 | 23 | 3 | 3 | 0 | 7.309% | 9.587% | 7.348% | 2.941% | 1.911% | 0%
15 | 20 | 15 to < 20 | 397 | 180 | 106 | 38 | 50 | 23 | 30.87% | 26.55% | 33.87% | 37.25% | 31.85% | 63.89%
20 | 25 | 20 to < 25 | 330 | 188 | 78 | 31 | 30 | 3 | 25.66% | 27.73% | 24.92% | 30.39% | 19.11% | 8.333%
25 | 30 | 25 to < 30 | 279 | 142 | 63 | 19 | 49 | 6 | 21.7% | 20.94% | 20.13% | 18.63% | 31.21% | 16.67%
30 | 35 | 30 to < 35 | 124 | 62 | 28 | 7 | 23 | 4 | 9.642% | 9.145% | 8.946% | 6.863% | 14.65% | 11.11%
35 | 40 | 35 to < 40 | 18 | 14 | 3 | 1 | 0 | 0 | 1.4% | 2.065% | 0.9585% | 0.9804% | 0% | 0%
40 | 45 | 40 to < 45 | 7 | 3 | 1 | 1 | 2 | 0 | 0.5443% | 0.4425% | 0.3195% | 0.9804% | 1.274% | 0%
45 | 50 | 45 to < 50 | 2 | 1 | 1 | 0 | 0 | 0 | 0.1555% | 0.1475% | 0.3195% | 0% | 0% | 0%
|  |  | 1286 | 678 | 313 | 102 | 157 | 36

## Sheet1
Year | Equipment Type | Size Category | Heating Section Type | Subcategory | Minimum Efficiency |  |  | 0 | 0
1989 | Air Conditioners Air Cooled | <65k |  | Split System | 10.0 SEER |  |  | 1973 | 1
1989 |  |  |  | Single Package | 9.7 SEER |  |  | 1974 | 1
1989 |  | 65k-135k |  | Split System and Single Package | 8.9 EER 8.3 IPLV |  |  | 1975 | 1
1989 |  | 135k-240k |  | Split System and Single Package | 8.2 EER 7.2 IPLV | 8.5 EER 7.5 IPLV | as of Jan 1, 1991 | 1976 | 1
1989 |  | 240k-760k |  | Split System and Single Package | 8.2 EER 7.2 IPLV | 8.5 EER 7.5 IPLV | as of Jan 1, 1991 | 1977 | 1
1989 |  | >=760k |  | Split System and Single Package | 8.0 EER 7.2 IPLV | 8.2 EER 7.5 IPLV | as of Jan 1, 1991 | 1978 | 2
1989 | Air Conditioners, Water and Evaporatively Cooled | <65k |  | Split System and Single Package | 9.3 EER 8.3 IPLV |  |  | 1979 | 2
1989 |  | 65k-135k |  | Split System and Single Package | 10.5 EER |  |  | 1980 | 2
1989 |  | 135k-240k |  | Split System and Single Package | 9.4 EER 8.5 IPLV | 9.6 EER 9.0 IPLV | as of Jan 1, 1991 | 1981 | 2
1989 |  | >=240k |  | Split System and Single Package | 9.4 EER 8.5 IPLV | 9.6 EER 9.0 IPLV | as of Jan 1, 1991 | 1982 | 2
1989 | Condensing Units, Air Cooled | >=135k |  |  | 9.7 EER 10.5 IPLV | 9.9 EER 11.0 IPLV | as of Jan 1, 1991 | 1983 | 2
1989 | Condensing Units, Water or Evaporatively Cooled | >=135k |  |  | 12.7 EER 12.7 IPLV | 12.9 EER 12.9 IPLV | as of Jan 1, 1991 | 1984 | 2
1999 | Air Conditioners Air Cooled | <65k |  | Split System | 10.0 SEER |  |  | 1985 | 2
1999 |  |  |  | Single Package | 9.7 SEER |  |  | 1986 | 2
1999 |  | 65k-135k |  | Split System and Single Package | 8.9 EER |  |  | 1987 | 2
1999 |  | 135k-240k |  | Split System and Single Package | 8.5 EER |  |  | 1988 | 2
1999 |  | 240k-760k |  | Split System and Single Package | 8.5 EER 7.5 IPLV |  |  | 1989 | 2
1999 |  | >=760k |  | Split System and Single Package | 8.2 EER 7.5 IPLV |  |  | 1990 | 2
1999 | Air Conditioners, Water and Evaporatively Cooled | <65k |  | Split System and Single Package | 9.3 EER |  |  | 1991 | 2
1999 |  | 65k-135k |  | Split System and Single Package | 10.5 EER |  |  | 1992 | 2
1999 |  | 135k-240k |  | Split System and Single Package | 9.6 EER |  |  | 1993 | 3
1999 |  | >=240k |  | Split System and Single Package | 9.6 EER 9.0 IPLV |  |  | 1994 | 3
1999 | Condensing Units, Air Cooled | >=135k |  |  | 9.9 EER 11.0 IPLV |  |  | 1995 | 3
1999 | Condensing Units, Water or Evaporatively Cooled | >=135k |  |  | 12.9 EER 12.9 IPLV |  |  | 1996 | 3
2001 | Air Conditioners Air Cooled | <65k | All | Split System | 10.0 SEER |  |  | 1997 | 3
2001 |  |  |  | Single Package | 9.7 SEER |  |  | 1998 | 3
2001 |  | 65k-135k | Electric Resistance ( or None) | Split System and Single Package | 10.3 EER |  |  | 1999 | 3
2001 |  |  | All Other |  | 10.1 EER |  |  | 2000 | 3
2001 |  | 135k-240k | Electric Resistance ( or None) | Split System and Single Package | 9.7 EER |  |  | 2001 | 3
2001 |  |  | All Other |  | 9.5 EER |  |  | 2002 | 4
2001 |  | 240k-760k | Electric Resistance ( or None) | Split System and Single Package | 9.5 EER 9.7 IPLV |  |  | 2003 | 4
2001 |  |  | All Other |  | 9.3 EER 9.5 IPLV |  |  | 2004 | 4
2001 |  | >=760k | Electric Resistance ( or None) | Split System and Single Package | 9.2 EER 9.4 IPLV |  |  | 2005 | 4
2001 |  |  | All Other |  | 9.0 EER 9.2 IPLV |  |  | 2006 | 5
2001 | Air Conditioners, Water and Evaporatively Cooled | <65k | All | Split System and Single Package | 12.1 EER |  |  | 2007 | 5
2001 |  | 65k-135k | Electric Resistance ( or None) | Split System and Single Package | 11.5 EER |  |  | 2008 | 5
2001 |  |  | All Other |  | 11.3 EER
2001 |  | 135k-240k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER
2001 |  |  | All Other |  | 10.8 EER
2001 |  | >=240k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER 10.3 IPLV
2001 |  |  | All Other |  | 10.8 EER 10.1 IPLV
2001 | Condensing Units, Air Cooled | >=135k |  |  | 10.1 EER 11.2 IPLV
2001 | Condensing Units, Water or Evaporatively Cooled | >=135k |  |  | 13.1 EER 13.1 IPLV
2004 | Air Conditioners Air Cooled | <65k | All | Split System | 10.0 SEER | 12.0 SEER ( asof 1/23/2006)
2004 |  |  |  | Single Package | 9.7 SEER | 12.0 SEER ( asof 1/23/2006)
2004 |  | 65k-135k | Electric Resistance ( or None) | Split System and Single Package | 10.3 EER
2004 |  |  | All Other |  | 10.1 EER
2004 |  | 135k-240k | Electric Resistance ( or None) | Split System and Single Package | 9.7 EER
2004 |  |  | All Other |  | 9.5 EER
2004 |  | 240k-760k | Electric Resistance ( or None) | Split System and Single Package | 9.5 EER 9.7 IPLV
2004 |  |  | All Other |  | 9.3 EER 9.5 IPLV
2004 |  | >=760k | Electric Resistance ( or None) | Split System and Single Package | 9.2 EER 9.4 IPLV
2004 |  |  | All Other |  | 9.0 EER 9.2 IPLV
2004 | Air Conditioners, Water and Evaporatively Cooled | <65k | All | Split System and Single Package | 12.1 EER
2004 |  | 65k-135k | Electric Resistance ( or None) | Split System and Single Package | 11.5 EER
2004 |  |  | All Other |  | 11.3 EER
2004 |  | 135k-240k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER
2004 |  |  | All Other |  | 10.8 EER
2004 |  | >=240k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER 10.3 IPLV
2004 |  |  | All Other |  | 10.8 EER 10.1 IPLV
2004 | Condensing Units, Air Cooled | >=135k |  |  | 10.1 EER 11.2 IPLV
2004 | Condensing Units, Water or Evaporatively Cooled | >=135k |  |  | 13.1 EER 13.1 IPLV
2007 | Air Conditioners Air Cooled | <65k | All | Split System | 10.0 SEER | 13.0 SEER ( asof 1/23/2006)
2007 |  |  |  | Single Package | 9.7 SEER | 13.0 SEER ( asof 1/23/2006)
2007 |  | 65k-135k | Electric Resistance ( or None) | Split System and Single Package | 10.3 EER | 11.2 EER (as of 1/1/2010)
2007 |  |  | All Other |  | 10.1 EER | 11.0 EER (as of 1/1/2010)
2007 |  | 135k-240k | Electric Resistance ( or None) | Split System and Single Package | 9.7 EER | 11.0 EER (as of 1/1/2010)
2007 |  |  | All Other |  | 9.5 EER | 10.8 EER (as of 1/1/2010)
2007 |  | 240k-760k | Electric Resistance ( or None) | Split System and Single Package | 9.5 EER 9.7 IPLV | 10.0 EER (as of 1/1/2010)
2007 |  |  | All Other |  | 9.3 EER 9.5 IPLV | 9.8 EER (as of 1/1/2010)
2007 |  | >=760k | Electric Resistance ( or None) | Split System and Single Package | 9.2 EER 9.4 IPLV | 9.7 EER (as of 1/1/2010)
2007 |  |  | All Other |  | 9.0 EER 9.2 IPLV | 9.5 EER (as of 1/1/2010)
2007 | Air Conditioners, Water and Evaporatively Cooled | <65k | All | Split System and Single Package | 12.1 EER
2007 |  | 65k-135k | Electric Resistance ( or None) | Split System and Single Package | 11.5 EER
2007 |  |  | All Other |  | 11.3 EER
2007 |  | 135k-240k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER
2007 |  |  | All Other |  | 10.8 EER
2007 |  | >=240k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER 10.3 IPLV
2007 |  |  | All Other |  | 10.8 EER 10.1 IPLV
2007 | Condensing Units, Air Cooled | >=135k |  |  | 10.1 EER 11.2 IPLV
2007 | Condensing Units, Water or Evaporatively Cooled | >=135k |  |  | 13.1 EER 13.1 IPLV
2010 | Air Conditioners Air Cooled | <65k | All | Split System | 13.0 SEER
2010 |  |  |  | Single Package | 13.0 SEER
2010 |  | 65k-135k | Electric Resistance ( or None) | Split System and Single Package | 11.2 EER 11.4 IEER
2010 |  |  | All Other |  | 11.0 EER 11.2 IEER
2010 |  | 135k-240k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER 11.2 IEER
2010 |  |  | All Other |  | 10.8 EER 11.0 IEER
2010 |  | 240k-760k | Electric Resistance ( or None) | Split System and Single Package | 10.0 EER 10.1 IEER
2010 |  |  | All Other |  | 9.8 EER 9.9 IEER
2010 |  | >=760k | Electric Resistance ( or None) | Split System and Single Package | 9.7 EER 9.8 IEER
2010 |  |  | All Other |  | 9.5 EER 9.6 IEER
2010 | Air Conditioners, Water Cooled | <65k | All | Split System and Single Package | 12.1 EER 12.3 IEER
2010 |  | 65k-135k | Electric Resistance ( or None) | Split System and Single Package | 11.5 EER 11.7 IEER | 12.1 EER 12.3 IEER | as of 6/1/2011
2010 |  |  | All Other |  | 11.3 EER 11.5 IEER | 11.9 EER 12.1 IEER | as of 6/1/2011
2010 |  | 135k-240k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER 11.2 IEER | 12.5 EER 12.5 IEER | as of 6/1/2011
2010 |  |  | All Other |  | 10.8 EER 11.0 IEER | 12.3 EER 12.5 IEER | as of 6/1/2011
2010 |  | >=240k to 760k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER 11.1 IEER | 12.4 EER 12.6 IEER | as of 6/1/2011
2010 |  |  | All Other |  | 10.8 EER 10.9 IEER | 12.2 EER 12.4 IEER | as of 6/1/2011
2010 |  | >=760k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER 11.1 IEER | 12.2 EER 12.4 IEER | as of 6/1/2011
2010 |  |  | All Other |  | 10.8 EER 10.9 IEER | 12.0 EER 12.2 IEER | as of 6/1/2011
2010 | Air Conditioners, Evap Cooled | <65k | All | Split System and Single Package | 12.1 EER 12.3 IEER
2010 |  | 65k-135k | Electric Resistance ( or None) | Split System and Single Package | 11.5 EER 11.7 IEER | 12.1 EER 12.3 IEER | as of 6/1/2011
2010 |  |  | All Other |  | 11.3 EER 11.5 IEER | 11.9 EER 12.1 IEER | as of 6/1/2011
2010 |  | 135k-240k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER 11.2 IEER | 12.0 EER 12.2 IEER | as of 6/1/2011
2010 |  |  | All Other |  | 10.8 EER 11.0 IEER | 11.8 EER 12.0 IEER | as of 6/1/2011
2010 |  | >=240k to 760k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER 11.1 IEER | 11.9 EER 12.1 IEER | as of 6/1/2011
2010 |  |  | All Other |  | 10.8 EER 10.9 IEER | 12.2 EER 11.9 IEER | as of 6/1/2011
2010 |  | >=760k | Electric Resistance ( or None) | Split System and Single Package | 11.0 EER 11.1 IEER | 11.7 EER 11.9 IEER | as of 6/1/2011
2010 |  |  | All Other |  | 10.8 EER 10.9 IEER | 11.5 EER 11.7 IEER | as of 6/1/2011
2010 | Condensing Units, Air Cooled | >=135k |  |  | 10.1 EER 11.4 IEER | 10.5 EER 11.8 IEER | as of 6/1/2011
2010 | Condensing Units, Water Cooled | >=135k |  |  | 13.1 EER 13.6 IEER | 13.5 EER 14.0 IEER | as of 6/1/2011
2010 | Condensing Units, Evaporatively Cooled |  |  |  | 13.1 EER 13.6 IEER | 13.5 EER 14.0 IEER | as of 6/1/2011