## Update steps (hidden)
Steps to update commercial HVAC measures for June 2017 DEER update
- Export EnergyImpacts from PEAR for all measures being fixed (in OrigEnergyImpacts tab)
- Fix energy impacts for split and packaged units less than 65 kBTUh.
These measures include both DXAC and DXHP system types
Updated version of MASControl used (based on version 30)
Fixed impacts are given Version = DEER2017 (from DEER2015) in PEAR
- Export EnergyImpacts from PEAR for all measures being updated with a new pre-existing technology (in FixedEnergyImpacts tab)
- Separate single zone from multi-zone HVAC type energy impacts from the 240 - 760 kBTUh measures to correct measure and measure technology descriptions.
Create separate measure definitions for each HVAC type and specify as "component" measure type.
- Create updated measure definitions for all measures getting a new pre-existing technology (in MeasureNewBase tab)
- Update the pre-existing efficiency levels for all measures getting a new pre-existing baseline (in the ScaledFactors tab).
- Update all of the non-weighted energy impacts based on the scale factors (i.e. do not include Ex vintage results, as these will need to be re-weighted within READI), (in ScaledEnergyImpacts tab).
- For each tier level included in the new 240-760 kBTUh measures, create a new measure definition that weights the two HVAC type energy impacts into a single measure definition.
- Remove the single-zone HVAC (cDXAC) energy impacts from the > 760 kBTUh measures and correct the measure and measure technology descriptions.
- transfer the updated Measure definitions and EnergyImpacts to the PEAR database
- Use READI to create the Existing vintage, IOU location and Com building type energy impacts
- Export energy impacts for updated measures from PEAR into this workbook to compare to previous results.

## Summary of Impact Changes
[15 empty] | Any | 1996 | CZ10 | OfS | DEER2015 | DEER2017 | DEER2017
IOU | Any | [7 empty] | BldgType | BldgVint | BldgLoc | Impact | MeasureID | Index | DEER2015 | DEER2017 Fixed | DEER2017 Fixed & New Base | DEER2015 | DEER2017 Fixed |  |  | EnergyImpactID | HVAC
Vintage | 1996 | [7 empty] | Asm | 1975 | CZ01 | APreWBkWh | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | 1 | 867 | 652 | 404 | 60.8 | 90.1 |  |  | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | cDXGF
Climate Zone | CZ10 | [7 empty] | ECC | 1985 | CZ02 | APreWBkW | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | 2 | 572 | 383 | 254 | 60.8 | 90.1 |  |  | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | cDXGF
[9 empty] | EPr | 1996 | CZ03 | APreWBtherm | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | 3 | 931 | 839 | 591 | 125 | 277 |  |  | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | cDXGF
Measure | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | [5 empty] | 1 | cDXGF | ERC | 2003 | CZ04 | AStdWBkWh | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | 4 | 637 | 569 | 440 | 125 | 277 |  |  | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | cDXGF
| DEER2015 | DEER2017 | DEER2017 | [5 empty] | ESe | 2007 | CZ05 | AStdWBkW | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | 5 | 965 | 873 | 624 | 159 | 310 |  |  | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | cDXGF
| Above Pre-Existing Technology |  |  | Above Code/Std Technology |  |  |  |  | EUn | 2011 | CZ06 | AStdWBtherm | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | 6 | 671 | 603 | 474 | 159 | 310 |  |  | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | cDXGF
Building | DEER2015 | DEER2017 Fixed | DEER2017 Fixed & New Base | DEER2015 | DEER2017 Fixed | DEER2017 Fixed & New Base |  |  | Gro | 2014 | CZ07 | APreEUkWh | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | 7 | 995 | 903 | 655 | 189 | 341 |  |  | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | cDXGF
Asm | 974 | 686 | 443 | 90.2 | 135 | 135 |  |  | Hsp | New | CZ08 | APreEUkW | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | 8 | 701 | 633 | 504 | 189 | 341 |  |  | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | cDXGF
ECC | 912 | 679 | 427 | 72.1 | 108 | 108 |  |  | Htl | Ex | CZ09 | APreEUtherm | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | 9 | 565 | 471 | 309 | 104 | 104 |  |  | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | cDXGF
EPr | 568 | 413 | 263 | 49.3 | 73.2 | 73.2 |  |  | MBT |  | CZ10 | AStdEUkWh | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | 10 | 793 | 701 | 539 | 332 | 334 |  |  | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | cDXGF
ERC | 682 | 508 | 329 | 61.1 | 102 | 102 |  |  | MLI |  | CZ11 | AStdEUkW | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | 11 | 837 | 745 | 583 | 376 | 378 |  |  | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | cDXGF
ESe | 585 | 414 | 265 | 50.1 | 76.7 | 76.7 |  |  | Nrs |  | CZ12 | AStdEUtherm | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | 12 | 876 | 784 | 622 | 415 | 417 |  |  | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | cDXGF
EUn | 1080 | 780 | 488 | 77.6 | 119 | 119 |  |  | OfL |  | CZ13 |  | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | 13 | 506 | 471 | 330 | 103 | 94.9 |  |  | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | cDXGF
Gro | 687 | 472 | 323 | 102 | 135 | 135 |  |  | OfS |  | CZ14 |  | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | 14 | 691 | 701 | 560 | 289 | 325 |  |  | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | cDXGF
Hsp | 1830 | 1290 | 804 | 106 | 189 | 189 |  |  | RFF |  | CZ15 |  | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | 15 | 735 | 745 | 604 | 333 | 369 |  |  | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | cDXGF
Htl | 1710 | 1230 | 772 | 121 | 194 | 194 |  |  | RSD |  | CZ16 |  | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | 16 | 774 | 784 | 643 | 372 | 408 |  |  | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | cDXGF
MBT | 1210 | 1030 | 621 | 82.3 | 105 | 105 |  |  | Rt3 |  | IOU |  | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | 17 | 782 | 652 | 439 | 59.2 | 84.5 |  |  | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | cDXGF
MLI | 717 | 517 | 327 | 54.9 | 86.7 | 86.7 |  |  | RtL |  |  |  | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | 18 | 505 | 383 | 271 | 60.8 | 84.5 |  |  | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | cDXGF
Nrs | 1300 | 791 | 522 | 96.3 | 183 | 183 |  |  | RtS |  |  |  | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | 19 | 830 | 839 | 626 | 107 | 271 |  |  | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | cDXGF
OfL | 958 | 743 | 457 | 66.7 | 96.5 | 96.5 |  |  | SCn |  |  |  | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | 20 | 570 | 569 | 457 | 125 | 271 |  |  | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | cDXGF
OfS | 867 | 652 | 404 | 60.8 | 90.1 | 90.1 |  |  | WRf |  |  |  | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | 21 | 864 | 873 | 660 | 141 | 305 |  |  | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | cDXGF
RFF | 1140 | 846 | 544 | 117 | 163 | 163 |  |  | Com |  |  |  | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | 22 | 603 | 603 | 491 | 159 | 305 |  |  | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | cDXGF
RSD | 975 | 712 | 458 | 102 | 138 | 138 | [6 empty] | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | 23 | 894 | 903 | 690 | 171 | 335 |  |  | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | cDXGF
Rt3 | 1130 | 857 | 539 | 96.3 | 137 | 137 | [6 empty] | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | 24 | 633 | 633 | 521 | 189 | 335 |  |  | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | cDXGF
RtL | 1110 | 836 | 530 | 103 | 144 | 144 | [6 empty] | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | 25 | 506 | 471 | 319 | 77.4 | 66.9 |  |  | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | cDXGF
RtS | 939 | 766 | 484 | 88.5 | 128 | 128 | [6 empty] | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | 26 | 691 | 701 | 550 | 263 | 297 |  |  | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | cDXGF
SCn | 581 | 361 | 246 | 54.3 | 101 | 101 | [6 empty] | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | 27 | 735 | 745 | 594 | 307 | 341 |  |  | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | cDXGF
WRf | 1100 | 971 | 594 | 83.5 | 118 | 118 | [6 empty] | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | 28 | 774 | 784 | 633 | 346 | 380 |  |  | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | cDXGF
Com | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [6 empty] | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | 29 | #N/A | 439 | 378 | #N/A | 44 |  |  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | 30 | #N/A | 467 | 406 | #N/A | 72 |  |  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | 31 | #N/A | 493 | 432 | #N/A | 98.2 |  |  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_SZ | 32 | #N/A | 516 | 67 | #N/A | 67 |  |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_SZ | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_SZ | 33 | #N/A | 555 | 107 | #N/A | 107 |  |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_SZ | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_SZ | 34 | #N/A | 605 | 156 | #N/A | 156 |  |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_SZ | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_MZ | 35 | #N/A | 131 | #N/A | #N/A | 75.9 |  |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_MZ | cPVVG
[13 empty] | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_MZ | 36 | #N/A | 189 | #N/A | #N/A | 134 |  |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_MZ | cPVVG
[13 empty] | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_MZ | 37 | #N/A | 261 | #N/A | #N/A | 206 |  |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_MZ | cPVVG
[13 empty] | NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-woutPreEcono | 38 | #N/A | 577 | 638 | #N/A | 31.1 |  |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-wPreEcono | 39 | #N/A | 352 | 388 | #N/A | 31.1 |  |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-woutPreEcono | 40 | #N/A | 606 | 667 | #N/A | 60.2 |  |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-wPreEcono | 41 | #N/A | 381 | 417 | #N/A | 60.2 |  |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-woutPreEcono | 42 | #N/A | 632 | 693 | #N/A | 85.4 |  |  | NE-HVAC-airAC-SpltPkg-65to135kBtuh-12p5eer | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-wPreEcono | 43 | #N/A | 406 | 442 | #N/A | 85.4 |  |  | NE-HVAC-airAC-SpltPkg-65to135kBtuh-12p5eer-wPreEcono | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-woutPreEcono | 44 | #N/A | 657 | 718 | #N/A | 111 |  |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-wPreEcono | 45 | #N/A | 432 | 468 | #N/A | 111 |  |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | cDXGF
[13 empty] | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | 46 | #N/A | 111 | #N/A | #N/A | 52.2 |  |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | cPVVG
[13 empty] | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | 47 | #N/A | 184 | #N/A | #N/A | 125 |  |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | cPVVG
[13 empty] | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | 48 | #N/A | 262 | #N/A | #N/A | 204 |  |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | cPVVG
Above Pre-existing kWh Savings Msr: NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer IOU: Any, Vintage: 1996, CZ: CZ10
Above Code/Std kWh Savings Msr: NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer IOU: Any, Vintage: 1996, CZ: CZ10

## MeasureFix
Measure table records of all Measures being "fixed"
Measure Table (exante.Measure)
This file created on 6/2/2017 4:15:26 PM while connected to AmazonWS-RDS as sptviewer.
Program/Database Description: READI v.2.4.7 (Preliminary Ex Ante Review data) options: include Non-DEER and Proposed data; 1/1/2013 - 12/31/2025
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | StdCostID | RUL_ID | LegacyID | MeasQualifierGroup | StartDate | ExpiryDate | ReviewStatus | MeasID_SCE | MeasID_PGE | MeasID_SDG | MeasID_SCG | MeasType | ReviewComment | part of baseline update
823 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 1
827 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 2
824 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 3
828 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 4
825 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 5
829 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 6
826 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 7
830 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 8
819 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 9
820 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 10
821 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 11
822 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 12
835 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 13
836 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 14
837 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 15
838 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 16
839 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 17
843 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 18
840 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 19
844 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 20
841 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 21
845 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 22
842 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 23
846 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 24
831 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 25
832 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 26
833 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 27
834 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update and pre-existing technology updated | 28
870 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
873 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
871 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
874 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
872 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
875 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
867 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, Fan W/CFM = 0.29, one-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, Fan W/CFM = 0.29, one-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
868 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
869 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
880 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
884 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
881 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
885 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
882 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
886 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
883 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
887 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
876 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-15.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
877 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-16.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
878 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-17.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
879 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 |  | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-18.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP |  | DEER1517 | 2017-01-01 |  | InEA_same |  |  |  |  | Standard | Measure EnergyImpacts corrected for June 2017 DEER Update | #N/A
Note on B8: Paul Reeves: These measures are also getting a new pre-existing technology, defined on the next tab

## MeasureNewBase
Measure table records of all Measures being updated with new pre-existing technology efficiency levels
Measure Table (exante.Measure)
This file created on 6/4/2017 9:09:03 AM while connected to AmazonWS-RDS as sptviewer.
Program/Database Description: READI v.2.4.7 (Preliminary Ex Ante Review data) options: include Non-DEER and Proposed data; 1/1/2013 - 12/31/2025
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | StdCostID | RUL_ID | LegacyID | MeasQualifierGroup | StartDate | ExpiryDate | ReviewStatus | MeasID_SCE | MeasID_PGE | MeasID_SDG | MeasID_SCG | MeasType | ReviewComment
823 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 1
827 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, w/ Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 2
824 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 3
828 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, w/ Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 4
825 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 5
829 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, w/ Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 6
826 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 7
830 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, w/ Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 8
819 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 9
820 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 10
821 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 11
822 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 11.6, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 12
835 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 13
836 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 14
837 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 15
838 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 16
839 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 17
843 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 18
840 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 19
844 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 20
841 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 21
845 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 22
842 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 23
846 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 24
831 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 25
832 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 26
833 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 27
834 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 11.5, one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | Available |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure corrected and updated for DEER June 2017 Update including Baseline Adjustment | 28
1 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.7, one-speed fan, w/Econo; 2006 - 2009: EER = 9.7, one-speed fan, w/Econo; 2010 - 2013: EER = 10.8, one-speed fan, w/Econo; 2014 - 2015: EER = 10.8, IEER = 12.2, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8, IEER = 12.2, EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12, min IEER = 13.5, EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.7, one-speed fan, w/Econo; 2006 - 2009: EER = 9.7, one-speed fan, w/Econo; 2010 - 2013: EER = 10.8, one-speed fan, w/Econo; 2014 - 2015: EER = 10.8, IEER = 12.2, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8, IEER = 12.2, EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12, min IEER = 13.5, EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.7, one-speed fan, w/Econo; 2006 - 2009: EER = 9.7, one-speed fan, w/Econo; 2010 - 2013: EER = 10.8, one-speed fan, w/Econo; 2014 - 2015: EER = 10.8, IEER = 12.2, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8, IEER = 12.2, EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1719 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_SZ | Single-Zone EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8, min IEER = 12.2, EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 2432 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_SZ | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.8 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.8, one-speed fan, w/Econo; 2010 - 2013: EER = 9.8, one-speed fan, w/Econo; 2014 - 2015: EER = 9.8, IEER 11.4, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8, IEER = 11.4, EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8, min IEER 12.2, EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Component | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1719 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_SZ | Single-Zone EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 2432 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_SZ | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.8 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.8, one-speed fan, w/Econo; 2010 - 2013: EER = 9.8, one-speed fan, w/Econo; 2014 - 2015: EER = 9.8, IEER 11.4, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8, IEER = 11.4, EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Component | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1719 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_SZ | Single-Zone EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 2432 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_SZ | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.8 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.8, one-speed fan, w/Econo; 2010 - 2013: EER = 9.8, one-speed fan, w/Econo; 2014 - 2015: EER = 9.8, IEER 11.4, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8, IEER = 11.4, EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Component | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1719 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_MZ | Multi-Zone EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8, min IEER = 12.2, EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 1280 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_MZ | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 10.0 (IEER = 11.3), var-speed fan, w/Econo; 2006 - 2009: EER = 10.0, var-speed fan, w/Econo; 2010 - 2013: EER = 10.0, var-speed fan, w/Econo; 2014 - 2015: EER = 10.0, IEER 11.6, varspeed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.0 IEER = 11.4, EIR = 0.282, Fan W/CFM = 0.72, var-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8, min IEER 12.2, EIR = 0.255, Fan W/CFM = 0.61, var-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Component | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1719 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_MZ | Multi-Zone EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 1280 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_MZ | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 10.0 (IEER = 11.3), var-speed fan, w/Econo; 2006 - 2009: EER = 10.0, var-speed fan, w/Econo; 2010 - 2013: EER = 10.0, var-speed fan, w/Econo; 2014 - 2015: EER = 10.0, IEER 11.6, varspeed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.0 IEER = 11.4, EIR = 0.282, Fan W/CFM = 0.72, var-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, Fan W/CFM = 0.61, var-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Component | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1719 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_MZ | Multi-Zone EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 1280 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_MZ | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 10.0 (IEER = 11.3), var-speed fan, w/Econo; 2006 - 2009: EER = 10.0, var-speed fan, w/Econo; 2010 - 2013: EER = 10.0, var-speed fan, w/Econo; 2014 - 2015: EER = 10.0, IEER 11.6, varspeed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.0 IEER = 11.4, EIR = 0.282, Fan W/CFM = 0.72, var-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, Fan W/CFM = 0.61, var-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Component | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1719 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8, min IEER = 12.2, EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 2428 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Mix of Single-zone 9.8 EER (20%) and Multi-zone 10.0 EER (80%) system configurations | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, Mix of Single-zone and Multi-zone system configurations | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8, Mix of Single-zone and Multi-zone system configurations |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1719 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 2432 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Mix of Single-zone 9.8 EER (20%) and Multi-zone 10.0 EER (80%) system configurations | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, Mix of Single-zone and Multi-zone system configurations | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5, Mix of Single-zone and Multi-zone system configurations |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1719 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 2432 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Mix of Single-zone 9.8 EER (20%) and Multi-zone 10.0 EER (80%) system configurations | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, Mix of Single-zone and Multi-zone system configurations | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5, Mix of Single-zone and Multi-zone system configurations |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-woutPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.0, one-speed fan, no Econo; 2006 - 2009: EER = 10.0, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2687 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.0, one-speed fan, w/Econo; 2006 - 2009: EER = 10.0, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-woutPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12, min IEER = 13.5 EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.0, one-speed fan, no Econo; 2006 - 2009: EER = 10.0, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12, min IEER = 13.5 EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12, min IEER = 13.5 EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2687 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.0, one-speed fan, w/Econo; 2006 - 2009: EER = 10.0, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12, min IEER = 13.5 EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-woutPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-SpltPkg-65to135kBtuh-12p5eer | DEER | CrossMeasWtd | None |  |  | None | airAC-SpltPkg-65to134kBtuh-12p5eer-woutPreEcono | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.0, one-speed fan, no Econo; 2006 - 2009: EER = 10.0, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2687 | NE-HVAC-airAC-SpltPkg-65to135kBtuh-12p5eer-wPreEcono | DEER | CrossMeasWtd | None |  |  | None | airAC-SpltPkg-65to134kBtuh-12p5eer-wPreEcono | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.0, one-speed fan, w/Econo; 2006 - 2009: EER = 10.0, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-woutPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 13, min IEER = 15, EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v2 | 2688 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER13.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.0, one-speed fan, no Econo; 2006 - 2009: EER = 10.0, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 13, min IEER = 15, EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 13, min IEER = 15, EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v2 | 2687 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER13.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.0, one-speed fan, w/Econo; 2006 - 2009: EER = 10.0, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 13, min IEER = 15, EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2, min IEER = 11.6, EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 1280 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9.2, one-speed fan, w/Econo; 2006 - 2009: EER = 9.2, one-speed fan, w/Econo; 2010 - 2013: EER = 9.5, one-speed fan, w/Econo; 2014 - 2015: EER = 9.5, IEER = 11, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5, IEEER = 11, EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2, min IEER = 11.6, EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed | Std and Meas Technologies vary by system configuration | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11, min IEER = 12.3, EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 1280 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9.2, one-speed fan, w/Econo; 2006 - 2009: EER = 9.2, one-speed fan, w/Econo; 2010 - 2013: EER = 9.5, one-speed fan, w/Econo; 2014 - 2015: EER = 9.5, IEER = 11, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5, IEEER = 11, EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11, min IEER = 12.3, EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed | Std and Meas Technologies vary by system configuration | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
1 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12, min IEER = 13.8, EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v2 | 1280 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9.2, one-speed fan, w/Econo; 2006 - 2009: EER = 9.2, one-speed fan, w/Econo; 2010 - 2013: EER = 9.5, one-speed fan, w/Econo; 2014 - 2015: EER = 9.5, IEER = 11, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5, IEEER = 11, EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12, min IEER = 13.8, EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed | Std and Meas Technologies vary by system configuration | FALSE | FALSE | June 2017 DEER Update | ErRobNc | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | InEA_mod |  |  |  |  | Standard | Measure updated for DEER June 2017 Update including Baseline Adjustment | #N/A
Note on B39: Paul Reeves: new measures for this update, separating the multi-zone and single-zone systems
Note on B45: Paul Reeves: weighted measures based on the multi and single-zone system measures

## ScaledFactors
|  | Energy Efficiency Levels | [17 empty] | New Above Pre-Existing imapct = [Old Above Pre-Existing] * FracAP + [Above Code/Std] * (1 - FracAP)
|  | Case |  | Pre-Existing Case by Vintage | [7 empty] | Updated Pre-Existing Case by Vintage | [7 empty] | Fraction of Above Pre-existing Impacts (FracAP)
MeasureID | EnergyImpactID | Measure | Code/Std | 1975 | 1985 | 1996 | 2003 | 2007 | 2011 | 2014 | New | 1975 | 1985 | 1996 | 2003 | 2007 | 2011 | 2014 | New | 1975 | 1985 | 1996 | 2003 | 2007 | 2011 | 2014 | New
NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | 15 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | 15 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | 16 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | 16 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | 17 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | 17 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | 18 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | 18 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | 15 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | 16 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | 17 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | 18 | 14 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13 | 14 | 14 | 11.6 | 11.6 | 11.6 | 13 | 13 | 13 | 14 | 14 | 55.81% | 55.81% | 55.81% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | 15 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | 16 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | 17 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | 18 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | 15 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | 15 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | 16 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | 16 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | 17 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | 17 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | 18 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | 18 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | 15 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | 16 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | 17 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | 18 | 14 | 10 | 10 | 10 | 13 | 13 | 13 | 14 | 14 | 11.5 | 11.5 | 11.5 | 13 | 13 | 13 | 14 | 14 | 62.5% | 62.5% | 62.5% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | 11.5 | 10.8 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10.8 | 10.8 | 10.8 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 10.8 | 10.8 | 10.8 | 84.62% | 84.62% | 84.62% | 84.62% | 84.62% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | 12 | 10.8 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10.8 | 10.8 | 10.8 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 10.8 | 10.8 | 10.8 | 84.62% | 84.62% | 84.62% | 84.62% | 84.62% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | 12.5 | 10.8 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10.8 | 10.8 | 10.8 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 10.8 | 10.8 | 10.8 | 84.62% | 84.62% | 84.62% | 84.62% | 84.62% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_SZ | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_SZ | 10.8 | 9.8 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_SZ | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_SZ | 11.5 | 9.8 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_SZ | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_SZ | 12.5 | 9.8 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_MZ | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer_MZ | 11.5 | 10 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_MZ | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer_MZ | 12 | 10 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_MZ | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer_MZ | 12.5 | 10 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-woutPreEcono | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | 11.5 | 11 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 111.1% | 111.1% | 111.1% | 111.1% | 111.1% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-wPreEcono | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | 11.5 | 11 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 111.1% | 111.1% | 111.1% | 111.1% | 111.1% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-woutPreEcono | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | 12 | 11 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 111.1% | 111.1% | 111.1% | 111.1% | 111.1% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-wPreEcono | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | 12 | 11 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 111.1% | 111.1% | 111.1% | 111.1% | 111.1% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-woutPreEcono | NE-HVAC-airAC-SpltPkg-65to135kBtuh-12p5eer | 12.5 | 11 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 111.1% | 111.1% | 111.1% | 111.1% | 111.1% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-wPreEcono | NE-HVAC-airAC-SpltPkg-65to135kBtuh-12p5eer-wPreEcono | 12.5 | 11 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 111.1% | 111.1% | 111.1% | 111.1% | 111.1% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-woutPreEcono | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | 13 | 11 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 111.1% | 111.1% | 111.1% | 111.1% | 111.1% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-wPreEcono | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | 13 | 11 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 111.1% | 111.1% | 111.1% | 111.1% | 111.1% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | 10.2 | 9.7 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.7 | 9.7 | 9.7 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.7 | 9.7 | 9.7 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | 11 | 9.7 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.7 | 9.7 | 9.7 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.7 | 9.7 | 9.7 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | 12 | 9.7 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.7 | 9.7 | 9.7 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.7 | 9.7 | 9.7 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%