## Measures
MeasureID | MeasureDescription | PreTechID | StdTechID
RE-HV-RefChrg-Dec-TXV-typ | Decrease Refrigerant Charge - Typical (8% rated charge) - TXV | RefgChg-Res-8pct-Dec-TXV | RefgChg-Res-Std
RE-HV-RefChrg-Inc-TXV-typ | Increase Refrigerant Charge - Typical (8% rated charge) - TXV | RefgChg-Res-8pct-Inc-TXV | RefgChg-Res-Std
RE-HV-RefChrg-Inc-TXV-4pct | Increase Refrigerant Charge (4% rated charge) - TXV | RefgChg-Res-4pct-Inc-TXV | RefgChg-Res-Std
RE-HV-RefChrg-Inc-TXV-16pct | Increase Refrigerant Charge (16% rated charge) - TXV | RefgChg-Res-16pct-Inc-TXV | RefgChg-Res-Std
RE-HV-RefChrg-Dec-NTXV-typ | Decrease Refrigerant Charge - Typical (8% rated charge) - NTXV | RefgChg-Res-8pct-Dec-NTXV | RefgChg-Res-Std
RE-HV-RefChrg-Inc-NTXV-typ | Increase Refrigerant Charge - Typical (8% rated charge) - NTXV | RefgChg-Res-8pct-Inc-NTXV | RefgChg-Res-Std
RE-HV-RefChrg-Inc-NTXV-4pct | Increase Refrigerant Charge (4% rated charge) - NTXV | RefgChg-Res-4pct-Inc-NTXV | RefgChg-Res-Std
RE-HV-RefChrg-Inc-NTXV-16pct | Increase Refrigerant Charge (16% rated charge) - NTXV | RefgChg-Res-16pct-Inc-NTXV | RefgChg-Res-Std

## 2012_LabTestData_NonTXV
[11 empty] | Fan heat factor: | 0.85
Data from: Draft Evaluation Report: Lab Tests of a Residential 3-Ton Split System Air Conditioner under Typical Installed Conditions, CPUC, 2012
Charge | Charge |  |  |  | net cap | sens cap | fan | tot | fan |  |  | gross capacity |  | EIR |  | gross sensible cap
oz | Pct | Src table | RunID | EER | kBtuh | kBtuh | kW | kW | cfm |  | wt | kBtuh | Cap Mult | EIR | eir Mult | kBtuh | Cap Mult
| Non-TXV, Rating Condition B | [16 empty] | dChg
140.6 | +30 | Table 11 | 182 C | 9.64 | 31.49 | 23.98 | 0.558 | 3.27 | 1190 |  | 50% | 33.1088 | 0.99237 | 0.27956 | 1.1354 | 25.5988 | 1.0727 | -30%
129.8 | +10 | Table 11 | 180 B | 10.35 | 32.43 | 24.34 | 0.548 | 3.13 | 1190 |  | 50% | 34.0198 | 1.0197 | 0.25904 | 1.052 | 25.9298 | 1.0866 | -10%
113.6 | +5 | Table 11 | 179B | 10.5 | 32.54 | 24.11 | 0.553 | 3.1 | 1190 |  | 50% | 34.1443 | 1.0234 | 0.25459 | 1.034 | 25.7143 | 1.0776 | -5%
108.2 | 0 | Table 11 | 178-2 | 10.68 | 31.73 | 22.23 | 0.563 | 2.97 | 1200 |  |  | 33.3633 | 1 | 0.24623 | 1 | 23.8633 | 1 | 0%
102.8 | -5 | Table 11 | 184-2 | 10.22 | 29.68 | 20.09 | 0.565 | 2.91 | 1200 |  | 50% | 31.3191 | 0.93873 | 0.25555 | 1.0378 | 21.7291 | 0.91057 | 5%
97.4 | -10 | Table 11 | 185-2 | 9.85 | 28.07 | 17.92 | 0.568 | 2.85 | 1200 |  | 50% | 29.7178 | 0.89073 | 0.26208 | 1.0644 | 19.5678 | 0.82 | 10%
86.6 | -20 | Table 11 | 186-2 | 7.63 | 20.74 | 12.04 | 0.563 | 2.72 | 1190 |  | 50% | 22.3733 | 0.6706 | 0.32905 | 1.3363 | 13.6733 | 0.57298 | 20%
Non-TXV, Rating Condition A
132.6 | +30 | Table 10 | 62 | 8.91 | 30.77 | 23.4 | 0.561 | 3.45 | 1180 |  | 50% | 32.3975 | 0.9846 | 0.30435 | 1.0681 | 25.0275 | 1.011 | -30%
112.2 | +10 | Table 10 | 60a | 9.29 | 31.6 | 23.67 | 0.555 | 3.4 | 1170 |  | 50% | 33.2101 | 1.0093 | 0.29238 | 1.0261 | 25.2801 | 1.0212 | -10%
113.6 | +5 | Table 10 | 59a | 9.36 | 29.88 | 21.32 | 0.56 | 3.19 | 1180 |  | 50% | 31.5046 | 0.95746 | 0.28492 | 0.99994 | 22.9446 | 0.92689 | -5%
102 | 0 | Table 10 | 53 | 9.49 | 31.3 | 23.15 | 0.553 | 3.3 | 1170 |  |  | 32.9043 | 1 | 0.28493 | 1 | 24.7543 | 1 | 0%
96.9 | -5 | Table 10 | 54 | 8.94 | 28.38 | 19.99 | 0.55 | 3.17 | 1165 |  | 50% | 29.9756 | 0.91099 | 0.29831 | 1.047 | 21.5856 | 0.87199 | 5%
91.8 | -10 | Table 10 | 55 | 7.47 | 23.35 | 15.04 | 0.565 | 3.13 | 1170 |  | 50% | 24.9891 | 0.75945 | 0.35033 | 1.2295 | 16.6791 | 0.67379 | 10%
81.6 | -20 | Table 10 | 56a | 6.7 | 20.37 | 12.88 | 0.56 | 3.04 | 1180 |  | 50% | 21.9946 | 0.66844 | 0.38483 | 1.3506 | 14.5046 | 0.58594 | 20%
TXV, Rating Condition A
132.6 | +30 | Table 9 | 40 | 8.12 | 31.321 | 23.36 | 0.56 | 3.86 | 1150 |  | 0% | 32.9456 | 0.99683 | 0.34186 | 1.2202 | 24.9846 | 0.99341 | -30%
112.2 | +10 | Table 9 | 36 | 9.24 | 31.8 | 23.16 | 0.563 | 3.44 | 1150 |  | 0% | 33.4333 | 1.0116 | 0.2937 | 1.0483 | 24.7933 | 0.9858 | -10%
107.2 | +5 | Table 9 | 33 | 9.42 | 30.52 | 22.95 | 0.562 | 3.24 | 1140 |  | 0% | 32.1504 | 0.97277 | 0.28429 | 1.0147 | 24.5804 | 0.97734 | -5%
102 | 0 | Table 9 | 23 | 9.6 | 31.42 | 23.52 | 0.562 | 3.275 | 1160 |  |  | 33.0504 | 1 | 0.28016 | 1 | 25.1504 | 1 | 0%
96.9 | -5 | Table 9 | 44 | 9.46 | 30.32 | 22.02 | 0.558 | 3.21 | 1140 |  | 0% | 31.9388 | 0.96637 | 0.28339 | 1.0115 | 23.6388 | 0.9399 | 5%
91.8 | -10 | Table 9 | 45 | 9.22 | 29.2 | 20.5 | 0.556 | 3.17 | 1140 |  | 0% | 30.813 | 0.9323 | 0.28954 | 1.0335 | 22.113 | 0.87923 | 10%
81.6 | -20 | Table 9 | 48 | 8.28 | 25.83 | 16.76 | 0.561 | 3.12 | 1170 |  | 0% | 27.4575 | 0.83078 | 0.31809 | 1.1354 | 18.3875 | 0.7311 | 20%
71.4 | -30 | Table 9 | 49 | 6.98 | 21.7 | 13.03 | 0.557 | 3.03 | 1170 |  | 0% | 23.3159 | 0.70546 | 0.362 | 1.2921 | 14.6459 | 0.58233
Changes in Adjustment Factors for Refrigerant Charge Measures
[12 empty] | Cap Mult |  | EIR Mult |  | Sens Cap Mult
[12 empty] | prev | 2018 | prev | 2018 | prev | 2018
[10 empty] | High Over-Charge | +30 | 0.82553 | 0.98848 | 1.35 | 1.1018 | 0.88858 | 1.0419
[10 empty] | 10% Over-Charge | +10 | 0.89428 | 1.0145 | 1.16 | 1.0391 | 0.94748 | 1.0539
[10 empty] | Typical Over-Charge | +8 |  | 1.0049 |  | 1.0302 |  | 1.0332
[10 empty] | For interpolation | +5 |  | 0.99044 |  | 1.017 |  | 1.0022
[10 empty] | Standard | 0 | 1 | 1 | 1 | 1 | 1 | 1
[10 empty] | Low Under-Charge | -4 |  | 0.93989 |  | 1.0339 |  | 0.91302
[10 empty] | For interpolation | -5 |  | 0.92486 |  | 1.0424 |  | 0.89128
[10 empty] | Typical Under-Charge | -8 |  | 0.865 |  | 1.0947 |  | 0.80465
[10 empty] | 10% Under-Charge | -10 | 0.88677 | 0.82509 | 1.11 | 1.1469 | 0.91168 | 0.74689
[10 empty] | High Under-Charge | -16 |  | 0.73175 |  | 1.2649 |  | 0.64643
[10 empty] | For interpolation | -20 |  | 0.66952 |  | 1.3435 |  | 0.57946
[10 empty] | Old High Under-Charge | -30 | 0.84 |  | 1.16 |  | 0.91
[6 empty] | Cap | EIR | SCap
[6 empty] | 0.732 | 1.265 | 0.646 |  | RefgChg-Res-16pct-Inc-TXV
[6 empty] | 0.865 | 1.095 | 0.805 |  | RefgChg-Res-8pct-Inc-TXV
[6 empty] | 0.94 | 1.034 | 0.913 |  | RefgChg-Res-4pct-Inc-TXV
[6 empty] | 1.005 | 1.03 | 1.033 |  | RefgChg-Res-8pct-Dec-TXV
Note on M5: This column lists a weighting factor determined from field data itemizing TXV and non-TXV units for overcharged and undercharged systems.
Note on N1: This factor accounts for the assumption that 15% of the fan power becomes heat in the duct due to friction, and is not included in the test measurements for capacity.

## 2012_LabTestData_TXV
[11 empty] | Fan heat factor: | 0.85
Data from: Draft Evaluation Report: Lab Tests of a Residential 3-Ton Split System Air Conditioner under Typical Installed Conditions, CPUC, 2012
Charge | Charge |  |  |  | net cap | sens cap | fan | tot | fan |  |  | gross capacity |  | EIR |  | gross sensible cap
oz | Pct | Src table | RunID | EER | kBtuh | kBtuh | kW | kW | cfm |  | wt | kBtuh | Cap Mult | EIR | eir Mult | kBtuh | Cap Mult
| Non-TXV, Rating Condition B | [16 empty] | dChg
140.6 | +30 | Table 11 | 182 C | 9.64 | 31.49 | 23.98 | 0.558 | 3.27 | 1190 |  | 0% | 33.1088 | 0.99237 | 0.27956 | 1.1354 | 25.5988 | 1.0727 | -30%
129.8 | +10 | Table 11 | 180 B | 10.35 | 32.43 | 24.34 | 0.548 | 3.13 | 1190 |  | 0% | 34.0198 | 1.0197 | 0.25904 | 1.052 | 25.9298 | 1.0866 | -10%
113.6 | +5 | Table 11 | 179B | 10.5 | 32.54 | 24.11 | 0.553 | 3.1 | 1190 |  | 0% | 34.1443 | 1.0234 | 0.25459 | 1.034 | 25.7143 | 1.0776 | -5%
108.2 | 0 | Table 11 | 178-2 | 10.68 | 31.73 | 22.23 | 0.563 | 2.97 | 1200 |  |  | 33.3633 | 1 | 0.24623 | 1 | 23.8633 | 1 | 0%
102.8 | -5 | Table 11 | 184-2 | 10.22 | 29.68 | 20.09 | 0.565 | 2.91 | 1200 |  | 0% | 31.3191 | 0.93873 | 0.25555 | 1.0378 | 21.7291 | 0.91057 | 5%
97.4 | -10 | Table 11 | 185-2 | 9.85 | 28.07 | 17.92 | 0.568 | 2.85 | 1200 |  | 0% | 29.7178 | 0.89073 | 0.26208 | 1.0644 | 19.5678 | 0.82 | 10%
86.6 | -20 | Table 11 | 186-2 | 7.63 | 20.74 | 12.04 | 0.563 | 2.72 | 1190 |  | 0% | 22.3733 | 0.6706 | 0.32905 | 1.3363 | 13.6733 | 0.57298 | 20%
Non-TXV, Rating Condition A
132.6 | +30 | Table 10 | 62 | 8.91 | 30.77 | 23.4 | 0.561 | 3.45 | 1180 |  | 0% | 32.3975 | 0.9846 | 0.30435 | 1.0681 | 25.0275 | 1.011 | -30%
112.2 | +10 | Table 10 | 60a | 9.29 | 31.6 | 23.67 | 0.555 | 3.4 | 1170 |  | 0% | 33.2101 | 1.0093 | 0.29238 | 1.0261 | 25.2801 | 1.0212 | -10%
113.6 | +5 | Table 10 | 59a | 9.36 | 29.88 | 21.32 | 0.56 | 3.19 | 1180 |  | 0% | 31.5046 | 0.95746 | 0.28492 | 0.99994 | 22.9446 | 0.92689 | -5%
102 | 0 | Table 10 | 53 | 9.49 | 31.3 | 23.15 | 0.553 | 3.3 | 1170 |  |  | 32.9043 | 1 | 0.28493 | 1 | 24.7543 | 1 | 0%
96.9 | -5 | Table 10 | 54 | 8.94 | 28.38 | 19.99 | 0.55 | 3.17 | 1165 |  | 0% | 29.9756 | 0.91099 | 0.29831 | 1.047 | 21.5856 | 0.87199 | 5%
91.8 | -10 | Table 10 | 55 | 7.47 | 23.35 | 15.04 | 0.565 | 3.13 | 1170 |  | 0% | 24.9891 | 0.75945 | 0.35033 | 1.2295 | 16.6791 | 0.67379 | 10%
81.6 | -20 | Table 10 | 56a | 6.7 | 20.37 | 12.88 | 0.56 | 3.04 | 1180 |  | 0% | 21.9946 | 0.66844 | 0.38483 | 1.3506 | 14.5046 | 0.58594 | 20%
TXV, Rating Condition A
132.6 | +30 | Table 9 | 40 | 8.12 | 31.321 | 23.36 | 0.56 | 3.86 | 1150 |  | 100% | 32.9456 | 0.99683 | 0.34186 | 1.2202 | 24.9846 | 0.99341 | -30%
112.2 | +10 | Table 9 | 36 | 9.24 | 31.8 | 23.16 | 0.563 | 3.44 | 1150 |  | 100% | 33.4333 | 1.0116 | 0.2937 | 1.0483 | 24.7933 | 0.9858 | -10%
107.2 | +5 | Table 9 | 33 | 9.42 | 30.52 | 22.95 | 0.562 | 3.24 | 1140 |  | 100% | 32.1504 | 0.97277 | 0.28429 | 1.0147 | 24.5804 | 0.97734 | -5%
102 | 0 | Table 9 | 23 | 9.6 | 31.42 | 23.52 | 0.562 | 3.275 | 1160 |  |  | 33.0504 | 1 | 0.28016 | 1 | 25.1504 | 1 | 0%
96.9 | -5 | Table 9 | 44 | 9.46 | 30.32 | 22.02 | 0.558 | 3.21 | 1140 |  | 100% | 31.9388 | 0.96637 | 0.28339 | 1.0115 | 23.6388 | 0.9399 | 5%
91.8 | -10 | Table 9 | 45 | 9.22 | 29.2 | 20.5 | 0.556 | 3.17 | 1140 |  | 100% | 30.813 | 0.9323 | 0.28954 | 1.0335 | 22.113 | 0.87923 | 10%
81.6 | -20 | Table 9 | 48 | 8.28 | 25.83 | 16.76 | 0.561 | 3.12 | 1170 |  | 100% | 27.4575 | 0.83078 | 0.31809 | 1.1354 | 18.3875 | 0.7311 | 20%
71.4 | -30 | Table 9 | 49 | 6.98 | 21.7 | 13.03 | 0.557 | 3.03 | 1170 |  | 100% | 23.3159 | 0.70546 | 0.362 | 1.2921 | 14.6459 | 0.58233
Changes in Adjustment Factors for Refrigerant Charge Measures
[12 empty] | Cap Mult |  | EIR Mult |  | Sens Cap Mult
[12 empty] | prev | 2018 | prev | 2018 | prev | 2018
[10 empty] | High Over-Charge | +30 | 0.82553 | 0.99683 | 1.35 | 1.2202 | 0.88858 | 0.99341
[10 empty] | 10% Over-Charge | +10 | 0.89428 | 1.0116 | 1.16 | 1.0483 | 0.94748 | 0.9858
[10 empty] | Typical Over-Charge | +8 |  | 0.99606 |  | 1.0349 |  | 0.98242
[10 empty] | For interpolation | +5 |  | 0.97277 |  | 1.0147 |  | 0.97734
[10 empty] | Standard | 0 | 1 | 1 | 1 | 1 | 1 | 1
[10 empty] | Low Under-Charge | -4 |  | 0.97309 |  | 1.0092 |  | 0.95192
[10 empty] | For interpolation | -5 |  | 0.96637 |  | 1.0115 |  | 0.9399
[10 empty] | Typical Under-Charge | -8 |  | 0.94593 |  | 1.0225 |  | 0.9035
[10 empty] | 10% Under-Charge | -10 | 0.88677 | 0.9323 | 1.11 | 1.0335 | 0.91168 | 0.87923
[10 empty] | High Under-Charge | -16 |  | 0.87139 |  | 1.0946 |  | 0.79035
[10 empty] | For interpolation | -20 |  | 0.83078 |  | 1.1354 |  | 0.7311
[10 empty] | Old High Under-Charge | -30 | 0.84 |  | 1.16 |  | 0.91
[6 empty] | Cap | EIR | SCap
[6 empty] | 0.871 | 1.095 | 0.79 |  | RefgChg-Res-16pct-Inc-TXV
[6 empty] | 0.946 | 1.023 | 0.903 |  | RefgChg-Res-8pct-Inc-TXV
[6 empty] | 0.973 | 1.009 | 0.952 |  | RefgChg-Res-4pct-Inc-TXV
[6 empty] | 0.996 | 1.035 | 0.982 |  | RefgChg-Res-8pct-Dec-TXV
Note on M5: This column lists a weighting factor determined from field data itemizing TXV and non-TXV units for overcharged and undercharged systems.
Note on N1: This factor accounts for the assumption that 15% of the fan power becomes heat in the duct due to friction, and is not included in the test measurements for capacity.