## RefgChgCalcs
Adjustment factors for refrigerant charge measures
|  | Valve | Charge | Cap Mult |  | EIR Mult |  | Sens Cap Mult |  | Coil Bypass Mult
| Measure Condition | Type | Adjust | prev | 2018 | prev | 2018 | prev | 2018 | prev | 2018 | Measure ID | Description
Decrease | Typical Over-Charge | Non-TXV | 7.5% | 0.902 | 1.013 | 1.153 | 1.003 | 0.951 | 1.0151 | 1 | 0.9467 | NE-HVAC-RefChrg-Dec-Typ-ntxv | Decrease Refrigerant Charge - Typical (any adjustment >= 4%, typical value of 7.5%)
Decrease | Typical Over-Charge | TXV | 7% | 0.902 | 0.9995 | 1.153 | 1.0083 | 0.951 | 1.0112 | 1 | 0.9665 | NE-HVAC-RefChrg-Dec-Typ-txv | Decrease Refrigerant Charge - Typical (any adjustment >= 4%, typical value of 7%)
Increase | Typical Under-Charge | Non-TXV | 10% | 0.884 | 0.9255 | 1.117 | 1.0499 | 0.912 | 0.9413 | 1 | 1.1301 | NE-HVAC-RefChrg-Inc-Typ-ntxv | Increase Refrigerant Charge - Typical (any adjustment >= 4%, typical value of 10%)
Increase | Typical Under-Charge | TXV | 8.5% | 0.884 | 0.9734 | 1.117 | 1.0045 | 0.912 | 0.9843 | 1 | 1.011 | NE-HVAC-RefChrg-Inc-Typ-txv | Increase Refrigerant Charge - Typical (any adjustment >= 4%, typical value of 8.5%)
Increase | Low Under-Charge | Non-TXV | 4.5% | 0.902 | 0.967 | 1.153 | 1.019 | 0.951 | 0.9746 | 1 | 1.052 | NE-HVAC-RefChrg-Inc-Low-ntxv | Increase Refrigerant Charge - Typical (adjustment < 5% and >= 4%, typical value of 4.5%)
Increase | Low Under-Charge | TXV | 4.5% | 0.902 | 0.9883 | 1.153 | 0.9984 | 0.951 | 0.9942 | 1 | 0.9944 | NE-HVAC-RefChrg-Inc-Low-txv | Increase Refrigerant Charge - Typical (adjustment < 5% and >= 4%, typical value of 4.5%)
Increase | High Under-Charge | Non-TXV | 16% | 0.884 | 0.8785 | 1.117 | 1.0932 | 0.912 | 0.9022 | 1 | 1.2333 | NE-HVAC-RefChrg-Inc-High-ntxv | Increase Refrigerant Charge - Typical (any adjustment >= 10%, typical value of 16%)
Increase | High Under-Charge | TXV | 17% | 0.884 | 0.9274 | 1.117 | 1.0412 | 0.912 | 0.948 | 1 | 1.114 | NE-HVAC-RefChrg-Inc-High-txv | Increase Refrigerant Charge - Typical (any adjustment >= 10%, typical value of 17%)
| Low Under-Charge | TXV | 4% | NA | 0.99 | NA | 0.998 | NA | 0.995 | NA | 0.994
| Low Under-Charge | Non-TXV | 4% | NA | 0.971 | NA | 1.017 | NA | 0.977 | NA | 1.046
| High Under-Charge | TXV | 16% | 0.839 | 0.934 | 1.156 | 1.035 | 0.907 | 0.953 | 0.907 | 1.097
| High Under-Charge | Non-TXV | 16% | 0.839 | 0.879 | 1.156 | 1.093 | 0.907 | 0.902 | 0.907 | 1.233
Curve fits from refrigerant charge lab test data
| Fault Type | Valve Type |  | Total Capacity |  | EIR |  | Sensible Capacity |  | Coil By-Pass
| Over-Charge | Non-TXV |  | C2 | 0 | C2 | 0 | C2 | 0 | C2 | 0
|  |  |  | C1 | 0.17397 | C1 | 0.040605 | C1 | 0.20198 | C1 | -0.71086
|  |  |  | C0 | 1 | C0 | 1 | C0 | 1 | C0 | 1
| Over-Charge | TXV |  | C2 | 0 | C2 | 0 | C2 | -0.44105 | C2 | 0.99412
|  |  |  | C1 | -0.0075946 | C1 | 0.11804 | C1 | 0.19133 | C1 | -0.54746
|  |  |  | C0 | 1 | C0 | 1 | C0 | 1 | C0 | 1
| Under-Charge | Non-TXV |  | C2 | -0.23227 | C2 | 1.3986 | C2 | -0.40115 | C2 | 2.6279
|  |  |  | C1 | 0.72215 | C1 | -0.35887 | C1 | 0.54691 | C1 | -1.0379
|  |  |  | C0 | 1 | C0 | 1 | C0 | 1 | C0 | 1
| Under-Charge | TXV |  | C2 | -1.3419 | C2 | 2.2185 | C2 | -1.4205 | C2 | 6.3626
|  |  |  | C1 | 0.19873 | C1 | 0.13508 | C1 | 0.064268 | C1 | 0.41119
|  |  |  | C0 | 1 | C0 | 1 | C0 | 1 | C0 | 1